## Cover Page
AER Rule | Field Name | Value(s)
1 | Constrained connection point ID | H031 Molendinar
2 | Constraint primary driver | Asset condition
3 | Constraint investment type | Asset renewal
4 | Constrained connection point latitude (decimal degrees) | -27.9783
| Constrained connection point longitude (decimal degrees) | 153.3614
5 | Effect on residential customers
| Annual Energy | Not available
| Maximum Demand | Not available
6, 7 | Effect on industrial and commercial customers
| Annual Energy | Not available
| Maximum Demand | Not available
8 | Load profile (maximum day, MVA)
50% PoE
Load profile (minimum day, MVA)
Minimum demand data (MVA)
| Max. demand, maximum demand day (MVA) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| 10% PoE | 456.6 | 453.6 | 451.4 | 447.4 | 445.5 | 446.1 | 443.7 | 444.7 | 445.2 | 444.6 | 474.5
| 50% PoE | 447.6 | 444.8 | 442.3 | 440.2 | 439.2 | 438.9 | 439.9 | 438.9 | 439.2 | 439 | 438.9
9 | Max. demand, minimum demand day (MW) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Maximum demand data | 249.5 | 269.1 | 268.5 | 268.5 | 268.6 | 268.4 | 267.9 | 267.3 | 267.3 | 266.9 | 265.9
10 | Load profile (maximum day, MW)
Load profile 50%
| Max. demand, maximum demand day (MW) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| 10% PoE | 456.4 | 453.3 | 451 | 447.1 | 445.4 | 445.7 | 443.3 | 444.6 | 444.9 | 444.2 | 474.1
| 50% PoE | 447.3 | 444.4 | 441.9 | 439.8 | 438.8 | 438.4 | 439.5 | 438.5 | 438.8 | 438.6 | 438.4
11 | Load profile (minimum day, MW)
Minimum demand data (MW)
| Min. demand, minimum demand day (MW) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Mininum demand data | 99.9 | 99.8 | 99.9 | 102 | 102 | 102.4 | 102.4 | 102.9 | 102.4 | 102.5 | 102.6
12 | Voltage level (kV) | 275
13 | Maximum load at risk per year | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Load at risk (MW, peak) | 0 | 0 | 0 | 0 | 303.9393 | 304.1567 | 304.5409 | 304.7272 | 305.2914 | 305.451 | 305.66
| Load at risk (MVA, peak) | 0 | 0 | 0 | 0 | 337.7104 | 337.9519 | 338.3787 | 338.5857 | 339.2127 | 339.39 | 339.6223
14 | Load duration curve
15 | Preferred investment | Molendinar 275kV secondary systems replacement
16 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Capital cost ($m, nominal) | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0
17 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Operating cost ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
18 | Preferred investment cost accuracy | 0.3
19 | Preferred investment proposed timing | 2024-06-30
20 | Demand reduction to defer the investment by 1 year | 0
21 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Annual deferral value ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Load transfer capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Historic load trace
24 | Historic ratings
25 | Limitation asset | Transformers
26 | Unplanned outages
27 | Maximum fault level (kA) | 8.1
28 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Economic cost ($m) | 0 | 0 | 0 | 0 | 3.5088 | 3.5809 | 3.6224 | 3.6217 | 3.7534 | 3.9194 | 3.9989
29 | VCR ($m/MWh) | 0.03971
30 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Annual unserved energy (MWh) | 0 | 0 | 0 | 0 | 88.3608 | 90.1765 | 91.2215 | 91.2033 | 94.5215 | 98.7018 | 100.7014

## 8. Load profile max (50% PoE)
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:00 | 234 | 232.8 | 229.9 | 230 | 232.8 | 233.1 | 233 | 234.1 | 234.8 | 235.1 | 235.4
0:30 | 220.9 | 218.8 | 218.8 | 218.8 | 218.8 | 220.9 | 221.1 | 221.2 | 221.2 | 221.1 | 221
1:00 | 217.1 | 215.1 | 215 | 214.9 | 215 | 217.1 | 217.3 | 217.4 | 217.4 | 217.3 | 217.2
1:30 | 213 | 210.9 | 208.8 | 210.9 | 210.9 | 211 | 211 | 213.2 | 213.1 | 213.1 | 213.2
2:00 | 205.5 | 203.3 | 203.3 | 203.2 | 203.2 | 204.7 | 205.7 | 205.6 | 205.6 | 205.5 | 205.5
2:30 | 198.2 | 198.2 | 198.2 | 198.1 | 198.1 | 198.9 | 198.8 | 199.2 | 200.1 | 201 | 201.9
3:00 | 195 | 194.6 | 194.8 | 194.8 | 194.5 | 194.7 | 194.7 | 195.2 | 195 | 195 | 195.1
3:30 | 192.8 | 193.3 | 193.3 | 193.3 | 193.3 | 193.5 | 193.5 | 193 | 193 | 193 | 193
4:00 | 189.1 | 189.4 | 189.4 | 189.4 | 189.4 | 194.1 | 189.6 | 189.2 | 189.2 | 189.2 | 189.2
4:30 | 188.5 | 188.9 | 188.8 | 188.8 | 188.8 | 189.1 | 189.1 | 188.7 | 188.7 | 188.7 | 188.7
5:00 | 191 | 191.4 | 191.4 | 191.4 | 191.4 | 191.6 | 191.6 | 191.2 | 191.2 | 191.2 | 191.2
5:30 | 200.5 | 201 | 201 | 200.9 | 200.9 | 201.2 | 201.2 | 200.8 | 200.8 | 200.7 | 200.7
6:00 | 213.6 | 213.1 | 213.1 | 213.1 | 213.1 | 213.3 | 213.3 | 213.9 | 214 | 214.1 | 214.2
6:30 | 235.5 | 232.7 | 232.8 | 232.7 | 232.7 | 233.7 | 233.5 | 233.1 | 233.2 | 235.2 | 237.2
7:00 | 253.3 | 253 | 250.5 | 251.4 | 251.1 | 252 | 251.9 | 253.7 | 253.4 | 253 | 252.7
7:30 | 283.4 | 282.6 | 282 | 281.3 | 280.7 | 282.7 | 281.9 | 283.4 | 283.1 | 284.5 | 285.9
8:00 | 307.2 | 305.7 | 304.6 | 303.6 | 305 | 304.4 | 305.7 | 306.6 | 308 | 307 | 306.1
8:30 | 313.3 | 310 | 307.6 | 318 | 340.4 | 339 | 336.3 | 333.1 | 329.7 | 327.8 | 325.8
9:00 | 323.7 | 327.6 | 338.1 | 345.5 | 342.7 | 340.6 | 337.3 | 333.1 | 329.4 | 325.2 | 321
9:30 | 328.6 | 326.3 | 323.8 | 356 | 352 | 349.4 | 345 | 340.1 | 335.8 | 331.2 | 326.6
10:00 | 333.7 | 330.6 | 329.5 | 346.2 | 359.3 | 356 | 351 | 345.1 | 339.6 | 334.8 | 330.1
10:30 | 340.3 | 336.4 | 334.2 | 334.5 | 368.3 | 364.5 | 359.1 | 352.2 | 345.9 | 340.5 | 335.3
11:00 | 344.8 | 342.8 | 340.3 | 339.7 | 344.7 | 371 | 364.8 | 357.9 | 350.6 | 344.9 | 339.2
11:30 | 352.5 | 346.8 | 344.1 | 343.3 | 342.4 | 343 | 370.2 | 363.1 | 355.8 | 349 | 342.3
12:00 | 359.1 | 356.7 | 353.5 | 351.4 | 350.6 | 350.1 | 374.7 | 366.7 | 359.3 | 351.8 | 344.5
12:30 | 364.3 | 359.5 | 355 | 353.3 | 352.4 | 352.1 | 352.5 | 370.7 | 363 | 355.8 | 348.7
13:00 | 369.4 | 365.7 | 365 | 363.3 | 362.2 | 361.3 | 359.3 | 379.2 | 371.5 | 364.5 | 357.6
13:30 | 378 | 374.2 | 373.1 | 373.1 | 371.8 | 369.8 | 370.4 | 387.2 | 380 | 373.1 | 366.3
14:00 | 387 | 382.4 | 379.2 | 378.9 | 379.4 | 379 | 377.7 | 397.4 | 390.6 | 384 | 377.4
14:30 | 394.9 | 390.3 | 387.8 | 386.9 | 386.8 | 385.3 | 385.1 | 388.6 | 406.8 | 400.7 | 394.7
15:00 | 406.6 | 398.8 | 396.4 | 395.9 | 393.2 | 393.9 | 391.4 | 392.5 | 418 | 411.6 | 405.3
15:30 | 414.7 | 409.6 | 408.3 | 407.1 | 402.7 | 401.7 | 401.9 | 400.7 | 400.4 | 417.2 | 434.7
16:00 | 436.6 | 432.5 | 429.3 | 429.9 | 428.1 | 428.3 | 427.2 | 427.5 | 426.3 | 427.3 | 428.4
16:30 | 447.6 | 444.8 | 442.3 | 440.2 | 439.2 | 438.9 | 439.9 | 438.9 | 439.2 | 439 | 438.9
17:00 | 445.5 | 442.3 | 440.5 | 439.2 | 438.5 | 437.2 | 435.7 | 435.7 | 436.9 | 435.4 | 434
17:30 | 439 | 435.8 | 434.7 | 434.7 | 432 | 432 | 430.3 | 431.4 | 431.9 | 432.4 | 432.9
18:00 | 420.8 | 420.5 | 420.4 | 418.8 | 416.8 | 417.6 | 417.7 | 417.8 | 418.9 | 418.9 | 418.9
18:30 | 412.2 | 410.8 | 411.3 | 410.7 | 410.2 | 410.8 | 412.1 | 413 | 414.5 | 415.7 | 416.8
19:00 | 406.7 | 405.8 | 405.9 | 405.1 | 404.5 | 404.9 | 405.9 | 406.5 | 408.3 | 408.6 | 408.8
19:30 | 400.6 | 399.7 | 400 | 399 | 398.5 | 399.3 | 400.2 | 400.6 | 401.9 | 402.3 | 402.7
20:00 | 386.2 | 385.5 | 385.3 | 384.6 | 384.1 | 384.9 | 385.2 | 385.5 | 386.6 | 386.7 | 386.9
20:30 | 378.3 | 379 | 379 | 377.9 | 377.4 | 376.5 | 378.8 | 379 | 380 | 380.3 | 380.7
21:00 | 363.2 | 363 | 363 | 362.1 | 361.7 | 362 | 362.8 | 362.7 | 363.6 | 364.2 | 364.7
21:30 | 337.3 | 337.3 | 336.5 | 335.8 | 336.3 | 337.3 | 337.8 | 337.2 | 337.6 | 338.1 | 338.5
22:00 | 317.6 | 317.1 | 317 | 335.8 | 317.1 | 317.3 | 318 | 317.8 | 318 | 318.3 | 318.5
22:30 | 285.4 | 284.8 | 284.7 | 285.2 | 285.2 | 285 | 284.9 | 285 | 285 | 284.8 | 284.6
23:00 | 273.6 | 273.6 | 273.5 | 273.4 | 273.4 | 273.7 | 273.7 | 273.8 | 273.8 | 273.6 | 273.3
23:30 | 254.3 | 252.7 | 252.7 | 252.6 | 252.6 | 252.9 | 254.5 | 254.6 | 254.6 | 254.4 | 254.1

## 8. Load profile min
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:00 | 190 | 190.2 | 190.2 | 190.1 | 191.9 | 191.8 | 191 | 191 | 190.3 | 190.9 | 190.9
0:30 | 178 | 178.2 | 180.2 | 178.2 | 180.3 | 176.2 | 179.6 | 179.6 | 177.8 | 180 | 180.3
1:00 | 171.8 | 171 | 172.8 | 172 | 172.7 | 172.5 | 173.9 | 174.4 | 174.3 | 175.2 | 176.4
1:30 | 167.2 | 168.5 | 168.3 | 167 | 167.7 | 169.5 | 171.4 | 168.1 | 168.4 | 170.2 | 169
2:00 | 161.1 | 163.6 | 161.8 | 161.2 | 161.2 | 165.1 | 165.9 | 166.2 | 165.3 | 165.7 | 165.5
2:30 | 159.2 | 158.8 | 159.4 | 159 | 158.4 | 162.1 | 161.7 | 161.6 | 163.8 | 163.2 | 164.7
3:00 | 157.7 | 157.7 | 158.6 | 157.7 | 157.7 | 161.7 | 162.4 | 162.2 | 162.5 | 162.8 | 163.2
3:30 | 153 | 155.7 | 154 | 154.4 | 155.8 | 156.7 | 156.4 | 158.5 | 158.6 | 158.5 | 160.6
4:00 | 152.5 | 155 | 154.2 | 155 | 155.1 | 158.7 | 157.1 | 156.5 | 157.1 | 157.7 | 158.3
4:30 | 135.4 | 137.1 | 137.2 | 142.1 | 139.1 | 138.4 | 137.5 | 133.1 | 139.7 | 139.5 | 141.4
5:00 | 155.1 | 155.8 | 155.8 | 156.8 | 157.2 | 167.7 | 157 | 158.3 | 156.2 | 156.8 | 156.6
5:30 | 162.7 | 163.8 | 162.9 | 162.9 | 164.6 | 167.5 | 167.6 | 168.1 | 168.6 | 164.4 | 161.3
6:00 | 171.7 | 172.5 | 172.8 | 172.6 | 170.7 | 172.2 | 173.3 | 174.1 | 173.8 | 174 | 174.7
6:30 | 177.6 | 179.4 | 179.9 | 177.7 | 177.8 | 177 | 181.3 | 179.6 | 181.6 | 181.7 | 182.1
7:00 | 183.2 | 185.6 | 185.7 | 185.9 | 187.8 | 183.9 | 183.5 | 179 | 185.8 | 185.9 | 188.4
7:30 | 196.3 | 198.5 | 198.5 | 198.4 | 198.4 | 198.6 | 200.4 | 197.6 | 200.5 | 200.6 | 200.8
8:00 | 215.8 | 219.6 | 219.4 | 219 | 218.7 | 218.7 | 220.5 | 220.2 | 220 | 221 | 221.5
8:30 | 229.3 | 231.9 | 231.2 | 239.9 | 251.3 | 253.8 | 253.3 | 252.6 | 251.7 | 251.2 | 249.1
9:00 | 235.9 | 255.3 | 254.1 | 253.1 | 251.8 | 251.1 | 250 | 248.5 | 246.9 | 245.8 | 241.6
9:30 | 259.3 | 257.2 | 255.6 | 254 | 252.3 | 251.5 | 249.6 | 247.6 | 245.5 | 243.6 | 237.8
10:00 | 264.2 | 261.9 | 260.2 | 258.5 | 259.8 | 258.5 | 256.7 | 254.5 | 252.3 | 250.5 | 244.5
10:30 | 259.5 | 256.7 | 254.8 | 252.9 | 251 | 249.5 | 247.2 | 244.5 | 241.9 | 238.7 | 230.5
11:00 | 251.1 | 247.8 | 245.6 | 243.5 | 241 | 239.5 | 236.7 | 230.2 | 227.1 | 224.6 | 213.1
11:30 | 254.3 | 250.9 | 248.5 | 246.2 | 244 | 242 | 239.3 | 236 | 229.4 | 226.5 | 214.4
12:00 | 258.7 | 258.7 | 256.7 | 254.5 | 252.6 | 251 | 248.4 | 245.6 | 242.9 | 239.7 | 231.2
12:30 | 256.1 | 256.6 | 254.7 | 252.7 | 250.9 | 249.5 | 247 | 244.5 | 241.8 | 238.8 | 230.9
13:00 | 258.2 | 255.3 | 256.3 | 254.4 | 252.7 | 251.5 | 249.2 | 246.4 | 244.1 | 241.8 | 234.6
13:30 | 243.8 | 260.8 | 262.1 | 257.6 | 256.2 | 258 | 256.1 | 253.9 | 251.8 | 249.9 | 243.9
14:00 | 242.9 | 258.6 | 264.1 | 262.8 | 261.7 | 262.6 | 264.6 | 262.9 | 261.3 | 259.8 | 255
14:30 | 249.2 | 275.4 | 274.8 | 274 | 273.3 | 272.8 | 271.9 | 270.8 | 269.7 | 268.7 | 265.5
15:00 | 249.9 | 277 | 276.6 | 276 | 275.5 | 275.4 | 274.7 | 274 | 273.4 | 272.9 | 271
15:30 | 247.9 | 251.7 | 257.4 | 266.6 | 276.7 | 276.7 | 276.1 | 275.6 | 275 | 274.6 | 273.2
16:00 | 249.4 | 246 | 254.1 | 258.7 | 264.6 | 263.7 | 264.6 | 264.3 | 264.1 | 264 | 263.4
16:30 | 250.9 | 250.5 | 250.7 | 250.7 | 250.5 | 250.8 | 253 | 253 | 253.2 | 253.4 | 253.7
17:00 | 253.2 | 253.1 | 253.1 | 253 | 253.5 | 253.7 | 253.7 | 253.7 | 253.8 | 254 | 254.3
17:30 | 256.3 | 256.2 | 256.2 | 256.1 | 258.3 | 258.5 | 258.5 | 258.5 | 258.7 | 258.8 | 259.2
18:00 | 252.3 | 253.1 | 254.5 | 253 | 252.9 | 254.6 | 256.6 | 256.9 | 256.1 | 255 | 253.5
18:30 | 249.2 | 253.5 | 253.5 | 253.5 | 253.4 | 253.6 | 253.6 | 253.6 | 253.8 | 253.9 | 254.3
19:00 | 245.7 | 247.9 | 247.8 | 247.8 | 248.3 | 248.5 | 248.4 | 250.1 | 250.2 | 250.2 | 252
19:30 | 238.9 | 242.8 | 242.8 | 241.1 | 241 | 241.3 | 243.5 | 243.4 | 243.4 | 243.5 | 243.5
20:00 | 238.8 | 241 | 237.6 | 239.3 | 243.1 | 243.2 | 239.8 | 239.8 | 239.8 | 239.8 | 239.8
20:30 | 234.2 | 238.6 | 238.5 | 238.5 | 238.4 | 238.6 | 240.7 | 240.7 | 240.6 | 240.6 | 240.5
21:00 | 227.7 | 231.7 | 231.7 | 231.8 | 233.9 | 234.3 | 237 | 234 | 234 | 234 | 231
21:30 | 227.1 | 231.1 | 231.1 | 231 | 233.2 | 231.1 | 230.9 | 230.9 | 230.9 | 230.9 | 230.9
22:00 | 222.7 | 226.6 | 226.6 | 226.6 | 226.6 | 226.9 | 228.8 | 228.8 | 228.8 | 228.8 | 228.8
22:30 | 217.2 | 219.2 | 219.2 | 219.2 | 219.2 | 219.3 | 219.3 | 220 | 220.7 | 220.3 | 221.2
23:00 | 212.9 | 212.8 | 212.9 | 212.8 | 212.8 | 213 | 215.1 | 215.1 | 214.9 | 214.9 | 214.7
23:30 | 204.7 | 204.6 | 204.7 | 212.8 | 204.6 | 204.8 | 204.6 | 204.6 | 204.6 | 204.5 | 204.4

## 10. Load profile (50% PoE)
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:00 | 226.4 | 225.5 | 222.7 | 222.4 | 225.5 | 225.4 | 225.9 | 227 | 227.2 | 227.8 | 228.5
0:30 | 212 | 209.8 | 209.8 | 209.8 | 209.8 | 211.9 | 212.3 | 212.2 | 212.2 | 212.1 | 212
1:00 | 207.3 | 205 | 205.1 | 205 | 205 | 207.2 | 207.5 | 207.3 | 207.3 | 207.2 | 207.1
1:30 | 202.1 | 199.9 | 197.8 | 199.9 | 199.9 | 200 | 199.9 | 202.1 | 202.2 | 202.1 | 202
2:00 | 193.6 | 191.4 | 191.3 | 191.3 | 191.3 | 192.7 | 193.7 | 193.6 | 193.6 | 193.5 | 193.5
2:30 | 185.8 | 185.8 | 185.9 | 185.8 | 185.8 | 186.5 | 186.4 | 186.7 | 187.7 | 188.6 | 189.5
3:00 | 182.1 | 181.7 | 182 | 182 | 181.6 | 181.8 | 181.7 | 182.2 | 182.2 | 182.2 | 182.1
3:30 | 179.8 | 180.2 | 180.2 | 180.2 | 180.2 | 180.4 | 180.3 | 179.9 | 179.9 | 179.9 | 179.9
4:00 | 175.7 | 176.1 | 176 | 176 | 176.1 | 175.6 | 176.3 | 175.9 | 175.8 | 175.8 | 175.8
4:30 | 175.2 | 175.6 | 175.6 | 175.6 | 175.7 | 175.9 | 175.8 | 175.3 | 175.3 | 175.3 | 175.3
5:00 | 178.1 | 178.5 | 178.5 | 178.5 | 178.5 | 178.8 | 178.7 | 178.3 | 178.3 | 178.3 | 178.4
5:30 | 188.8 | 189.1 | 189.1 | 189.1 | 189.1 | 189.3 | 189.4 | 188.9 | 188.9 | 189 | 189
6:00 | 202.4 | 201.9 | 202 | 202 | 202 | 202.2 | 202.2 | 202.8 | 202.9 | 203 | 203.1
6:30 | 227.1 | 224.3 | 224.3 | 224.3 | 224.3 | 224.8 | 225.2 | 224.6 | 224.8 | 226.9 | 229
7:00 | 246.9 | 246.6 | 244 | 246.5 | 246.2 | 245.3 | 245.3 | 247.8 | 247.5 | 247 | 246.5
7:30 | 282 | 281.2 | 280.6 | 279.9 | 279.3 | 281.3 | 280.5 | 281.9 | 281.7 | 283 | 284.4
8:00 | 306 | 304.4 | 303.3 | 302.3 | 303.6 | 303 | 304.3 | 305.5 | 306.5 | 305.5 | 304.5
8:30 | 312.4 | 309.1 | 306.6 | 317 | 339.6 | 338.2 | 335.4 | 332.1 | 328.8 | 327 | 325.2
9:00 | 323.1 | 326.9 | 337.4 | 344.8 | 341.9 | 339.8 | 336.4 | 332.1 | 328.7 | 324.1 | 319.5
9:30 | 327.9 | 325.7 | 323.3 | 355.7 | 351.4 | 348.9 | 344.3 | 339.3 | 335.1 | 330.3 | 325.6
10:00 | 333.2 | 330 | 329.1 | 345.9 | 359.1 | 355.6 | 350.5 | 344.5 | 338.8 | 334.1 | 329.6
10:30 | 339.9 | 335.9 | 333.6 | 334.2 | 368.1 | 364.4 | 358.9 | 351.7 | 345.3 | 340 | 334.9
11:00 | 344.5 | 342.4 | 339.8 | 339.2 | 344.3 | 370.8 | 364.6 | 357.7 | 350.1 | 344.5 | 338.9
11:30 | 351.8 | 346.5 | 343.7 | 342.8 | 342 | 342.8 | 370 | 362.9 | 355.6 | 348.6 | 341.9
12:00 | 358.5 | 356 | 352.7 | 351 | 350.2 | 349.8 | 374.5 | 366.5 | 359.1 | 351.4 | 343.9
12:30 | 363.8 | 358.9 | 354.8 | 353.2 | 352.2 | 352 | 352.3 | 370.3 | 362.6 | 355.3 | 348.2
13:00 | 368.9 | 365.2 | 364.5 | 362.8 | 361.7 | 361.2 | 359 | 378.5 | 371.1 | 364.1 | 357.1
13:30 | 377.6 | 373.7 | 372.5 | 372.6 | 371.4 | 369.4 | 369.9 | 386.7 | 379.4 | 372.5 | 365.6
14:00 | 386.6 | 382 | 378.7 | 378.4 | 378.9 | 378.5 | 377.2 | 397 | 390.1 | 383.4 | 376.8
14:30 | 394.4 | 389.9 | 387.4 | 386.5 | 386.4 | 384.9 | 384.6 | 388.1 | 406.4 | 400.3 | 394.3
15:00 | 405.7 | 398.4 | 396 | 395.5 | 392.8 | 393.5 | 391 | 392.1 | 417.6 | 411.2 | 405
15:30 | 414 | 408.8 | 407.4 | 406.1 | 402.2 | 401.3 | 401.5 | 400.2 | 400 | 416.8 | 434.3
16:00 | 436.6 | 432 | 428.8 | 429.4 | 427.6 | 427.8 | 426.6 | 426.9 | 425.6 | 426.6 | 427.6
16:30 | 447.3 | 444.4 | 441.9 | 439.8 | 438.8 | 438.4 | 439.5 | 438.5 | 438.8 | 438.6 | 438.4
17:00 | 445.4 | 442.1 | 440.3 | 438.8 | 438.2 | 436.8 | 435.3 | 435.7 | 436.5 | 435 | 433.6
17:30 | 438.8 | 435.6 | 434.6 | 434.6 | 431.9 | 432 | 430.3 | 431.4 | 431.9 | 432.3 | 432.8
18:00 | 420.7 | 420.4 | 420.3 | 418.7 | 416.8 | 417.5 | 417.7 | 417.8 | 418.9 | 418.9 | 418.9
18:30 | 412.1 | 410.8 | 411.2 | 410.7 | 410.2 | 410.8 | 412 | 413 | 414.5 | 415.6 | 416.8
19:00 | 406.6 | 405.8 | 405.9 | 405 | 404.5 | 404.8 | 405.8 | 406.4 | 408.2 | 408.5 | 408.8
19:30 | 400.5 | 399.6 | 400 | 399 | 398.4 | 399.3 | 400.2 | 400.6 | 401.9 | 402.3 | 402.7
20:00 | 386.2 | 385.4 | 385.3 | 384.6 | 384.1 | 384.8 | 385.2 | 385.4 | 386.5 | 386.7 | 386.8
20:30 | 377.6 | 378.9 | 378.8 | 377.8 | 377.2 | 375.9 | 378.7 | 378.8 | 379.9 | 380.2 | 380.6
21:00 | 362.8 | 362.6 | 362.5 | 361.7 | 361.3 | 361.6 | 362.3 | 362.3 | 363.2 | 363.7 | 364.3
21:30 | 336.7 | 336.7 | 335.9 | 335.2 | 335.8 | 336.8 | 337.3 | 336.8 | 337.1 | 337.6 | 338
22:00 | 317.2 | 316.9 | 316.8 | 335.2 | 316.9 | 317 | 317.5 | 317.3 | 317.6 | 317.8 | 318.1
22:30 | 284.6 | 283.6 | 283.6 | 284.4 | 284.4 | 283.9 | 283.8 | 283.9 | 283.9 | 283.7 | 283.4
23:00 | 272.6 | 272.5 | 272.5 | 272.4 | 272.4 | 272.7 | 272.7 | 272.8 | 272.8 | 272.6 | 272.3
23:30 | 250.6 | 251.1 | 251 | 251 | 251 | 251.2 | 250.9 | 251 | 251 | 250.8 | 250.5

## 11. Load profile min
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:00 | 157.1 | 157.1 | 157.1 | 157.1 | 159 | 159.8 | 159.9 | 159.9 | 160.2 | 159.9 | 159.9
0:30 | 146.2 | 146.2 | 146.3 | 146.2 | 146.2 | 146.3 | 148.6 | 148.6 | 148.4 | 148.5 | 148.3
1:00 | 138.9 | 138.7 | 138.8 | 138.8 | 138.8 | 139 | 141.2 | 141.2 | 141.2 | 141.2 | 141.2
1:30 | 133.1 | 133 | 133.1 | 133 | 133.1 | 133.2 | 135.4 | 135.3 | 135.2 | 135.4 | 135.4
2:00 | 126.2 | 126.2 | 126.2 | 126.2 | 126.2 | 126.6 | 128.7 | 129 | 128.9 | 128.9 | 129
2:30 | 121.8 | 121.7 | 121.9 | 121.7 | 122 | 124.6 | 124.5 | 124.4 | 124.5 | 124.6 | 124.7
3:00 | 120 | 120 | 120.1 | 119.9 | 119.9 | 122.5 | 122.7 | 122.7 | 122.7 | 122.6 | 122.6
3:30 | 116.1 | 116.1 | 116.1 | 116.2 | 116.1 | 118.6 | 118.9 | 118.8 | 118.6 | 118.8 | 118.8
4:00 | 115 | 115.1 | 115.1 | 117.1 | 117.3 | 117.8 | 117.6 | 117.6 | 117.7 | 117.6 | 117.5
4:30 | 99.9 | 99.8 | 99.9 | 102 | 102 | 102.4 | 102.4 | 102.9 | 102.4 | 102.5 | 102.6
5:00 | 118.3 | 118.3 | 118.3 | 119.3 | 120.4 | 121.2 | 120.9 | 120.8 | 120.4 | 120.8 | 120.7
5:30 | 127.1 | 127.2 | 127.1 | 127.1 | 129.3 | 129.7 | 129.5 | 129.2 | 129.3 | 129.5 | 129.5
6:00 | 138.1 | 138 | 138.1 | 138 | 137.8 | 138.6 | 140.5 | 140.6 | 140.5 | 140.7 | 140.8
6:30 | 146.9 | 147 | 146.9 | 146.9 | 146.9 | 147.3 | 149.6 | 149.6 | 149.7 | 149.8 | 150
7:00 | 152.8 | 153 | 153 | 153 | 155.3 | 155.3 | 155.4 | 159.1 | 155.6 | 155.7 | 156
7:30 | 166.9 | 169.1 | 169.1 | 169 | 168.9 | 169.1 | 171.3 | 171.2 | 171.4 | 171.5 | 171.7
8:00 | 189.7 | 193.7 | 193.3 | 193 | 192.6 | 192.9 | 194.6 | 194.2 | 193.9 | 194.9 | 195.3
8:30 | 204.7 | 208.6 | 207.7 | 217.2 | 230.1 | 232.9 | 232.1 | 231.5 | 230.6 | 230 | 227.9
9:00 | 213.2 | 234.7 | 233.5 | 232.1 | 230.7 | 229.8 | 228.2 | 226.2 | 224.4 | 222.9 | 217.7
9:30 | 239.5 | 236.9 | 234.9 | 233 | 231.4 | 230.2 | 227.8 | 225.2 | 222.6 | 220.5 | 213.3
10:00 | 249.5 | 246.7 | 244.6 | 242.6 | 240.3 | 238.8 | 236.4 | 233.6 | 231 | 228.6 | 221
10:30 | 239.6 | 236.3 | 233.9 | 231.5 | 229.2 | 227.7 | 224.8 | 221.4 | 218.2 | 215.9 | 207.4
11:00 | 229 | 224.9 | 221.9 | 219 | 216.1 | 213.9 | 210.4 | 206.7 | 203.1 | 199.5 | 189.2
11:30 | 233 | 228.8 | 225.7 | 222.7 | 219.7 | 217.3 | 213.8 | 209.9 | 205.7 | 202.3 | 191.5
12:00 | 242.9 | 238.8 | 236.3 | 233.7 | 231.2 | 229.4 | 226.2 | 222.9 | 219.4 | 216.8 | 207.9
12:30 | 235.8 | 236.1 | 233.8 | 231.4 | 228.9 | 227.2 | 224.4 | 221 | 218 | 215.6 | 207.1
13:00 | 242.3 | 239 | 236 | 233.7 | 231.7 | 230 | 227.2 | 224.2 | 221.1 | 218.2 | 209.6
13:30 | 226.9 | 245.2 | 242.8 | 241.5 | 239.7 | 237.8 | 235.4 | 232.8 | 230.2 | 228 | 220.8
14:00 | 226.8 | 249.3 | 255.1 | 253.7 | 252.4 | 251.9 | 249.7 | 247.7 | 245.8 | 244 | 238.4
14:30 | 239.9 | 267.8 | 266.4 | 265.6 | 264.7 | 264.9 | 263.8 | 262.7 | 261.5 | 260.5 | 257.1
15:00 | 240.7 | 269.1 | 268.5 | 268.5 | 268.1 | 267.8 | 267.1 | 266.3 | 265.7 | 265 | 263
15:30 | 238.6 | 242.5 | 248.4 | 258 | 268.6 | 268.4 | 267.9 | 267.3 | 267.3 | 266.9 | 265.9
16:00 | 240.4 | 243.9 | 245.2 | 250 | 263 | 255.2 | 256.1 | 255.9 | 256 | 255.8 | 255.6
16:30 | 242.2 | 241.7 | 242 | 242 | 241.9 | 242 | 244.3 | 244.5 | 244.6 | 244.8 | 245.3
17:00 | 243.7 | 243.7 | 243.7 | 243.6 | 245.6 | 245.8 | 245.6 | 245.7 | 245.8 | 246 | 246.3
17:30 | 248.1 | 248 | 247.9 | 247.9 | 250.1 | 250.2 | 250.2 | 250.3 | 250.4 | 250.6 | 251.1
18:00 | 244.4 | 246.7 | 246.6 | 246.6 | 246.5 | 246.6 | 248.7 | 249.1 | 248.2 | 247.2 | 245.6
18:30 | 240.6 | 245.1 | 245.1 | 245.1 | 244.9 | 245.1 | 245.1 | 245.2 | 245.3 | 245.5 | 246
19:00 | 236.8 | 239 | 239 | 238.9 | 240.8 | 241 | 240.9 | 241.3 | 241.3 | 241.4 | 241.9
19:30 | 230.1 | 232.8 | 232.8 | 232.3 | 232.2 | 232.5 | 234.8 | 234.9 | 234.9 | 234.9 | 235.1
20:00 | 225.6 | 227.8 | 228.4 | 228.7 | 230 | 230.2 | 230.7 | 230.7 | 230.7 | 230.7 | 230.7
20:30 | 219.9 | 224.4 | 224.4 | 224.3 | 224.2 | 224.4 | 226.7 | 226.7 | 226.6 | 226.6 | 226.5
21:00 | 211.4 | 215.9 | 215.9 | 216 | 218.1 | 218.4 | 217.6 | 218.2 | 218.2 | 218.2 | 218.9
21:30 | 203.4 | 207.9 | 207.9 | 207.8 | 210.2 | 210.1 | 210 | 210 | 210 | 210 | 209.9
22:00 | 196.5 | 201.1 | 201.1 | 201 | 201 | 201.2 | 203.5 | 203.5 | 203.5 | 203.5 | 203.4
22:30 | 190.6 | 193 | 193 | 192.9 | 192.9 | 193 | 193 | 193.8 | 194.6 | 194.1 | 195.3
23:00 | 187.2 | 187.1 | 187.1 | 187.1 | 187.1 | 187.2 | 189.5 | 189.5 | 189.4 | 189.4 | 189.4
23:30 | 175.6 | 175.6 | 175.6 | 187.1 | 175.5 | 175.7 | 175.6 | 175.6 | 175.6 | 175.6 | 175.5

## 14. Load duration curve
*The data range is from 01-03-18 to 01-03-19

## 23. Historic load trace
Date/Time | Load (MVA) | Load (MW)
2016-03-01 00:30 | 173 | 173
2016-03-01 01:00 | 173 | 173
2016-03-01 01:30 | 171 | 171
2016-03-01 02:00 | 169 | 169
2016-03-01 02:30 | 172 | 172
2016-03-01 03:00 | 170 | 170
2016-03-01 03:30 | 170 | 170
2016-03-01 04:00 | 171 | 171
2016-03-01 04:30 | 175 | 175
2016-03-01 05:00 | 179 | 178
2016-03-01 05:30 | 189 | 189
2016-03-01 06:00 | 216 | 216
2016-03-01 06:30 | 234 | 234
2016-03-01 07:00 | 248 | 248
2016-03-01 07:30 | 260 | 260
2016-03-01 08:00 | 265 | 265
2016-03-01 08:30 | 272 | 272
2016-03-01 09:00 | 282 | 281
2016-03-01 09:30 | 286 | 286
2016-03-01 10:00 | 287 | 286
2016-03-01 10:30 | 290 | 289
2016-03-01 11:00 | 292 | 291
2016-03-01 11:30 | 289 | 288
2016-03-01 12:00 | 276 | 275
2016-03-01 12:30 | 282 | 281
2016-03-01 13:00 | 275 | 274
2016-03-01 13:30 | 276 | 275
2016-03-01 14:00 | 277 | 276
2016-03-01 14:30 | 280 | 280
2016-03-01 15:00 | 278 | 278
2016-03-01 15:30 | 279 | 278
2016-03-01 16:00 | 282 | 281
2016-03-01 16:30 | 279 | 278
2016-03-01 17:00 | 276 | 275
2016-03-01 17:30 | 285 | 284
2016-03-01 18:00 | 282 | 282
2016-03-01 18:30 | 282 | 282
2016-03-01 19:00 | 287 | 287
2016-03-01 19:30 | 283 | 282
2016-03-01 20:00 | 276 | 275
2016-03-01 20:30 | 258 | 258
2016-03-01 21:00 | 246 | 246
2016-03-01 21:30 | 240 | 240
2016-03-01 22:00 | 233 | 233
2016-03-01 22:30 | 218 | 217
2016-03-01 23:00 | 189 | 188
2016-03-01 23:30 | 185 | 185
2016-03-02 | 177 | 177
2016-03-02 00:30 | 171 | 170
2016-03-02 01:00 | 166 | 165
2016-03-02 01:30 | 164 | 164
2016-03-02 02:00 | 165 | 165
2016-03-02 02:30 | 165 | 165
2016-03-02 03:00 | 167 | 167
2016-03-02 03:30 | 167 | 167
2016-03-02 04:00 | 170 | 170
2016-03-02 04:30 | 173 | 173
2016-03-02 05:00 | 181 | 180
2016-03-02 05:30 | 196 | 195
2016-03-02 06:00 | 218 | 217
2016-03-02 06:30 | 236 | 236
2016-03-02 07:00 | 250 | 250
2016-03-02 07:30 | 258 | 257
2016-03-02 08:00 | 268 | 267
2016-03-02 08:30 | 272 | 272
2016-03-02 09:00 | 269 | 269
2016-03-02 09:30 | 280 | 280
2016-03-02 10:00 | 283 | 283
2016-03-02 10:30 | 292 | 292
2016-03-02 11:00 | 293 | 293
2016-03-02 11:30 | 290 | 290
2016-03-02 12:00 | 291 | 291
2016-03-02 12:30 | 297 | 297
2016-03-02 13:00 | 298 | 298
2016-03-02 13:30 | 300 | 300
2016-03-02 14:00 | 299 | 299
2016-03-02 14:30 | 301 | 301
2016-03-02 15:00 | 308 | 308
2016-03-02 15:30 | 314 | 314
2016-03-02 16:00 | 315 | 315
2016-03-02 16:30 | 317 | 317
2016-03-02 17:00 | 307 | 307
2016-03-02 17:30 | 306 | 306
2016-03-02 18:00 | 306 | 306
2016-03-02 18:30 | 309 | 309
2016-03-02 19:00 | 306 | 306
2016-03-02 19:30 | 311 | 311
2016-03-02 20:00 | 298 | 298
2016-03-02 20:30 | 278 | 278
2016-03-02 21:00 | 267 | 266
2016-03-02 21:30 | 257 | 256
2016-03-02 22:00 | 244 | 244
2016-03-02 22:30 | 227 | 226
2016-03-02 23:00 | 212 | 212
2016-03-02 23:30 | 203 | 203
2016-03-03 | 190 | 190
2016-03-03 00:30 | 185 | 185
2016-03-03 01:00 | 182 | 181
2016-03-03 01:30 | 172 | 171
2016-03-03 02:00 | 163 | 162
2016-03-03 02:30 | 163 | 162
2016-03-03 03:00 | 163 | 162
2016-03-03 03:30 | 164 | 163
2016-03-03 04:00 | 167 | 166
2016-03-03 04:30 | 169 | 169
2016-03-03 05:00 | 165 | 165
2016-03-03 05:30 | 187 | 187
2016-03-03 06:00 | 215 | 215
2016-03-03 06:30 | 246 | 246
2016-03-03 07:00 | 258 | 258
2016-03-03 07:30 | 266 | 265
2016-03-03 08:00 | 271 | 270
2016-03-03 08:30 | 273 | 273
2016-03-03 09:00 | 279 | 279
2016-03-03 09:30 | 277 | 277
2016-03-03 10:00 | 279 | 279
2016-03-03 10:30 | 277 | 277
2016-03-03 11:00 | 281 | 281
2016-03-03 11:30 | 280 | 280
2016-03-03 12:00 | 280 | 280
2016-03-03 12:30 | 281 | 281
2016-03-03 13:00 | 282 | 282
2016-03-03 13:30 | 287 | 286
2016-03-03 14:00 | 296 | 295
2016-03-03 14:30 | 302 | 301
2016-03-03 15:00 | 298 | 297
2016-03-03 15:30 | 305 | 304
2016-03-03 16:00 | 316 | 315
2016-03-03 16:30 | 322 | 321
2016-03-03 17:00 | 317 | 316
2016-03-03 17:30 | 312 | 311
2016-03-03 18:00 | 309 | 308
2016-03-03 18:30 | 318 | 318
2016-03-03 19:00 | 306 | 306
2016-03-03 19:30 | 298 | 298
2016-03-03 20:00 | 295 | 294
2016-03-03 20:30 | 288 | 287
2016-03-03 21:00 | 271 | 269
2016-03-03 21:30 | 257 | 257
2016-03-03 22:00 | 244 | 243
2016-03-03 22:30 | 224 | 224
2016-03-03 23:00 | 210 | 210
2016-03-03 23:30 | 199 | 199
2016-03-04 | 188 | 188
2016-03-04 00:30 | 180 | 180
2016-03-04 01:00 | 177 | 177
2016-03-04 01:30 | 178 | 178
2016-03-04 02:00 | 177 | 176
2016-03-04 02:30 | 176 | 175
2016-03-04 03:00 | 176 | 175
2016-03-04 03:30 | 174 | 174
2016-03-04 04:00 | 177 | 176
2016-03-04 04:30 | 181 | 180
2016-03-04 05:00 | 185 | 185
2016-03-04 05:30 | 196 | 196
2016-03-04 06:00 | 220 | 220
2016-03-04 06:30 | 242 | 242
2016-03-04 07:00 | 251 | 251
2016-03-04 07:30 | 260 | 260
2016-03-04 08:00 | 270 | 270
2016-03-04 08:30 | 279 | 279
2016-03-04 09:00 | 275 | 274
2016-03-04 09:30 | 272 | 271
2016-03-04 10:00 | 280 | 280
2016-03-04 10:30 | 284 | 284
2016-03-04 11:00 | 285 | 285
2016-03-04 11:30 | 280 | 280
2016-03-04 12:00 | 276 | 276
2016-03-04 12:30 | 279 | 279
2016-03-04 13:00 | 280 | 280
2016-03-04 13:30 | 284 | 284
2016-03-04 14:00 | 288 | 288
2016-03-04 14:30 | 286 | 286
2016-03-04 15:00 | 293 | 293
2016-03-04 15:30 | 298 | 298
2016-03-04 16:00 | 301 | 301
2016-03-04 16:30 | 301 | 301
2016-03-04 17:00 | 299 | 298
2016-03-04 17:30 | 294 | 293
2016-03-04 18:00 | 288 | 288
2016-03-04 18:30 | 295 | 295
2016-03-04 19:00 | 285 | 285
2016-03-04 19:30 | 282 | 282
2016-03-04 20:00 | 271 | 271
2016-03-04 20:30 | 260 | 260
2016-03-04 21:00 | 253 | 253
2016-03-04 21:30 | 246 | 246
2016-03-04 22:00 | 243 | 242
2016-03-04 22:30 | 235 | 234
2016-03-04 23:00 | 219 | 219
2016-03-04 23:30 | 205 | 205
2016-03-05 | 190 | 190
2016-03-05 00:30 | 181 | 181
2016-03-05 01:00 | 177 | 177
2016-03-05 01:30 | 176 | 176
2016-03-05 02:00 | 173 | 173
2016-03-05 02:30 | 174 | 174
2016-03-05 03:00 | 174 | 174
2016-03-05 03:30 | 172 | 172
2016-03-05 04:00 | 173 | 172
2016-03-05 04:30 | 177 | 177
2016-03-05 05:00 | 177 | 177
2016-03-05 05:30 | 187 | 187
2016-03-05 06:00 | 196 | 196
2016-03-05 06:30 | 197 | 197
2016-03-05 07:00 | 202 | 202
2016-03-05 07:30 | 211 | 211
2016-03-05 08:00 | 213 | 213
2016-03-05 08:30 | 227 | 227
2016-03-05 09:00 | 240 | 240
2016-03-05 09:30 | 242 | 242
2016-03-05 10:00 | 243 | 243
2016-03-05 10:30 | 247 | 247
2016-03-05 11:00 | 251 | 251
2016-03-05 11:30 | 248 | 247
2016-03-05 12:00 | 245 | 244
2016-03-05 12:30 | 244 | 243
2016-03-05 13:00 | 251 | 250
2016-03-05 13:30 | 248 | 247
2016-03-05 14:00 | 247 | 245
2016-03-05 14:30 | 248 | 246
2016-03-05 15:00 | 254 | 252
2016-03-05 15:30 | 256 | 254
2016-03-05 16:00 | 258 | 256
2016-03-05 16:30 | 264 | 262
2016-03-05 17:00 | 260 | 258
2016-03-05 17:30 | 256 | 254
2016-03-05 18:00 | 260 | 257
2016-03-05 18:30 | 264 | 263
2016-03-05 19:00 | 260 | 258
2016-03-05 19:30 | 258 | 256
2016-03-05 20:00 | 253 | 251
2016-03-05 20:30 | 244 | 242
2016-03-05 21:00 | 235 | 234
2016-03-05 21:30 | 228 | 227
2016-03-05 22:00 | 224 | 223
2016-03-05 22:30 | 217 | 215
2016-03-05 23:00 | 205 | 203
2016-03-05 23:30 | 197 | 194
2016-03-06 | 188 | 187
2016-03-06 00:30 | 186 | 186
2016-03-06 01:00 | 182 | 181
2016-03-06 01:30 | 178 | 177
2016-03-06 02:00 | 174 | 173
2016-03-06 02:30 | 173 | 172
2016-03-06 03:00 | 172 | 171
2016-03-06 03:30 | 172 | 171
2016-03-06 04:00 | 175 | 174
2016-03-06 04:30 | 173 | 172
2016-03-06 05:00 | 181 | 180
2016-03-06 05:30 | 185 | 184
2016-03-06 06:00 | 191 | 190
2016-03-06 06:30 | 195 | 195
2016-03-06 07:00 | 199 | 199
2016-03-06 07:30 | 209 | 209
2016-03-06 08:00 | 222 | 222
2016-03-06 08:30 | 228 | 228
2016-03-06 09:00 | 235 | 234
2016-03-06 09:30 | 233 | 232
2016-03-06 10:00 | 230 | 229
2016-03-06 10:30 | 232 | 231
2016-03-06 11:00 | 235 | 234
2016-03-06 11:30 | 233 | 233
2016-03-06 12:00 | 236 | 236
2016-03-06 12:30 | 240 | 239
2016-03-06 13:00 | 242 | 242
2016-03-06 13:30 | 248 | 248
2016-03-06 14:00 | 256 | 256
2016-03-06 14:30 | 260 | 260
2016-03-06 15:00 | 264 | 264
2016-03-06 15:30 | 268 | 268
2016-03-06 16:00 | 274 | 274
2016-03-06 16:30 | 278 | 278
2016-03-06 17:00 | 279 | 279
2016-03-06 17:30 | 278 | 278
2016-03-06 18:00 | 280 | 280
2016-03-06 18:30 | 289 | 289
2016-03-06 19:00 | 283 | 283
2016-03-06 19:30 | 279 | 278
2016-03-06 20:00 | 266 | 266
2016-03-06 20:30 | 261 | 260
2016-03-06 21:00 | 250 | 249
2016-03-06 21:30 | 245 | 244
2016-03-06 22:00 | 238 | 237
2016-03-06 22:30 | 232 | 231
2016-03-06 23:00 | 221 | 219
2016-03-06 23:30 | 211 | 210
2016-03-07 | 195 | 195
2016-03-07 00:30 | 188 | 188
2016-03-07 01:00 | 188 | 187
2016-03-07 01:30 | 186 | 186
2016-03-07 02:00 | 184 | 184
2016-03-07 02:30 | 184 | 184
2016-03-07 03:00 | 184 | 184
2016-03-07 03:30 | 185 | 185
2016-03-07 04:00 | 189 | 189
2016-03-07 04:30 | 192 | 192
2016-03-07 05:00 | 197 | 197
2016-03-07 05:30 | 208 | 208
2016-03-07 06:00 | 227 | 227
2016-03-07 06:30 | 239 | 239
2016-03-07 07:00 | 251 | 249
2016-03-07 07:30 | 262 | 260
2016-03-07 08:00 | 274 | 274
2016-03-07 08:30 | 279 | 278
2016-03-07 09:00 | 281 | 281
2016-03-07 09:30 | 281 | 281
2016-03-07 10:00 | 286 | 286
2016-03-07 10:30 | 293 | 293
2016-03-07 11:00 | 290 | 290
2016-03-07 11:30 | 292 | 292
2016-03-07 12:00 | 289 | 289
2016-03-07 12:30 | 290 | 290
2016-03-07 13:00 | 291 | 291
2016-03-07 13:30 | 295 | 295
2016-03-07 14:00 | 297 | 297
2016-03-07 14:30 | 295 | 295
2016-03-07 15:00 | 303 | 303
2016-03-07 15:30 | 306 | 306
2016-03-07 16:00 | 306 | 306
2016-03-07 16:30 | 310 | 310
2016-03-07 17:00 | 306 | 305
2016-03-07 17:30 | 299 | 298
2016-03-07 18:00 | 302 | 301
2016-03-07 18:30 | 312 | 312
2016-03-07 19:00 | 305 | 304
2016-03-07 19:30 | 300 | 299
2016-03-07 20:00 | 285 | 284
2016-03-07 20:30 | 275 | 274
2016-03-07 21:00 | 265 | 264
2016-03-07 21:30 | 252 | 251
2016-03-07 22:00 | 245 | 244
2016-03-07 22:30 | 234 | 233
2016-03-07 23:00 | 207 | 206
2016-03-07 23:30 | 190 | 190
2016-03-08 | 186 | 186
2016-03-08 00:30 | 184 | 184
2016-03-08 01:00 | 182 | 182
2016-03-08 01:30 | 181 | 180
2016-03-08 02:00 | 181 | 181
2016-03-08 02:30 | 181 | 181
2016-03-08 03:00 | 181 | 181
2016-03-08 03:30 | 182 | 181
2016-03-08 04:00 | 184 | 184
2016-03-08 04:30 | 189 | 189
2016-03-08 05:00 | 194 | 194
2016-03-08 05:30 | 212 | 212
2016-03-08 06:00 | 229 | 228
2016-03-08 06:30 | 237 | 236
2016-03-08 07:00 | 247 | 247
2016-03-08 07:30 | 260 | 259
2016-03-08 08:00 | 272 | 270
2016-03-08 08:30 | 275 | 274
2016-03-08 09:00 | 286 | 286
2016-03-08 09:30 | 295 | 294
2016-03-08 10:00 | 301 | 300
2016-03-08 10:30 | 301 | 299
2016-03-08 11:00 | 297 | 295
2016-03-08 11:30 | 291 | 290
2016-03-08 12:00 | 296 | 295
2016-03-08 12:30 | 301 | 300
2016-03-08 13:00 | 308 | 307
2016-03-08 13:30 | 308 | 307
2016-03-08 14:00 | 311 | 311
2016-03-08 14:30 | 317 | 316
2016-03-08 15:00 | 323 | 323
2016-03-08 15:30 | 322 | 321
2016-03-08 16:00 | 315 | 314
2016-03-08 16:30 | 326 | 324
2016-03-08 17:00 | 320 | 319
2016-03-08 17:30 | 312 | 310
2016-03-08 18:00 | 309 | 308
2016-03-08 18:30 | 328 | 328
2016-03-08 19:00 | 321 | 320
2016-03-08 19:30 | 311 | 310
2016-03-08 20:00 | 298 | 298
2016-03-08 20:30 | 283 | 283
2016-03-08 21:00 | 274 | 273
2016-03-08 21:30 | 261 | 261
2016-03-08 22:00 | 249 | 249
2016-03-08 22:30 | 242 | 242
2016-03-08 23:00 | 222 | 221
2016-03-08 23:30 | 204 | 204
2016-03-09 | 187 | 187
2016-03-09 00:30 | 176 | 176
2016-03-09 01:00 | 167 | 167
2016-03-09 01:30 | 162 | 162
2016-03-09 02:00 | 160 | 160
2016-03-09 02:30 | 158 | 158
2016-03-09 03:00 | 158 | 158
2016-03-09 03:30 | 160 | 160
2016-03-09 04:00 | 164 | 164
2016-03-09 04:30 | 169 | 169
2016-03-09 05:00 | 182 | 182
2016-03-09 05:30 | 195 | 195
2016-03-09 06:00 | 219 | 219
2016-03-09 06:30 | 240 | 240
2016-03-09 07:00 | 264 | 264
2016-03-09 07:30 | 276 | 275
2016-03-09 08:00 | 280 | 280
2016-03-09 08:30 | 284 | 284
2016-03-09 09:00 | 291 | 291
2016-03-09 09:30 | 290 | 290
2016-03-09 10:00 | 289 | 289
2016-03-09 10:30 | 290 | 290
2016-03-09 11:00 | 289 | 289
2016-03-09 11:30 | 291 | 291
2016-03-09 12:00 | 292 | 292
2016-03-09 12:30 | 289 | 289
2016-03-09 13:00 | 295 | 295
2016-03-09 13:30 | 297 | 297
2016-03-09 14:00 | 298 | 298
2016-03-09 14:30 | 297 | 297
2016-03-09 15:00 | 301 | 301
2016-03-09 15:30 | 330 | 330
2016-03-09 16:00 | 335 | 335
2016-03-09 16:30 | 334 | 334
2016-03-09 17:00 | 308 | 308
2016-03-09 17:30 | 303 | 303
2016-03-09 18:00 | 304 | 303
2016-03-09 18:30 | 314 | 314
2016-03-09 19:00 | 306 | 306
2016-03-09 19:30 | 304 | 303
2016-03-09 20:00 | 288 | 288
2016-03-09 20:30 | 270 | 270
2016-03-09 21:00 | 264 | 264
2016-03-09 21:30 | 257 | 257
2016-03-09 22:00 | 258 | 258
2016-03-09 22:30 | 248 | 248
2016-03-09 23:00 | 230 | 230
2016-03-09 23:30 | 214 | 214
2016-03-10 | 192 | 192
2016-03-10 00:30 | 184 | 184
2016-03-10 01:00 | 180 | 180
2016-03-10 01:30 | 178 | 178
2016-03-10 02:00 | 176 | 176
2016-03-10 02:30 | 175 | 175
2016-03-10 03:00 | 176 | 176
2016-03-10 03:30 | 176 | 176
2016-03-10 04:00 | 177 | 177
2016-03-10 04:30 | 182 | 182
2016-03-10 05:00 | 191 | 191
2016-03-10 05:30 | 204 | 204
2016-03-10 06:00 | 223 | 222
2016-03-10 06:30 | 235 | 235
2016-03-10 07:00 | 247 | 247
2016-03-10 07:30 | 261 | 260
2016-03-10 08:00 | 266 | 265
2016-03-10 08:30 | 274 | 274
2016-03-10 09:00 | 280 | 280
2016-03-10 09:30 | 284 | 284
2016-03-10 10:00 | 286 | 286
2016-03-10 10:30 | 287 | 286
2016-03-10 11:00 | 287 | 287
2016-03-10 11:30 | 293 | 293
2016-03-10 12:00 | 297 | 297
2016-03-10 12:30 | 299 | 299
2016-03-10 13:00 | 305 | 305
2016-03-10 13:30 | 307 | 307
2016-03-10 14:00 | 311 | 310
2016-03-10 14:30 | 314 | 313
2016-03-10 15:00 | 315 | 314
2016-03-10 15:30 | 319 | 318
2016-03-10 16:00 | 323 | 322
2016-03-10 16:30 | 322 | 321
2016-03-10 17:00 | 322 | 320
2016-03-10 17:30 | 324 | 322
2016-03-10 18:00 | 328 | 327
2016-03-10 18:30 | 336 | 335
2016-03-10 19:00 | 332 | 330
2016-03-10 19:30 | 319 | 319
2016-03-10 20:00 | 304 | 304
2016-03-10 20:30 | 291 | 290
2016-03-10 21:00 | 286 | 285
2016-03-10 21:30 | 271 | 271
2016-03-10 22:00 | 263 | 263
2016-03-10 22:30 | 252 | 251
2016-03-10 23:00 | 239 | 238
2016-03-10 23:30 | 224 | 223
2016-03-11 | 212 | 212
2016-03-11 00:30 | 203 | 203
2016-03-11 01:00 | 198 | 198
2016-03-11 01:30 | 191 | 191
2016-03-11 02:00 | 190 | 189
2016-03-11 02:30 | 190 | 189
2016-03-11 03:00 | 188 | 188
2016-03-11 03:30 | 190 | 189
2016-03-11 04:00 | 190 | 190
2016-03-11 04:30 | 193 | 193
2016-03-11 05:00 | 199 | 199
2016-03-11 05:30 | 205 | 205
2016-03-11 06:00 | 231 | 231
2016-03-11 06:30 | 249 | 249
2016-03-11 07:00 | 266 | 266
2016-03-11 07:30 | 274 | 274
2016-03-11 08:00 | 284 | 284
2016-03-11 08:30 | 290 | 290
2016-03-11 09:00 | 293 | 293
2016-03-11 09:30 | 298 | 298
2016-03-11 10:00 | 300 | 300
2016-03-11 10:30 | 298 | 298
2016-03-11 11:00 | 299 | 299
2016-03-11 11:30 | 301 | 301
2016-03-11 12:00 | 305 | 304
2016-03-11 12:30 | 309 | 308
2016-03-11 13:00 | 316 | 316
2016-03-11 13:30 | 325 | 325
2016-03-11 14:00 | 330 | 330
2016-03-11 14:30 | 330 | 330
2016-03-11 15:00 | 334 | 334
2016-03-11 15:30 | 335 | 335
2016-03-11 16:00 | 337 | 337
2016-03-11 16:30 | 333 | 333
2016-03-11 17:00 | 318 | 317
2016-03-11 17:30 | 311 | 310
2016-03-11 18:00 | 310 | 310
2016-03-11 18:30 | 317 | 317
2016-03-11 19:00 | 313 | 313
2016-03-11 19:30 | 306 | 306
2016-03-11 20:00 | 296 | 296
2016-03-11 20:30 | 285 | 285
2016-03-11 21:00 | 279 | 279
2016-03-11 21:30 | 267 | 267
2016-03-11 22:00 | 263 | 263
2016-03-11 22:30 | 253 | 252
2016-03-11 23:00 | 243 | 242
2016-03-11 23:30 | 235 | 234
2016-03-12 | 208 | 208
2016-03-12 00:30 | 199 | 199
2016-03-12 01:00 | 192 | 192
2016-03-12 01:30 | 192 | 192
2016-03-12 02:00 | 186 | 185
2016-03-12 02:30 | 182 | 181
2016-03-12 03:00 | 181 | 181
2016-03-12 03:30 | 180 | 180
2016-03-12 04:00 | 174 | 174
2016-03-12 04:30 | 175 | 175
2016-03-12 05:00 | 179 | 178
2016-03-12 05:30 | 182 | 182
2016-03-12 06:00 | 191 | 191
2016-03-12 06:30 | 195 | 195
2016-03-12 07:00 | 205 | 205
2016-03-12 07:30 | 211 | 211
2016-03-12 08:00 | 221 | 221
2016-03-12 08:30 | 228 | 228
2016-03-12 09:00 | 249 | 249
2016-03-12 09:30 | 255 | 255
2016-03-12 10:00 | 260 | 259
2016-03-12 10:30 | 259 | 259
2016-03-12 11:00 | 258 | 257
2016-03-12 11:30 | 259 | 258
2016-03-12 12:00 | 260 | 259
2016-03-12 12:30 | 262 | 261
2016-03-12 13:00 | 263 | 263
2016-03-12 13:30 | 266 | 266
2016-03-12 14:00 | 268 | 268
2016-03-12 14:30 | 269 | 269
2016-03-12 15:00 | 274 | 274
2016-03-12 15:30 | 283 | 283
2016-03-12 16:00 | 288 | 287
2016-03-12 16:30 | 291 | 290
2016-03-12 17:00 | 290 | 289
2016-03-12 17:30 | 286 | 285
2016-03-12 18:00 | 285 | 284
2016-03-12 18:30 | 295 | 294
2016-03-12 19:00 | 286 | 285
2016-03-12 19:30 | 281 | 280
2016-03-12 20:00 | 273 | 273
2016-03-12 20:30 | 266 | 266
2016-03-12 21:00 | 262 | 262
2016-03-12 21:30 | 254 | 254
2016-03-12 22:00 | 252 | 251
2016-03-12 22:30 | 248 | 248
2016-03-12 23:00 | 235 | 235
2016-03-12 23:30 | 226 | 226
2016-03-13 | 213 | 213
2016-03-13 00:30 | 204 | 204
2016-03-13 01:00 | 200 | 200
2016-03-13 01:30 | 194 | 194
2016-03-13 02:00 | 193 | 192
2016-03-13 02:30 | 193 | 193
2016-03-13 03:00 | 195 | 195
2016-03-13 03:30 | 189 | 188
2016-03-13 04:00 | 195 | 195
2016-03-13 04:30 | 199 | 199
2016-03-13 05:00 | 202 | 202
2016-03-13 05:30 | 202 | 202
2016-03-13 06:00 | 209 | 209
2016-03-13 06:30 | 213 | 213
2016-03-13 07:00 | 222 | 222
2016-03-13 07:30 | 230 | 230
2016-03-13 08:00 | 235 | 235
2016-03-13 08:30 | 248 | 248
2016-03-13 09:00 | 250 | 250
2016-03-13 09:30 | 246 | 246
2016-03-13 10:00 | 258 | 258
2016-03-13 10:30 | 263 | 262
2016-03-13 11:00 | 263 | 262
2016-03-13 11:30 | 258 | 258
2016-03-13 12:00 | 261 | 260
2016-03-13 12:30 | 261 | 261
2016-03-13 13:00 | 263 | 262
2016-03-13 13:30 | 267 | 267
2016-03-13 14:00 | 265 | 265
2016-03-13 14:30 | 264 | 264
2016-03-13 15:00 | 263 | 262
2016-03-13 15:30 | 267 | 267
2016-03-13 16:00 | 267 | 266
2016-03-13 16:30 | 272 | 271
2016-03-13 17:00 | 271 | 270
2016-03-13 17:30 | 269 | 268
2016-03-13 18:00 | 276 | 275
2016-03-13 18:30 | 291 | 291
2016-03-13 19:00 | 291 | 290
2016-03-13 19:30 | 283 | 282
2016-03-13 20:00 | 275 | 274
2016-03-13 20:30 | 263 | 261
2016-03-13 21:00 | 256 | 256
2016-03-13 21:30 | 247 | 247
2016-03-13 22:00 | 240 | 240
2016-03-13 22:30 | 236 | 236
2016-03-13 23:00 | 224 | 224
2016-03-13 23:30 | 215 | 215
2016-03-14 | 200 | 200
2016-03-14 00:30 | 195 | 195
2016-03-14 01:00 | 192 | 192
2016-03-14 01:30 | 189 | 189
2016-03-14 02:00 | 185 | 184
2016-03-14 02:30 | 182 | 181
2016-03-14 03:00 | 182 | 182
2016-03-14 03:30 | 183 | 183
2016-03-14 04:00 | 187 | 186
2016-03-14 04:30 | 193 | 192
2016-03-14 05:00 | 199 | 199
2016-03-14 05:30 | 201 | 201
2016-03-14 06:00 | 221 | 220
2016-03-14 06:30 | 238 | 238
2016-03-14 07:00 | 250 | 250
2016-03-14 07:30 | 260 | 260
2016-03-14 08:00 | 269 | 269
2016-03-14 08:30 | 276 | 276
2016-03-14 09:00 | 280 | 280
2016-03-14 09:30 | 280 | 280
2016-03-14 10:00 | 284 | 284
2016-03-14 10:30 | 290 | 290
2016-03-14 11:00 | 285 | 285
2016-03-14 11:30 | 287 | 287
2016-03-14 12:00 | 296 | 296
2016-03-14 12:30 | 299 | 299
2016-03-14 13:00 | 297 | 297
2016-03-14 13:30 | 297 | 297
2016-03-14 14:00 | 294 | 294
2016-03-14 14:30 | 294 | 294
2016-03-14 15:00 | 293 | 293
2016-03-14 15:30 | 298 | 298
2016-03-14 16:00 | 302 | 301
2016-03-14 16:30 | 309 | 309
2016-03-14 17:00 | 305 | 304
2016-03-14 17:30 | 297 | 296
2016-03-14 18:00 | 298 | 298
2016-03-14 18:30 | 308 | 308
2016-03-14 19:00 | 297 | 297
2016-03-14 19:30 | 296 | 296
2016-03-14 20:00 | 290 | 289
2016-03-14 20:30 | 265 | 264
2016-03-14 21:00 | 260 | 260
2016-03-14 21:30 | 246 | 245
2016-03-14 22:00 | 232 | 232
2016-03-14 22:30 | 230 | 230
2016-03-14 23:00 | 218 | 218
2016-03-14 23:30 | 202 | 201
2016-03-15 | 184 | 184
2016-03-15 00:30 | 168 | 168
2016-03-15 01:00 | 164 | 163
2016-03-15 01:30 | 166 | 165
2016-03-15 02:00 | 162 | 161
2016-03-15 02:30 | 160 | 160
2016-03-15 03:00 | 160 | 159
2016-03-15 03:30 | 157 | 156
2016-03-15 04:00 | 164 | 164
2016-03-15 04:30 | 167 | 167
2016-03-15 05:00 | 178 | 178
2016-03-15 05:30 | 187 | 187
2016-03-15 06:00 | 219 | 219
2016-03-15 06:30 | 241 | 240
2016-03-15 07:00 | 249 | 249
2016-03-15 07:30 | 257 | 257
2016-03-15 08:00 | 261 | 261
2016-03-15 08:30 | 265 | 265
2016-03-15 09:00 | 271 | 271
2016-03-15 09:30 | 279 | 278
2016-03-15 10:00 | 285 | 284
2016-03-15 10:30 | 285 | 285
2016-03-15 11:00 | 286 | 285
2016-03-15 11:30 | 290 | 289
2016-03-15 12:00 | 292 | 292
2016-03-15 12:30 | 298 | 298
2016-03-15 13:00 | 294 | 294
2016-03-15 13:30 | 298 | 298
2016-03-15 14:00 | 299 | 299
2016-03-15 14:30 | 295 | 294
2016-03-15 15:00 | 292 | 291
2016-03-15 15:30 | 298 | 298
2016-03-15 16:00 | 297 | 296
2016-03-15 16:30 | 301 | 300
2016-03-15 17:00 | 302 | 300
2016-03-15 17:30 | 293 | 292
2016-03-15 18:00 | 295 | 294
2016-03-15 18:30 | 304 | 303
2016-03-15 19:00 | 291 | 291
2016-03-15 19:30 | 284 | 284
2016-03-15 20:00 | 274 | 273
2016-03-15 20:30 | 260 | 259
2016-03-15 21:00 | 254 | 253
2016-03-15 21:30 | 244 | 243
2016-03-15 22:00 | 230 | 230
2016-03-15 22:30 | 215 | 215
2016-03-15 23:00 | 208 | 208
2016-03-15 23:30 | 200 | 200
2016-03-16 | 174 | 174
2016-03-16 00:30 | 157 | 157
2016-03-16 01:00 | 165 | 164
2016-03-16 01:30 | 166 | 166
2016-03-16 02:00 | 164 | 164
2016-03-16 02:30 | 162 | 162
2016-03-16 03:00 | 164 | 164
2016-03-16 03:30 | 160 | 160
2016-03-16 04:00 | 164 | 164
2016-03-16 04:30 | 171 | 171
2016-03-16 05:00 | 180 | 180
2016-03-16 05:30 | 193 | 193
2016-03-16 06:00 | 224 | 224
2016-03-16 06:30 | 243 | 242
2016-03-16 07:00 | 261 | 260
2016-03-16 07:30 | 270 | 270
2016-03-16 08:00 | 269 | 269
2016-03-16 08:30 | 272 | 272
2016-03-16 09:00 | 272 | 272
2016-03-16 09:30 | 275 | 275
2016-03-16 10:00 | 279 | 279
2016-03-16 10:30 | 282 | 282
2016-03-16 11:00 | 280 | 280
2016-03-16 11:30 | 282 | 282
2016-03-16 12:00 | 287 | 287
2016-03-16 12:30 | 282 | 282
2016-03-16 13:00 | 283 | 283
2016-03-16 13:30 | 292 | 292
2016-03-16 14:00 | 296 | 296
2016-03-16 14:30 | 294 | 294
2016-03-16 15:00 | 299 | 299
2016-03-16 15:30 | 302 | 302
2016-03-16 16:00 | 301 | 300
2016-03-16 16:30 | 302 | 302
2016-03-16 17:00 | 296 | 295
2016-03-16 17:30 | 290 | 290
2016-03-16 18:00 | 289 | 289
2016-03-16 18:30 | 291 | 291
2016-03-16 19:00 | 289 | 288
2016-03-16 19:30 | 287 | 286
2016-03-16 20:00 | 274 | 273
2016-03-16 20:30 | 260 | 259
2016-03-16 21:00 | 252 | 251
2016-03-16 21:30 | 242 | 240
2016-03-16 22:00 | 228 | 227
2016-03-16 22:30 | 209 | 209
2016-03-16 23:00 | 203 | 203
2016-03-16 23:30 | 188 | 188
2016-03-17 | 173 | 172
2016-03-17 00:30 | 152 | 152
2016-03-17 01:00 | 139 | 139
2016-03-17 01:30 | 155 | 155
2016-03-17 02:00 | 157 | 157
2016-03-17 02:30 | 155 | 155
2016-03-17 03:00 | 155 | 155
2016-03-17 03:30 | 158 | 158
2016-03-17 04:00 | 158 | 158
2016-03-17 04:30 | 171 | 171
2016-03-17 05:00 | 180 | 180
2016-03-17 05:30 | 191 | 191
2016-03-17 06:00 | 215 | 214
2016-03-17 06:30 | 233 | 232
2016-03-17 07:00 | 249 | 247
2016-03-17 07:30 | 253 | 252
2016-03-17 08:00 | 271 | 270
2016-03-17 08:30 | 271 | 269
2016-03-17 09:00 | 268 | 267
2016-03-17 09:30 | 274 | 274
2016-03-17 10:00 | 279 | 279
2016-03-17 10:30 | 285 | 285
2016-03-17 11:00 | 289 | 289
2016-03-17 11:30 | 294 | 294
2016-03-17 12:00 | 287 | 287
2016-03-17 12:30 | 295 | 295
2016-03-17 13:00 | 298 | 298
2016-03-17 13:30 | 299 | 299
2016-03-17 14:00 | 299 | 299
2016-03-17 14:30 | 287 | 287
2016-03-17 15:00 | 288 | 288
2016-03-17 15:30 | 293 | 293
2016-03-17 16:00 | 295 | 295
2016-03-17 16:30 | 295 | 295
2016-03-17 17:00 | 286 | 286
2016-03-17 17:30 | 291 | 291
2016-03-17 18:00 | 293 | 293
2016-03-17 18:30 | 295 | 295
2016-03-17 19:00 | 295 | 295
2016-03-17 19:30 | 288 | 288
2016-03-17 20:00 | 283 | 283
2016-03-17 20:30 | 269 | 269
2016-03-17 21:00 | 261 | 261
2016-03-17 21:30 | 248 | 247
2016-03-17 22:00 | 239 | 239
2016-03-17 22:30 | 225 | 225
2016-03-17 23:00 | 213 | 213
2016-03-17 23:30 | 201 | 201
2016-03-18 | 178 | 178
2016-03-18 00:30 | 168 | 168
2016-03-18 01:00 | 165 | 165
2016-03-18 01:30 | 162 | 162
2016-03-18 02:00 | 161 | 161
2016-03-18 02:30 | 149 | 149
2016-03-18 03:00 | 150 | 150
2016-03-18 03:30 | 147 | 147
2016-03-18 04:00 | 161 | 161
2016-03-18 04:30 | 165 | 165
2016-03-18 05:00 | 178 | 178
2016-03-18 05:30 | 189 | 189
2016-03-18 06:00 | 213 | 212
2016-03-18 06:30 | 229 | 229
2016-03-18 07:00 | 241 | 241
2016-03-18 07:30 | 247 | 247
2016-03-18 08:00 | 249 | 249
2016-03-18 08:30 | 253 | 253
2016-03-18 09:00 | 258 | 258
2016-03-18 09:30 | 262 | 262
2016-03-18 10:00 | 262 | 262
2016-03-18 10:30 | 265 | 265
2016-03-18 11:00 | 269 | 269
2016-03-18 11:30 | 273 | 273
2016-03-18 12:00 | 272 | 272
2016-03-18 12:30 | 273 | 273
2016-03-18 13:00 | 274 | 274
2016-03-18 13:30 | 278 | 278
2016-03-18 14:00 | 283 | 283
2016-03-18 14:30 | 288 | 288
2016-03-18 15:00 | 296 | 296
2016-03-18 15:30 | 301 | 301
2016-03-18 16:00 | 311 | 310
2016-03-18 16:30 | 316 | 315
2016-03-18 17:00 | 312 | 311
2016-03-18 17:30 | 298 | 298
2016-03-18 18:00 | 298 | 298
2016-03-18 18:30 | 307 | 307
2016-03-18 19:00 | 299 | 299
2016-03-18 19:30 | 293 | 293
2016-03-18 20:00 | 282 | 281
2016-03-18 20:30 | 268 | 268
2016-03-18 21:00 | 264 | 264
2016-03-18 21:30 | 258 | 258
2016-03-18 22:00 | 252 | 252
2016-03-18 22:30 | 238 | 238
2016-03-18 23:00 | 225 | 225
2016-03-18 23:30 | 212 | 212
2016-03-19 | 188 | 187
2016-03-19 00:30 | 173 | 172
2016-03-19 01:00 | 163 | 163
2016-03-19 01:30 | 159 | 159
2016-03-19 02:00 | 162 | 162
2016-03-19 02:30 | 161 | 161
2016-03-19 03:00 | 158 | 158
2016-03-19 03:30 | 158 | 158
2016-03-19 04:00 | 158 | 158
2016-03-19 04:30 | 163 | 163
2016-03-19 05:00 | 170 | 169
2016-03-19 05:30 | 172 | 172
2016-03-19 06:00 | 181 | 181
2016-03-19 06:30 | 187 | 186
2016-03-19 07:00 | 204 | 202
2016-03-19 07:30 | 218 | 217
2016-03-19 08:00 | 229 | 229
2016-03-19 08:30 | 238 | 238
2016-03-19 09:00 | 244 | 244
2016-03-19 09:30 | 255 | 255
2016-03-19 10:00 | 257 | 257
2016-03-19 10:30 | 259 | 259
2016-03-19 11:00 | 259 | 259
2016-03-19 11:30 | 257 | 257
2016-03-19 12:00 | 259 | 259
2016-03-19 12:30 | 266 | 266
2016-03-19 13:00 | 273 | 273
2016-03-19 13:30 | 283 | 283
2016-03-19 14:00 | 291 | 291
2016-03-19 14:30 | 286 | 286
2016-03-19 15:00 | 282 | 282
2016-03-19 15:30 | 273 | 273
2016-03-19 16:00 | 271 | 270
2016-03-19 16:30 | 279 | 279
2016-03-19 17:00 | 279 | 279
2016-03-19 17:30 | 279 | 279
2016-03-19 18:00 | 278 | 278
2016-03-19 18:30 | 280 | 280
2016-03-19 19:00 | 276 | 276
2016-03-19 19:30 | 269 | 269
2016-03-19 20:00 | 255 | 255
2016-03-19 20:30 | 248 | 248
2016-03-19 21:00 | 241 | 241
2016-03-19 21:30 | 233 | 233
2016-03-19 22:00 | 227 | 227
2016-03-19 22:30 | 220 | 220
2016-03-19 23:00 | 212 | 212
2016-03-19 23:30 | 201 | 201
2016-03-20 | 185 | 185
2016-03-20 00:30 | 171 | 171
2016-03-20 01:00 | 161 | 161
2016-03-20 01:30 | 160 | 160
2016-03-20 02:00 | 158 | 158
2016-03-20 02:30 | 157 | 157
2016-03-20 03:00 | 157 | 157
2016-03-20 03:30 | 150 | 150
2016-03-20 04:00 | 152 | 152
2016-03-20 04:30 | 153 | 153
2016-03-20 05:00 | 155 | 154
2016-03-20 05:30 | 157 | 157
2016-03-20 06:00 | 165 | 165
2016-03-20 06:30 | 170 | 170
2016-03-20 07:00 | 183 | 183
2016-03-20 07:30 | 196 | 196
2016-03-20 08:00 | 205 | 203
2016-03-20 08:30 | 208 | 206
2016-03-20 09:00 | 215 | 214
2016-03-20 09:30 | 218 | 218
2016-03-20 10:00 | 224 | 224
2016-03-20 10:30 | 222 | 221
2016-03-20 11:00 | 224 | 224
2016-03-20 11:30 | 227 | 227
2016-03-20 12:00 | 228 | 227
2016-03-20 12:30 | 226 | 226
2016-03-20 13:00 | 222 | 222
2016-03-20 13:30 | 223 | 222
2016-03-20 14:00 | 232 | 232
2016-03-20 14:30 | 238 | 238
2016-03-20 15:00 | 250 | 250
2016-03-20 15:30 | 255 | 255
2016-03-20 16:00 | 256 | 256
2016-03-20 16:30 | 253 | 253
2016-03-20 17:00 | 264 | 264
2016-03-20 17:30 | 271 | 271
2016-03-20 18:00 | 280 | 280
2016-03-20 18:30 | 282 | 282
2016-03-20 19:00 | 272 | 272
2016-03-20 19:30 | 267 | 267
2016-03-20 20:00 | 260 | 260
2016-03-20 20:30 | 250 | 249
2016-03-20 21:00 | 245 | 245
2016-03-20 21:30 | 234 | 234
2016-03-20 22:00 | 226 | 226
2016-03-20 22:30 | 218 | 218
2016-03-20 23:00 | 202 | 202
2016-03-20 23:30 | 196 | 196
2016-03-21 | 179 | 179
2016-03-21 00:30 | 172 | 172
2016-03-21 01:00 | 168 | 168
2016-03-21 01:30 | 165 | 165
2016-03-21 02:00 | 163 | 163
2016-03-21 02:30 | 164 | 164
2016-03-21 03:00 | 164 | 164
2016-03-21 03:30 | 168 | 168
2016-03-21 04:00 | 172 | 172
2016-03-21 04:30 | 175 | 175
2016-03-21 05:00 | 185 | 184
2016-03-21 05:30 | 198 | 197
2016-03-21 06:00 | 221 | 221
2016-03-21 06:30 | 238 | 238
2016-03-21 07:00 | 248 | 248
2016-03-21 07:30 | 254 | 253
2016-03-21 08:00 | 255 | 255
2016-03-21 08:30 | 251 | 251
2016-03-21 09:00 | 268 | 268
2016-03-21 09:30 | 265 | 264
2016-03-21 10:00 | 272 | 272
2016-03-21 10:30 | 274 | 274
2016-03-21 11:00 | 270 | 270
2016-03-21 11:30 | 267 | 266
2016-03-21 12:00 | 266 | 266
2016-03-21 12:30 | 266 | 266
2016-03-21 13:00 | 271 | 271
2016-03-21 13:30 | 262 | 261
2016-03-21 14:00 | 267 | 266
2016-03-21 14:30 | 268 | 268
2016-03-21 15:00 | 273 | 272
2016-03-21 15:30 | 279 | 278
2016-03-21 16:00 | 276 | 275
2016-03-21 16:30 | 279 | 278
2016-03-21 17:00 | 277 | 277
2016-03-21 17:30 | 283 | 283
2016-03-21 18:00 | 288 | 288
2016-03-21 18:30 | 283 | 283
2016-03-21 19:00 | 275 | 274
2016-03-21 19:30 | 271 | 271
2016-03-21 20:00 | 262 | 262
2016-03-21 20:30 | 249 | 249
2016-03-21 21:00 | 246 | 246
2016-03-21 21:30 | 236 | 235
2016-03-21 22:00 | 219 | 219
2016-03-21 22:30 | 205 | 205
2016-03-21 23:00 | 194 | 194
2016-03-21 23:30 | 186 | 185
2016-03-22 | 172 | 171
2016-03-22 00:30 | 165 | 165
2016-03-22 01:00 | 160 | 160
2016-03-22 01:30 | 158 | 158
2016-03-22 02:00 | 154 | 154
2016-03-22 02:30 | 153 | 153
2016-03-22 03:00 | 153 | 153
2016-03-22 03:30 | 154 | 154
2016-03-22 04:00 | 163 | 163
2016-03-22 04:30 | 170 | 170
2016-03-22 05:00 | 172 | 172
2016-03-22 05:30 | 183 | 183
2016-03-22 06:00 | 214 | 214
2016-03-22 06:30 | 226 | 226
2016-03-22 07:00 | 234 | 234
2016-03-22 07:30 | 245 | 241
2016-03-22 08:00 | 245 | 242
2016-03-22 08:30 | 246 | 243
2016-03-22 09:00 | 248 | 246
2016-03-22 09:30 | 248 | 246
2016-03-22 10:00 | 246 | 244
2016-03-22 10:30 | 246 | 244
2016-03-22 11:00 | 247 | 244
2016-03-22 11:30 | 247 | 244
2016-03-22 12:00 | 247 | 244
2016-03-22 12:30 | 252 | 250
2016-03-22 13:00 | 261 | 259
2016-03-22 13:30 | 263 | 261
2016-03-22 14:00 | 263 | 261
2016-03-22 14:30 | 266 | 263
2016-03-22 15:00 | 267 | 264
2016-03-22 15:30 | 272 | 268
2016-03-22 16:00 | 278 | 274
2016-03-22 16:30 | 280 | 276
2016-03-22 17:00 | 276 | 271
2016-03-22 17:30 | 279 | 273
2016-03-22 18:00 | 285 | 280
2016-03-22 18:30 | 285 | 281
2016-03-22 19:00 | 282 | 277
2016-03-22 19:30 | 274 | 269
2016-03-22 20:00 | 271 | 265
2016-03-22 20:30 | 252 | 250
2016-03-22 21:00 | 242 | 241
2016-03-22 21:30 | 228 | 227
2016-03-22 22:00 | 222 | 221
2016-03-22 22:30 | 221 | 220
2016-03-22 23:00 | 206 | 204
2016-03-22 23:30 | 192 | 190
2016-03-23 | 176 | 172
2016-03-23 00:30 | 169 | 166
2016-03-23 01:00 | 169 | 165
2016-03-23 01:30 | 169 | 165
2016-03-23 02:00 | 160 | 155
2016-03-23 02:30 | 155 | 151
2016-03-23 03:00 | 157 | 152
2016-03-23 03:30 | 157 | 152
2016-03-23 04:00 | 166 | 162
2016-03-23 04:30 | 172 | 169
2016-03-23 05:00 | 179 | 177
2016-03-23 05:30 | 192 | 190
2016-03-23 06:00 | 214 | 212
2016-03-23 06:30 | 224 | 221
2016-03-23 07:00 | 239 | 235
2016-03-23 07:30 | 246 | 242
2016-03-23 08:00 | 247 | 246
2016-03-23 08:30 | 245 | 245
2016-03-23 09:00 | 249 | 249
2016-03-23 09:30 | 247 | 247
2016-03-23 10:00 | 252 | 252
2016-03-23 10:30 | 257 | 256
2016-03-23 11:00 | 260 | 259
2016-03-23 11:30 | 264 | 264
2016-03-23 12:00 | 266 | 265
2016-03-23 12:30 | 264 | 264
2016-03-23 13:00 | 269 | 268
2016-03-23 13:30 | 269 | 268
2016-03-23 14:00 | 273 | 273
2016-03-23 14:30 | 286 | 286
2016-03-23 15:00 | 293 | 292
2016-03-23 15:30 | 297 | 296
2016-03-23 16:00 | 296 | 295
2016-03-23 16:30 | 303 | 302
2016-03-23 17:00 | 300 | 299
2016-03-23 17:30 | 297 | 296
2016-03-23 18:00 | 303 | 302
2016-03-23 18:30 | 302 | 301
2016-03-23 19:00 | 294 | 293
2016-03-23 19:30 | 286 | 285
2016-03-23 20:00 | 275 | 274
2016-03-23 20:30 | 264 | 263
2016-03-23 21:00 | 254 | 254
2016-03-23 21:30 | 246 | 246
2016-03-23 22:00 | 236 | 236
2016-03-23 22:30 | 226 | 226
2016-03-23 23:00 | 216 | 216
2016-03-23 23:30 | 201 | 201
2016-03-24 | 178 | 178
2016-03-24 00:30 | 168 | 168
2016-03-24 01:00 | 165 | 165
2016-03-24 01:30 | 163 | 163
2016-03-24 02:00 | 163 | 163
2016-03-24 02:30 | 161 | 160
2016-03-24 03:00 | 162 | 162
2016-03-24 03:30 | 164 | 164
2016-03-24 04:00 | 167 | 167
2016-03-24 04:30 | 170 | 170
2016-03-24 05:00 | 182 | 181
2016-03-24 05:30 | 193 | 193
2016-03-24 06:00 | 208 | 208
2016-03-24 06:30 | 225 | 225
2016-03-24 07:00 | 240 | 240
2016-03-24 07:30 | 248 | 247
2016-03-24 08:00 | 251 | 251
2016-03-24 08:30 | 257 | 257
2016-03-24 09:00 | 260 | 260
2016-03-24 09:30 | 260 | 259
2016-03-24 10:00 | 261 | 260
2016-03-24 10:30 | 264 | 263
2016-03-24 11:00 | 264 | 264
2016-03-24 11:30 | 271 | 271
2016-03-24 12:00 | 273 | 273
2016-03-24 12:30 | 268 | 267
2016-03-24 13:00 | 268 | 268
2016-03-24 13:30 | 272 | 271
2016-03-24 14:00 | 278 | 277
2016-03-24 14:30 | 277 | 277
2016-03-24 15:00 | 278 | 278
2016-03-24 15:30 | 287 | 287
2016-03-24 16:00 | 291 | 291
2016-03-24 16:30 | 285 | 285
2016-03-24 17:00 | 284 | 284
2016-03-24 17:30 | 283 | 283
2016-03-24 18:00 | 289 | 289
2016-03-24 18:30 | 292 | 291
2016-03-24 19:00 | 284 | 284
2016-03-24 19:30 | 280 | 280
2016-03-24 20:00 | 273 | 273
2016-03-24 20:30 | 262 | 262
2016-03-24 21:00 | 259 | 259
2016-03-24 21:30 | 250 | 250
2016-03-24 22:00 | 245 | 243
2016-03-24 22:30 | 238 | 237
2016-03-24 23:00 | 221 | 220
2016-03-24 23:30 | 205 | 204
2016-03-25 | 182 | 182
2016-03-25 00:30 | 173 | 173
2016-03-25 01:00 | 170 | 170
2016-03-25 01:30 | 168 | 168
2016-03-25 02:00 | 167 | 166
2016-03-25 02:30 | 164 | 163
2016-03-25 03:00 | 164 | 163
2016-03-25 03:30 | 165 | 164
2016-03-25 04:00 | 166 | 165
2016-03-25 04:30 | 169 | 168
2016-03-25 05:00 | 171 | 170
2016-03-25 05:30 | 173 | 172
2016-03-25 06:00 | 180 | 179
2016-03-25 06:30 | 187 | 186
2016-03-25 07:00 | 196 | 194
2016-03-25 07:30 | 202 | 199
2016-03-25 08:00 | 210 | 206
2016-03-25 08:30 | 214 | 212
2016-03-25 09:00 | 218 | 218
2016-03-25 09:30 | 218 | 218
2016-03-25 10:00 | 215 | 215
2016-03-25 10:30 | 213 | 213
2016-03-25 11:00 | 210 | 210
2016-03-25 11:30 | 209 | 209
2016-03-25 12:00 | 211 | 210
2016-03-25 12:30 | 209 | 208
2016-03-25 13:00 | 215 | 215
2016-03-25 13:30 | 216 | 216
2016-03-25 14:00 | 216 | 216
2016-03-25 14:30 | 222 | 221
2016-03-25 15:00 | 229 | 229
2016-03-25 15:30 | 234 | 234
2016-03-25 16:00 | 240 | 240
2016-03-25 16:30 | 246 | 246
2016-03-25 17:00 | 250 | 250
2016-03-25 17:30 | 249 | 248
2016-03-25 18:00 | 262 | 262
2016-03-25 18:30 | 265 | 265
2016-03-25 19:00 | 259 | 259
2016-03-25 19:30 | 252 | 251
2016-03-25 20:00 | 245 | 244
2016-03-25 20:30 | 234 | 233
2016-03-25 21:00 | 236 | 235
2016-03-25 21:30 | 230 | 230
2016-03-25 22:00 | 229 | 229
2016-03-25 22:30 | 220 | 220
2016-03-25 23:00 | 210 | 210
2016-03-25 23:30 | 204 | 204
2016-03-26 | 188 | 188
2016-03-26 00:30 | 175 | 174
2016-03-26 01:00 | 171 | 170
2016-03-26 01:30 | 169 | 168
2016-03-26 02:00 | 168 | 167
2016-03-26 02:30 | 169 | 168
2016-03-26 03:00 | 169 | 167
2016-03-26 03:30 | 168 | 167
2016-03-26 04:00 | 169 | 167
2016-03-26 04:30 | 172 | 171
2016-03-26 05:00 | 174 | 173
2016-03-26 05:30 | 177 | 176
2016-03-26 06:00 | 184 | 183
2016-03-26 06:30 | 187 | 187
2016-03-26 07:00 | 195 | 195
2016-03-26 07:30 | 204 | 204
2016-03-26 08:00 | 215 | 215
2016-03-26 08:30 | 221 | 221
2016-03-26 09:00 | 227 | 227
2016-03-26 09:30 | 225 | 225
2016-03-26 10:00 | 227 | 227
2016-03-26 10:30 | 227 | 227
2016-03-26 11:00 | 228 | 227
2016-03-26 11:30 | 229 | 229
2016-03-26 12:00 | 230 | 230
2016-03-26 12:30 | 231 | 231
2016-03-26 13:00 | 235 | 235
2016-03-26 13:30 | 241 | 241
2016-03-26 14:00 | 242 | 242
2016-03-26 14:30 | 246 | 246
2016-03-26 15:00 | 261 | 261
2016-03-26 15:30 | 259 | 259
2016-03-26 16:00 | 269 | 267
2016-03-26 16:30 | 273 | 271
2016-03-26 17:00 | 275 | 272
2016-03-26 17:30 | 273 | 271
2016-03-26 18:00 | 274 | 272
2016-03-26 18:30 | 279 | 277
2016-03-26 19:00 | 270 | 268
2016-03-26 19:30 | 267 | 266
2016-03-26 20:00 | 262 | 261
2016-03-26 20:30 | 252 | 250
2016-03-26 21:00 | 244 | 243
2016-03-26 21:30 | 235 | 234
2016-03-26 22:00 | 234 | 234
2016-03-26 22:30 | 226 | 225
2016-03-26 23:00 | 213 | 212
2016-03-26 23:30 | 201 | 201
2016-03-27 | 186 | 186
2016-03-27 00:30 | 179 | 179
2016-03-27 01:00 | 177 | 176
2016-03-27 01:30 | 175 | 174
2016-03-27 02:00 | 173 | 172
2016-03-27 02:30 | 171 | 170
2016-03-27 03:00 | 171 | 170
2016-03-27 03:30 | 170 | 169
2016-03-27 04:00 | 170 | 169
2016-03-27 04:30 | 172 | 171
2016-03-27 05:00 | 169 | 168
2016-03-27 05:30 | 174 | 173
2016-03-27 06:00 | 183 | 182
2016-03-27 06:30 | 191 | 190
2016-03-27 07:00 | 195 | 195
2016-03-27 07:30 | 204 | 204
2016-03-27 08:00 | 210 | 210
2016-03-27 08:30 | 214 | 214
2016-03-27 09:00 | 217 | 217
2016-03-27 09:30 | 223 | 223
2016-03-27 10:00 | 226 | 226
2016-03-27 10:30 | 228 | 228
2016-03-27 11:00 | 229 | 228
2016-03-27 11:30 | 226 | 225
2016-03-27 12:00 | 223 | 222
2016-03-27 12:30 | 223 | 222
2016-03-27 13:00 | 219 | 218
2016-03-27 13:30 | 214 | 213
2016-03-27 14:00 | 212 | 211
2016-03-27 14:30 | 213 | 212
2016-03-27 15:00 | 221 | 220
2016-03-27 15:30 | 221 | 220
2016-03-27 16:00 | 226 | 225
2016-03-27 16:30 | 233 | 232
2016-03-27 17:00 | 236 | 235
2016-03-27 17:30 | 242 | 241
2016-03-27 18:00 | 246 | 246
2016-03-27 18:30 | 245 | 245
2016-03-27 19:00 | 240 | 239
2016-03-27 19:30 | 239 | 238
2016-03-27 20:00 | 235 | 234
2016-03-27 20:30 | 225 | 225
2016-03-27 21:00 | 225 | 225
2016-03-27 21:30 | 222 | 222
2016-03-27 22:00 | 219 | 219
2016-03-27 22:30 | 210 | 210
2016-03-27 23:00 | 201 | 201
2016-03-27 23:30 | 194 | 194
2016-03-28 | 181 | 181
2016-03-28 00:30 | 173 | 172
2016-03-28 01:00 | 170 | 169
2016-03-28 01:30 | 169 | 168
2016-03-28 02:00 | 170 | 169
2016-03-28 02:30 | 168 | 167
2016-03-28 03:00 | 169 | 167
2016-03-28 03:30 | 167 | 165
2016-03-28 04:00 | 167 | 166
2016-03-28 04:30 | 169 | 168
2016-03-28 05:00 | 172 | 170
2016-03-28 05:30 | 178 | 176
2016-03-28 06:00 | 187 | 186
2016-03-28 06:30 | 191 | 191
2016-03-28 07:00 | 196 | 195
2016-03-28 07:30 | 205 | 205
2016-03-28 08:00 | 212 | 212
2016-03-28 08:30 | 219 | 218
2016-03-28 09:00 | 229 | 229
2016-03-28 09:30 | 233 | 232
2016-03-28 10:00 | 228 | 228
2016-03-28 10:30 | 221 | 220
2016-03-28 11:00 | 220 | 219
2016-03-28 11:30 | 223 | 222
2016-03-28 12:00 | 226 | 226
2016-03-28 12:30 | 226 | 226
2016-03-28 13:00 | 229 | 228
2016-03-28 13:30 | 238 | 237
2016-03-28 14:00 | 242 | 242
2016-03-28 14:30 | 242 | 242
2016-03-28 15:00 | 252 | 251
2016-03-28 15:30 | 256 | 255
2016-03-28 16:00 | 259 | 259
2016-03-28 16:30 | 260 | 260
2016-03-28 17:00 | 262 | 261
2016-03-28 17:30 | 264 | 263
2016-03-28 18:00 | 265 | 264
2016-03-28 18:30 | 266 | 265
2016-03-28 19:00 | 275 | 273
2016-03-28 19:30 | 271 | 269
2016-03-28 20:00 | 268 | 266
2016-03-28 20:30 | 249 | 249
2016-03-28 21:00 | 244 | 244
2016-03-28 21:30 | 238 | 238
2016-03-28 22:00 | 231 | 231
2016-03-28 22:30 | 222 | 222
2016-03-28 23:00 | 210 | 210
2016-03-28 23:30 | 203 | 203
2016-03-29 | 188 | 188
2016-03-29 00:30 | 179 | 179
2016-03-29 01:00 | 176 | 176
2016-03-29 01:30 | 173 | 173
2016-03-29 02:00 | 172 | 172
2016-03-29 02:30 | 170 | 170
2016-03-29 03:00 | 168 | 168
2016-03-29 03:30 | 172 | 172
2016-03-29 04:00 | 175 | 175
2016-03-29 04:30 | 182 | 182
2016-03-29 05:00 | 187 | 187
2016-03-29 05:30 | 196 | 196
2016-03-29 06:00 | 216 | 216
2016-03-29 06:30 | 225 | 225
2016-03-29 07:00 | 233 | 233
2016-03-29 07:30 | 241 | 241
2016-03-29 08:00 | 253 | 253
2016-03-29 08:30 | 256 | 255
2016-03-29 09:00 | 259 | 258
2016-03-29 09:30 | 256 | 255
2016-03-29 10:00 | 264 | 263
2016-03-29 10:30 | 263 | 263
2016-03-29 11:00 | 265 | 265
2016-03-29 11:30 | 268 | 268
2016-03-29 12:00 | 268 | 268
2016-03-29 12:30 | 270 | 269
2016-03-29 13:00 | 271 | 271
2016-03-29 13:30 | 274 | 274
2016-03-29 14:00 | 282 | 281
2016-03-29 14:30 | 287 | 286
2016-03-29 15:00 | 292 | 292
2016-03-29 15:30 | 296 | 296
2016-03-29 16:00 | 300 | 299
2016-03-29 16:30 | 305 | 305
2016-03-29 17:00 | 306 | 306
2016-03-29 17:30 | 303 | 303
2016-03-29 18:00 | 308 | 308
2016-03-29 18:30 | 308 | 308
2016-03-29 19:00 | 298 | 298
2016-03-29 19:30 | 294 | 294
2016-03-29 20:00 | 285 | 285
2016-03-29 20:30 | 269 | 268
2016-03-29 21:00 | 261 | 261
2016-03-29 21:30 | 252 | 252
2016-03-29 22:00 | 241 | 241
2016-03-29 22:30 | 233 | 233
2016-03-29 23:00 | 217 | 216
2016-03-29 23:30 | 207 | 206
2016-03-30 | 188 | 188
2016-03-30 00:30 | 182 | 182
2016-03-30 01:00 | 183 | 183
2016-03-30 01:30 | 179 | 178
2016-03-30 02:00 | 179 | 179
2016-03-30 02:30 | 176 | 176
2016-03-30 03:00 | 177 | 177
2016-03-30 03:30 | 178 | 178
2016-03-30 04:00 | 180 | 180
2016-03-30 04:30 | 186 | 186
2016-03-30 05:00 | 193 | 192
2016-03-30 05:30 | 205 | 205
2016-03-30 06:00 | 223 | 223
2016-03-30 06:30 | 231 | 229
2016-03-30 07:00 | 247 | 246
2016-03-30 07:30 | 258 | 256
2016-03-30 08:00 | 258 | 257
2016-03-30 08:30 | 267 | 266
2016-03-30 09:00 | 270 | 270
2016-03-30 09:30 | 275 | 275
2016-03-30 10:00 | 273 | 272
2016-03-30 10:30 | 274 | 274
2016-03-30 11:00 | 277 | 277
2016-03-30 11:30 | 279 | 278
2016-03-30 12:00 | 281 | 281
2016-03-30 12:30 | 293 | 293
2016-03-30 13:00 | 307 | 306
2016-03-30 13:30 | 312 | 311
2016-03-30 14:00 | 323 | 322
2016-03-30 14:30 | 319 | 319
2016-03-30 15:00 | 312 | 312
2016-03-30 15:30 | 311 | 311
2016-03-30 16:00 | 304 | 304
2016-03-30 16:30 | 305 | 305
2016-03-30 17:00 | 303 | 303
2016-03-30 17:30 | 303 | 303
2016-03-30 18:00 | 301 | 301
2016-03-30 18:30 | 303 | 302
2016-03-30 19:00 | 293 | 292
2016-03-30 19:30 | 286 | 286
2016-03-30 20:00 | 276 | 275
2016-03-30 20:30 | 268 | 268
2016-03-30 21:00 | 263 | 263
2016-03-30 21:30 | 255 | 255
2016-03-30 22:00 | 256 | 256
2016-03-30 22:30 | 248 | 248
2016-03-30 23:00 | 232 | 232
2016-03-30 23:30 | 220 | 219
2016-03-31 | 203 | 203
2016-03-31 00:30 | 191 | 191
2016-03-31 01:00 | 185 | 184
2016-03-31 01:30 | 180 | 180
2016-03-31 02:00 | 178 | 178
2016-03-31 02:30 | 176 | 176
2016-03-31 03:00 | 175 | 175
2016-03-31 03:30 | 177 | 177
2016-03-31 04:00 | 181 | 180
2016-03-31 04:30 | 186 | 185
2016-03-31 05:00 | 193 | 192
2016-03-31 05:30 | 201 | 201
2016-03-31 06:00 | 217 | 216
2016-03-31 06:30 | 228 | 228
2016-03-31 07:00 | 237 | 237
2016-03-31 07:30 | 247 | 246
2016-03-31 08:00 | 253 | 253
2016-03-31 08:30 | 259 | 258
2016-03-31 09:00 | 267 | 267
2016-03-31 09:30 | 271 | 270
2016-03-31 10:00 | 273 | 272
2016-03-31 10:30 | 274 | 273
2016-03-31 11:00 | 275 | 274
2016-03-31 11:30 | 278 | 278
2016-03-31 12:00 | 279 | 279
2016-03-31 12:30 | 280 | 279
2016-03-31 13:00 | 285 | 285
2016-03-31 13:30 | 290 | 290
2016-03-31 14:00 | 289 | 288
2016-03-31 14:30 | 292 | 292
2016-03-31 15:00 | 292 | 292
2016-03-31 15:30 | 294 | 293
2016-03-31 16:00 | 303 | 302
2016-03-31 16:30 | 310 | 309
2016-03-31 17:00 | 307 | 306
2016-03-31 17:30 | 304 | 304
2016-03-31 18:00 | 309 | 308
2016-03-31 18:30 | 308 | 308
2016-03-31 19:00 | 297 | 297
2016-03-31 19:30 | 290 | 290
2016-03-31 20:00 | 280 | 280
2016-03-31 20:30 | 266 | 266
2016-03-31 21:00 | 252 | 252
2016-03-31 21:30 | 237 | 236
2016-03-31 22:00 | 238 | 238
2016-03-31 22:30 | 235 | 235
2016-03-31 23:00 | 222 | 222
2016-03-31 23:30 | 206 | 206
2016-04-01 | 200 | 200
2016-04-01 00:30 | 189 | 189
2016-04-01 01:00 | 181 | 180
2016-04-01 01:30 | 176 | 176
2016-04-01 02:00 | 173 | 173
2016-04-01 02:30 | 172 | 172
2016-04-01 03:00 | 172 | 172
2016-04-01 03:30 | 172 | 172
2016-04-01 04:00 | 175 | 175
2016-04-01 04:30 | 181 | 181
2016-04-01 05:00 | 191 | 191
2016-04-01 05:30 | 201 | 201
2016-04-01 06:00 | 219 | 219
2016-04-01 06:30 | 237 | 237
2016-04-01 07:00 | 249 | 249
2016-04-01 07:30 | 257 | 257
2016-04-01 08:00 | 261 | 261
2016-04-01 08:30 | 261 | 261
2016-04-01 09:00 | 264 | 264
2016-04-01 09:30 | 268 | 268
2016-04-01 10:00 | 268 | 268
2016-04-01 10:30 | 264 | 263
2016-04-01 11:00 | 263 | 262
2016-04-01 11:30 | 263 | 263
2016-04-01 12:00 | 268 | 268
2016-04-01 12:30 | 270 | 270
2016-04-01 13:00 | 271 | 271
2016-04-01 13:30 | 280 | 280
2016-04-01 14:00 | 285 | 285
2016-04-01 14:30 | 292 | 292
2016-04-01 15:00 | 297 | 297
2016-04-01 15:30 | 302 | 302
2016-04-01 16:00 | 307 | 307
2016-04-01 16:30 | 308 | 308
2016-04-01 17:00 | 301 | 300
2016-04-01 17:30 | 300 | 300
2016-04-01 18:00 | 303 | 303
2016-04-01 18:30 | 300 | 300
2016-04-01 19:00 | 290 | 290
2016-04-01 19:30 | 285 | 285
2016-04-01 20:00 | 282 | 282
2016-04-01 20:30 | 270 | 270
2016-04-01 21:00 | 258 | 258
2016-04-01 21:30 | 251 | 251
2016-04-01 22:00 | 251 | 251
2016-04-01 22:30 | 240 | 240
2016-04-01 23:00 | 224 | 224
2016-04-01 23:30 | 217 | 217
2016-04-02 | 203 | 203
2016-04-02 00:30 | 194 | 194
2016-04-02 01:00 | 185 | 185
2016-04-02 01:30 | 179 | 179
2016-04-02 02:00 | 176 | 176
2016-04-02 02:30 | 174 | 174
2016-04-02 03:00 | 173 | 173
2016-04-02 03:30 | 173 | 172
2016-04-02 04:00 | 174 | 174
2016-04-02 04:30 | 175 | 175
2016-04-02 05:00 | 181 | 181
2016-04-02 05:30 | 186 | 186
2016-04-02 06:00 | 196 | 196
2016-04-02 06:30 | 207 | 207
2016-04-02 07:00 | 221 | 221
2016-04-02 07:30 | 230 | 228
2016-04-02 08:00 | 238 | 237
2016-04-02 08:30 | 246 | 246
2016-04-02 09:00 | 254 | 254
2016-04-02 09:30 | 260 | 260
2016-04-02 10:00 | 261 | 261
2016-04-02 10:30 | 262 | 262
2016-04-02 11:00 | 262 | 262
2016-04-02 11:30 | 262 | 262
2016-04-02 12:00 | 264 | 263
2016-04-02 12:30 | 268 | 268
2016-04-02 13:00 | 272 | 272
2016-04-02 13:30 | 274 | 274
2016-04-02 14:00 | 274 | 274
2016-04-02 14:30 | 282 | 282
2016-04-02 15:00 | 298 | 297
2016-04-02 15:30 | 304 | 303
2016-04-02 16:00 | 307 | 306
2016-04-02 16:30 | 311 | 311
2016-04-02 17:00 | 310 | 309
2016-04-02 17:30 | 307 | 306
2016-04-02 18:00 | 312 | 312
2016-04-02 18:30 | 314 | 313
2016-04-02 19:00 | 304 | 303
2016-04-02 19:30 | 298 | 297
2016-04-02 20:00 | 288 | 288
2016-04-02 20:30 | 275 | 274
2016-04-02 21:00 | 265 | 265
2016-04-02 21:30 | 254 | 254
2016-04-02 22:00 | 253 | 253
2016-04-02 22:30 | 247 | 247
2016-04-02 23:00 | 235 | 235
2016-04-02 23:30 | 219 | 218
2016-04-03 | 203 | 203
2016-04-03 00:30 | 193 | 193
2016-04-03 01:00 | 184 | 184
2016-04-03 01:30 | 179 | 179
2016-04-03 02:00 | 176 | 176
2016-04-03 02:30 | 173 | 173
2016-04-03 03:00 | 172 | 172
2016-04-03 03:30 | 171 | 171
2016-04-03 04:00 | 171 | 171
2016-04-03 04:30 | 172 | 172
2016-04-03 05:00 | 176 | 176
2016-04-03 05:30 | 180 | 180
2016-04-03 06:00 | 185 | 185
2016-04-03 06:30 | 193 | 192
2016-04-03 07:00 | 205 | 204
2016-04-03 07:30 | 213 | 213
2016-04-03 08:00 | 225 | 224
2016-04-03 08:30 | 231 | 231
2016-04-03 09:00 | 237 | 237
2016-04-03 09:30 | 240 | 240
2016-04-03 10:00 | 244 | 244
2016-04-03 10:30 | 245 | 245
2016-04-03 11:00 | 245 | 245
2016-04-03 11:30 | 246 | 246
2016-04-03 12:00 | 247 | 247
2016-04-03 12:30 | 247 | 246
2016-04-03 13:00 | 250 | 250
2016-04-03 13:30 | 255 | 255
2016-04-03 14:00 | 260 | 260
2016-04-03 14:30 | 266 | 265
2016-04-03 15:00 | 276 | 276
2016-04-03 15:30 | 279 | 278
2016-04-03 16:00 | 281 | 281
2016-04-03 16:30 | 288 | 288
2016-04-03 17:00 | 296 | 296
2016-04-03 17:30 | 303 | 303
2016-04-03 18:00 | 315 | 315
2016-04-03 18:30 | 311 | 311
2016-04-03 19:00 | 298 | 298
2016-04-03 19:30 | 297 | 296
2016-04-03 20:00 | 286 | 286
2016-04-03 20:30 | 272 | 272
2016-04-03 21:00 | 261 | 261
2016-04-03 21:30 | 249 | 249
2016-04-03 22:00 | 243 | 243
2016-04-03 22:30 | 239 | 238
2016-04-03 23:00 | 226 | 225
2016-04-03 23:30 | 215 | 214
2016-04-04 | 199 | 198
2016-04-04 00:30 | 191 | 191
2016-04-04 01:00 | 184 | 184
2016-04-04 01:30 | 179 | 178
2016-04-04 02:00 | 175 | 175
2016-04-04 02:30 | 174 | 174
2016-04-04 03:00 | 174 | 174
2016-04-04 03:30 | 175 | 175
2016-04-04 04:00 | 179 | 178
2016-04-04 04:30 | 183 | 183
2016-04-04 05:00 | 194 | 194
2016-04-04 05:30 | 210 | 210
2016-04-04 06:00 | 222 | 222
2016-04-04 06:30 | 236 | 233
2016-04-04 07:00 | 256 | 253
2016-04-04 07:30 | 264 | 262
2016-04-04 08:00 | 273 | 272
2016-04-04 08:30 | 280 | 279
2016-04-04 09:00 | 282 | 282
2016-04-04 09:30 | 283 | 282
2016-04-04 10:00 | 285 | 285
2016-04-04 10:30 | 284 | 283
2016-04-04 11:00 | 279 | 278
2016-04-04 11:30 | 275 | 275
2016-04-04 12:00 | 271 | 271
2016-04-04 12:30 | 272 | 271
2016-04-04 13:00 | 271 | 270
2016-04-04 13:30 | 280 | 280
2016-04-04 14:00 | 291 | 290
2016-04-04 14:30 | 297 | 297
2016-04-04 15:00 | 301 | 300
2016-04-04 15:30 | 302 | 301
2016-04-04 16:00 | 303 | 302
2016-04-04 16:30 | 311 | 310
2016-04-04 17:00 | 312 | 310
2016-04-04 17:30 | 315 | 313
2016-04-04 18:00 | 322 | 320
2016-04-04 18:30 | 318 | 316
2016-04-04 19:00 | 307 | 304
2016-04-04 19:30 | 305 | 302
2016-04-04 20:00 | 298 | 295
2016-04-04 20:30 | 277 | 274
2016-04-04 21:00 | 262 | 261
2016-04-04 21:30 | 252 | 250
2016-04-04 22:00 | 251 | 249
2016-04-04 22:30 | 242 | 241
2016-04-04 23:00 | 227 | 227
2016-04-04 23:30 | 214 | 213
2016-04-05 | 200 | 199
2016-04-05 00:30 | 192 | 191
2016-04-05 01:00 | 186 | 184
2016-04-05 01:30 | 179 | 177
2016-04-05 02:00 | 175 | 173
2016-04-05 02:30 | 172 | 170
2016-04-05 03:00 | 172 | 170
2016-04-05 03:30 | 173 | 170
2016-04-05 04:00 | 177 | 174
2016-04-05 04:30 | 181 | 179
2016-04-05 05:00 | 191 | 189
2016-04-05 05:30 | 203 | 202
2016-04-05 06:00 | 215 | 215
2016-04-05 06:30 | 226 | 225
2016-04-05 07:00 | 254 | 254
2016-04-05 07:30 | 263 | 262
2016-04-05 08:00 | 268 | 267
2016-04-05 08:30 | 270 | 270
2016-04-05 09:00 | 275 | 274
2016-04-05 09:30 | 276 | 276
2016-04-05 10:00 | 280 | 279
2016-04-05 10:30 | 275 | 274
2016-04-05 11:00 | 272 | 271
2016-04-05 11:30 | 272 | 272
2016-04-05 12:00 | 269 | 268
2016-04-05 12:30 | 266 | 266
2016-04-05 13:00 | 271 | 270
2016-04-05 13:30 | 275 | 274
2016-04-05 14:00 | 281 | 280
2016-04-05 14:30 | 286 | 285
2016-04-05 15:00 | 291 | 291
2016-04-05 15:30 | 293 | 292
2016-04-05 16:00 | 306 | 306
2016-04-05 16:30 | 311 | 311
2016-04-05 17:00 | 305 | 305
2016-04-05 17:30 | 308 | 308
2016-04-05 18:00 | 314 | 314
2016-04-05 18:30 | 311 | 311
2016-04-05 19:00 | 299 | 299
2016-04-05 19:30 | 297 | 297
2016-04-05 20:00 | 288 | 288
2016-04-05 20:30 | 273 | 273
2016-04-05 21:00 | 261 | 260
2016-04-05 21:30 | 251 | 250
2016-04-05 22:00 | 244 | 243
2016-04-05 22:30 | 238 | 238
2016-04-05 23:00 | 223 | 223
2016-04-05 23:30 | 207 | 205
2016-04-06 | 197 | 195
2016-04-06 00:30 | 190 | 188
2016-04-06 01:00 | 183 | 181
2016-04-06 01:30 | 176 | 175
2016-04-06 02:00 | 173 | 171
2016-04-06 02:30 | 170 | 169
2016-04-06 03:00 | 170 | 169
2016-04-06 03:30 | 171 | 169
2016-04-06 04:00 | 174 | 173
2016-04-06 04:30 | 179 | 178
2016-04-06 05:00 | 190 | 188
2016-04-06 05:30 | 201 | 199
2016-04-06 06:00 | 215 | 212
2016-04-06 06:30 | 227 | 226
2016-04-06 07:00 | 244 | 244
2016-04-06 07:30 | 261 | 260
2016-04-06 08:00 | 268 | 268
2016-04-06 08:30 | 270 | 270
2016-04-06 09:00 | 274 | 274
2016-04-06 09:30 | 276 | 275
2016-04-06 10:00 | 278 | 277
2016-04-06 10:30 | 276 | 276
2016-04-06 11:00 | 272 | 272
2016-04-06 11:30 | 270 | 269
2016-04-06 12:00 | 272 | 272
2016-04-06 12:30 | 276 | 276
2016-04-06 13:00 | 280 | 280
2016-04-06 13:30 | 284 | 284
2016-04-06 14:00 | 296 | 296
2016-04-06 14:30 | 298 | 297
2016-04-06 15:00 | 300 | 299
2016-04-06 15:30 | 304 | 304
2016-04-06 16:00 | 311 | 311
2016-04-06 16:30 | 319 | 319
2016-04-06 17:00 | 311 | 311
2016-04-06 17:30 | 309 | 309
2016-04-06 18:00 | 317 | 317
2016-04-06 18:30 | 312 | 312
2016-04-06 19:00 | 300 | 300
2016-04-06 19:30 | 299 | 299
2016-04-06 20:00 | 289 | 289
2016-04-06 20:30 | 279 | 279
2016-04-06 21:00 | 266 | 266
2016-04-06 21:30 | 253 | 251
2016-04-06 22:00 | 255 | 254
2016-04-06 22:30 | 245 | 244
2016-04-06 23:00 | 232 | 231
2016-04-06 23:30 | 220 | 219
2016-04-07 | 202 | 201
2016-04-07 00:30 | 192 | 192
2016-04-07 01:00 | 184 | 184
2016-04-07 01:30 | 182 | 182
2016-04-07 02:00 | 181 | 181
2016-04-07 02:30 | 179 | 179
2016-04-07 03:00 | 181 | 181
2016-04-07 03:30 | 184 | 183
2016-04-07 04:00 | 187 | 187
2016-04-07 04:30 | 189 | 188
2016-04-07 05:00 | 195 | 195
2016-04-07 05:30 | 202 | 202
2016-04-07 06:00 | 222 | 221
2016-04-07 06:30 | 241 | 241
2016-04-07 07:00 | 254 | 254
2016-04-07 07:30 | 266 | 266
2016-04-07 08:00 | 187 | 187
2016-04-07 08:30 | 187 | 186
2016-04-07 09:00 | 184 | 183
2016-04-07 09:30 | 185 | 184
2016-04-07 10:00 | 186 | 186
2016-04-07 10:30 | 184 | 183
2016-04-07 11:00 | 182 | 182
2016-04-07 11:30 | 184 | 183
2016-04-07 12:00 | 190 | 190
2016-04-07 12:30 | 193 | 193
2016-04-07 13:00 | 196 | 196
2016-04-07 13:30 | 199 | 199
2016-04-07 14:00 | 199 | 199
2016-04-07 14:30 | 202 | 202
2016-04-07 15:00 | 207 | 207
2016-04-07 15:30 | 211 | 211
2016-04-07 16:00 | 212 | 212
2016-04-07 16:30 | 214 | 214
2016-04-07 17:00 | 213 | 212
2016-04-07 17:30 | 216 | 216
2016-04-07 18:00 | 220 | 219
2016-04-07 18:30 | 216 | 216
2016-04-07 19:00 | 207 | 207
2016-04-07 19:30 | 207 | 207
2016-04-07 20:00 | 204 | 204
2016-04-07 20:30 | 196 | 196
2016-04-07 21:00 | 184 | 184
2016-04-07 21:30 | 174 | 173
2016-04-07 22:00 | 172 | 172
2016-04-07 22:30 | 163 | 163
2016-04-07 23:00 | 153 | 153
2016-04-07 23:30 | 147 | 147
2016-04-08 | 137 | 137
2016-04-08 00:30 | 132 | 132
2016-04-08 01:00 | 127 | 127
2016-04-08 01:30 | 123 | 123
2016-04-08 02:00 | 120 | 120
2016-04-08 02:30 | 119 | 119
2016-04-08 03:00 | 118 | 118
2016-04-08 03:30 | 119 | 119
2016-04-08 04:00 | 121 | 121
2016-04-08 04:30 | 124 | 124
2016-04-08 05:00 | 130 | 130
2016-04-08 05:30 | 133 | 133
2016-04-08 06:00 | 145 | 145
2016-04-08 06:30 | 158 | 158
2016-04-08 07:00 | 173 | 173
2016-04-08 07:30 | 184 | 184
2016-04-08 08:00 | 190 | 190
2016-04-08 08:30 | 194 | 193
2016-04-08 09:00 | 196 | 195
2016-04-08 09:30 | 201 | 201
2016-04-08 10:00 | 199 | 199
2016-04-08 10:30 | 200 | 200
2016-04-08 11:00 | 196 | 196
2016-04-08 11:30 | 198 | 198
2016-04-08 12:00 | 200 | 199
2016-04-08 12:30 | 195 | 195
2016-04-08 13:00 | 195 | 195
2016-04-08 13:30 | 197 | 197
2016-04-08 14:00 | 228 | 228
2016-04-08 14:30 | 291 | 291
2016-04-08 15:00 | 298 | 298
2016-04-08 15:30 | 305 | 304
2016-04-08 16:00 | 307 | 307
2016-04-08 16:30 | 313 | 313
2016-04-08 17:00 | 313 | 313
2016-04-08 17:30 | 307 | 307
2016-04-08 18:00 | 308 | 308
2016-04-08 18:30 | 304 | 304
2016-04-08 19:00 | 292 | 292
2016-04-08 19:30 | 291 | 290
2016-04-08 20:00 | 285 | 284
2016-04-08 20:30 | 278 | 277
2016-04-08 21:00 | 262 | 261
2016-04-08 21:30 | 249 | 248
2016-04-08 22:00 | 244 | 243
2016-04-08 22:30 | 233 | 233
2016-04-08 23:00 | 221 | 220
2016-04-08 23:30 | 211 | 211
2016-04-09 | 192 | 192
2016-04-09 00:30 | 179 | 179
2016-04-09 01:00 | 172 | 171
2016-04-09 01:30 | 169 | 168
2016-04-09 02:00 | 168 | 168
2016-04-09 02:30 | 167 | 166
2016-04-09 03:00 | 166 | 166
2016-04-09 03:30 | 165 | 165
2016-04-09 04:00 | 168 | 168
2016-04-09 04:30 | 172 | 172
2016-04-09 05:00 | 176 | 175
2016-04-09 05:30 | 179 | 178
2016-04-09 06:00 | 186 | 185
2016-04-09 06:30 | 196 | 196
2016-04-09 07:00 | 216 | 216
2016-04-09 07:30 | 224 | 223
2016-04-09 08:00 | 230 | 230
2016-04-09 08:30 | 241 | 241
2016-04-09 09:00 | 248 | 248
2016-04-09 09:30 | 250 | 250
2016-04-09 10:00 | 250 | 250
2016-04-09 10:30 | 253 | 253
2016-04-09 11:00 | 253 | 253
2016-04-09 11:30 | 252 | 252
2016-04-09 12:00 | 249 | 249
2016-04-09 12:30 | 249 | 249
2016-04-09 13:00 | 252 | 252
2016-04-09 13:30 | 255 | 254
2016-04-09 14:00 | 255 | 255
2016-04-09 14:30 | 259 | 259
2016-04-09 15:00 | 263 | 263
2016-04-09 15:30 | 266 | 266
2016-04-09 16:00 | 277 | 277
2016-04-09 16:30 | 289 | 289
2016-04-09 17:00 | 290 | 290
2016-04-09 17:30 | 295 | 295
2016-04-09 18:00 | 304 | 303
2016-04-09 18:30 | 297 | 297
2016-04-09 19:00 | 286 | 285
2016-04-09 19:30 | 284 | 283
2016-04-09 20:00 | 277 | 277
2016-04-09 20:30 | 264 | 263
2016-04-09 21:00 | 251 | 250
2016-04-09 21:30 | 243 | 242
2016-04-09 22:00 | 235 | 235
2016-04-09 22:30 | 227 | 227
2016-04-09 23:00 | 215 | 215
2016-04-09 23:30 | 202 | 202
2016-04-10 | 186 | 186
2016-04-10 00:30 | 178 | 178
2016-04-10 01:00 | 172 | 171
2016-04-10 01:30 | 165 | 165
2016-04-10 02:00 | 157 | 157
2016-04-10 02:30 | 155 | 155
2016-04-10 03:00 | 155 | 155
2016-04-10 03:30 | 154 | 154
2016-04-10 04:00 | 152 | 152
2016-04-10 04:30 | 154 | 154
2016-04-10 05:00 | 158 | 158
2016-04-10 05:30 | 161 | 161
2016-04-10 06:00 | 162 | 162
2016-04-10 06:30 | 176 | 175
2016-04-10 07:00 | 185 | 185
2016-04-10 07:30 | 196 | 196
2016-04-10 08:00 | 207 | 206
2016-04-10 08:30 | 211 | 210
2016-04-10 09:00 | 218 | 218
2016-04-10 09:30 | 222 | 222
2016-04-10 10:00 | 225 | 225
2016-04-10 10:30 | 225 | 225
2016-04-10 11:00 | 225 | 225
2016-04-10 11:30 | 224 | 224
2016-04-10 12:00 | 228 | 228
2016-04-10 12:30 | 228 | 228
2016-04-10 13:00 | 226 | 226
2016-04-10 13:30 | 231 | 231
2016-04-10 14:00 | 237 | 237
2016-04-10 14:30 | 244 | 244
2016-04-10 15:00 | 252 | 251
2016-04-10 15:30 | 262 | 261
2016-04-10 16:00 | 265 | 264
2016-04-10 16:30 | 275 | 274
2016-04-10 17:00 | 280 | 279
2016-04-10 17:30 | 291 | 291
2016-04-10 18:00 | 297 | 297
2016-04-10 18:30 | 293 | 292
2016-04-10 19:00 | 278 | 278
2016-04-10 19:30 | 272 | 272
2016-04-10 20:00 | 261 | 260
2016-04-10 20:30 | 248 | 248
2016-04-10 21:00 | 235 | 235
2016-04-10 21:30 | 228 | 228
2016-04-10 22:00 | 221 | 221
2016-04-10 22:30 | 213 | 213
2016-04-10 23:00 | 203 | 203
2016-04-10 23:30 | 195 | 194
2016-04-11 | 185 | 185
2016-04-11 00:30 | 174 | 174
2016-04-11 01:00 | 170 | 170
2016-04-11 01:30 | 167 | 167
2016-04-11 02:00 | 165 | 165
2016-04-11 02:30 | 158 | 158
2016-04-11 03:00 | 157 | 156
2016-04-11 03:30 | 157 | 157
2016-04-11 04:00 | 161 | 160
2016-04-11 04:30 | 164 | 164
2016-04-11 05:00 | 172 | 172
2016-04-11 05:30 | 177 | 176
2016-04-11 06:00 | 201 | 201
2016-04-11 06:30 | 222 | 222
2016-04-11 07:00 | 239 | 239
2016-04-11 07:30 | 254 | 254
2016-04-11 08:00 | 263 | 263
2016-04-11 08:30 | 273 | 273
2016-04-11 09:00 | 276 | 276
2016-04-11 09:30 | 278 | 278
2016-04-11 10:00 | 279 | 279
2016-04-11 10:30 | 277 | 277
2016-04-11 11:00 | 276 | 276
2016-04-11 11:30 | 273 | 272
2016-04-11 12:00 | 268 | 267
2016-04-11 12:30 | 270 | 270
2016-04-11 13:00 | 278 | 277
2016-04-11 13:30 | 280 | 280
2016-04-11 14:00 | 276 | 275
2016-04-11 14:30 | 276 | 275
2016-04-11 15:00 | 282 | 282
2016-04-11 15:30 | 286 | 286
2016-04-11 16:00 | 291 | 291
2016-04-11 16:30 | 300 | 300
2016-04-11 17:00 | 302 | 301
2016-04-11 17:30 | 313 | 313
2016-04-11 18:00 | 318 | 318
2016-04-11 18:30 | 316 | 316
2016-04-11 19:00 | 304 | 304
2016-04-11 19:30 | 298 | 298
2016-04-11 20:00 | 288 | 287
2016-04-11 20:30 | 271 | 270
2016-04-11 21:00 | 256 | 256
2016-04-11 21:30 | 241 | 241
2016-04-11 22:00 | 235 | 235
2016-04-11 22:30 | 224 | 224
2016-04-11 23:00 | 210 | 210
2016-04-11 23:30 | 193 | 193
2016-04-12 | 182 | 182
2016-04-12 00:30 | 174 | 174
2016-04-12 01:00 | 168 | 168
2016-04-12 01:30 | 162 | 162
2016-04-12 02:00 | 157 | 157
2016-04-12 02:30 | 155 | 155
2016-04-12 03:00 | 154 | 154
2016-04-12 03:30 | 155 | 154
2016-04-12 04:00 | 159 | 159
2016-04-12 04:30 | 165 | 165
2016-04-12 05:00 | 177 | 177
2016-04-12 05:30 | 193 | 193
2016-04-12 06:00 | 212 | 212
2016-04-12 06:30 | 233 | 233
2016-04-12 07:00 | 255 | 255
2016-04-12 07:30 | 268 | 267
2016-04-12 08:00 | 271 | 270
2016-04-12 08:30 | 268 | 267
2016-04-12 09:00 | 270 | 270
2016-04-12 09:30 | 274 | 273
2016-04-12 10:00 | 273 | 272
2016-04-12 10:30 | 268 | 268
2016-04-12 11:00 | 269 | 268
2016-04-12 11:30 | 269 | 269
2016-04-12 12:00 | 265 | 264
2016-04-12 12:30 | 262 | 262
2016-04-12 13:00 | 260 | 259
2016-04-12 13:30 | 259 | 258
2016-04-12 14:00 | 257 | 256
2016-04-12 14:30 | 257 | 257
2016-04-12 15:00 | 266 | 265
2016-04-12 15:30 | 274 | 273
2016-04-12 16:00 | 279 | 278
2016-04-12 16:30 | 287 | 286
2016-04-12 17:00 | 293 | 292
2016-04-12 17:30 | 299 | 298
2016-04-12 18:00 | 300 | 299
2016-04-12 18:30 | 298 | 298
2016-04-12 19:00 | 287 | 287
2016-04-12 19:30 | 283 | 282
2016-04-12 20:00 | 273 | 272
2016-04-12 20:30 | 257 | 257
2016-04-12 21:00 | 244 | 243
2016-04-12 21:30 | 230 | 230
2016-04-12 22:00 | 226 | 226
2016-04-12 22:30 | 219 | 218
2016-04-12 23:00 | 204 | 204
2016-04-12 23:30 | 190 | 190
2016-04-13 | 175 | 175
2016-04-13 00:30 | 167 | 167
2016-04-13 01:00 | 160 | 160
2016-04-13 01:30 | 154 | 154
2016-04-13 02:00 | 151 | 151
2016-04-13 02:30 | 148 | 148
2016-04-13 03:00 | 148 | 148
2016-04-13 03:30 | 149 | 149
2016-04-13 04:00 | 153 | 153
2016-04-13 04:30 | 159 | 159
2016-04-13 05:00 | 170 | 170
2016-04-13 05:30 | 184 | 183
2016-04-13 06:00 | 205 | 205
2016-04-13 06:30 | 223 | 223
2016-04-13 07:00 | 240 | 240
2016-04-13 07:30 | 247 | 247
2016-04-13 08:00 | 249 | 249
2016-04-13 08:30 | 186 | 186
2016-04-13 09:00 | 169 | 169
2016-04-13 09:30 | 168 | 167
2016-04-13 10:00 | 168 | 167
2016-04-13 10:30 | 168 | 167
2016-04-13 11:00 | 169 | 169
2016-04-13 11:30 | 169 | 168
2016-04-13 12:00 | 167 | 167
2016-04-13 12:30 | 166 | 165
2016-04-13 13:00 | 168 | 168
2016-04-13 13:30 | 175 | 175
2016-04-13 14:00 | 180 | 179
2016-04-13 14:30 | 179 | 179
2016-04-13 15:00 | 180 | 179
2016-04-13 15:30 | 183 | 182
2016-04-13 16:00 | 188 | 188
2016-04-13 16:30 | 193 | 192
2016-04-13 17:00 | 195 | 194
2016-04-13 17:30 | 200 | 199
2016-04-13 18:00 | 202 | 201
2016-04-13 18:30 | 201 | 200
2016-04-13 19:00 | 193 | 192
2016-04-13 19:30 | 187 | 187
2016-04-13 20:00 | 182 | 182
2016-04-13 20:30 | 174 | 173
2016-04-13 21:00 | 164 | 164
2016-04-13 21:30 | 156 | 155
2016-04-13 22:00 | 150 | 150
2016-04-13 22:30 | 145 | 145
2016-04-13 23:00 | 137 | 137
2016-04-13 23:30 | 127 | 127
2016-04-14 | 117 | 117
2016-04-14 00:30 | 112 | 112
2016-04-14 01:00 | 108 | 108
2016-04-14 01:30 | 103 | 103
2016-04-14 02:00 | 100 | 100
2016-04-14 02:30 | 99 | 99
2016-04-14 03:00 | 99 | 99
2016-04-14 03:30 | 101 | 101
2016-04-14 04:00 | 103 | 103
2016-04-14 04:30 | 106 | 106
2016-04-14 05:00 | 114 | 114
2016-04-14 05:30 | 125 | 125
2016-04-14 06:00 | 141 | 140
2016-04-14 06:30 | 154 | 154
2016-04-14 07:00 | 169 | 169
2016-04-14 07:30 | 176 | 176
2016-04-14 08:00 | 176 | 175
2016-04-14 08:30 | 173 | 173
2016-04-14 09:00 | 177 | 177
2016-04-14 09:30 | 177 | 176
2016-04-14 10:00 | 177 | 177
2016-04-14 10:30 | 174 | 174
2016-04-14 11:00 | 173 | 173
2016-04-14 11:30 | 175 | 175
2016-04-14 12:00 | 175 | 175
2016-04-14 12:30 | 172 | 172
2016-04-14 13:00 | 166 | 166
2016-04-14 13:30 | 168 | 167
2016-04-14 14:00 | 168 | 168
2016-04-14 14:30 | 195 | 195
2016-04-14 15:00 | 254 | 253
2016-04-14 15:30 | 261 | 261
2016-04-14 16:00 | 270 | 270
2016-04-14 16:30 | 278 | 278
2016-04-14 17:00 | 283 | 282
2016-04-14 17:30 | 293 | 292
2016-04-14 18:00 | 298 | 297
2016-04-14 18:30 | 298 | 297
2016-04-14 19:00 | 286 | 286
2016-04-14 19:30 | 282 | 281
2016-04-14 20:00 | 273 | 273
2016-04-14 20:30 | 256 | 256
2016-04-14 21:00 | 241 | 241
2016-04-14 21:30 | 227 | 227
2016-04-14 22:00 | 221 | 221
2016-04-14 22:30 | 213 | 213
2016-04-14 23:00 | 201 | 201
2016-04-14 23:30 | 187 | 187
2016-04-15 | 172 | 172
2016-04-15 00:30 | 164 | 164
2016-04-15 01:00 | 158 | 158
2016-04-15 01:30 | 151 | 151
2016-04-15 02:00 | 146 | 146
2016-04-15 02:30 | 144 | 144
2016-04-15 03:00 | 144 | 144
2016-04-15 03:30 | 144 | 144
2016-04-15 04:00 | 147 | 147
2016-04-15 04:30 | 153 | 153
2016-04-15 05:00 | 164 | 164
2016-04-15 05:30 | 179 | 179
2016-04-15 06:00 | 198 | 198
2016-04-15 06:30 | 217 | 217
2016-04-15 07:00 | 236 | 234
2016-04-15 07:30 | 241 | 240
2016-04-15 08:00 | 242 | 241
2016-04-15 08:30 | 241 | 240
2016-04-15 09:00 | 249 | 249
2016-04-15 09:30 | 268 | 268
2016-04-15 10:00 | 263 | 263
2016-04-15 10:30 | 266 | 266
2016-04-15 11:00 | 272 | 272
2016-04-15 11:30 | 266 | 266
2016-04-15 12:00 | 254 | 254
2016-04-15 12:30 | 249 | 249
2016-04-15 13:00 | 245 | 245
2016-04-15 13:30 | 236 | 236
2016-04-15 14:00 | 237 | 237
2016-04-15 14:30 | 239 | 239
2016-04-15 15:00 | 242 | 242
2016-04-15 15:30 | 248 | 248
2016-04-15 16:00 | 254 | 254
2016-04-15 16:30 | 261 | 261
2016-04-15 17:00 | 266 | 265
2016-04-15 17:30 | 272 | 271
2016-04-15 18:00 | 272 | 271
2016-04-15 18:30 | 271 | 270
2016-04-15 19:00 | 260 | 260
2016-04-15 19:30 | 264 | 263
2016-04-15 20:00 | 261 | 260
2016-04-15 20:30 | 248 | 247
2016-04-15 21:00 | 237 | 237
2016-04-15 21:30 | 227 | 227
2016-04-15 22:00 | 226 | 225
2016-04-15 22:30 | 221 | 220
2016-04-15 23:00 | 210 | 209
2016-04-15 23:30 | 194 | 193
2016-04-16 | 177 | 177
2016-04-16 00:30 | 169 | 169
2016-04-16 01:00 | 161 | 161
2016-04-16 01:30 | 154 | 154
2016-04-16 02:00 | 150 | 150
2016-04-16 02:30 | 148 | 148
2016-04-16 03:00 | 146 | 146
2016-04-16 03:30 | 146 | 146
2016-04-16 04:00 | 147 | 147
2016-04-16 04:30 | 149 | 149
2016-04-16 05:00 | 155 | 155
2016-04-16 05:30 | 161 | 161
2016-04-16 06:00 | 170 | 170
2016-04-16 06:30 | 183 | 183
2016-04-16 07:00 | 197 | 197
2016-04-16 07:30 | 208 | 207
2016-04-16 08:00 | 219 | 219
2016-04-16 08:30 | 226 | 225
2016-04-16 09:00 | 224 | 224
2016-04-16 09:30 | 227 | 227
2016-04-16 10:00 | 229 | 229
2016-04-16 10:30 | 225 | 224
2016-04-16 11:00 | 220 | 219
2016-04-16 11:30 | 219 | 219
2016-04-16 12:00 | 220 | 219
2016-04-16 12:30 | 224 | 223
2016-04-16 13:00 | 226 | 226
2016-04-16 13:30 | 229 | 229
2016-04-16 14:00 | 229 | 229
2016-04-16 14:30 | 231 | 231
2016-04-16 15:00 | 237 | 237
2016-04-16 15:30 | 242 | 241
2016-04-16 16:00 | 248 | 247
2016-04-16 16:30 | 252 | 251
2016-04-16 17:00 | 259 | 258
2016-04-16 17:30 | 267 | 267
2016-04-16 18:00 | 268 | 268
2016-04-16 18:30 | 267 | 266
2016-04-16 19:00 | 257 | 257
2016-04-16 19:30 | 254 | 253
2016-04-16 20:00 | 248 | 247
2016-04-16 20:30 | 237 | 236
2016-04-16 21:00 | 226 | 226
2016-04-16 21:30 | 219 | 219
2016-04-16 22:00 | 220 | 220
2016-04-16 22:30 | 217 | 217
2016-04-16 23:00 | 207 | 207
2016-04-16 23:30 | 192 | 192
2016-04-17 | 176 | 176
2016-04-17 00:30 | 168 | 167
2016-04-17 01:00 | 161 | 161
2016-04-17 01:30 | 153 | 153
2016-04-17 02:00 | 149 | 149
2016-04-17 02:30 | 147 | 147
2016-04-17 03:00 | 146 | 146
2016-04-17 03:30 | 145 | 145
2016-04-17 04:00 | 146 | 146
2016-04-17 04:30 | 147 | 147
2016-04-17 05:00 | 151 | 151
2016-04-17 05:30 | 156 | 156
2016-04-17 06:00 | 161 | 161
2016-04-17 06:30 | 167 | 167
2016-04-17 07:00 | 178 | 178
2016-04-17 07:30 | 187 | 187
2016-04-17 08:00 | 194 | 194
2016-04-17 08:30 | 202 | 202
2016-04-17 09:00 | 205 | 205
2016-04-17 09:30 | 204 | 204
2016-04-17 10:00 | 206 | 206
2016-04-17 10:30 | 203 | 203
2016-04-17 11:00 | 201 | 200
2016-04-17 11:30 | 204 | 204
2016-04-17 12:00 | 200 | 200
2016-04-17 12:30 | 201 | 201
2016-04-17 13:00 | 203 | 203
2016-04-17 13:30 | 207 | 207
2016-04-17 14:00 | 212 | 211
2016-04-17 14:30 | 218 | 217
2016-04-17 15:00 | 224 | 224
2016-04-17 15:30 | 233 | 233
2016-04-17 16:00 | 243 | 243
2016-04-17 16:30 | 252 | 252
2016-04-17 17:00 | 261 | 261
2016-04-17 17:30 | 275 | 275
2016-04-17 18:00 | 280 | 279
2016-04-17 18:30 | 277 | 277
2016-04-17 19:00 | 266 | 265
2016-04-17 19:30 | 259 | 258
2016-04-17 20:00 | 253 | 251
2016-04-17 20:30 | 240 | 238
2016-04-17 21:00 | 226 | 226
2016-04-17 21:30 | 216 | 215
2016-04-17 22:00 | 214 | 214
2016-04-17 22:30 | 208 | 208
2016-04-17 23:00 | 198 | 198
2016-04-17 23:30 | 184 | 184
2016-04-18 | 169 | 169
2016-04-18 00:30 | 161 | 161
2016-04-18 01:00 | 154 | 153
2016-04-18 01:30 | 149 | 148
2016-04-18 02:00 | 146 | 145
2016-04-18 02:30 | 144 | 144
2016-04-18 03:00 | 144 | 144
2016-04-18 03:30 | 146 | 145
2016-04-18 04:00 | 150 | 150
2016-04-18 04:30 | 155 | 155
2016-04-18 05:00 | 167 | 167
2016-04-18 05:30 | 182 | 182
2016-04-18 06:00 | 204 | 204
2016-04-18 06:30 | 223 | 222
2016-04-18 07:00 | 241 | 240
2016-04-18 07:30 | 246 | 246
2016-04-18 08:00 | 245 | 245
2016-04-18 08:30 | 245 | 245
2016-04-18 09:00 | 245 | 245
2016-04-18 09:30 | 244 | 244
2016-04-18 10:00 | 246 | 246
2016-04-18 10:30 | 246 | 246
2016-04-18 11:00 | 247 | 247
2016-04-18 11:30 | 251 | 251
2016-04-18 12:00 | 251 | 251
2016-04-18 12:30 | 256 | 256
2016-04-18 13:00 | 263 | 262
2016-04-18 13:30 | 265 | 265
2016-04-18 14:00 | 265 | 265
2016-04-18 14:30 | 263 | 263
2016-04-18 15:00 | 268 | 268
2016-04-18 15:30 | 275 | 274
2016-04-18 16:00 | 282 | 282
2016-04-18 16:30 | 291 | 290
2016-04-18 17:00 | 296 | 295
2016-04-18 17:30 | 305 | 304
2016-04-18 18:00 | 306 | 306
2016-04-18 18:30 | 302 | 302
2016-04-18 19:00 | 289 | 289
2016-04-18 19:30 | 284 | 283
2016-04-18 20:00 | 272 | 272
2016-04-18 20:30 | 256 | 256
2016-04-18 21:00 | 245 | 245
2016-04-18 21:30 | 231 | 231
2016-04-18 22:00 | 227 | 227
2016-04-18 22:30 | 220 | 220
2016-04-18 23:00 | 208 | 208
2016-04-18 23:30 | 192 | 192
2016-04-19 | 176 | 176
2016-04-19 00:30 | 167 | 167
2016-04-19 01:00 | 160 | 160
2016-04-19 01:30 | 153 | 153
2016-04-19 02:00 | 149 | 149
2016-04-19 02:30 | 147 | 147
2016-04-19 03:00 | 147 | 147
2016-04-19 03:30 | 148 | 148
2016-04-19 04:00 | 152 | 152
2016-04-19 04:30 | 158 | 158
2016-04-19 05:00 | 170 | 170
2016-04-19 05:30 | 185 | 185
2016-04-19 06:00 | 206 | 205
2016-04-19 06:30 | 227 | 226
2016-04-19 07:00 | 242 | 241
2016-04-19 07:30 | 246 | 246
2016-04-19 08:00 | 247 | 247
2016-04-19 08:30 | 245 | 245
2016-04-19 09:00 | 252 | 252
2016-04-19 09:30 | 249 | 248
2016-04-19 10:00 | 244 | 244
2016-04-19 10:30 | 242 | 242
2016-04-19 11:00 | 241 | 241
2016-04-19 11:30 | 239 | 239
2016-04-19 12:00 | 242 | 242
2016-04-19 12:30 | 243 | 242
2016-04-19 13:00 | 248 | 248
2016-04-19 13:30 | 255 | 255
2016-04-19 14:00 | 265 | 265
2016-04-19 14:30 | 265 | 265
2016-04-19 15:00 | 270 | 270
2016-04-19 15:30 | 271 | 271
2016-04-19 16:00 | 271 | 271
2016-04-19 16:30 | 275 | 275
2016-04-19 17:00 | 279 | 279
2016-04-19 17:30 | 289 | 289
2016-04-19 18:00 | 290 | 290
2016-04-19 18:30 | 288 | 288
2016-04-19 19:00 | 276 | 276
2016-04-19 19:30 | 272 | 272
2016-04-19 20:00 | 263 | 263
2016-04-19 20:30 | 248 | 247
2016-04-19 21:00 | 233 | 233
2016-04-19 21:30 | 220 | 220
2016-04-19 22:00 | 215 | 214
2016-04-19 22:30 | 208 | 207
2016-04-19 23:00 | 195 | 195
2016-04-19 23:30 | 180 | 180
2016-04-20 | 167 | 166
2016-04-20 00:30 | 159 | 158
2016-04-20 01:00 | 152 | 152
2016-04-20 01:30 | 146 | 145
2016-04-20 02:00 | 142 | 141
2016-04-20 02:30 | 139 | 139
2016-04-20 03:00 | 139 | 139
2016-04-20 03:30 | 140 | 140
2016-04-20 04:00 | 144 | 144
2016-04-20 04:30 | 149 | 149
2016-04-20 05:00 | 161 | 161
2016-04-20 05:30 | 176 | 175
2016-04-20 06:00 | 196 | 195
2016-04-20 06:30 | 216 | 216
2016-04-20 07:00 | 233 | 232
2016-04-20 07:30 | 236 | 236
2016-04-20 08:00 | 258 | 258
2016-04-20 08:30 | 258 | 258
2016-04-20 09:00 | 259 | 259
2016-04-20 09:30 | 259 | 258
2016-04-20 10:00 | 261 | 261
2016-04-20 10:30 | 262 | 262
2016-04-20 11:00 | 266 | 266
2016-04-20 11:30 | 273 | 272
2016-04-20 12:00 | 273 | 272
2016-04-20 12:30 | 269 | 268
2016-04-20 13:00 | 270 | 269
2016-04-20 13:30 | 276 | 275
2016-04-20 14:00 | 281 | 280
2016-04-20 14:30 | 285 | 284
2016-04-20 15:00 | 293 | 292
2016-04-20 15:30 | 301 | 300
2016-04-20 16:00 | 310 | 309
2016-04-20 16:30 | 306 | 305
2016-04-20 17:00 | 289 | 287
2016-04-20 17:30 | 295 | 293
2016-04-20 18:00 | 296 | 294
2016-04-20 18:30 | 294 | 293
2016-04-20 19:00 | 283 | 281
2016-04-20 19:30 | 275 | 274
2016-04-20 20:00 | 268 | 267
2016-04-20 20:30 | 253 | 252
2016-04-20 21:00 | 238 | 238
2016-04-20 21:30 | 225 | 225
2016-04-20 22:00 | 220 | 220
2016-04-20 22:30 | 212 | 212
2016-04-20 23:00 | 199 | 199
2016-04-20 23:30 | 185 | 185
2016-04-21 | 170 | 170
2016-04-21 00:30 | 162 | 161
2016-04-21 01:00 | 155 | 154
2016-04-21 01:30 | 149 | 148
2016-04-21 02:00 | 145 | 145
2016-04-21 02:30 | 143 | 142
2016-04-21 03:00 | 143 | 142
2016-04-21 03:30 | 144 | 143
2016-04-21 04:00 | 147 | 147
2016-04-21 04:30 | 152 | 152
2016-04-21 05:00 | 163 | 162
2016-04-21 05:30 | 177 | 177
2016-04-21 06:00 | 201 | 200
2016-04-21 06:30 | 218 | 217
2016-04-21 07:00 | 234 | 234
2016-04-21 07:30 | 243 | 243
2016-04-21 08:00 | 270 | 269
2016-04-21 08:30 | 266 | 265
2016-04-21 09:00 | 267 | 267
2016-04-21 09:30 | 266 | 266
2016-04-21 10:00 | 271 | 271
2016-04-21 10:30 | 278 | 278
2016-04-21 11:00 | 279 | 279
2016-04-21 11:30 | 285 | 285
2016-04-21 12:00 | 284 | 284
2016-04-21 12:30 | 286 | 286
2016-04-21 13:00 | 283 | 283
2016-04-21 13:30 | 284 | 284
2016-04-21 14:00 | 284 | 284
2016-04-21 14:30 | 289 | 289
2016-04-21 15:00 | 290 | 289
2016-04-21 15:30 | 285 | 285
2016-04-21 16:00 | 271 | 270
2016-04-21 16:30 | 278 | 277
2016-04-21 17:00 | 282 | 281
2016-04-21 17:30 | 291 | 291
2016-04-21 18:00 | 293 | 293
2016-04-21 18:30 | 293 | 292
2016-04-21 19:00 | 282 | 281
2016-04-21 19:30 | 279 | 278
2016-04-21 20:00 | 271 | 270
2016-04-21 20:30 | 256 | 256
2016-04-21 21:00 | 242 | 242
2016-04-21 21:30 | 228 | 228
2016-04-21 22:00 | 222 | 221
2016-04-21 22:30 | 213 | 213
2016-04-21 23:00 | 200 | 200
2016-04-21 23:30 | 185 | 185
2016-04-22 | 170 | 170
2016-04-22 00:30 | 162 | 162
2016-04-22 01:00 | 156 | 156
2016-04-22 01:30 | 150 | 149
2016-04-22 02:00 | 145 | 145
2016-04-22 02:30 | 144 | 143
2016-04-22 03:00 | 143 | 143
2016-04-22 03:30 | 144 | 143
2016-04-22 04:00 | 147 | 147
2016-04-22 04:30 | 153 | 152
2016-04-22 05:00 | 164 | 164
2016-04-22 05:30 | 177 | 177
2016-04-22 06:00 | 194 | 194
2016-04-22 06:30 | 215 | 215
2016-04-22 07:00 | 233 | 232
2016-04-22 07:30 | 239 | 238
2016-04-22 08:00 | 242 | 242
2016-04-22 08:30 | 242 | 242
2016-04-22 09:00 | 245 | 245
2016-04-22 09:30 | 243 | 242
2016-04-22 10:00 | 241 | 241
2016-04-22 10:30 | 242 | 241
2016-04-22 11:00 | 243 | 243
2016-04-22 11:30 | 243 | 243
2016-04-22 12:00 | 242 | 241
2016-04-22 12:30 | 240 | 239
2016-04-22 13:00 | 241 | 240
2016-04-22 13:30 | 244 | 244
2016-04-22 14:00 | 248 | 247
2016-04-22 14:30 | 251 | 250
2016-04-22 15:00 | 255 | 254
2016-04-22 15:30 | 263 | 262
2016-04-22 16:00 | 272 | 271
2016-04-22 16:30 | 275 | 274
2016-04-22 17:00 | 274 | 273
2016-04-22 17:30 | 283 | 282
2016-04-22 18:00 | 281 | 281
2016-04-22 18:30 | 280 | 279
2016-04-22 19:00 | 269 | 268
2016-04-22 19:30 | 269 | 268
2016-04-22 20:00 | 262 | 261
2016-04-22 20:30 | 251 | 251
2016-04-22 21:00 | 240 | 240
2016-04-22 21:30 | 234 | 233
2016-04-22 22:00 | 234 | 234
2016-04-22 22:30 | 227 | 227
2016-04-22 23:00 | 212 | 212
2016-04-22 23:30 | 202 | 202
2016-04-23 | 186 | 186
2016-04-23 00:30 | 174 | 173
2016-04-23 01:00 | 163 | 163
2016-04-23 01:30 | 162 | 162
2016-04-23 02:00 | 161 | 160
2016-04-23 02:30 | 158 | 157
2016-04-23 03:00 | 157 | 156
2016-04-23 03:30 | 155 | 154
2016-04-23 04:00 | 154 | 152
2016-04-23 04:30 | 156 | 155
2016-04-23 05:00 | 159 | 158
2016-04-23 05:30 | 162 | 161
2016-04-23 06:00 | 170 | 169
2016-04-23 06:30 | 181 | 181
2016-04-23 07:00 | 196 | 196
2016-04-23 07:30 | 203 | 203
2016-04-23 08:00 | 211 | 211
2016-04-23 08:30 | 214 | 213
2016-04-23 09:00 | 218 | 218
2016-04-23 09:30 | 219 | 218
2016-04-23 10:00 | 215 | 215
2016-04-23 10:30 | 216 | 216
2016-04-23 11:00 | 216 | 216
2016-04-23 11:30 | 213 | 213
2016-04-23 12:00 | 213 | 213
2016-04-23 12:30 | 213 | 213
2016-04-23 13:00 | 211 | 211
2016-04-23 13:30 | 210 | 210
2016-04-23 14:00 | 212 | 212
2016-04-23 14:30 | 216 | 216
2016-04-23 15:00 | 221 | 221
2016-04-23 15:30 | 227 | 227
2016-04-23 16:00 | 236 | 236
2016-04-23 16:30 | 243 | 243
2016-04-23 17:00 | 251 | 251
2016-04-23 17:30 | 257 | 257
2016-04-23 18:00 | 257 | 257
2016-04-23 18:30 | 254 | 254
2016-04-23 19:00 | 243 | 243
2016-04-23 19:30 | 244 | 244
2016-04-23 20:00 | 239 | 239
2016-04-23 20:30 | 228 | 228
2016-04-23 21:00 | 223 | 223
2016-04-23 21:30 | 215 | 215
2016-04-23 22:00 | 207 | 207
2016-04-23 22:30 | 202 | 202
2016-04-23 23:00 | 196 | 196
2016-04-23 23:30 | 186 | 185
2016-04-24 | 165 | 165
2016-04-24 00:30 | 156 | 155
2016-04-24 01:00 | 151 | 150
2016-04-24 01:30 | 147 | 146
2016-04-24 02:00 | 146 | 144
2016-04-24 02:30 | 144 | 142
2016-04-24 03:00 | 144 | 143
2016-04-24 03:30 | 144 | 144
2016-04-24 04:00 | 147 | 147
2016-04-24 04:30 | 152 | 152
2016-04-24 05:00 | 155 | 155
2016-04-24 05:30 | 158 | 158
2016-04-24 06:00 | 164 | 164
2016-04-24 06:30 | 175 | 175
2016-04-24 07:00 | 186 | 186
2016-04-24 07:30 | 192 | 192
2016-04-24 08:00 | 198 | 198
2016-04-24 08:30 | 200 | 199
2016-04-24 09:00 | 203 | 202
2016-04-24 09:30 | 203 | 203
2016-04-24 10:00 | 205 | 205
2016-04-24 10:30 | 203 | 203
2016-04-24 11:00 | 197 | 197
2016-04-24 11:30 | 202 | 202
2016-04-24 12:00 | 199 | 199
2016-04-24 12:30 | 202 | 201
2016-04-24 13:00 | 202 | 202
2016-04-24 13:30 | 203 | 203
2016-04-24 14:00 | 201 | 201
2016-04-24 14:30 | 209 | 209
2016-04-24 15:00 | 219 | 219
2016-04-24 15:30 | 227 | 227
2016-04-24 16:00 | 221 | 221
2016-04-24 16:30 | 228 | 228
2016-04-24 17:00 | 238 | 238
2016-04-24 17:30 | 253 | 253
2016-04-24 18:00 | 257 | 256
2016-04-24 18:30 | 255 | 254
2016-04-24 19:00 | 247 | 246
2016-04-24 19:30 | 246 | 244
2016-04-24 20:00 | 243 | 242
2016-04-24 20:30 | 230 | 229
2016-04-24 21:00 | 225 | 225
2016-04-24 21:30 | 214 | 214
2016-04-24 22:00 | 210 | 210
2016-04-24 22:30 | 206 | 206
2016-04-24 23:00 | 200 | 200
2016-04-24 23:30 | 191 | 190
2016-04-25 | 173 | 173
2016-04-25 00:30 | 159 | 158
2016-04-25 01:00 | 151 | 151
2016-04-25 01:30 | 148 | 148
2016-04-25 02:00 | 147 | 147
2016-04-25 02:30 | 149 | 149
2016-04-25 03:00 | 146 | 146
2016-04-25 03:30 | 142 | 141
2016-04-25 04:00 | 142 | 142
2016-04-25 04:30 | 147 | 147
2016-04-25 05:00 | 150 | 150
2016-04-25 05:30 | 154 | 154
2016-04-25 06:00 | 160 | 160
2016-04-25 06:30 | 168 | 168
2016-04-25 07:00 | 177 | 177
2016-04-25 07:30 | 182 | 182
2016-04-25 08:00 | 189 | 189
2016-04-25 08:30 | 195 | 195
2016-04-25 09:00 | 203 | 203
2016-04-25 09:30 | 202 | 202
2016-04-25 10:00 | 199 | 199
2016-04-25 10:30 | 198 | 197
2016-04-25 11:00 | 202 | 201
2016-04-25 11:30 | 202 | 202
2016-04-25 12:00 | 198 | 197
2016-04-25 12:30 | 195 | 195
2016-04-25 13:00 | 199 | 198
2016-04-25 13:30 | 197 | 196
2016-04-25 14:00 | 206 | 205
2016-04-25 14:30 | 214 | 213
2016-04-25 15:00 | 213 | 213
2016-04-25 15:30 | 216 | 216
2016-04-25 16:00 | 229 | 229
2016-04-25 16:30 | 244 | 243
2016-04-25 17:00 | 257 | 255
2016-04-25 17:30 | 270 | 269
2016-04-25 18:00 | 269 | 269
2016-04-25 18:30 | 266 | 266
2016-04-25 19:00 | 256 | 255
2016-04-25 19:30 | 249 | 249
2016-04-25 20:00 | 244 | 243
2016-04-25 20:30 | 230 | 230
2016-04-25 21:00 | 219 | 219
2016-04-25 21:30 | 211 | 210
2016-04-25 22:00 | 210 | 209
2016-04-25 22:30 | 205 | 205
2016-04-25 23:00 | 197 | 197
2016-04-25 23:30 | 185 | 185
2016-04-26 | 172 | 172
2016-04-26 00:30 | 165 | 165
2016-04-26 01:00 | 158 | 158
2016-04-26 01:30 | 151 | 151
2016-04-26 02:00 | 147 | 147
2016-04-26 02:30 | 146 | 145
2016-04-26 03:00 | 145 | 145
2016-04-26 03:30 | 146 | 146
2016-04-26 04:00 | 149 | 149
2016-04-26 04:30 | 155 | 155
2016-04-26 05:00 | 167 | 166
2016-04-26 05:30 | 183 | 183
2016-04-26 06:00 | 206 | 206
2016-04-26 06:30 | 227 | 226
2016-04-26 07:00 | 244 | 244
2016-04-26 07:30 | 250 | 250
2016-04-26 08:00 | 247 | 247
2016-04-26 08:30 | 244 | 244
2016-04-26 09:00 | 247 | 247
2016-04-26 09:30 | 245 | 245
2016-04-26 10:00 | 240 | 239
2016-04-26 10:30 | 231 | 231
2016-04-26 11:00 | 228 | 227
2016-04-26 11:30 | 229 | 228
2016-04-26 12:00 | 238 | 237
2016-04-26 12:30 | 233 | 233
2016-04-26 13:00 | 232 | 231
2016-04-26 13:30 | 231 | 230
2016-04-26 14:00 | 242 | 241
2016-04-26 14:30 | 249 | 249
2016-04-26 15:00 | 251 | 250
2016-04-26 15:30 | 258 | 257
2016-04-26 16:00 | 262 | 261
2016-04-26 16:30 | 267 | 266
2016-04-26 17:00 | 276 | 275
2016-04-26 17:30 | 290 | 289
2016-04-26 18:00 | 286 | 285
2016-04-26 18:30 | 279 | 278
2016-04-26 19:00 | 264 | 264
2016-04-26 19:30 | 254 | 254
2016-04-26 20:00 | 246 | 246
2016-04-26 20:30 | 239 | 238
2016-04-26 21:00 | 228 | 227
2016-04-26 21:30 | 215 | 215
2016-04-26 22:00 | 220 | 220
2016-04-26 22:30 | 209 | 209
2016-04-26 23:00 | 201 | 201
2016-04-26 23:30 | 185 | 185
2016-04-27 | 161 | 161
2016-04-27 00:30 | 149 | 149
2016-04-27 01:00 | 134 | 134
2016-04-27 01:30 | 128 | 128
2016-04-27 02:00 | 133 | 133
2016-04-27 02:30 | 120 | 120
2016-04-27 03:00 | 130 | 130
2016-04-27 03:30 | 121 | 121
2016-04-27 04:00 | 149 | 149
2016-04-27 04:30 | 160 | 160
2016-04-27 05:00 | 171 | 171
2016-04-27 05:30 | 186 | 186
2016-04-27 06:00 | 201 | 200
2016-04-27 06:30 | 218 | 218
2016-04-27 07:00 | 226 | 225
2016-04-27 07:30 | 234 | 234
2016-04-27 08:00 | 235 | 235
2016-04-27 08:30 | 238 | 238
2016-04-27 09:00 | 239 | 239
2016-04-27 09:30 | 242 | 242
2016-04-27 10:00 | 245 | 245
2016-04-27 10:30 | 245 | 245
2016-04-27 11:00 | 239 | 239
2016-04-27 11:30 | 241 | 241
2016-04-27 12:00 | 238 | 237
2016-04-27 12:30 | 235 | 234
2016-04-27 13:00 | 238 | 237
2016-04-27 13:30 | 240 | 239
2016-04-27 14:00 | 241 | 240
2016-04-27 14:30 | 242 | 241
2016-04-27 15:00 | 247 | 246
2016-04-27 15:30 | 257 | 256
2016-04-27 16:00 | 264 | 262
2016-04-27 16:30 | 267 | 266
2016-04-27 17:00 | 281 | 280
2016-04-27 17:30 | 290 | 289
2016-04-27 18:00 | 283 | 282
2016-04-27 18:30 | 275 | 274
2016-04-27 19:00 | 266 | 265
2016-04-27 19:30 | 267 | 267
2016-04-27 20:00 | 264 | 263
2016-04-27 20:30 | 247 | 247
2016-04-27 21:00 | 236 | 236
2016-04-27 21:30 | 222 | 222
2016-04-27 22:00 | 225 | 224
2016-04-27 22:30 | 220 | 219
2016-04-27 23:00 | 211 | 210
2016-04-27 23:30 | 195 | 194
2016-04-28 | 179 | 178
2016-04-28 00:30 | 170 | 168
2016-04-28 01:00 | 161 | 159
2016-04-28 01:30 | 156 | 153
2016-04-28 02:00 | 152 | 150
2016-04-28 02:30 | 150 | 149
2016-04-28 03:00 | 150 | 149
2016-04-28 03:30 | 152 | 151
2016-04-28 04:00 | 156 | 155
2016-04-28 04:30 | 162 | 161
2016-04-28 05:00 | 173 | 173
2016-04-28 05:30 | 185 | 185
2016-04-28 06:00 | 207 | 207
2016-04-28 06:30 | 230 | 229
2016-04-28 07:00 | 245 | 242
2016-04-28 07:30 | 249 | 246
2016-04-28 08:00 | 247 | 245
2016-04-28 08:30 | 246 | 245
2016-04-28 09:00 | 247 | 246
2016-04-28 09:30 | 241 | 240
2016-04-28 10:00 | 242 | 242
2016-04-28 10:30 | 248 | 245
2016-04-28 11:00 | 239 | 238
2016-04-28 11:30 | 239 | 238
2016-04-28 12:00 | 237 | 237
2016-04-28 12:30 | 239 | 239
2016-04-28 13:00 | 244 | 244
2016-04-28 13:30 | 246 | 246
2016-04-28 14:00 | 243 | 242
2016-04-28 14:30 | 254 | 254
2016-04-28 15:00 | 260 | 260
2016-04-28 15:30 | 266 | 265
2016-04-28 16:00 | 271 | 271
2016-04-28 16:30 | 273 | 272
2016-04-28 17:00 | 276 | 275
2016-04-28 17:30 | 286 | 286
2016-04-28 18:00 | 284 | 283
2016-04-28 18:30 | 276 | 276
2016-04-28 19:00 | 264 | 263
2016-04-28 19:30 | 261 | 260
2016-04-28 20:00 | 264 | 263
2016-04-28 20:30 | 253 | 253
2016-04-28 21:00 | 236 | 236
2016-04-28 21:30 | 222 | 222
2016-04-28 22:00 | 228 | 228
2016-04-28 22:30 | 218 | 218
2016-04-28 23:00 | 204 | 204
2016-04-28 23:30 | 188 | 188
2016-04-29 | 171 | 171
2016-04-29 00:30 | 161 | 160
2016-04-29 01:00 | 151 | 151
2016-04-29 01:30 | 153 | 153
2016-04-29 02:00 | 145 | 145
2016-04-29 02:30 | 148 | 148
2016-04-29 03:00 | 143 | 143
2016-04-29 03:30 | 141 | 141
2016-04-29 04:00 | 119 | 119
2016-04-29 04:30 | 155 | 155
2016-04-29 05:00 | 167 | 167
2016-04-29 05:30 | 177 | 177
2016-04-29 06:00 | 202 | 202
2016-04-29 06:30 | 223 | 223
2016-04-29 07:00 | 232 | 231
2016-04-29 07:30 | 238 | 238
2016-04-29 08:00 | 242 | 242
2016-04-29 08:30 | 246 | 246
2016-04-29 09:00 | 249 | 249
2016-04-29 09:30 | 249 | 248
2016-04-29 10:00 | 247 | 246
2016-04-29 10:30 | 242 | 242
2016-04-29 11:00 | 241 | 241
2016-04-29 11:30 | 242 | 242
2016-04-29 12:00 | 240 | 240
2016-04-29 12:30 | 237 | 237
2016-04-29 13:00 | 237 | 237
2016-04-29 13:30 | 245 | 245
2016-04-29 14:00 | 250 | 250
2016-04-29 14:30 | 249 | 249
2016-04-29 15:00 | 242 | 242
2016-04-29 15:30 | 247 | 247
2016-04-29 16:00 | 251 | 251
2016-04-29 16:30 | 256 | 256
2016-04-29 17:00 | 267 | 267
2016-04-29 17:30 | 275 | 275
2016-04-29 18:00 | 269 | 269
2016-04-29 18:30 | 261 | 261
2016-04-29 19:00 | 252 | 251
2016-04-29 19:30 | 249 | 249
2016-04-29 20:00 | 243 | 243
2016-04-29 20:30 | 235 | 234
2016-04-29 21:00 | 222 | 222
2016-04-29 21:30 | 213 | 213
2016-04-29 22:00 | 214 | 214
2016-04-29 22:30 | 211 | 211
2016-04-29 23:00 | 197 | 197
2016-04-29 23:30 | 186 | 186
2016-04-30 | 173 | 173
2016-04-30 00:30 | 160 | 160
2016-04-30 01:00 | 150 | 150
2016-04-30 01:30 | 145 | 145
2016-04-30 02:00 | 143 | 143
2016-04-30 02:30 | 145 | 145
2016-04-30 03:00 | 145 | 145
2016-04-30 03:30 | 145 | 145
2016-04-30 04:00 | 150 | 150
2016-04-30 04:30 | 150 | 150
2016-04-30 05:00 | 153 | 153
2016-04-30 05:30 | 159 | 159
2016-04-30 06:00 | 165 | 165
2016-04-30 06:30 | 176 | 175
2016-04-30 07:00 | 189 | 189
2016-04-30 07:30 | 198 | 197
2016-04-30 08:00 | 210 | 210
2016-04-30 08:30 | 221 | 221
2016-04-30 09:00 | 226 | 226
2016-04-30 09:30 | 226 | 226
2016-04-30 10:00 | 224 | 224
2016-04-30 10:30 | 217 | 216
2016-04-30 11:00 | 211 | 211
2016-04-30 11:30 | 212 | 212
2016-04-30 12:00 | 209 | 209
2016-04-30 12:30 | 211 | 211
2016-04-30 13:00 | 206 | 206
2016-04-30 13:30 | 212 | 212
2016-04-30 14:00 | 217 | 216
2016-04-30 14:30 | 217 | 216
2016-04-30 15:00 | 223 | 223
2016-04-30 15:30 | 226 | 226
2016-04-30 16:00 | 236 | 236
2016-04-30 16:30 | 242 | 242
2016-04-30 17:00 | 248 | 248
2016-04-30 17:30 | 258 | 255
2016-04-30 18:00 | 254 | 250
2016-04-30 18:30 | 247 | 243
2016-04-30 19:00 | 240 | 236
2016-04-30 19:30 | 236 | 234
2016-04-30 20:00 | 231 | 230
2016-04-30 20:30 | 224 | 223
2016-04-30 21:00 | 209 | 209
2016-04-30 21:30 | 208 | 208
2016-04-30 22:00 | 208 | 208
2016-04-30 22:30 | 205 | 205
2016-04-30 23:00 | 197 | 197
2016-04-30 23:30 | 186 | 186
2016-05-01 | 171 | 171
2016-05-01 00:30 | 164 | 164
2016-05-01 01:00 | 155 | 155
2016-05-01 01:30 | 147 | 146
2016-05-01 02:00 | 128 | 128
2016-05-01 02:30 | 137 | 137
2016-05-01 03:00 | 138 | 138
2016-05-01 03:30 | 138 | 138
2016-05-01 04:00 | 139 | 139
2016-05-01 04:30 | 140 | 140
2016-05-01 05:00 | 149 | 149
2016-05-01 05:30 | 149 | 148
2016-05-01 06:00 | 154 | 154
2016-05-01 06:30 | 161 | 161
2016-05-01 07:00 | 175 | 175
2016-05-01 07:30 | 195 | 194
2016-05-01 08:00 | 206 | 206
2016-05-01 08:30 | 215 | 215
2016-05-01 09:00 | 225 | 225
2016-05-01 09:30 | 231 | 230
2016-05-01 10:00 | 233 | 233
2016-05-01 10:30 | 232 | 232
2016-05-01 11:00 | 228 | 228
2016-05-01 11:30 | 227 | 227
2016-05-01 12:00 | 224 | 224
2016-05-01 12:30 | 218 | 218
2016-05-01 13:00 | 217 | 217
2016-05-01 13:30 | 218 | 218
2016-05-01 14:00 | 222 | 221
2016-05-01 14:30 | 225 | 225
2016-05-01 15:00 | 226 | 225
2016-05-01 15:30 | 229 | 229
2016-05-01 16:00 | 226 | 226
2016-05-01 16:30 | 228 | 228
2016-05-01 17:00 | 239 | 238
2016-05-01 17:30 | 250 | 250
2016-05-01 18:00 | 253 | 253
2016-05-01 18:30 | 250 | 250
2016-05-01 19:00 | 243 | 242
2016-05-01 19:30 | 244 | 243
2016-05-01 20:00 | 242 | 241
2016-05-01 20:30 | 230 | 229
2016-05-01 21:00 | 219 | 218
2016-05-01 21:30 | 212 | 210
2016-05-01 22:00 | 209 | 209
2016-05-01 22:30 | 202 | 202
2016-05-01 23:00 | 193 | 193
2016-05-01 23:30 | 185 | 185
2016-05-02 | 172 | 172
2016-05-02 00:30 | 163 | 163
2016-05-02 01:00 | 159 | 158
2016-05-02 01:30 | 155 | 154
2016-05-02 02:00 | 147 | 146
2016-05-02 02:30 | 145 | 144
2016-05-02 03:00 | 145 | 144
2016-05-02 03:30 | 147 | 145
2016-05-02 04:00 | 147 | 146
2016-05-02 04:30 | 148 | 147
2016-05-02 05:00 | 152 | 151
2016-05-02 05:30 | 160 | 159
2016-05-02 06:00 | 167 | 166
2016-05-02 06:30 | 175 | 175
2016-05-02 07:00 | 183 | 183
2016-05-02 07:30 | 190 | 190
2016-05-02 08:00 | 199 | 199
2016-05-02 08:30 | 207 | 206
2016-05-02 09:00 | 210 | 209
2016-05-02 09:30 | 212 | 212
2016-05-02 10:00 | 218 | 218
2016-05-02 10:30 | 218 | 217
2016-05-02 11:00 | 218 | 218
2016-05-02 11:30 | 213 | 213
2016-05-02 12:00 | 207 | 207
2016-05-02 12:30 | 200 | 200
2016-05-02 13:00 | 198 | 198
2016-05-02 13:30 | 201 | 201
2016-05-02 14:00 | 208 | 208
2016-05-02 14:30 | 210 | 210
2016-05-02 15:00 | 221 | 221
2016-05-02 15:30 | 220 | 220
2016-05-02 16:00 | 225 | 225
2016-05-02 16:30 | 238 | 238
2016-05-02 17:00 | 256 | 256
2016-05-02 17:30 | 267 | 266
2016-05-02 18:00 | 262 | 261
2016-05-02 18:30 | 255 | 254
2016-05-02 19:00 | 242 | 242
2016-05-02 19:30 | 238 | 237
2016-05-02 20:00 | 229 | 228
2016-05-02 20:30 | 218 | 218
2016-05-02 21:00 | 211 | 211
2016-05-02 21:30 | 205 | 205
2016-05-02 22:00 | 201 | 201
2016-05-02 22:30 | 183 | 183
2016-05-02 23:00 | 185 | 185
2016-05-02 23:30 | 174 | 174
2016-05-03 | 155 | 155
2016-05-03 00:30 | 146 | 145
2016-05-03 01:00 | 118 | 117
2016-05-03 01:30 | 123 | 123
2016-05-03 02:00 | 123 | 123
2016-05-03 02:30 | 120 | 120
2016-05-03 03:00 | 117 | 117
2016-05-03 03:30 | 118 | 118
2016-05-03 04:00 | 121 | 121
2016-05-03 04:30 | 128 | 127
2016-05-03 05:00 | 134 | 134
2016-05-03 05:30 | 154 | 153
2016-05-03 06:00 | 189 | 189
2016-05-03 06:30 | 213 | 212
2016-05-03 07:00 | 230 | 229
2016-05-03 07:30 | 236 | 235
2016-05-03 08:00 | 235 | 235
2016-05-03 08:30 | 232 | 232
2016-05-03 09:00 | 230 | 230
2016-05-03 09:30 | 226 | 226
2016-05-03 10:00 | 225 | 225
2016-05-03 10:30 | 225 | 225
2016-05-03 11:00 | 223 | 223
2016-05-03 11:30 | 225 | 225
2016-05-03 12:00 | 231 | 231
2016-05-03 12:30 | 233 | 233
2016-05-03 13:00 | 232 | 232
2016-05-03 13:30 | 236 | 236
2016-05-03 14:00 | 241 | 241
2016-05-03 14:30 | 247 | 247
2016-05-03 15:00 | 253 | 253
2016-05-03 15:30 | 259 | 259
2016-05-03 16:00 | 265 | 265
2016-05-03 16:30 | 272 | 272
2016-05-03 17:00 | 283 | 282
2016-05-03 17:30 | 292 | 292
2016-05-03 18:00 | 288 | 288
2016-05-03 18:30 | 282 | 282
2016-05-03 19:00 | 270 | 270
2016-05-03 19:30 | 263 | 263
2016-05-03 20:00 | 256 | 255
2016-05-03 20:30 | 242 | 242
2016-05-03 21:00 | 229 | 229
2016-05-03 21:30 | 220 | 220
2016-05-03 22:00 | 212 | 212
2016-05-03 22:30 | 202 | 201
2016-05-03 23:00 | 189 | 189
2016-05-03 23:30 | 177 | 177
2016-05-04 | 164 | 164
2016-05-04 00:30 | 161 | 161
2016-05-04 01:00 | 156 | 156
2016-05-04 01:30 | 155 | 155
2016-05-04 02:00 | 141 | 141
2016-05-04 02:30 | 143 | 143
2016-05-04 03:00 | 143 | 143
2016-05-04 03:30 | 142 | 142
2016-05-04 04:00 | 145 | 145
2016-05-04 04:30 | 150 | 150
2016-05-04 05:00 | 159 | 159
2016-05-04 05:30 | 177 | 176
2016-05-04 06:00 | 194 | 193
2016-05-04 06:30 | 217 | 217
2016-05-04 07:00 | 233 | 231
2016-05-04 07:30 | 236 | 233
2016-05-04 08:00 | 230 | 228
2016-05-04 08:30 | 224 | 222
2016-05-04 09:00 | 225 | 222
2016-05-04 09:30 | 225 | 222
2016-05-04 10:00 | 224 | 221
2016-05-04 10:30 | 221 | 218
2016-05-04 11:00 | 219 | 216
2016-05-04 11:30 | 220 | 217
2016-05-04 12:00 | 218 | 216
2016-05-04 12:30 | 218 | 216
2016-05-04 13:00 | 218 | 215
2016-05-04 13:30 | 223 | 221
2016-05-04 14:00 | 226 | 223
2016-05-04 14:30 | 232 | 229
2016-05-04 15:00 | 238 | 234
2016-05-04 15:30 | 245 | 241
2016-05-04 16:00 | 254 | 250
2016-05-04 16:30 | 261 | 256
2016-05-04 17:00 | 274 | 270
2016-05-04 17:30 | 288 | 283
2016-05-04 18:00 | 284 | 280
2016-05-04 18:30 | 277 | 272
2016-05-04 19:00 | 271 | 265
2016-05-04 19:30 | 262 | 259
2016-05-04 20:00 | 252 | 250
2016-05-04 20:30 | 236 | 234
2016-05-04 21:00 | 225 | 222
2016-05-04 21:30 | 218 | 215
2016-05-04 22:00 | 215 | 211
2016-05-04 22:30 | 207 | 202
2016-05-04 23:00 | 199 | 194
2016-05-04 23:30 | 183 | 177
2016-05-05 | 168 | 163
2016-05-05 00:30 | 158 | 152
2016-05-05 01:00 | 153 | 146
2016-05-05 01:30 | 149 | 143
2016-05-05 02:00 | 145 | 141
2016-05-05 02:30 | 141 | 137
2016-05-05 03:00 | 140 | 137
2016-05-05 03:30 | 126 | 122
2016-05-05 04:00 | 123 | 120
2016-05-05 04:30 | 132 | 129
2016-05-05 05:00 | 159 | 157
2016-05-05 05:30 | 168 | 165
2016-05-05 06:00 | 191 | 186
2016-05-05 06:30 | 212 | 208
2016-05-05 07:00 | 224 | 220
2016-05-05 07:30 | 234 | 230
2016-05-05 08:00 | 237 | 235
2016-05-05 08:30 | 226 | 225
2016-05-05 09:00 | 224 | 222
2016-05-05 09:30 | 223 | 221
2016-05-05 10:00 | 238 | 237
2016-05-05 10:30 | 238 | 235
2016-05-05 11:00 | 237 | 234
2016-05-05 11:30 | 236 | 233
2016-05-05 12:00 | 216 | 212
2016-05-05 12:30 | 222 | 218
2016-05-05 13:00 | 222 | 218
2016-05-05 13:30 | 226 | 223
2016-05-05 14:00 | 229 | 226
2016-05-05 14:30 | 232 | 230
2016-05-05 15:00 | 236 | 236
2016-05-05 15:30 | 244 | 244
2016-05-05 16:00 | 251 | 251
2016-05-05 16:30 | 258 | 258
2016-05-05 17:00 | 265 | 265
2016-05-05 17:30 | 279 | 279
2016-05-05 18:00 | 277 | 277
2016-05-05 18:30 | 273 | 273
2016-05-05 19:00 | 261 | 261
2016-05-05 19:30 | 256 | 256
2016-05-05 20:00 | 249 | 249
2016-05-05 20:30 | 234 | 233
2016-05-05 21:00 | 223 | 220
2016-05-05 21:30 | 208 | 206
2016-05-05 22:00 | 204 | 203
2016-05-05 22:30 | 196 | 195
2016-05-05 23:00 | 185 | 185
2016-05-05 23:30 | 170 | 170
2016-05-06 | 156 | 154
2016-05-06 00:30 | 147 | 146
2016-05-06 01:00 | 140 | 139
2016-05-06 01:30 | 141 | 140
2016-05-06 02:00 | 145 | 145
2016-05-06 02:30 | 142 | 141
2016-05-06 03:00 | 142 | 141
2016-05-06 03:30 | 143 | 142
2016-05-06 04:00 | 146 | 145
2016-05-06 04:30 | 151 | 150
2016-05-06 05:00 | 160 | 159
2016-05-06 05:30 | 171 | 168
2016-05-06 06:00 | 189 | 186
2016-05-06 06:30 | 212 | 212
2016-05-06 07:00 | 230 | 229
2016-05-06 07:30 | 232 | 231
2016-05-06 08:00 | 236 | 234
2016-05-06 08:30 | 239 | 236
2016-05-06 09:00 | 239 | 237
2016-05-06 09:30 | 243 | 241
2016-05-06 10:00 | 235 | 233
2016-05-06 10:30 | 230 | 229
2016-05-06 11:00 | 227 | 226
2016-05-06 11:30 | 227 | 226
2016-05-06 12:00 | 226 | 225
2016-05-06 12:30 | 225 | 224
2016-05-06 13:00 | 228 | 226
2016-05-06 13:30 | 233 | 232
2016-05-06 14:00 | 240 | 238
2016-05-06 14:30 | 245 | 244
2016-05-06 15:00 | 248 | 246
2016-05-06 15:30 | 252 | 250
2016-05-06 16:00 | 255 | 252
2016-05-06 16:30 | 264 | 261
2016-05-06 17:00 | 273 | 269
2016-05-06 17:30 | 284 | 281
2016-05-06 18:00 | 281 | 276
2016-05-06 18:30 | 271 | 267
2016-05-06 19:00 | 257 | 254
2016-05-06 19:30 | 247 | 246
2016-05-06 20:00 | 244 | 242
2016-05-06 20:30 | 230 | 230
2016-05-06 21:00 | 223 | 223
2016-05-06 21:30 | 216 | 215
2016-05-06 22:00 | 219 | 218
2016-05-06 22:30 | 208 | 207
2016-05-06 23:00 | 197 | 197
2016-05-06 23:30 | 187 | 186
2016-05-07 | 170 | 169
2016-05-07 00:30 | 163 | 161
2016-05-07 01:00 | 153 | 150
2016-05-07 01:30 | 151 | 149
2016-05-07 02:00 | 150 | 147
2016-05-07 02:30 | 146 | 143
2016-05-07 03:00 | 144 | 142
2016-05-07 03:30 | 144 | 142
2016-05-07 04:00 | 144 | 142
2016-05-07 04:30 | 147 | 145
2016-05-07 05:00 | 151 | 149
2016-05-07 05:30 | 158 | 156
2016-05-07 06:00 | 166 | 164
2016-05-07 06:30 | 177 | 176
2016-05-07 07:00 | 188 | 188
2016-05-07 07:30 | 197 | 196
2016-05-07 08:00 | 205 | 204
2016-05-07 08:30 | 209 | 208
2016-05-07 09:00 | 211 | 211
2016-05-07 09:30 | 209 | 208
2016-05-07 10:00 | 208 | 207
2016-05-07 10:30 | 205 | 204
2016-05-07 11:00 | 205 | 203
2016-05-07 11:30 | 205 | 204
2016-05-07 12:00 | 206 | 205
2016-05-07 12:30 | 205 | 204
2016-05-07 13:00 | 206 | 205
2016-05-07 13:30 | 208 | 207
2016-05-07 14:00 | 210 | 209
2016-05-07 14:30 | 214 | 213
2016-05-07 15:00 | 220 | 219
2016-05-07 15:30 | 226 | 225
2016-05-07 16:00 | 230 | 229
2016-05-07 16:30 | 241 | 241
2016-05-07 17:00 | 252 | 252
2016-05-07 17:30 | 268 | 268
2016-05-07 18:00 | 266 | 265
2016-05-07 18:30 | 259 | 257
2016-05-07 19:00 | 244 | 244
2016-05-07 19:30 | 241 | 241
2016-05-07 20:00 | 235 | 235
2016-05-07 20:30 | 227 | 227
2016-05-07 21:00 | 221 | 220
2016-05-07 21:30 | 216 | 215
2016-05-07 22:00 | 214 | 213
2016-05-07 22:30 | 209 | 208
2016-05-07 23:00 | 202 | 201
2016-05-07 23:30 | 188 | 187
2016-05-08 | 173 | 172
2016-05-08 00:30 | 165 | 163
2016-05-08 01:00 | 157 | 156
2016-05-08 01:30 | 155 | 153
2016-05-08 02:00 | 149 | 147
2016-05-08 02:30 | 144 | 142
2016-05-08 03:00 | 142 | 140
2016-05-08 03:30 | 141 | 138
2016-05-08 04:00 | 142 | 139
2016-05-08 04:30 | 146 | 143
2016-05-08 05:00 | 150 | 148
2016-05-08 05:30 | 151 | 149
2016-05-08 06:00 | 157 | 155
2016-05-08 06:30 | 164 | 162
2016-05-08 07:00 | 174 | 173
2016-05-08 07:30 | 180 | 180
2016-05-08 08:00 | 194 | 194
2016-05-08 08:30 | 201 | 201
2016-05-08 09:00 | 207 | 206
2016-05-08 09:30 | 212 | 212
2016-05-08 10:00 | 217 | 216
2016-05-08 10:30 | 212 | 211
2016-05-08 11:00 | 210 | 209
2016-05-08 11:30 | 206 | 205
2016-05-08 12:00 | 202 | 201
2016-05-08 12:30 | 198 | 198
2016-05-08 13:00 | 200 | 200
2016-05-08 13:30 | 202 | 201
2016-05-08 14:00 | 211 | 210
2016-05-08 14:30 | 218 | 218
2016-05-08 15:00 | 223 | 223
2016-05-08 15:30 | 233 | 232
2016-05-08 16:00 | 234 | 233
2016-05-08 16:30 | 241 | 240
2016-05-08 17:00 | 251 | 250
2016-05-08 17:30 | 266 | 263
2016-05-08 18:00 | 265 | 260
2016-05-08 18:30 | 260 | 255
2016-05-08 19:00 | 251 | 247
2016-05-08 19:30 | 251 | 248
2016-05-08 20:00 | 247 | 243
2016-05-08 20:30 | 236 | 232
2016-05-08 21:00 | 225 | 223
2016-05-08 21:30 | 218 | 215
2016-05-08 22:00 | 203 | 203
2016-05-08 22:30 | 196 | 196
2016-05-08 23:00 | 189 | 188
2016-05-08 23:30 | 181 | 181
2016-05-09 | 165 | 164
2016-05-09 00:30 | 153 | 151
2016-05-09 01:00 | 143 | 141
2016-05-09 01:30 | 139 | 137
2016-05-09 02:00 | 136 | 133
2016-05-09 02:30 | 138 | 135
2016-05-09 03:00 | 139 | 137
2016-05-09 03:30 | 140 | 138
2016-05-09 04:00 | 143 | 141
2016-05-09 04:30 | 150 | 148
2016-05-09 05:00 | 161 | 160
2016-05-09 05:30 | 166 | 165
2016-05-09 06:00 | 185 | 184
2016-05-09 06:30 | 210 | 210
2016-05-09 07:00 | 226 | 225
2016-05-09 07:30 | 242 | 237
2016-05-09 08:00 | 245 | 241
2016-05-09 08:30 | 241 | 240
2016-05-09 09:00 | 251 | 251
2016-05-09 09:30 | 254 | 254
2016-05-09 10:00 | 257 | 257
2016-05-09 10:30 | 264 | 264
2016-05-09 11:00 | 264 | 264
2016-05-09 11:30 | 264 | 264
2016-05-09 12:00 | 262 | 262
2016-05-09 12:30 | 263 | 263
2016-05-09 13:00 | 265 | 265
2016-05-09 13:30 | 262 | 262
2016-05-09 14:00 | 264 | 263
2016-05-09 14:30 | 268 | 268
2016-05-09 15:00 | 271 | 271
2016-05-09 15:30 | 272 | 272
2016-05-09 16:00 | 277 | 277
2016-05-09 16:30 | 280 | 280
2016-05-09 17:00 | 299 | 299
2016-05-09 17:30 | 310 | 310
2016-05-09 18:00 | 301 | 301
2016-05-09 18:30 | 291 | 291
2016-05-09 19:00 | 273 | 273
2016-05-09 19:30 | 269 | 269
2016-05-09 20:00 | 262 | 262
2016-05-09 20:30 | 248 | 247
2016-05-09 21:00 | 233 | 232
2016-05-09 21:30 | 223 | 222
2016-05-09 22:00 | 214 | 213
2016-05-09 22:30 | 208 | 207
2016-05-09 23:00 | 198 | 197
2016-05-09 23:30 | 187 | 187
2016-05-10 | 174 | 173
2016-05-10 00:30 | 165 | 164
2016-05-10 01:00 | 157 | 155
2016-05-10 01:30 | 150 | 149
2016-05-10 02:00 | 142 | 140
2016-05-10 02:30 | 140 | 139
2016-05-10 03:00 | 136 | 135
2016-05-10 03:30 | 142 | 141
2016-05-10 04:00 | 142 | 140
2016-05-10 04:30 | 151 | 149
2016-05-10 05:00 | 163 | 161
2016-05-10 05:30 | 175 | 173
2016-05-10 06:00 | 200 | 199
2016-05-10 06:30 | 224 | 224
2016-05-10 07:00 | 232 | 231
2016-05-10 07:30 | 246 | 245
2016-05-10 08:00 | 252 | 251
2016-05-10 08:30 | 254 | 253
2016-05-10 09:00 | 260 | 260
2016-05-10 09:30 | 261 | 260
2016-05-10 10:00 | 257 | 256
2016-05-10 10:30 | 254 | 253
2016-05-10 11:00 | 251 | 250
2016-05-10 11:30 | 250 | 249
2016-05-10 12:00 | 248 | 247
2016-05-10 12:30 | 244 | 243
2016-05-10 13:00 | 239 | 239
2016-05-10 13:30 | 252 | 251
2016-05-10 14:00 | 245 | 244
2016-05-10 14:30 | 252 | 251
2016-05-10 15:00 | 258 | 257
2016-05-10 15:30 | 258 | 258
2016-05-10 16:00 | 262 | 262
2016-05-10 16:30 | 269 | 269
2016-05-10 17:00 | 281 | 280
2016-05-10 17:30 | 291 | 291
2016-05-10 18:00 | 286 | 286
2016-05-10 18:30 | 282 | 281
2016-05-10 19:00 | 269 | 268
2016-05-10 19:30 | 261 | 261
2016-05-10 20:00 | 255 | 254
2016-05-10 20:30 | 239 | 238
2016-05-10 21:00 | 231 | 228
2016-05-10 21:30 | 224 | 219
2016-05-10 22:00 | 222 | 216
2016-05-10 22:30 | 210 | 204
2016-05-10 23:00 | 197 | 192
2016-05-10 23:30 | 182 | 179
2016-05-11 | 167 | 165
2016-05-11 00:30 | 160 | 159
2016-05-11 01:00 | 158 | 157
2016-05-11 01:30 | 155 | 154
2016-05-11 02:00 | 150 | 149
2016-05-11 02:30 | 147 | 145
2016-05-11 03:00 | 148 | 146
2016-05-11 03:30 | 146 | 145
2016-05-11 04:00 | 149 | 148
2016-05-11 04:30 | 156 | 154
2016-05-11 05:00 | 165 | 164
2016-05-11 05:30 | 170 | 169
2016-05-11 06:00 | 200 | 199
2016-05-11 06:30 | 229 | 226
2016-05-11 07:00 | 254 | 250
2016-05-11 07:30 | 266 | 260
2016-05-11 08:00 | 264 | 260
2016-05-11 08:30 | 259 | 256
2016-05-11 09:00 | 256 | 253
2016-05-11 09:30 | 255 | 252
2016-05-11 10:00 | 242 | 241
2016-05-11 10:30 | 241 | 240
2016-05-11 11:00 | 242 | 241
2016-05-11 11:30 | 243 | 242
2016-05-11 12:00 | 236 | 236
2016-05-11 12:30 | 231 | 231
2016-05-11 13:00 | 222 | 222
2016-05-11 13:30 | 226 | 226
2016-05-11 14:00 | 234 | 234
2016-05-11 14:30 | 248 | 248
2016-05-11 15:00 | 244 | 244
2016-05-11 15:30 | 243 | 242
2016-05-11 16:00 | 247 | 247
2016-05-11 16:30 | 259 | 259
2016-05-11 17:00 | 269 | 269
2016-05-11 17:30 | 279 | 279
2016-05-11 18:00 | 273 | 273
2016-05-11 18:30 | 270 | 270
2016-05-11 19:00 | 263 | 263
2016-05-11 19:30 | 262 | 262
2016-05-11 20:00 | 260 | 260
2016-05-11 20:30 | 247 | 247
2016-05-11 21:00 | 230 | 230
2016-05-11 21:30 | 215 | 215
2016-05-11 22:00 | 213 | 213
2016-05-11 22:30 | 205 | 205
2016-05-11 23:00 | 192 | 192
2016-05-11 23:30 | 182 | 182
2016-05-12 | 168 | 167
2016-05-12 00:30 | 160 | 159
2016-05-12 01:00 | 157 | 156
2016-05-12 01:30 | 151 | 151
2016-05-12 02:00 | 149 | 149
2016-05-12 02:30 | 147 | 147
2016-05-12 03:00 | 148 | 148
2016-05-12 03:30 | 149 | 148
2016-05-12 04:00 | 154 | 154
2016-05-12 04:30 | 160 | 160
2016-05-12 05:00 | 168 | 168
2016-05-12 05:30 | 176 | 176
2016-05-12 06:00 | 198 | 198
2016-05-12 06:30 | 233 | 231
2016-05-12 07:00 | 253 | 249
2016-05-12 07:30 | 257 | 253
2016-05-12 08:00 | 248 | 246
2016-05-12 08:30 | 235 | 235
2016-05-12 09:00 | 226 | 226
2016-05-12 09:30 | 219 | 219
2016-05-12 10:00 | 213 | 213
2016-05-12 10:30 | 209 | 209
2016-05-12 11:00 | 209 | 209
2016-05-12 11:30 | 208 | 208
2016-05-12 12:00 | 209 | 209
2016-05-12 12:30 | 210 | 210
2016-05-12 13:00 | 213 | 213
2016-05-12 13:30 | 218 | 218
2016-05-12 14:00 | 223 | 223
2016-05-12 14:30 | 225 | 225
2016-05-12 15:00 | 230 | 230
2016-05-12 15:30 | 241 | 241
2016-05-12 16:00 | 248 | 247
2016-05-12 16:30 | 252 | 251
2016-05-12 17:00 | 263 | 262
2016-05-12 17:30 | 279 | 278
2016-05-12 18:00 | 277 | 276
2016-05-12 18:30 | 275 | 275
2016-05-12 19:00 | 264 | 263
2016-05-12 19:30 | 261 | 261
2016-05-12 20:00 | 253 | 253
2016-05-12 20:30 | 243 | 243
2016-05-12 21:00 | 229 | 229
2016-05-12 21:30 | 220 | 220
2016-05-12 22:00 | 221 | 221
2016-05-12 22:30 | 212 | 212
2016-05-12 23:00 | 204 | 204
2016-05-12 23:30 | 192 | 192
2016-05-13 | 180 | 180
2016-05-13 00:30 | 170 | 170
2016-05-13 01:00 | 161 | 161
2016-05-13 01:30 | 157 | 157
2016-05-13 02:00 | 150 | 149
2016-05-13 02:30 | 143 | 142
2016-05-13 03:00 | 146 | 145
2016-05-13 03:30 | 147 | 147
2016-05-13 04:00 | 150 | 150
2016-05-13 04:30 | 155 | 155
2016-05-13 05:00 | 163 | 163
2016-05-13 05:30 | 178 | 178
2016-05-13 06:00 | 205 | 205
2016-05-13 06:30 | 233 | 230
2016-05-13 07:00 | 249 | 248
2016-05-13 07:30 | 254 | 253
2016-05-13 08:00 | 250 | 248
2016-05-13 08:30 | 241 | 240
2016-05-13 09:00 | 237 | 236
2016-05-13 09:30 | 233 | 232
2016-05-13 10:00 | 228 | 227
2016-05-13 10:30 | 221 | 221
2016-05-13 11:00 | 217 | 217
2016-05-13 11:30 | 214 | 214
2016-05-13 12:00 | 186 | 186
2016-05-13 12:30 | 213 | 212
2016-05-13 13:00 | 216 | 216
2016-05-13 13:30 | 257 | 256
2016-05-13 14:00 | 231 | 231
2016-05-13 14:30 | 238 | 237
2016-05-13 15:00 | 240 | 240
2016-05-13 15:30 | 249 | 249
2016-05-13 16:00 | 255 | 254
2016-05-13 16:30 | 263 | 263
2016-05-13 17:00 | 274 | 273
2016-05-13 17:30 | 283 | 283
2016-05-13 18:00 | 277 | 276
2016-05-13 18:30 | 271 | 271
2016-05-13 19:00 | 260 | 260
2016-05-13 19:30 | 254 | 254
2016-05-13 20:00 | 252 | 251
2016-05-13 20:30 | 242 | 241
2016-05-13 21:00 | 230 | 229
2016-05-13 21:30 | 219 | 217
2016-05-13 22:00 | 215 | 215
2016-05-13 22:30 | 212 | 212
2016-05-13 23:00 | 200 | 200
2016-05-13 23:30 | 192 | 191
2016-05-14 | 174 | 173
2016-05-14 00:30 | 161 | 161
2016-05-14 01:00 | 155 | 155
2016-05-14 01:30 | 152 | 152
2016-05-14 02:00 | 152 | 152
2016-05-14 02:30 | 148 | 148
2016-05-14 03:00 | 149 | 149
2016-05-14 03:30 | 143 | 142
2016-05-14 04:00 | 149 | 149
2016-05-14 04:30 | 152 | 152
2016-05-14 05:00 | 156 | 156
2016-05-14 05:30 | 163 | 163
2016-05-14 06:00 | 173 | 173
2016-05-14 06:30 | 187 | 187
2016-05-14 07:00 | 200 | 200
2016-05-14 07:30 | 207 | 207
2016-05-14 08:00 | 218 | 218
2016-05-14 08:30 | 224 | 224
2016-05-14 09:00 | 226 | 225
2016-05-14 09:30 | 223 | 222
2016-05-14 10:00 | 223 | 222
2016-05-14 10:30 | 218 | 217
2016-05-14 11:00 | 209 | 208
2016-05-14 11:30 | 207 | 207
2016-05-14 12:00 | 205 | 204
2016-05-14 12:30 | 206 | 205
2016-05-14 13:00 | 203 | 202
2016-05-14 13:30 | 204 | 203
2016-05-14 14:00 | 205 | 205
2016-05-14 14:30 | 211 | 210
2016-05-14 15:00 | 218 | 218
2016-05-14 15:30 | 227 | 226
2016-05-14 16:00 | 234 | 234
2016-05-14 16:30 | 246 | 245
2016-05-14 17:00 | 260 | 260
2016-05-14 17:30 | 268 | 267
2016-05-14 18:00 | 263 | 263
2016-05-14 18:30 | 254 | 253
2016-05-14 19:00 | 238 | 238
2016-05-14 19:30 | 232 | 231
2016-05-14 20:00 | 227 | 226
2016-05-14 20:30 | 215 | 215
2016-05-14 21:00 | 210 | 210
2016-05-14 21:30 | 204 | 203
2016-05-14 22:00 | 204 | 204
2016-05-14 22:30 | 198 | 197
2016-05-14 23:00 | 192 | 192
2016-05-14 23:30 | 183 | 183
2016-05-15 | 170 | 170
2016-05-15 00:30 | 163 | 163
2016-05-15 01:00 | 158 | 158
2016-05-15 01:30 | 154 | 154
2016-05-15 02:00 | 146 | 146
2016-05-15 02:30 | 141 | 141
2016-05-15 03:00 | 142 | 142
2016-05-15 03:30 | 142 | 141
2016-05-15 04:00 | 145 | 144
2016-05-15 04:30 | 148 | 147
2016-05-15 05:00 | 150 | 149
2016-05-15 05:30 | 151 | 150
2016-05-15 06:00 | 156 | 156
2016-05-15 06:30 | 165 | 165
2016-05-15 07:00 | 177 | 176
2016-05-15 07:30 | 185 | 185
2016-05-15 08:00 | 195 | 195
2016-05-15 08:30 | 201 | 201
2016-05-15 09:00 | 202 | 202
2016-05-15 09:30 | 203 | 203
2016-05-15 10:00 | 200 | 200
2016-05-15 10:30 | 197 | 197
2016-05-15 11:00 | 194 | 194
2016-05-15 11:30 | 193 | 193
2016-05-15 12:00 | 192 | 192
2016-05-15 12:30 | 194 | 193
2016-05-15 13:00 | 194 | 194
2016-05-15 13:30 | 197 | 197
2016-05-15 14:00 | 200 | 200
2016-05-15 14:30 | 205 | 205
2016-05-15 15:00 | 211 | 211
2016-05-15 15:30 | 223 | 223
2016-05-15 16:00 | 233 | 232
2016-05-15 16:30 | 242 | 241
2016-05-15 17:00 | 262 | 262
2016-05-15 17:30 | 274 | 274
2016-05-15 18:00 | 276 | 276
2016-05-15 18:30 | 269 | 269
2016-05-15 19:00 | 256 | 256
2016-05-15 19:30 | 249 | 249
2016-05-15 20:00 | 245 | 245
2016-05-15 20:30 | 236 | 236
2016-05-15 21:00 | 228 | 228
2016-05-15 21:30 | 215 | 215
2016-05-15 22:00 | 212 | 212
2016-05-15 22:30 | 203 | 203
2016-05-15 23:00 | 192 | 191
2016-05-15 23:30 | 180 | 180
2016-05-16 | 164 | 164
2016-05-16 00:30 | 156 | 156
2016-05-16 01:00 | 151 | 150
2016-05-16 01:30 | 149 | 148
2016-05-16 02:00 | 143 | 142
2016-05-16 02:30 | 141 | 140
2016-05-16 03:00 | 142 | 141
2016-05-16 03:30 | 145 | 144
2016-05-16 04:00 | 150 | 149
2016-05-16 04:30 | 157 | 156
2016-05-16 05:00 | 164 | 162
2016-05-16 05:30 | 173 | 170
2016-05-16 06:00 | 196 | 196
2016-05-16 06:30 | 219 | 219
2016-05-16 07:00 | 233 | 233
2016-05-16 07:30 | 241 | 241
2016-05-16 08:00 | 235 | 235
2016-05-16 08:30 | 233 | 231
2016-05-16 09:00 | 227 | 224
2016-05-16 09:30 | 226 | 223
2016-05-16 10:00 | 226 | 223
2016-05-16 10:30 | 223 | 219
2016-05-16 11:00 | 219 | 215
2016-05-16 11:30 | 218 | 214
2016-05-16 12:00 | 212 | 210
2016-05-16 12:30 | 210 | 208
2016-05-16 13:00 | 212 | 211
2016-05-16 13:30 | 216 | 214
2016-05-16 14:00 | 221 | 219
2016-05-16 14:30 | 224 | 222
2016-05-16 15:00 | 227 | 226
2016-05-16 15:30 | 236 | 235
2016-05-16 16:00 | 248 | 247
2016-05-16 16:30 | 260 | 260
2016-05-16 17:00 | 275 | 275
2016-05-16 17:30 | 284 | 284
2016-05-16 18:00 | 278 | 278
2016-05-16 18:30 | 274 | 274
2016-05-16 19:00 | 262 | 262
2016-05-16 19:30 | 259 | 259
2016-05-16 20:00 | 252 | 252
2016-05-16 20:30 | 241 | 240
2016-05-16 21:00 | 230 | 230
2016-05-16 21:30 | 220 | 219
2016-05-16 22:00 | 218 | 217
2016-05-16 22:30 | 214 | 212
2016-05-16 23:00 | 200 | 199
2016-05-16 23:30 | 189 | 187
2016-05-17 | 172 | 171
2016-05-17 00:30 | 160 | 158
2016-05-17 01:00 | 153 | 151
2016-05-17 01:30 | 149 | 148
2016-05-17 02:00 | 147 | 146
2016-05-17 02:30 | 144 | 143
2016-05-17 03:00 | 143 | 142
2016-05-17 03:30 | 144 | 143
2016-05-17 04:00 | 147 | 145
2016-05-17 04:30 | 153 | 152
2016-05-17 05:00 | 169 | 167
2016-05-17 05:30 | 183 | 181
2016-05-17 06:00 | 203 | 202
2016-05-17 06:30 | 221 | 220
2016-05-17 07:00 | 232 | 232
2016-05-17 07:30 | 242 | 242
2016-05-17 08:00 | 239 | 239
2016-05-17 08:30 | 243 | 243
2016-05-17 09:00 | 250 | 250
2016-05-17 09:30 | 242 | 241
2016-05-17 10:00 | 235 | 235
2016-05-17 10:30 | 232 | 232
2016-05-17 11:00 | 228 | 227
2016-05-17 11:30 | 228 | 227
2016-05-17 12:00 | 233 | 232
2016-05-17 12:30 | 242 | 241
2016-05-17 13:00 | 248 | 248
2016-05-17 13:30 | 252 | 252
2016-05-17 14:00 | 251 | 251
2016-05-17 14:30 | 247 | 247
2016-05-17 15:00 | 241 | 241
2016-05-17 15:30 | 249 | 249
2016-05-17 16:00 | 255 | 255
2016-05-17 16:30 | 264 | 264
2016-05-17 17:00 | 281 | 281
2016-05-17 17:30 | 297 | 296
2016-05-17 18:00 | 288 | 288
2016-05-17 18:30 | 281 | 280
2016-05-17 19:00 | 274 | 272
2016-05-17 19:30 | 269 | 268
2016-05-17 20:00 | 267 | 267
2016-05-17 20:30 | 252 | 252
2016-05-17 21:00 | 241 | 241
2016-05-17 21:30 | 229 | 229
2016-05-17 22:00 | 230 | 230
2016-05-17 22:30 | 223 | 223
2016-05-17 23:00 | 220 | 219
2016-05-17 23:30 | 211 | 210
2016-05-18 | 195 | 194
2016-05-18 00:30 | 185 | 184
2016-05-18 01:00 | 182 | 181
2016-05-18 01:30 | 174 | 173
2016-05-18 02:00 | 166 | 165
2016-05-18 02:30 | 159 | 158
2016-05-18 03:00 | 154 | 153
2016-05-18 03:30 | 152 | 151
2016-05-18 04:00 | 154 | 154
2016-05-18 04:30 | 162 | 161
2016-05-18 05:00 | 180 | 179
2016-05-18 05:30 | 194 | 194
2016-05-18 06:00 | 218 | 218
2016-05-18 06:30 | 240 | 238
2016-05-18 07:00 | 246 | 245
2016-05-18 07:30 | 250 | 249
2016-05-18 08:00 | 246 | 245
2016-05-18 08:30 | 240 | 239
2016-05-18 09:00 | 242 | 242
2016-05-18 09:30 | 241 | 241
2016-05-18 10:00 | 239 | 239
2016-05-18 10:30 | 235 | 235
2016-05-18 11:00 | 239 | 239
2016-05-18 11:30 | 236 | 236
2016-05-18 12:00 | 238 | 237
2016-05-18 12:30 | 242 | 242
2016-05-18 13:00 | 238 | 237
2016-05-18 13:30 | 245 | 244
2016-05-18 14:00 | 249 | 249
2016-05-18 14:30 | 239 | 239
2016-05-18 15:00 | 244 | 243
2016-05-18 15:30 | 249 | 249
2016-05-18 16:00 | 255 | 254
2016-05-18 16:30 | 270 | 269
2016-05-18 17:00 | 281 | 280
2016-05-18 17:30 | 298 | 296
2016-05-18 18:00 | 288 | 287
2016-05-18 18:30 | 282 | 281
2016-05-18 19:00 | 272 | 270
2016-05-18 19:30 | 274 | 273
2016-05-18 20:00 | 270 | 269
2016-05-18 20:30 | 258 | 256
2016-05-18 21:00 | 243 | 241
2016-05-18 21:30 | 232 | 229
2016-05-18 22:00 | 228 | 228
2016-05-18 22:30 | 214 | 214
2016-05-18 23:00 | 201 | 201
2016-05-18 23:30 | 176 | 176
2016-05-19 | 158 | 158
2016-05-19 00:30 | 150 | 149
2016-05-19 01:00 | 153 | 152
2016-05-19 01:30 | 153 | 151
2016-05-19 02:00 | 151 | 150
2016-05-19 02:30 | 145 | 145
2016-05-19 03:00 | 142 | 141
2016-05-19 03:30 | 147 | 147
2016-05-19 04:00 | 150 | 150
2016-05-19 04:30 | 156 | 156
2016-05-19 05:00 | 168 | 168
2016-05-19 05:30 | 179 | 179
2016-05-19 06:00 | 203 | 203
2016-05-19 06:30 | 223 | 222
2016-05-19 07:00 | 234 | 233
2016-05-19 07:30 | 246 | 245
2016-05-19 08:00 | 243 | 242
2016-05-19 08:30 | 234 | 234
2016-05-19 09:00 | 237 | 237
2016-05-19 09:30 | 239 | 239
2016-05-19 10:00 | 240 | 240
2016-05-19 10:30 | 251 | 251
2016-05-19 11:00 | 246 | 246
2016-05-19 11:30 | 251 | 250
2016-05-19 12:00 | 248 | 248
2016-05-19 12:30 | 247 | 247
2016-05-19 13:00 | 238 | 237
2016-05-19 13:30 | 238 | 238
2016-05-19 14:00 | 240 | 240
2016-05-19 14:30 | 243 | 243
2016-05-19 15:00 | 246 | 245
2016-05-19 15:30 | 248 | 248
2016-05-19 16:00 | 252 | 252
2016-05-19 16:30 | 266 | 265
2016-05-19 17:00 | 278 | 278
2016-05-19 17:30 | 291 | 291
2016-05-19 18:00 | 286 | 286
2016-05-19 18:30 | 280 | 280
2016-05-19 19:00 | 273 | 272
2016-05-19 19:30 | 268 | 267
2016-05-19 20:00 | 267 | 266
2016-05-19 20:30 | 252 | 252
2016-05-19 21:00 | 231 | 230
2016-05-19 21:30 | 219 | 219
2016-05-19 22:00 | 218 | 218
2016-05-19 22:30 | 210 | 210
2016-05-19 23:00 | 200 | 200
2016-05-19 23:30 | 190 | 190
2016-05-20 | 171 | 171
2016-05-20 00:30 | 161 | 161
2016-05-20 01:00 | 158 | 158
2016-05-20 01:30 | 155 | 155
2016-05-20 02:00 | 152 | 151
2016-05-20 02:30 | 148 | 147
2016-05-20 03:00 | 144 | 143
2016-05-20 03:30 | 143 | 142
2016-05-20 04:00 | 149 | 149
2016-05-20 04:30 | 152 | 152
2016-05-20 05:00 | 170 | 170
2016-05-20 05:30 | 184 | 184
2016-05-20 06:00 | 206 | 206
2016-05-20 06:30 | 232 | 232
2016-05-20 07:00 | 248 | 247
2016-05-20 07:30 | 253 | 250
2016-05-20 08:00 | 248 | 246
2016-05-20 08:30 | 241 | 240
2016-05-20 09:00 | 238 | 237
2016-05-20 09:30 | 238 | 236
2016-05-20 10:00 | 234 | 234
2016-05-20 10:30 | 233 | 232
2016-05-20 11:00 | 229 | 228
2016-05-20 11:30 | 228 | 227
2016-05-20 12:00 | 224 | 224
2016-05-20 12:30 | 222 | 222
2016-05-20 13:00 | 223 | 222
2016-05-20 13:30 | 227 | 226
2016-05-20 14:00 | 229 | 229
2016-05-20 14:30 | 233 | 232
2016-05-20 15:00 | 238 | 237
2016-05-20 15:30 | 248 | 247
2016-05-20 16:00 | 253 | 252
2016-05-20 16:30 | 263 | 260
2016-05-20 17:00 | 273 | 268
2016-05-20 17:30 | 282 | 277
2016-05-20 18:00 | 276 | 271
2016-05-20 18:30 | 269 | 262
2016-05-20 19:00 | 259 | 255
2016-05-20 19:30 | 255 | 254
2016-05-20 20:00 | 254 | 252
2016-05-20 20:30 | 251 | 250
2016-05-20 21:00 | 239 | 237
2016-05-20 21:30 | 225 | 223
2016-05-20 22:00 | 225 | 224
2016-05-20 22:30 | 221 | 220
2016-05-20 23:00 | 210 | 210
2016-05-20 23:30 | 201 | 200
2016-05-21 | 186 | 185
2016-05-21 00:30 | 172 | 171
2016-05-21 01:00 | 164 | 163
2016-05-21 01:30 | 161 | 159
2016-05-21 02:00 | 159 | 157
2016-05-21 02:30 | 157 | 155
2016-05-21 03:00 | 154 | 151
2016-05-21 03:30 | 147 | 144
2016-05-21 04:00 | 151 | 148
2016-05-21 04:30 | 154 | 152
2016-05-21 05:00 | 161 | 159
2016-05-21 05:30 | 164 | 162
2016-05-21 06:00 | 173 | 172
2016-05-21 06:30 | 180 | 179
2016-05-21 07:00 | 193 | 193
2016-05-21 07:30 | 205 | 205
2016-05-21 08:00 | 215 | 214
2016-05-21 08:30 | 222 | 222
2016-05-21 09:00 | 223 | 222
2016-05-21 09:30 | 221 | 221
2016-05-21 10:00 | 217 | 217
2016-05-21 10:30 | 211 | 211
2016-05-21 11:00 | 206 | 206
2016-05-21 11:30 | 202 | 202
2016-05-21 12:00 | 202 | 202
2016-05-21 12:30 | 206 | 206
2016-05-21 13:00 | 201 | 201
2016-05-21 13:30 | 205 | 205
2016-05-21 14:00 | 209 | 209
2016-05-21 14:30 | 213 | 213
2016-05-21 15:00 | 220 | 220
2016-05-21 15:30 | 227 | 227
2016-05-21 16:00 | 237 | 237
2016-05-21 16:30 | 256 | 255
2016-05-21 17:00 | 268 | 268
2016-05-21 17:30 | 271 | 270
2016-05-21 18:00 | 263 | 262
2016-05-21 18:30 | 256 | 256
2016-05-21 19:00 | 242 | 241
2016-05-21 19:30 | 237 | 236
2016-05-21 20:00 | 238 | 236
2016-05-21 20:30 | 225 | 223
2016-05-21 21:00 | 217 | 215
2016-05-21 21:30 | 208 | 205
2016-05-21 22:00 | 210 | 207
2016-05-21 22:30 | 208 | 205
2016-05-21 23:00 | 204 | 200
2016-05-21 23:30 | 191 | 189
2016-05-22 | 171 | 170
2016-05-22 00:30 | 165 | 164
2016-05-22 01:00 | 153 | 152
2016-05-22 01:30 | 154 | 152
2016-05-22 02:00 | 145 | 143
2016-05-22 02:30 | 138 | 137
2016-05-22 03:00 | 131 | 131
2016-05-22 03:30 | 137 | 136
2016-05-22 04:00 | 145 | 145
2016-05-22 04:30 | 148 | 148
2016-05-22 05:00 | 149 | 149
2016-05-22 05:30 | 152 | 152
2016-05-22 06:00 | 159 | 159
2016-05-22 06:30 | 163 | 163
2016-05-22 07:00 | 171 | 171
2016-05-22 07:30 | 188 | 188
2016-05-22 08:00 | 200 | 199
2016-05-22 08:30 | 204 | 204
2016-05-22 09:00 | 201 | 201
2016-05-22 09:30 | 207 | 207
2016-05-22 10:00 | 209 | 209
2016-05-22 10:30 | 210 | 210
2016-05-22 11:00 | 206 | 206
2016-05-22 11:30 | 194 | 194
2016-05-22 12:00 | 191 | 190
2016-05-22 12:30 | 189 | 189
2016-05-22 13:00 | 191 | 190
2016-05-22 13:30 | 193 | 192
2016-05-22 14:00 | 193 | 193
2016-05-22 14:30 | 198 | 197
2016-05-22 15:00 | 206 | 205
2016-05-22 15:30 | 214 | 214
2016-05-22 16:00 | 211 | 211
2016-05-22 16:30 | 235 | 233
2016-05-22 17:00 | 261 | 258
2016-05-22 17:30 | 275 | 270
2016-05-22 18:00 | 267 | 264
2016-05-22 18:30 | 265 | 261
2016-05-22 19:00 | 255 | 250
2016-05-22 19:30 | 252 | 247
2016-05-22 20:00 | 246 | 243
2016-05-22 20:30 | 227 | 227
2016-05-22 21:00 | 213 | 212
2016-05-22 21:30 | 203 | 202
2016-05-22 22:00 | 203 | 202
2016-05-22 22:30 | 203 | 203
2016-05-22 23:00 | 196 | 195
2016-05-22 23:30 | 184 | 183
2016-05-23 | 160 | 159
2016-05-23 00:30 | 150 | 148
2016-05-23 01:00 | 128 | 125
2016-05-23 01:30 | 131 | 129
2016-05-23 02:00 | 128 | 125
2016-05-23 02:30 | 117 | 113
2016-05-23 03:00 | 126 | 123
2016-05-23 03:30 | 116 | 113
2016-05-23 04:00 | 120 | 117
2016-05-23 04:30 | 125 | 123
2016-05-23 05:00 | 137 | 136
2016-05-23 05:30 | 159 | 158
2016-05-23 06:00 | 210 | 207
2016-05-23 06:30 | 235 | 231
2016-05-23 07:00 | 257 | 252
2016-05-23 07:30 | 263 | 257
2016-05-23 08:00 | 258 | 252
2016-05-23 08:30 | 257 | 252
2016-05-23 09:00 | 244 | 239
2016-05-23 09:30 | 220 | 216
2016-05-23 10:00 | 163 | 161
2016-05-23 10:30 | 161 | 160
2016-05-23 11:00 | 160 | 159
2016-05-23 11:30 | 159 | 158
2016-05-23 12:00 | 162 | 160
2016-05-23 12:30 | 164 | 163
2016-05-23 13:00 | 166 | 165
2016-05-23 13:30 | 168 | 167
2016-05-23 14:00 | 174 | 173
2016-05-23 14:30 | 176 | 175
2016-05-23 15:00 | 177 | 176
2016-05-23 15:30 | 180 | 179
2016-05-23 16:00 | 187 | 185
2016-05-23 16:30 | 194 | 192
2016-05-23 17:00 | 200 | 199
2016-05-23 17:30 | 205 | 204
2016-05-23 18:00 | 200 | 199
2016-05-23 18:30 | 196 | 194
2016-05-23 19:00 | 190 | 188
2016-05-23 19:30 | 188 | 186
2016-05-23 20:00 | 184 | 181
2016-05-23 20:30 | 170 | 169
2016-05-23 21:00 | 156 | 156
2016-05-23 21:30 | 147 | 147
2016-05-23 22:00 | 148 | 148
2016-05-23 22:30 | 143 | 143
2016-05-23 23:00 | 135 | 135
2016-05-23 23:30 | 128 | 127
2016-05-24 | 115 | 114
2016-05-24 00:30 | 109 | 107
2016-05-24 01:00 | 106 | 104
2016-05-24 01:30 | 105 | 102
2016-05-24 02:00 | 104 | 101
2016-05-24 02:30 | 102 | 99
2016-05-24 03:00 | 100 | 98
2016-05-24 03:30 | 101 | 98
2016-05-24 04:00 | 102 | 100
2016-05-24 04:30 | 105 | 103
2016-05-24 05:00 | 113 | 111
2016-05-24 05:30 | 121 | 120
2016-05-24 06:00 | 140 | 138
2016-05-24 06:30 | 163 | 160
2016-05-24 07:00 | 173 | 172
2016-05-24 07:30 | 177 | 174
2016-05-24 08:00 | 174 | 171
2016-05-24 08:30 | 169 | 166
2016-05-24 09:00 | 166 | 163
2016-05-24 09:30 | 164 | 161
2016-05-24 10:00 | 161 | 158
2016-05-24 10:30 | 159 | 157
2016-05-24 11:00 | 156 | 154
2016-05-24 11:30 | 154 | 152
2016-05-24 12:00 | 151 | 149
2016-05-24 12:30 | 151 | 149
2016-05-24 13:00 | 152 | 150
2016-05-24 13:30 | 155 | 152
2016-05-24 14:00 | 157 | 155
2016-05-24 14:30 | 160 | 158
2016-05-24 15:00 | 164 | 162
2016-05-24 15:30 | 171 | 169
2016-05-24 16:00 | 179 | 175
2016-05-24 16:30 | 190 | 186
2016-05-24 17:00 | 197 | 193
2016-05-24 17:30 | 202 | 198
2016-05-24 18:00 | 199 | 195
2016-05-24 18:30 | 198 | 194
2016-05-24 19:00 | 186 | 184
2016-05-24 19:30 | 187 | 186
2016-05-24 20:00 | 184 | 183
2016-05-24 20:30 | 176 | 174
2016-05-24 21:00 | 165 | 163
2016-05-24 21:30 | 152 | 150
2016-05-24 22:00 | 147 | 146
2016-05-24 22:30 | 140 | 140
2016-05-24 23:00 | 135 | 134
2016-05-24 23:30 | 132 | 131
2016-05-25 | 120 | 119
2016-05-25 00:30 | 114 | 112
2016-05-25 01:00 | 110 | 108
2016-05-25 01:30 | 106 | 104
2016-05-25 02:00 | 101 | 99
2016-05-25 02:30 | 100 | 98
2016-05-25 03:00 | 101 | 99
2016-05-25 03:30 | 91 | 89
2016-05-25 04:00 | 87 | 85
2016-05-25 04:30 | 111 | 109
2016-05-25 05:00 | 121 | 120
2016-05-25 05:30 | 127 | 126
2016-05-25 06:00 | 150 | 148
2016-05-25 06:30 | 168 | 166
2016-05-25 07:00 | 175 | 174
2016-05-25 07:30 | 177 | 176
2016-05-25 08:00 | 171 | 170
2016-05-25 08:30 | 165 | 164
2016-05-25 09:00 | 163 | 162
2016-05-25 09:30 | 157 | 156
2016-05-25 10:00 | 157 | 157
2016-05-25 10:30 | 156 | 155
2016-05-25 11:00 | 153 | 153
2016-05-25 11:30 | 154 | 153
2016-05-25 12:00 | 151 | 151
2016-05-25 12:30 | 152 | 152
2016-05-25 13:00 | 156 | 155
2016-05-25 13:30 | 158 | 157
2016-05-25 14:00 | 164 | 163
2016-05-25 14:30 | 169 | 167
2016-05-25 15:00 | 176 | 174
2016-05-25 15:30 | 182 | 180
2016-05-25 16:00 | 189 | 187
2016-05-25 16:30 | 196 | 194
2016-05-25 17:00 | 208 | 207
2016-05-25 17:30 | 218 | 214
2016-05-25 18:00 | 217 | 213
2016-05-25 18:30 | 216 | 211
2016-05-25 19:00 | 205 | 201
2016-05-25 19:30 | 200 | 197
2016-05-25 20:00 | 195 | 191
2016-05-25 20:30 | 181 | 179
2016-05-25 21:00 | 172 | 170
2016-05-25 21:30 | 161 | 159
2016-05-25 22:00 | 158 | 157
2016-05-25 22:30 | 150 | 149
2016-05-25 23:00 | 143 | 143
2016-05-25 23:30 | 137 | 136
2016-05-26 | 128 | 127
2016-05-26 00:30 | 119 | 118
2016-05-26 01:00 | 114 | 113
2016-05-26 01:30 | 112 | 110
2016-05-26 02:00 | 107 | 105
2016-05-26 02:30 | 104 | 102
2016-05-26 03:00 | 101 | 99
2016-05-26 03:30 | 102 | 100
2016-05-26 04:00 | 104 | 103
2016-05-26 04:30 | 107 | 106
2016-05-26 05:00 | 120 | 120
2016-05-26 05:30 | 127 | 126
2016-05-26 06:00 | 147 | 145
2016-05-26 06:30 | 164 | 163
2016-05-26 07:00 | 181 | 180
2016-05-26 07:30 | 188 | 186
2016-05-26 08:00 | 184 | 182
2016-05-26 08:30 | 182 | 180
2016-05-26 09:00 | 177 | 175
2016-05-26 09:30 | 178 | 176
2016-05-26 10:00 | 177 | 175
2016-05-26 10:30 | 191 | 189
2016-05-26 11:00 | 186 | 184
2016-05-26 11:30 | 168 | 166
2016-05-26 12:00 | 162 | 161
2016-05-26 12:30 | 158 | 157
2016-05-26 13:00 | 161 | 160
2016-05-26 13:30 | 167 | 166
2016-05-26 14:00 | 170 | 169
2016-05-26 14:30 | 170 | 169
2016-05-26 15:00 | 175 | 174
2016-05-26 15:30 | 178 | 177
2016-05-26 16:00 | 183 | 181
2016-05-26 16:30 | 191 | 190
2016-05-26 17:00 | 205 | 204
2016-05-26 17:30 | 214 | 212
2016-05-26 18:00 | 209 | 207
2016-05-26 18:30 | 206 | 205
2016-05-26 19:00 | 203 | 202
2016-05-26 19:30 | 201 | 200
2016-05-26 20:00 | 192 | 191
2016-05-26 20:30 | 185 | 182
2016-05-26 21:00 | 174 | 171
2016-05-26 21:30 | 158 | 157
2016-05-26 22:00 | 158 | 158
2016-05-26 22:30 | 155 | 154
2016-05-26 23:00 | 151 | 150
2016-05-26 23:30 | 143 | 142
2016-05-27 | 132 | 130
2016-05-27 00:30 | 128 | 125
2016-05-27 01:00 | 122 | 119
2016-05-27 01:30 | 111 | 110
2016-05-27 02:00 | 105 | 104
2016-05-27 02:30 | 102 | 101
2016-05-27 03:00 | 100 | 99
2016-05-27 03:30 | 100 | 98
2016-05-27 04:00 | 103 | 102
2016-05-27 04:30 | 108 | 107
2016-05-27 05:00 | 115 | 114
2016-05-27 05:30 | 126 | 123
2016-05-27 06:00 | 140 | 138
2016-05-27 06:30 | 159 | 156
2016-05-27 07:00 | 171 | 169
2016-05-27 07:30 | 175 | 172
2016-05-27 08:00 | 173 | 170
2016-05-27 08:30 | 171 | 168
2016-05-27 09:00 | 170 | 167
2016-05-27 09:30 | 168 | 166
2016-05-27 10:00 | 159 | 156
2016-05-27 10:30 | 156 | 154
2016-05-27 11:00 | 152 | 149
2016-05-27 11:30 | 154 | 151
2016-05-27 12:00 | 153 | 151
2016-05-27 12:30 | 155 | 152
2016-05-27 13:00 | 153 | 152
2016-05-27 13:30 | 155 | 154
2016-05-27 14:00 | 156 | 155
2016-05-27 14:30 | 177 | 176
2016-05-27 15:00 | 236 | 234
2016-05-27 15:30 | 246 | 244
2016-05-27 16:00 | 253 | 251
2016-05-27 16:30 | 264 | 262
2016-05-27 17:00 | 284 | 282
2016-05-27 17:30 | 291 | 289
2016-05-27 18:00 | 282 | 280
2016-05-27 18:30 | 274 | 273
2016-05-27 19:00 | 269 | 267
2016-05-27 19:30 | 267 | 266
2016-05-27 20:00 | 262 | 260
2016-05-27 20:30 | 249 | 247
2016-05-27 21:00 | 233 | 230
2016-05-27 21:30 | 223 | 219
2016-05-27 22:00 | 227 | 223
2016-05-27 22:30 | 220 | 218
2016-05-27 23:00 | 212 | 212
2016-05-27 23:30 | 205 | 204
2016-05-28 | 191 | 190
2016-05-28 00:30 | 174 | 172
2016-05-28 01:00 | 159 | 157
2016-05-28 01:30 | 159 | 156
2016-05-28 02:00 | 156 | 153
2016-05-28 02:30 | 154 | 151
2016-05-28 03:00 | 152 | 149
2016-05-28 03:30 | 149 | 146
2016-05-28 04:00 | 150 | 146
2016-05-28 04:30 | 153 | 150
2016-05-28 05:00 | 158 | 155
2016-05-28 05:30 | 169 | 166
2016-05-28 06:00 | 184 | 182
2016-05-28 06:30 | 202 | 200
2016-05-28 07:00 | 216 | 215
2016-05-28 07:30 | 220 | 220
2016-05-28 08:00 | 224 | 224
2016-05-28 08:30 | 228 | 228
2016-05-28 09:00 | 229 | 229
2016-05-28 09:30 | 228 | 228
2016-05-28 10:00 | 232 | 232
2016-05-28 10:30 | 232 | 231
2016-05-28 11:00 | 245 | 242
2016-05-28 11:30 | 227 | 223
2016-05-28 12:00 | 228 | 224
2016-05-28 12:30 | 218 | 214
2016-05-28 13:00 | 226 | 224
2016-05-28 13:30 | 226 | 223
2016-05-28 14:00 | 222 | 220
2016-05-28 14:30 | 224 | 222
2016-05-28 15:00 | 228 | 226
2016-05-28 15:30 | 233 | 230
2016-05-28 16:00 | 242 | 240
2016-05-28 16:30 | 261 | 258
2016-05-28 17:00 | 276 | 272
2016-05-28 17:30 | 283 | 280
2016-05-28 18:00 | 280 | 276
2016-05-28 18:30 | 277 | 272
2016-05-28 19:00 | 262 | 258
2016-05-28 19:30 | 259 | 256
2016-05-28 20:00 | 256 | 253
2016-05-28 20:30 | 247 | 243
2016-05-28 21:00 | 237 | 236
2016-05-28 21:30 | 228 | 227
2016-05-28 22:00 | 223 | 222
2016-05-28 22:30 | 219 | 218
2016-05-28 23:00 | 209 | 209
2016-05-28 23:30 | 203 | 203
2016-05-29 | 190 | 189
2016-05-29 00:30 | 178 | 177
2016-05-29 01:00 | 169 | 169
2016-05-29 01:30 | 168 | 168
2016-05-29 02:00 | 159 | 158
2016-05-29 02:30 | 159 | 158
2016-05-29 03:00 | 160 | 159
2016-05-29 03:30 | 160 | 159
2016-05-29 04:00 | 160 | 159
2016-05-29 04:30 | 162 | 161
2016-05-29 05:00 | 160 | 160
2016-05-29 05:30 | 165 | 165
2016-05-29 06:00 | 174 | 173
2016-05-29 06:30 | 185 | 185
2016-05-29 07:00 | 199 | 198
2016-05-29 07:30 | 220 | 219
2016-05-29 08:00 | 228 | 228
2016-05-29 08:30 | 253 | 252
2016-05-29 09:00 | 237 | 236
2016-05-29 09:30 | 236 | 236
2016-05-29 10:00 | 210 | 209
2016-05-29 10:30 | 170 | 168
2016-05-29 11:00 | 165 | 163
2016-05-29 11:30 | 162 | 160
2016-05-29 12:00 | 163 | 161
2016-05-29 12:30 | 167 | 165
2016-05-29 13:00 | 178 | 176
2016-05-29 13:30 | 199 | 197
2016-05-29 14:00 | 203 | 202
2016-05-29 14:30 | 209 | 208
2016-05-29 15:00 | 218 | 217
2016-05-29 15:30 | 230 | 229
2016-05-29 16:00 | 240 | 239
2016-05-29 16:30 | 259 | 258
2016-05-29 17:00 | 279 | 275
2016-05-29 17:30 | 291 | 286
2016-05-29 18:00 | 288 | 283
2016-05-29 18:30 | 285 | 281
2016-05-29 19:00 | 280 | 276
2016-05-29 19:30 | 279 | 275
2016-05-29 20:00 | 276 | 272
2016-05-29 20:30 | 269 | 263
2016-05-29 21:00 | 260 | 254
2016-05-29 21:30 | 243 | 240
2016-05-29 22:00 | 231 | 229
2016-05-29 22:30 | 225 | 222
2016-05-29 23:00 | 209 | 207
2016-05-29 23:30 | 197 | 196
2016-05-30 | 185 | 183
2016-05-30 00:30 | 176 | 174
2016-05-30 01:00 | 179 | 176
2016-05-30 01:30 | 171 | 168
2016-05-30 02:00 | 159 | 156
2016-05-30 02:30 | 154 | 150
2016-05-30 03:00 | 156 | 153
2016-05-30 03:30 | 156 | 153
2016-05-30 04:00 | 160 | 157
2016-05-30 04:30 | 167 | 165
2016-05-30 05:00 | 187 | 185
2016-05-30 05:30 | 201 | 200
2016-05-30 06:00 | 234 | 232
2016-05-30 06:30 | 261 | 258
2016-05-30 07:00 | 279 | 274
2016-05-30 07:30 | 285 | 281
2016-05-30 08:00 | 285 | 281
2016-05-30 08:30 | 276 | 272
2016-05-30 09:00 | 281 | 278
2016-05-30 09:30 | 270 | 267
2016-05-30 10:00 | 256 | 253
2016-05-30 10:30 | 246 | 246
2016-05-30 11:00 | 239 | 238
2016-05-30 11:30 | 232 | 231
2016-05-30 12:00 | 233 | 233
2016-05-30 12:30 | 235 | 235
2016-05-30 13:00 | 233 | 232
2016-05-30 13:30 | 238 | 238
2016-05-30 14:00 | 239 | 239
2016-05-30 14:30 | 244 | 244
2016-05-30 15:00 | 251 | 249
2016-05-30 15:30 | 269 | 265
2016-05-30 16:00 | 284 | 280
2016-05-30 16:30 | 303 | 300
2016-05-30 17:00 | 320 | 318
2016-05-30 17:30 | 322 | 321
2016-05-30 18:00 | 317 | 315
2016-05-30 18:30 | 316 | 314
2016-05-30 19:00 | 306 | 303
2016-05-30 19:30 | 303 | 300
2016-05-30 20:00 | 295 | 292
2016-05-30 20:30 | 285 | 281
2016-05-30 21:00 | 270 | 267
2016-05-30 21:30 | 249 | 248
2016-05-30 22:00 | 251 | 250
2016-05-30 22:30 | 245 | 244
2016-05-30 23:00 | 232 | 230
2016-05-30 23:30 | 219 | 216
2016-05-31 | 207 | 204
2016-05-31 00:30 | 213 | 210
2016-05-31 01:00 | 197 | 193
2016-05-31 01:30 | 201 | 198
2016-05-31 02:00 | 177 | 175
2016-05-31 02:30 | 173 | 171
2016-05-31 03:00 | 171 | 168
2016-05-31 03:30 | 169 | 166
2016-05-31 04:00 | 175 | 173
2016-05-31 04:30 | 184 | 182
2016-05-31 05:00 | 199 | 198
2016-05-31 05:30 | 208 | 208
2016-05-31 06:00 | 242 | 240
2016-05-31 06:30 | 293 | 291
2016-05-31 07:00 | 299 | 295
2016-05-31 07:30 | 308 | 305
2016-05-31 08:00 | 305 | 302
2016-05-31 08:30 | 300 | 297
2016-05-31 09:00 | 295 | 293
2016-05-31 09:30 | 272 | 270
2016-05-31 10:00 | 271 | 271
2016-05-31 10:30 | 275 | 275
2016-05-31 11:00 | 244 | 244
2016-05-31 11:30 | 240 | 239
2016-05-31 12:00 | 274 | 273
2016-05-31 12:30 | 252 | 252
2016-05-31 13:00 | 263 | 263
2016-05-31 13:30 | 262 | 262
2016-05-31 14:00 | 290 | 290
2016-05-31 14:30 | 291 | 291
2016-05-31 15:00 | 269 | 269
2016-05-31 15:30 | 278 | 278
2016-05-31 16:00 | 285 | 285
2016-05-31 16:30 | 301 | 301
2016-05-31 17:00 | 317 | 317
2016-05-31 17:30 | 320 | 320
2016-05-31 18:00 | 317 | 316
2016-05-31 18:30 | 314 | 313
2016-05-31 19:00 | 304 | 303
2016-05-31 19:30 | 297 | 297
2016-05-31 20:00 | 295 | 295
2016-05-31 20:30 | 277 | 277
2016-05-31 21:00 | 264 | 263
2016-05-31 21:30 | 251 | 250
2016-05-31 22:00 | 252 | 251
2016-05-31 22:30 | 240 | 240
2016-05-31 23:00 | 231 | 231
2016-05-31 23:30 | 232 | 232
2016-06-01 | 208 | 208
2016-06-01 00:30 | 216 | 216
2016-06-01 01:00 | 196 | 196
2016-06-01 01:30 | 176 | 176
2016-06-01 02:00 | 170 | 170
2016-06-01 02:30 | 171 | 171
2016-06-01 03:00 | 171 | 171
2016-06-01 03:30 | 171 | 171
2016-06-01 04:00 | 173 | 173
2016-06-01 04:30 | 178 | 177
2016-06-01 05:00 | 193 | 192
2016-06-01 05:30 | 210 | 208
2016-06-01 06:00 | 238 | 237
2016-06-01 06:30 | 269 | 268
2016-06-01 07:00 | 277 | 277
2016-06-01 07:30 | 284 | 284
2016-06-01 08:00 | 284 | 283
2016-06-01 08:30 | 279 | 278
2016-06-01 09:00 | 279 | 279
2016-06-01 09:30 | 274 | 274
2016-06-01 10:00 | 268 | 267
2016-06-01 10:30 | 268 | 268
2016-06-01 11:00 | 267 | 266
2016-06-01 11:30 | 256 | 256
2016-06-01 12:00 | 255 | 255
2016-06-01 12:30 | 256 | 254
2016-06-01 13:00 | 260 | 259
2016-06-01 13:30 | 271 | 270
2016-06-01 14:00 | 277 | 276
2016-06-01 14:30 | 265 | 264
2016-06-01 15:00 | 271 | 271
2016-06-01 15:30 | 287 | 287
2016-06-01 16:00 | 282 | 282
2016-06-01 16:30 | 295 | 295
2016-06-01 17:00 | 311 | 310
2016-06-01 17:30 | 323 | 322
2016-06-01 18:00 | 329 | 328
2016-06-01 18:30 | 313 | 313
2016-06-01 19:00 | 307 | 307
2016-06-01 19:30 | 317 | 317
2016-06-01 20:00 | 303 | 303
2016-06-01 20:30 | 310 | 310
2016-06-01 21:00 | 289 | 289
2016-06-01 21:30 | 264 | 264
2016-06-01 22:00 | 277 | 277
2016-06-01 22:30 | 247 | 247
2016-06-01 23:00 | 231 | 231
2016-06-01 23:30 | 221 | 221
2016-06-02 | 206 | 206
2016-06-02 00:30 | 190 | 190
2016-06-02 01:00 | 185 | 184
2016-06-02 01:30 | 197 | 197
2016-06-02 02:00 | 192 | 192
2016-06-02 02:30 | 182 | 182
2016-06-02 03:00 | 174 | 174
2016-06-02 03:30 | 170 | 170
2016-06-02 04:00 | 176 | 175
2016-06-02 04:30 | 187 | 186
2016-06-02 05:00 | 203 | 202
2016-06-02 05:30 | 221 | 220
2016-06-02 06:00 | 259 | 259
2016-06-02 06:30 | 262 | 262
2016-06-02 07:00 | 282 | 282
2016-06-02 07:30 | 290 | 290
2016-06-02 08:00 | 286 | 286
2016-06-02 08:30 | 284 | 284
2016-06-02 09:00 | 282 | 282
2016-06-02 09:30 | 265 | 265
2016-06-02 10:00 | 262 | 262
2016-06-02 10:30 | 258 | 257
2016-06-02 11:00 | 253 | 253
2016-06-02 11:30 | 263 | 262
2016-06-02 12:00 | 271 | 271
2016-06-02 12:30 | 274 | 274
2016-06-02 13:00 | 273 | 273
2016-06-02 13:30 | 271 | 271
2016-06-02 14:00 | 271 | 270
2016-06-02 14:30 | 277 | 277
2016-06-02 15:00 | 285 | 285
2016-06-02 15:30 | 282 | 282
2016-06-02 16:00 | 288 | 288
2016-06-02 16:30 | 294 | 294
2016-06-02 17:00 | 316 | 316
2016-06-02 17:30 | 323 | 323
2016-06-02 18:00 | 320 | 319
2016-06-02 18:30 | 318 | 318
2016-06-02 19:00 | 307 | 307
2016-06-02 19:30 | 301 | 300
2016-06-02 20:00 | 313 | 313
2016-06-02 20:30 | 306 | 306
2016-06-02 21:00 | 273 | 273
2016-06-02 21:30 | 255 | 255
2016-06-02 22:00 | 249 | 248
2016-06-02 22:30 | 242 | 241
2016-06-02 23:00 | 228 | 228
2016-06-02 23:30 | 215 | 215
2016-06-03 | 197 | 197
2016-06-03 00:30 | 183 | 183
2016-06-03 01:00 | 176 | 175
2016-06-03 01:30 | 167 | 166
2016-06-03 02:00 | 156 | 156
2016-06-03 02:30 | 149 | 149
2016-06-03 03:00 | 149 | 149
2016-06-03 03:30 | 150 | 150
2016-06-03 04:00 | 155 | 155
2016-06-03 04:30 | 162 | 162
2016-06-03 05:00 | 175 | 175
2016-06-03 05:30 | 190 | 190
2016-06-03 06:00 | 226 | 225
2016-06-03 06:30 | 258 | 258
2016-06-03 07:00 | 282 | 282
2016-06-03 07:30 | 293 | 288
2016-06-03 08:00 | 289 | 284
2016-06-03 08:30 | 286 | 282
2016-06-03 09:00 | 283 | 278
2016-06-03 09:30 | 273 | 268
2016-06-03 10:00 | 273 | 269
2016-06-03 10:30 | 273 | 269
2016-06-03 11:00 | 273 | 269
2016-06-03 11:30 | 274 | 270
2016-06-03 12:00 | 276 | 271
2016-06-03 12:30 | 277 | 272
2016-06-03 13:00 | 277 | 273
2016-06-03 13:30 | 275 | 270
2016-06-03 14:00 | 272 | 268
2016-06-03 14:30 | 272 | 267
2016-06-03 15:00 | 267 | 261
2016-06-03 15:30 | 275 | 270
2016-06-03 16:00 | 287 | 282
2016-06-03 16:30 | 302 | 298
2016-06-03 17:00 | 317 | 313
2016-06-03 17:30 | 324 | 319
2016-06-03 18:00 | 316 | 311
2016-06-03 18:30 | 309 | 306
2016-06-03 19:00 | 297 | 297
2016-06-03 19:30 | 293 | 293
2016-06-03 20:00 | 290 | 290
2016-06-03 20:30 | 277 | 277
2016-06-03 21:00 | 270 | 270
2016-06-03 21:30 | 259 | 259
2016-06-03 22:00 | 255 | 255
2016-06-03 22:30 | 243 | 243
2016-06-03 23:00 | 231 | 231
2016-06-03 23:30 | 223 | 223
2016-06-04 | 206 | 206
2016-06-04 00:30 | 196 | 196
2016-06-04 01:00 | 183 | 182
2016-06-04 01:30 | 172 | 171
2016-06-04 02:00 | 168 | 167
2016-06-04 02:30 | 156 | 156
2016-06-04 03:00 | 156 | 156
2016-06-04 03:30 | 151 | 151
2016-06-04 04:00 | 154 | 154
2016-06-04 04:30 | 159 | 159
2016-06-04 05:00 | 162 | 162
2016-06-04 05:30 | 166 | 166
2016-06-04 06:00 | 177 | 177
2016-06-04 06:30 | 188 | 188
2016-06-04 07:00 | 203 | 203
2016-06-04 07:30 | 224 | 224
2016-06-04 08:00 | 251 | 251
2016-06-04 08:30 | 270 | 269
2016-06-04 09:00 | 285 | 284
2016-06-04 09:30 | 291 | 290
2016-06-04 10:00 | 297 | 297
2016-06-04 10:30 | 301 | 299
2016-06-04 11:00 | 300 | 298
2016-06-04 11:30 | 300 | 298
2016-06-04 12:00 | 292 | 290
2016-06-04 12:30 | 290 | 289
2016-06-04 13:00 | 284 | 282
2016-06-04 13:30 | 278 | 277
2016-06-04 14:00 | 273 | 272
2016-06-04 14:30 | 268 | 267
2016-06-04 15:00 | 268 | 267
2016-06-04 15:30 | 277 | 276
2016-06-04 16:00 | 283 | 283
2016-06-04 16:30 | 295 | 295
2016-06-04 17:00 | 301 | 301
2016-06-04 17:30 | 297 | 297
2016-06-04 18:00 | 289 | 289
2016-06-04 18:30 | 287 | 286
2016-06-04 19:00 | 276 | 275
2016-06-04 19:30 | 268 | 268
2016-06-04 20:00 | 265 | 265
2016-06-04 20:30 | 255 | 255
2016-06-04 21:00 | 248 | 248
2016-06-04 21:30 | 239 | 239
2016-06-04 22:00 | 236 | 236
2016-06-04 22:30 | 234 | 234
2016-06-04 23:00 | 225 | 225
2016-06-04 23:30 | 214 | 213
2016-06-05 | 198 | 197
2016-06-05 00:30 | 188 | 187
2016-06-05 01:00 | 181 | 180
2016-06-05 01:30 | 170 | 170
2016-06-05 02:00 | 167 | 166
2016-06-05 02:30 | 161 | 161
2016-06-05 03:00 | 158 | 157
2016-06-05 03:30 | 150 | 150
2016-06-05 04:00 | 148 | 148
2016-06-05 04:30 | 149 | 149
2016-06-05 05:00 | 153 | 153
2016-06-05 05:30 | 155 | 155
2016-06-05 06:00 | 162 | 162
2016-06-05 06:30 | 171 | 170
2016-06-05 07:00 | 185 | 185
2016-06-05 07:30 | 197 | 197
2016-06-05 08:00 | 220 | 220
2016-06-05 08:30 | 227 | 227
2016-06-05 09:00 | 234 | 233
2016-06-05 09:30 | 236 | 236
2016-06-05 10:00 | 230 | 230
2016-06-05 10:30 | 225 | 225
2016-06-05 11:00 | 222 | 222
2016-06-05 11:30 | 222 | 222
2016-06-05 12:00 | 232 | 232
2016-06-05 12:30 | 219 | 219
2016-06-05 13:00 | 217 | 217
2016-06-05 13:30 | 218 | 218
2016-06-05 14:00 | 220 | 220
2016-06-05 14:30 | 226 | 226
2016-06-05 15:00 | 240 | 240
2016-06-05 15:30 | 247 | 247
2016-06-05 16:00 | 258 | 258
2016-06-05 16:30 | 268 | 268
2016-06-05 17:00 | 288 | 288
2016-06-05 17:30 | 297 | 296
2016-06-05 18:00 | 294 | 293
2016-06-05 18:30 | 292 | 290
2016-06-05 19:00 | 278 | 277
2016-06-05 19:30 | 271 | 270
2016-06-05 20:00 | 269 | 268
2016-06-05 20:30 | 255 | 255
2016-06-05 21:00 | 242 | 242
2016-06-05 21:30 | 228 | 228
2016-06-05 22:00 | 220 | 220
2016-06-05 22:30 | 217 | 217
2016-06-05 23:00 | 210 | 209
2016-06-05 23:30 | 199 | 199
2016-06-06 | 184 | 183
2016-06-06 00:30 | 175 | 174
2016-06-06 01:00 | 169 | 168
2016-06-06 01:30 | 161 | 160
2016-06-06 02:00 | 152 | 151
2016-06-06 02:30 | 148 | 147
2016-06-06 03:00 | 147 | 147
2016-06-06 03:30 | 149 | 149
2016-06-06 04:00 | 154 | 154
2016-06-06 04:30 | 160 | 160
2016-06-06 05:00 | 169 | 169
2016-06-06 05:30 | 177 | 177
2016-06-06 06:00 | 205 | 205
2016-06-06 06:30 | 241 | 241
2016-06-06 07:00 | 259 | 259
2016-06-06 07:30 | 263 | 263
2016-06-06 08:00 | 260 | 260
2016-06-06 08:30 | 266 | 266
2016-06-06 09:00 | 279 | 279
2016-06-06 09:30 | 278 | 278
2016-06-06 10:00 | 261 | 261
2016-06-06 10:30 | 265 | 265
2016-06-06 11:00 | 256 | 256
2016-06-06 11:30 | 247 | 247
2016-06-06 12:00 | 247 | 247
2016-06-06 12:30 | 248 | 248
2016-06-06 13:00 | 246 | 246
2016-06-06 13:30 | 244 | 243
2016-06-06 14:00 | 242 | 242
2016-06-06 14:30 | 241 | 241
2016-06-06 15:00 | 246 | 246
2016-06-06 15:30 | 249 | 248
2016-06-06 16:00 | 254 | 253
2016-06-06 16:30 | 274 | 274
2016-06-06 17:00 | 312 | 312
2016-06-06 17:30 | 320 | 320
2016-06-06 18:00 | 317 | 317
2016-06-06 18:30 | 317 | 316
2016-06-06 19:00 | 305 | 304
2016-06-06 19:30 | 306 | 305
2016-06-06 20:00 | 304 | 302
2016-06-06 20:30 | 289 | 287
2016-06-06 21:00 | 267 | 265
2016-06-06 21:30 | 251 | 249
2016-06-06 22:00 | 250 | 249
2016-06-06 22:30 | 242 | 242
2016-06-06 23:00 | 225 | 225
2016-06-06 23:30 | 210 | 210
2016-06-07 | 194 | 193
2016-06-07 00:30 | 186 | 185
2016-06-07 01:00 | 178 | 176
2016-06-07 01:30 | 173 | 171
2016-06-07 02:00 | 162 | 161
2016-06-07 02:30 | 156 | 155
2016-06-07 03:00 | 154 | 154
2016-06-07 03:30 | 155 | 154
2016-06-07 04:00 | 159 | 159
2016-06-07 04:30 | 166 | 166
2016-06-07 05:00 | 183 | 183
2016-06-07 05:30 | 200 | 200
2016-06-07 06:00 | 231 | 230
2016-06-07 06:30 | 269 | 268
2016-06-07 07:00 | 283 | 281
2016-06-07 07:30 | 288 | 287
2016-06-07 08:00 | 279 | 279
2016-06-07 08:30 | 298 | 297
2016-06-07 09:00 | 285 | 284
2016-06-07 09:30 | 277 | 276
2016-06-07 10:00 | 270 | 269
2016-06-07 10:30 | 260 | 259
2016-06-07 11:00 | 256 | 255
2016-06-07 11:30 | 256 | 255
2016-06-07 12:00 | 256 | 255
2016-06-07 12:30 | 256 | 256
2016-06-07 13:00 | 257 | 256
2016-06-07 13:30 | 261 | 261
2016-06-07 14:00 | 263 | 263
2016-06-07 14:30 | 265 | 264
2016-06-07 15:00 | 264 | 264
2016-06-07 15:30 | 257 | 256
2016-06-07 16:00 | 269 | 269
2016-06-07 16:30 | 290 | 288
2016-06-07 17:00 | 312 | 311
2016-06-07 17:30 | 327 | 327
2016-06-07 18:00 | 326 | 326
2016-06-07 18:30 | 324 | 324
2016-06-07 19:00 | 314 | 313
2016-06-07 19:30 | 312 | 311
2016-06-07 20:00 | 310 | 309
2016-06-07 20:30 | 291 | 291
2016-06-07 21:00 | 276 | 276
2016-06-07 21:30 | 261 | 261
2016-06-07 22:00 | 261 | 261
2016-06-07 22:30 | 254 | 254
2016-06-07 23:00 | 246 | 246
2016-06-07 23:30 | 240 | 240
2016-06-08 | 210 | 209
2016-06-08 00:30 | 197 | 196
2016-06-08 01:00 | 189 | 188
2016-06-08 01:30 | 187 | 186
2016-06-08 02:00 | 177 | 176
2016-06-08 02:30 | 170 | 169
2016-06-08 03:00 | 168 | 167
2016-06-08 03:30 | 169 | 169
2016-06-08 04:00 | 176 | 176
2016-06-08 04:30 | 186 | 186
2016-06-08 05:00 | 196 | 196
2016-06-08 05:30 | 208 | 208
2016-06-08 06:00 | 236 | 235
2016-06-08 06:30 | 266 | 264
2016-06-08 07:00 | 278 | 276
2016-06-08 07:30 | 268 | 267
2016-06-08 08:00 | 257 | 256
2016-06-08 08:30 | 216 | 214
2016-06-08 09:00 | 205 | 202
2016-06-08 09:30 | 197 | 194
2016-06-08 10:00 | 192 | 188
2016-06-08 10:30 | 188 | 185
2016-06-08 11:00 | 184 | 181
2016-06-08 11:30 | 183 | 181
2016-06-08 12:00 | 183 | 180
2016-06-08 12:30 | 183 | 181
2016-06-08 13:00 | 186 | 184
2016-06-08 13:30 | 190 | 187
2016-06-08 14:00 | 193 | 191
2016-06-08 14:30 | 197 | 195
2016-06-08 15:00 | 211 | 209
2016-06-08 15:30 | 232 | 231
2016-06-08 16:00 | 249 | 248
2016-06-08 16:30 | 274 | 273
2016-06-08 17:00 | 304 | 301
2016-06-08 17:30 | 313 | 310
2016-06-08 18:00 | 313 | 311
2016-06-08 18:30 | 312 | 310
2016-06-08 19:00 | 303 | 302
2016-06-08 19:30 | 297 | 297
2016-06-08 20:00 | 287 | 286
2016-06-08 20:30 | 274 | 273
2016-06-08 21:00 | 255 | 255
2016-06-08 21:30 | 241 | 241
2016-06-08 22:00 | 237 | 237
2016-06-08 22:30 | 230 | 228
2016-06-08 23:00 | 221 | 219
2016-06-08 23:30 | 212 | 210
2016-06-09 | 193 | 190
2016-06-09 00:30 | 181 | 177
2016-06-09 01:00 | 174 | 170
2016-06-09 01:30 | 171 | 166
2016-06-09 02:00 | 162 | 158
2016-06-09 02:30 | 157 | 152
2016-06-09 03:00 | 157 | 152
2016-06-09 03:30 | 158 | 152
2016-06-09 04:00 | 161 | 156
2016-06-09 04:30 | 166 | 162
2016-06-09 05:00 | 182 | 179
2016-06-09 05:30 | 199 | 195
2016-06-09 06:00 | 228 | 222
2016-06-09 06:30 | 253 | 251
2016-06-09 07:00 | 269 | 267
2016-06-09 07:30 | 271 | 269
2016-06-09 08:00 | 294 | 292
2016-06-09 08:30 | 283 | 281
2016-06-09 09:00 | 268 | 266
2016-06-09 09:30 | 259 | 257
2016-06-09 10:00 | 257 | 255
2016-06-09 10:30 | 254 | 253
2016-06-09 11:00 | 252 | 250
2016-06-09 11:30 | 249 | 248
2016-06-09 12:00 | 250 | 248
2016-06-09 12:30 | 250 | 247
2016-06-09 13:00 | 253 | 249
2016-06-09 13:30 | 253 | 249
2016-06-09 14:00 | 258 | 255
2016-06-09 14:30 | 261 | 257
2016-06-09 15:00 | 240 | 236
2016-06-09 15:30 | 247 | 244
2016-06-09 16:00 | 255 | 251
2016-06-09 16:30 | 270 | 264
2016-06-09 17:00 | 289 | 285
2016-06-09 17:30 | 302 | 299
2016-06-09 18:00 | 299 | 296
2016-06-09 18:30 | 298 | 294
2016-06-09 19:00 | 290 | 286
2016-06-09 19:30 | 282 | 280
2016-06-09 20:00 | 274 | 273
2016-06-09 20:30 | 261 | 259
2016-06-09 21:00 | 245 | 243
2016-06-09 21:30 | 236 | 233
2016-06-09 22:00 | 237 | 235
2016-06-09 22:30 | 230 | 227
2016-06-09 23:00 | 217 | 217
2016-06-09 23:30 | 203 | 203
2016-06-10 | 181 | 180
2016-06-10 00:30 | 165 | 165
2016-06-10 01:00 | 156 | 156
2016-06-10 01:30 | 153 | 153
2016-06-10 02:00 | 150 | 150
2016-06-10 02:30 | 149 | 149
2016-06-10 03:00 | 149 | 149
2016-06-10 03:30 | 149 | 149
2016-06-10 04:00 | 158 | 158
2016-06-10 04:30 | 162 | 162
2016-06-10 05:00 | 175 | 175
2016-06-10 05:30 | 184 | 184
2016-06-10 06:00 | 211 | 211
2016-06-10 06:30 | 238 | 238
2016-06-10 07:00 | 257 | 256
2016-06-10 07:30 | 271 | 269
2016-06-10 08:00 | 273 | 271
2016-06-10 08:30 | 258 | 257
2016-06-10 09:00 | 251 | 250
2016-06-10 09:30 | 247 | 246
2016-06-10 10:00 | 238 | 237
2016-06-10 10:30 | 233 | 232
2016-06-10 11:00 | 233 | 232
2016-06-10 11:30 | 227 | 227
2016-06-10 12:00 | 228 | 227
2016-06-10 12:30 | 223 | 222
2016-06-10 13:00 | 220 | 219
2016-06-10 13:30 | 221 | 221
2016-06-10 14:00 | 222 | 222
2016-06-10 14:30 | 227 | 226
2016-06-10 15:00 | 232 | 230
2016-06-10 15:30 | 236 | 235
2016-06-10 16:00 | 247 | 246
2016-06-10 16:30 | 265 | 264
2016-06-10 17:00 | 285 | 285
2016-06-10 17:30 | 289 | 289
2016-06-10 18:00 | 282 | 282
2016-06-10 18:30 | 280 | 280
2016-06-10 19:00 | 278 | 277
2016-06-10 19:30 | 274 | 273
2016-06-10 20:00 | 269 | 268
2016-06-10 20:30 | 260 | 258
2016-06-10 21:00 | 240 | 239
2016-06-10 21:30 | 230 | 230
2016-06-10 22:00 | 226 | 226
2016-06-10 22:30 | 224 | 224
2016-06-10 23:00 | 214 | 214
2016-06-10 23:30 | 203 | 202
2016-06-11 | 184 | 183
2016-06-11 00:30 | 174 | 173
2016-06-11 01:00 | 163 | 162
2016-06-11 01:30 | 155 | 154
2016-06-11 02:00 | 149 | 147
2016-06-11 02:30 | 146 | 144
2016-06-11 03:00 | 143 | 143
2016-06-11 03:30 | 144 | 144
2016-06-11 04:00 | 147 | 147
2016-06-11 04:30 | 152 | 152
2016-06-11 05:00 | 161 | 161
2016-06-11 05:30 | 172 | 172
2016-06-11 06:00 | 182 | 182
2016-06-11 06:30 | 193 | 193
2016-06-11 07:00 | 209 | 209
2016-06-11 07:30 | 228 | 226
2016-06-11 08:00 | 234 | 232
2016-06-11 08:30 | 235 | 233
2016-06-11 09:00 | 237 | 235
2016-06-11 09:30 | 239 | 237
2016-06-11 10:00 | 236 | 234
2016-06-11 10:30 | 232 | 230
2016-06-11 11:00 | 227 | 225
2016-06-11 11:30 | 218 | 216
2016-06-11 12:00 | 211 | 210
2016-06-11 12:30 | 217 | 216
2016-06-11 13:00 | 211 | 210
2016-06-11 13:30 | 209 | 208
2016-06-11 14:00 | 207 | 207
2016-06-11 14:30 | 208 | 207
2016-06-11 15:00 | 213 | 213
2016-06-11 15:30 | 222 | 222
2016-06-11 16:00 | 233 | 233
2016-06-11 16:30 | 250 | 250
2016-06-11 17:00 | 275 | 275
2016-06-11 17:30 | 283 | 281
2016-06-11 18:00 | 278 | 276
2016-06-11 18:30 | 274 | 272
2016-06-11 19:00 | 268 | 267
2016-06-11 19:30 | 270 | 269
2016-06-11 20:00 | 269 | 267
2016-06-11 20:30 | 260 | 258
2016-06-11 21:00 | 257 | 255
2016-06-11 21:30 | 248 | 246
2016-06-11 22:00 | 239 | 238
2016-06-11 22:30 | 235 | 234
2016-06-11 23:00 | 224 | 224
2016-06-11 23:30 | 216 | 216
2016-06-12 | 200 | 200
2016-06-12 00:30 | 184 | 184
2016-06-12 01:00 | 170 | 170
2016-06-12 01:30 | 163 | 163
2016-06-12 02:00 | 158 | 158
2016-06-12 02:30 | 154 | 154
2016-06-12 03:00 | 148 | 148
2016-06-12 03:30 | 148 | 147
2016-06-12 04:00 | 148 | 148
2016-06-12 04:30 | 150 | 150
2016-06-12 05:00 | 158 | 158
2016-06-12 05:30 | 164 | 164
2016-06-12 06:00 | 174 | 174
2016-06-12 06:30 | 183 | 183
2016-06-12 07:00 | 193 | 193
2016-06-12 07:30 | 207 | 207
2016-06-12 08:00 | 229 | 229
2016-06-12 08:30 | 239 | 239
2016-06-12 09:00 | 244 | 244
2016-06-12 09:30 | 244 | 244
2016-06-12 10:00 | 244 | 244
2016-06-12 10:30 | 233 | 233
2016-06-12 11:00 | 224 | 224
2016-06-12 11:30 | 212 | 212
2016-06-12 12:00 | 207 | 207
2016-06-12 12:30 | 209 | 209
2016-06-12 13:00 | 207 | 207
2016-06-12 13:30 | 207 | 207
2016-06-12 14:00 | 211 | 211
2016-06-12 14:30 | 220 | 220
2016-06-12 15:00 | 230 | 230
2016-06-12 15:30 | 236 | 236
2016-06-12 16:00 | 249 | 249
2016-06-12 16:30 | 275 | 274
2016-06-12 17:00 | 294 | 293
2016-06-12 17:30 | 304 | 302
2016-06-12 18:00 | 300 | 298
2016-06-12 18:30 | 297 | 295
2016-06-12 19:00 | 291 | 289
2016-06-12 19:30 | 285 | 284
2016-06-12 20:00 | 283 | 282
2016-06-12 20:30 | 278 | 277
2016-06-12 21:00 | 279 | 277
2016-06-12 21:30 | 263 | 261
2016-06-12 22:00 | 241 | 240
2016-06-12 22:30 | 234 | 234
2016-06-12 23:00 | 229 | 229
2016-06-12 23:30 | 217 | 217
2016-06-13 | 197 | 197
2016-06-13 00:30 | 180 | 180
2016-06-13 01:00 | 167 | 167
2016-06-13 01:30 | 163 | 162
2016-06-13 02:00 | 158 | 158
2016-06-13 02:30 | 156 | 156
2016-06-13 03:00 | 151 | 151
2016-06-13 03:30 | 151 | 151
2016-06-13 04:00 | 154 | 154
2016-06-13 04:30 | 160 | 160
2016-06-13 05:00 | 168 | 168
2016-06-13 05:30 | 180 | 180
2016-06-13 06:00 | 207 | 206
2016-06-13 06:30 | 229 | 228
2016-06-13 07:00 | 254 | 253
2016-06-13 07:30 | 265 | 265
2016-06-13 08:00 | 267 | 267
2016-06-13 08:30 | 265 | 265
2016-06-13 09:00 | 265 | 265
2016-06-13 09:30 | 261 | 261
2016-06-13 10:00 | 255 | 255
2016-06-13 10:30 | 251 | 251
2016-06-13 11:00 | 248 | 247
2016-06-13 11:30 | 243 | 243
2016-06-13 12:00 | 229 | 228
2016-06-13 12:30 | 237 | 237
2016-06-13 13:00 | 238 | 238
2016-06-13 13:30 | 240 | 239
2016-06-13 14:00 | 245 | 245
2016-06-13 14:30 | 252 | 252
2016-06-13 15:00 | 250 | 249
2016-06-13 15:30 | 251 | 251
2016-06-13 16:00 | 265 | 265
2016-06-13 16:30 | 295 | 294
2016-06-13 17:00 | 315 | 315
2016-06-13 17:30 | 329 | 328
2016-06-13 18:00 | 328 | 327
2016-06-13 18:30 | 317 | 316
2016-06-13 19:00 | 308 | 306
2016-06-13 19:30 | 307 | 305
2016-06-13 20:00 | 303 | 301
2016-06-13 20:30 | 288 | 286
2016-06-13 21:00 | 270 | 269
2016-06-13 21:30 | 258 | 256
2016-06-13 22:00 | 246 | 244
2016-06-13 22:30 | 230 | 228
2016-06-13 23:00 | 216 | 216
2016-06-13 23:30 | 206 | 206
2016-06-14 | 189 | 189
2016-06-14 00:30 | 180 | 180
2016-06-14 01:00 | 172 | 172
2016-06-14 01:30 | 167 | 167
2016-06-14 02:00 | 156 | 156
2016-06-14 02:30 | 147 | 147
2016-06-14 03:00 | 145 | 144
2016-06-14 03:30 | 148 | 147
2016-06-14 04:00 | 152 | 152
2016-06-14 04:30 | 157 | 157
2016-06-14 05:00 | 168 | 168
2016-06-14 05:30 | 179 | 179
2016-06-14 06:00 | 211 | 211
2016-06-14 06:30 | 254 | 253
2016-06-14 07:00 | 268 | 267
2016-06-14 07:30 | 272 | 270
2016-06-14 08:00 | 269 | 268
2016-06-14 08:30 | 264 | 263
2016-06-14 09:00 | 255 | 254
2016-06-14 09:30 | 257 | 255
2016-06-14 10:00 | 256 | 256
2016-06-14 10:30 | 240 | 240
2016-06-14 11:00 | 232 | 232
2016-06-14 11:30 | 231 | 231
2016-06-14 12:00 | 235 | 234
2016-06-14 12:30 | 238 | 238
2016-06-14 13:00 | 238 | 238
2016-06-14 13:30 | 234 | 234
2016-06-14 14:00 | 237 | 237
2016-06-14 14:30 | 244 | 244
2016-06-14 15:00 | 252 | 251
2016-06-14 15:30 | 254 | 254
2016-06-14 16:00 | 263 | 263
2016-06-14 16:30 | 283 | 282
2016-06-14 17:00 | 309 | 308
2016-06-14 17:30 | 327 | 327
2016-06-14 18:00 | 321 | 320
2016-06-14 18:30 | 313 | 313
2016-06-14 19:00 | 303 | 303
2016-06-14 19:30 | 304 | 304
2016-06-14 20:00 | 296 | 296
2016-06-14 20:30 | 282 | 281
2016-06-14 21:00 | 262 | 262
2016-06-14 21:30 | 245 | 245
2016-06-14 22:00 | 247 | 247
2016-06-14 22:30 | 240 | 240
2016-06-14 23:00 | 228 | 228
2016-06-14 23:30 | 214 | 214
2016-06-15 | 192 | 192
2016-06-15 00:30 | 178 | 178
2016-06-15 01:00 | 166 | 165
2016-06-15 01:30 | 161 | 160
2016-06-15 02:00 | 157 | 156
2016-06-15 02:30 | 154 | 153
2016-06-15 03:00 | 155 | 154
2016-06-15 03:30 | 157 | 156
2016-06-15 04:00 | 160 | 159
2016-06-15 04:30 | 167 | 166
2016-06-15 05:00 | 183 | 181
2016-06-15 05:30 | 202 | 202
2016-06-15 06:00 | 228 | 227
2016-06-15 06:30 | 262 | 262
2016-06-15 07:00 | 281 | 281
2016-06-15 07:30 | 290 | 290
2016-06-15 08:00 | 285 | 283
2016-06-15 08:30 | 272 | 270
2016-06-15 09:00 | 271 | 269
2016-06-15 09:30 | 270 | 269
2016-06-15 10:00 | 260 | 258
2016-06-15 10:30 | 254 | 252
2016-06-15 11:00 | 239 | 239
2016-06-15 11:30 | 235 | 235
2016-06-15 12:00 | 232 | 232
2016-06-15 12:30 | 231 | 230
2016-06-15 13:00 | 228 | 228
2016-06-15 13:30 | 224 | 224
2016-06-15 14:00 | 226 | 226
2016-06-15 14:30 | 231 | 230
2016-06-15 15:00 | 239 | 239
2016-06-15 15:30 | 249 | 249
2016-06-15 16:00 | 269 | 268
2016-06-15 16:30 | 285 | 285
2016-06-15 17:00 | 303 | 303
2016-06-15 17:30 | 314 | 313
2016-06-15 18:00 | 312 | 312
2016-06-15 18:30 | 310 | 309
2016-06-15 19:00 | 300 | 299
2016-06-15 19:30 | 302 | 301
2016-06-15 20:00 | 298 | 297
2016-06-15 20:30 | 280 | 278
2016-06-15 21:00 | 256 | 254
2016-06-15 21:30 | 237 | 236
2016-06-15 22:00 | 239 | 239
2016-06-15 22:30 | 226 | 226
2016-06-15 23:00 | 210 | 210
2016-06-15 23:30 | 198 | 197
2016-06-16 | 184 | 183
2016-06-16 00:30 | 177 | 176
2016-06-16 01:00 | 166 | 165
2016-06-16 01:30 | 155 | 155
2016-06-16 02:00 | 151 | 150
2016-06-16 02:30 | 147 | 146
2016-06-16 03:00 | 148 | 148
2016-06-16 03:30 | 150 | 149
2016-06-16 04:00 | 153 | 152
2016-06-16 04:30 | 160 | 159
2016-06-16 05:00 | 171 | 170
2016-06-16 05:30 | 186 | 184
2016-06-16 06:00 | 214 | 213
2016-06-16 06:30 | 245 | 245
2016-06-16 07:00 | 270 | 269
2016-06-16 07:30 | 276 | 276
2016-06-16 08:00 | 269 | 268
2016-06-16 08:30 | 263 | 262
2016-06-16 09:00 | 260 | 259
2016-06-16 09:30 | 250 | 250
2016-06-16 10:00 | 239 | 239
2016-06-16 10:30 | 231 | 231
2016-06-16 11:00 | 231 | 231
2016-06-16 11:30 | 233 | 233
2016-06-16 12:00 | 231 | 231
2016-06-16 12:30 | 231 | 231
2016-06-16 13:00 | 232 | 232
2016-06-16 13:30 | 232 | 232
2016-06-16 14:00 | 234 | 234
2016-06-16 14:30 | 237 | 237
2016-06-16 15:00 | 243 | 243
2016-06-16 15:30 | 250 | 250
2016-06-16 16:00 | 261 | 261
2016-06-16 16:30 | 282 | 282
2016-06-16 17:00 | 298 | 298
2016-06-16 17:30 | 309 | 307
2016-06-16 18:00 | 310 | 308
2016-06-16 18:30 | 305 | 304
2016-06-16 19:00 | 295 | 294
2016-06-16 19:30 | 296 | 296
2016-06-16 20:00 | 292 | 292
2016-06-16 20:30 | 282 | 282
2016-06-16 21:00 | 267 | 267
2016-06-16 21:30 | 246 | 246
2016-06-16 22:00 | 240 | 240
2016-06-16 22:30 | 226 | 226
2016-06-16 23:00 | 213 | 212
2016-06-16 23:30 | 202 | 202
2016-06-17 | 187 | 187
2016-06-17 00:30 | 185 | 185
2016-06-17 01:00 | 176 | 176
2016-06-17 01:30 | 166 | 166
2016-06-17 02:00 | 160 | 160
2016-06-17 02:30 | 152 | 152
2016-06-17 03:00 | 146 | 146
2016-06-17 03:30 | 147 | 147
2016-06-17 04:00 | 150 | 150
2016-06-17 04:30 | 156 | 156
2016-06-17 05:00 | 168 | 168
2016-06-17 05:30 | 184 | 184
2016-06-17 06:00 | 214 | 213
2016-06-17 06:30 | 246 | 245
2016-06-17 07:00 | 261 | 261
2016-06-17 07:30 | 270 | 270
2016-06-17 08:00 | 257 | 257
2016-06-17 08:30 | 251 | 251
2016-06-17 09:00 | 251 | 250
2016-06-17 09:30 | 247 | 247
2016-06-17 10:00 | 247 | 247
2016-06-17 10:30 | 252 | 252
2016-06-17 11:00 | 253 | 253
2016-06-17 11:30 | 251 | 251
2016-06-17 12:00 | 248 | 248
2016-06-17 12:30 | 247 | 247
2016-06-17 13:00 | 253 | 253
2016-06-17 13:30 | 257 | 257
2016-06-17 14:00 | 255 | 255
2016-06-17 14:30 | 252 | 251
2016-06-17 15:00 | 251 | 251
2016-06-17 15:30 | 255 | 254
2016-06-17 16:00 | 267 | 266
2016-06-17 16:30 | 281 | 281
2016-06-17 17:00 | 301 | 301
2016-06-17 17:30 | 311 | 311
2016-06-17 18:00 | 299 | 299
2016-06-17 18:30 | 290 | 290
2016-06-17 19:00 | 280 | 280
2016-06-17 19:30 | 281 | 281
2016-06-17 20:00 | 274 | 274
2016-06-17 20:30 | 263 | 262
2016-06-17 21:00 | 250 | 249
2016-06-17 21:30 | 236 | 236
2016-06-17 22:00 | 235 | 235
2016-06-17 22:30 | 232 | 232
2016-06-17 23:00 | 223 | 223
2016-06-17 23:30 | 211 | 211
2016-06-18 | 203 | 202
2016-06-18 00:30 | 192 | 192
2016-06-18 01:00 | 177 | 176
2016-06-18 01:30 | 164 | 164
2016-06-18 02:00 | 163 | 163
2016-06-18 02:30 | 161 | 161
2016-06-18 03:00 | 158 | 158
2016-06-18 03:30 | 158 | 158
2016-06-18 04:00 | 158 | 158
2016-06-18 04:30 | 161 | 161
2016-06-18 05:00 | 163 | 163
2016-06-18 05:30 | 163 | 163
2016-06-18 06:00 | 171 | 171
2016-06-18 06:30 | 184 | 184
2016-06-18 07:00 | 201 | 200
2016-06-18 07:30 | 225 | 224
2016-06-18 08:00 | 229 | 228
2016-06-18 08:30 | 239 | 238
2016-06-18 09:00 | 248 | 246
2016-06-18 09:30 | 247 | 245
2016-06-18 10:00 | 244 | 242
2016-06-18 10:30 | 233 | 231
2016-06-18 11:00 | 232 | 230
2016-06-18 11:30 | 235 | 233
2016-06-18 12:00 | 235 | 233
2016-06-18 12:30 | 236 | 234
2016-06-18 13:00 | 233 | 232
2016-06-18 13:30 | 226 | 225
2016-06-18 14:00 | 230 | 229
2016-06-18 14:30 | 233 | 231
2016-06-18 15:00 | 234 | 233
2016-06-18 15:30 | 242 | 241
2016-06-18 16:00 | 250 | 249
2016-06-18 16:30 | 261 | 261
2016-06-18 17:00 | 276 | 275
2016-06-18 17:30 | 276 | 276
2016-06-18 18:00 | 274 | 274
2016-06-18 18:30 | 271 | 271
2016-06-18 19:00 | 262 | 262
2016-06-18 19:30 | 261 | 261
2016-06-18 20:00 | 255 | 255
2016-06-18 20:30 | 246 | 245
2016-06-18 21:00 | 235 | 235
2016-06-18 21:30 | 227 | 227
2016-06-18 22:00 | 226 | 226
2016-06-18 22:30 | 222 | 222
2016-06-18 23:00 | 212 | 212
2016-06-18 23:30 | 203 | 203
2016-06-19 | 190 | 190
2016-06-19 00:30 | 182 | 181
2016-06-19 01:00 | 177 | 176
2016-06-19 01:30 | 168 | 167
2016-06-19 02:00 | 156 | 155
2016-06-19 02:30 | 153 | 152
2016-06-19 03:00 | 152 | 151
2016-06-19 03:30 | 151 | 150
2016-06-19 04:00 | 151 | 150
2016-06-19 04:30 | 157 | 156
2016-06-19 05:00 | 157 | 156
2016-06-19 05:30 | 162 | 161
2016-06-19 06:00 | 171 | 169
2016-06-19 06:30 | 179 | 177
2016-06-19 07:00 | 195 | 194
2016-06-19 07:30 | 212 | 212
2016-06-19 08:00 | 226 | 226
2016-06-19 08:30 | 244 | 244
2016-06-19 09:00 | 253 | 253
2016-06-19 09:30 | 260 | 260
2016-06-19 10:00 | 266 | 265
2016-06-19 10:30 | 266 | 265
2016-06-19 11:00 | 265 | 264
2016-06-19 11:30 | 263 | 263
2016-06-19 12:00 | 265 | 265
2016-06-19 12:30 | 266 | 266
2016-06-19 13:00 | 264 | 264
2016-06-19 13:30 | 268 | 268
2016-06-19 14:00 | 271 | 270
2016-06-19 14:30 | 275 | 274
2016-06-19 15:00 | 276 | 276
2016-06-19 15:30 | 278 | 278
2016-06-19 16:00 | 286 | 285
2016-06-19 16:30 | 305 | 303
2016-06-19 17:00 | 311 | 309
2016-06-19 17:30 | 309 | 307
2016-06-19 18:00 | 308 | 306
2016-06-19 18:30 | 308 | 306
2016-06-19 19:00 | 296 | 294
2016-06-19 19:30 | 287 | 286
2016-06-19 20:00 | 276 | 276
2016-06-19 20:30 | 263 | 263
2016-06-19 21:00 | 253 | 253
2016-06-19 21:30 | 243 | 243
2016-06-19 22:00 | 242 | 241
2016-06-19 22:30 | 236 | 235
2016-06-19 23:00 | 227 | 226
2016-06-19 23:30 | 213 | 212
2016-06-20 | 197 | 197
2016-06-20 00:30 | 187 | 187
2016-06-20 01:00 | 178 | 178
2016-06-20 01:30 | 171 | 171
2016-06-20 02:00 | 166 | 166
2016-06-20 02:30 | 163 | 163
2016-06-20 03:00 | 163 | 163
2016-06-20 03:30 | 165 | 164
2016-06-20 04:00 | 169 | 168
2016-06-20 04:30 | 176 | 176
2016-06-20 05:00 | 187 | 187
2016-06-20 05:30 | 194 | 194
2016-06-20 06:00 | 219 | 218
2016-06-20 06:30 | 246 | 246
2016-06-20 07:00 | 272 | 271
2016-06-20 07:30 | 281 | 281
2016-06-20 08:00 | 280 | 280
2016-06-20 08:30 | 271 | 271
2016-06-20 09:00 | 265 | 264
2016-06-20 09:30 | 256 | 256
2016-06-20 10:00 | 250 | 250
2016-06-20 10:30 | 243 | 243
2016-06-20 11:00 | 240 | 240
2016-06-20 11:30 | 236 | 236
2016-06-20 12:00 | 236 | 236
2016-06-20 12:30 | 235 | 235
2016-06-20 13:00 | 240 | 240
2016-06-20 13:30 | 245 | 245
2016-06-20 14:00 | 248 | 247
2016-06-20 14:30 | 254 | 254
2016-06-20 15:00 | 262 | 262
2016-06-20 15:30 | 273 | 273
2016-06-20 16:00 | 281 | 281
2016-06-20 16:30 | 293 | 293
2016-06-20 17:00 | 317 | 315
2016-06-20 17:30 | 334 | 333
2016-06-20 18:00 | 332 | 330
2016-06-20 18:30 | 325 | 324
2016-06-20 19:00 | 315 | 314
2016-06-20 19:30 | 310 | 310
2016-06-20 20:00 | 305 | 305
2016-06-20 20:30 | 290 | 290
2016-06-20 21:00 | 271 | 270
2016-06-20 21:30 | 255 | 255
2016-06-20 22:00 | 246 | 245
2016-06-20 22:30 | 233 | 232
2016-06-20 23:00 | 219 | 219
2016-06-20 23:30 | 214 | 214
2016-06-21 | 191 | 191
2016-06-21 00:30 | 180 | 180
2016-06-21 01:00 | 172 | 172
2016-06-21 01:30 | 169 | 169
2016-06-21 02:00 | 166 | 166
2016-06-21 02:30 | 162 | 162
2016-06-21 03:00 | 161 | 161
2016-06-21 03:30 | 162 | 162
2016-06-21 04:00 | 167 | 167
2016-06-21 04:30 | 172 | 172
2016-06-21 05:00 | 181 | 181
2016-06-21 05:30 | 194 | 193
2016-06-21 06:00 | 216 | 215
2016-06-21 06:30 | 251 | 251
2016-06-21 07:00 | 271 | 271
2016-06-21 07:30 | 282 | 282
2016-06-21 08:00 | 279 | 278
2016-06-21 08:30 | 270 | 270
2016-06-21 09:00 | 276 | 276
2016-06-21 09:30 | 270 | 270
2016-06-21 10:00 | 268 | 268
2016-06-21 10:30 | 264 | 264
2016-06-21 11:00 | 258 | 257
2016-06-21 11:30 | 255 | 254
2016-06-21 12:00 | 245 | 244
2016-06-21 12:30 | 229 | 229
2016-06-21 13:00 | 225 | 224
2016-06-21 13:30 | 240 | 239
2016-06-21 14:00 | 250 | 249
2016-06-21 14:30 | 251 | 250
2016-06-21 15:00 | 260 | 259
2016-06-21 15:30 | 267 | 266
2016-06-21 16:00 | 276 | 276
2016-06-21 16:30 | 291 | 291
2016-06-21 17:00 | 313 | 312
2016-06-21 17:30 | 322 | 321
2016-06-21 18:00 | 321 | 320
2016-06-21 18:30 | 321 | 320
2016-06-21 19:00 | 315 | 314
2016-06-21 19:30 | 316 | 315
2016-06-21 20:00 | 309 | 308
2016-06-21 20:30 | 290 | 290
2016-06-21 21:00 | 275 | 274
2016-06-21 21:30 | 256 | 256
2016-06-21 22:00 | 251 | 251
2016-06-21 22:30 | 238 | 237
2016-06-21 23:00 | 223 | 222
2016-06-21 23:30 | 210 | 210
2016-06-22 | 194 | 192
2016-06-22 00:30 | 181 | 179
2016-06-22 01:00 | 173 | 172
2016-06-22 01:30 | 170 | 169
2016-06-22 02:00 | 167 | 166
2016-06-22 02:30 | 158 | 157
2016-06-22 03:00 | 164 | 162
2016-06-22 03:30 | 158 | 156
2016-06-22 04:00 | 162 | 161
2016-06-22 04:30 | 161 | 160
2016-06-22 05:00 | 182 | 180
2016-06-22 05:30 | 197 | 190
2016-06-22 06:00 | 218 | 213
2016-06-22 06:30 | 248 | 243
2016-06-22 07:00 | 268 | 265
2016-06-22 07:30 | 281 | 279
2016-06-22 08:00 | 277 | 276
2016-06-22 08:30 | 279 | 277
2016-06-22 09:00 | 280 | 279
2016-06-22 09:30 | 275 | 274
2016-06-22 10:00 | 276 | 275
2016-06-22 10:30 | 277 | 274
2016-06-22 11:00 | 277 | 273
2016-06-22 11:30 | 261 | 259
2016-06-22 12:00 | 251 | 250
2016-06-22 12:30 | 233 | 233
2016-06-22 13:00 | 235 | 235
2016-06-22 13:30 | 240 | 239
2016-06-22 14:00 | 232 | 231
2016-06-22 14:30 | 236 | 235
2016-06-22 15:00 | 247 | 246
2016-06-22 15:30 | 263 | 262
2016-06-22 16:00 | 273 | 272
2016-06-22 16:30 | 278 | 278
2016-06-22 17:00 | 297 | 296
2016-06-22 17:30 | 322 | 317
2016-06-22 18:00 | 321 | 317
2016-06-22 18:30 | 319 | 314
2016-06-22 19:00 | 308 | 302
2016-06-22 19:30 | 309 | 303
2016-06-22 20:00 | 306 | 299
2016-06-22 20:30 | 287 | 281
2016-06-22 21:00 | 275 | 269
2016-06-22 21:30 | 266 | 259
2016-06-22 22:00 | 261 | 253
2016-06-22 22:30 | 248 | 241
2016-06-22 23:00 | 235 | 228
2016-06-22 23:30 | 217 | 213
2016-06-23 | 193 | 191
2016-06-23 00:30 | 180 | 179
2016-06-23 01:00 | 174 | 172
2016-06-23 01:30 | 170 | 168
2016-06-23 02:00 | 165 | 164
2016-06-23 02:30 | 162 | 161
2016-06-23 03:00 | 163 | 162
2016-06-23 03:30 | 162 | 160
2016-06-23 04:00 | 168 | 167
2016-06-23 04:30 | 175 | 174
2016-06-23 05:00 | 187 | 186
2016-06-23 05:30 | 198 | 194
2016-06-23 06:00 | 227 | 224
2016-06-23 06:30 | 253 | 250
2016-06-23 07:00 | 271 | 271
2016-06-23 07:30 | 288 | 286
2016-06-23 08:00 | 292 | 289
2016-06-23 08:30 | 291 | 288
2016-06-23 09:00 | 286 | 284
2016-06-23 09:30 | 284 | 282
2016-06-23 10:00 | 287 | 285
2016-06-23 10:30 | 282 | 280
2016-06-23 11:00 | 278 | 276
2016-06-23 11:30 | 277 | 275
2016-06-23 12:00 | 279 | 277
2016-06-23 12:30 | 275 | 274
2016-06-23 13:00 | 278 | 278
2016-06-23 13:30 | 279 | 279
2016-06-23 14:00 | 282 | 282
2016-06-23 14:30 | 281 | 281
2016-06-23 15:00 | 283 | 283
2016-06-23 15:30 | 288 | 288
2016-06-23 16:00 | 294 | 294
2016-06-23 16:30 | 312 | 312
2016-06-23 17:00 | 336 | 335
2016-06-23 17:30 | 351 | 350
2016-06-23 18:00 | 351 | 349
2016-06-23 18:30 | 348 | 346
2016-06-23 19:00 | 335 | 334
2016-06-23 19:30 | 330 | 329
2016-06-23 20:00 | 325 | 325
2016-06-23 20:30 | 307 | 307
2016-06-23 21:00 | 283 | 283
2016-06-23 21:30 | 265 | 265
2016-06-23 22:00 | 259 | 259
2016-06-23 22:30 | 244 | 244
2016-06-23 23:00 | 226 | 226
2016-06-23 23:30 | 211 | 210
2016-06-24 | 199 | 198
2016-06-24 00:30 | 191 | 190
2016-06-24 01:00 | 182 | 180
2016-06-24 01:30 | 177 | 175
2016-06-24 02:00 | 171 | 171
2016-06-24 02:30 | 166 | 166
2016-06-24 03:00 | 167 | 167
2016-06-24 03:30 | 168 | 168
2016-06-24 04:00 | 173 | 172
2016-06-24 04:30 | 178 | 178
2016-06-24 05:00 | 188 | 188
2016-06-24 05:30 | 201 | 198
2016-06-24 06:00 | 223 | 222
2016-06-24 06:30 | 251 | 250
2016-06-24 07:00 | 266 | 265
2016-06-24 07:30 | 276 | 275
2016-06-24 08:00 | 280 | 279
2016-06-24 08:30 | 275 | 275
2016-06-24 09:00 | 269 | 269
2016-06-24 09:30 | 249 | 248
2016-06-24 10:00 | 241 | 241
2016-06-24 10:30 | 232 | 232
2016-06-24 11:00 | 226 | 226
2016-06-24 11:30 | 226 | 226
2016-06-24 12:00 | 224 | 224
2016-06-24 12:30 | 223 | 223
2016-06-24 13:00 | 224 | 224
2016-06-24 13:30 | 229 | 229
2016-06-24 14:00 | 235 | 235
2016-06-24 14:30 | 238 | 238
2016-06-24 15:00 | 239 | 239
2016-06-24 15:30 | 252 | 252
2016-06-24 16:00 | 264 | 264
2016-06-24 16:30 | 279 | 279
2016-06-24 17:00 | 291 | 291
2016-06-24 17:30 | 296 | 295
2016-06-24 18:00 | 295 | 294
2016-06-24 18:30 | 295 | 294
2016-06-24 19:00 | 288 | 287
2016-06-24 19:30 | 293 | 292
2016-06-24 20:00 | 292 | 291
2016-06-24 20:30 | 281 | 281
2016-06-24 21:00 | 268 | 268
2016-06-24 21:30 | 251 | 251
2016-06-24 22:00 | 251 | 251
2016-06-24 22:30 | 243 | 242
2016-06-24 23:00 | 230 | 230
2016-06-24 23:30 | 222 | 221
2016-06-25 | 206 | 204
2016-06-25 00:30 | 197 | 196
2016-06-25 01:00 | 187 | 186
2016-06-25 01:30 | 178 | 178
2016-06-25 02:00 | 172 | 171
2016-06-25 02:30 | 169 | 168
2016-06-25 03:00 | 169 | 168
2016-06-25 03:30 | 168 | 167
2016-06-25 04:00 | 169 | 169
2016-06-25 04:30 | 175 | 175
2016-06-25 05:00 | 182 | 182
2016-06-25 05:30 | 189 | 189
2016-06-25 06:00 | 199 | 199
2016-06-25 06:30 | 214 | 214
2016-06-25 07:00 | 237 | 237
2016-06-25 07:30 | 249 | 249
2016-06-25 08:00 | 254 | 253
2016-06-25 08:30 | 258 | 255
2016-06-25 09:00 | 252 | 250
2016-06-25 09:30 | 241 | 240
2016-06-25 10:00 | 232 | 231
2016-06-25 10:30 | 223 | 221
2016-06-25 11:00 | 214 | 213
2016-06-25 11:30 | 208 | 206
2016-06-25 12:00 | 201 | 201
2016-06-25 12:30 | 200 | 199
2016-06-25 13:00 | 203 | 203
2016-06-25 13:30 | 206 | 205
2016-06-25 14:00 | 211 | 210
2016-06-25 14:30 | 218 | 218
2016-06-25 15:00 | 228 | 228
2016-06-25 15:30 | 241 | 241
2016-06-25 16:00 | 254 | 253
2016-06-25 16:30 | 277 | 277
2016-06-25 17:00 | 300 | 299
2016-06-25 17:30 | 319 | 318
2016-06-25 18:00 | 318 | 317
2016-06-25 18:30 | 317 | 317
2016-06-25 19:00 | 312 | 312
2016-06-25 19:30 | 312 | 311
2016-06-25 20:00 | 312 | 312
2016-06-25 20:30 | 303 | 303
2016-06-25 21:00 | 296 | 295
2016-06-25 21:30 | 282 | 282
2016-06-25 22:00 | 279 | 279
2016-06-25 22:30 | 269 | 269
2016-06-25 23:00 | 259 | 258
2016-06-25 23:30 | 240 | 239
2016-06-26 | 225 | 224
2016-06-26 00:30 | 210 | 210
2016-06-26 01:00 | 200 | 200
2016-06-26 01:30 | 190 | 190
2016-06-26 02:00 | 184 | 184
2016-06-26 02:30 | 181 | 181
2016-06-26 03:00 | 177 | 177
2016-06-26 03:30 | 175 | 175
2016-06-26 04:00 | 176 | 175
2016-06-26 04:30 | 182 | 182
2016-06-26 05:00 | 183 | 183
2016-06-26 05:30 | 185 | 184
2016-06-26 06:00 | 198 | 198
2016-06-26 06:30 | 207 | 207
2016-06-26 07:00 | 226 | 226
2016-06-26 07:30 | 246 | 245
2016-06-26 08:00 | 265 | 265
2016-06-26 08:30 | 263 | 263
2016-06-26 09:00 | 278 | 277
2016-06-26 09:30 | 274 | 274
2016-06-26 10:00 | 268 | 267
2016-06-26 10:30 | 261 | 260
2016-06-26 11:00 | 259 | 258
2016-06-26 11:30 | 250 | 248
2016-06-26 12:00 | 239 | 238
2016-06-26 12:30 | 238 | 237
2016-06-26 13:00 | 242 | 240
2016-06-26 13:30 | 247 | 245
2016-06-26 14:00 | 248 | 246
2016-06-26 14:30 | 254 | 253
2016-06-26 15:00 | 266 | 265
2016-06-26 15:30 | 275 | 274
2016-06-26 16:00 | 286 | 286
2016-06-26 16:30 | 310 | 309
2016-06-26 17:00 | 333 | 333
2016-06-26 17:30 | 342 | 342
2016-06-26 18:00 | 343 | 343
2016-06-26 18:30 | 339 | 339
2016-06-26 19:00 | 328 | 328
2016-06-26 19:30 | 324 | 324
2016-06-26 20:00 | 321 | 321
2016-06-26 20:30 | 306 | 305
2016-06-26 21:00 | 288 | 286
2016-06-26 21:30 | 270 | 268
2016-06-26 22:00 | 258 | 257
2016-06-26 22:30 | 247 | 244
2016-06-26 23:00 | 243 | 240
2016-06-26 23:30 | 225 | 223
2016-06-27 | 206 | 206
2016-06-27 00:30 | 191 | 191
2016-06-27 01:00 | 186 | 186
2016-06-27 01:30 | 179 | 179
2016-06-27 02:00 | 168 | 168
2016-06-27 02:30 | 163 | 163
2016-06-27 03:00 | 164 | 164
2016-06-27 03:30 | 165 | 165
2016-06-27 04:00 | 173 | 173
2016-06-27 04:30 | 180 | 180
2016-06-27 05:00 | 193 | 193
2016-06-27 05:30 | 208 | 208
2016-06-27 06:00 | 233 | 233
2016-06-27 06:30 | 258 | 257
2016-06-27 07:00 | 287 | 286
2016-06-27 07:30 | 305 | 304
2016-06-27 08:00 | 314 | 312
2016-06-27 08:30 | 315 | 313
2016-06-27 09:00 | 311 | 309
2016-06-27 09:30 | 294 | 292
2016-06-27 10:00 | 279 | 276
2016-06-27 10:30 | 270 | 267
2016-06-27 11:00 | 268 | 265
2016-06-27 11:30 | 276 | 273
2016-06-27 12:00 | 279 | 276
2016-06-27 12:30 | 265 | 263
2016-06-27 13:00 | 252 | 252
2016-06-27 13:30 | 251 | 251
2016-06-27 14:00 | 248 | 248
2016-06-27 14:30 | 248 | 248
2016-06-27 15:00 | 256 | 256
2016-06-27 15:30 | 266 | 266
2016-06-27 16:00 | 280 | 280
2016-06-27 16:30 | 303 | 302
2016-06-27 17:00 | 332 | 331
2016-06-27 17:30 | 357 | 357
2016-06-27 18:00 | 360 | 359
2016-06-27 18:30 | 359 | 358
2016-06-27 19:00 | 349 | 349
2016-06-27 19:30 | 347 | 346
2016-06-27 20:00 | 343 | 342
2016-06-27 20:30 | 332 | 331
2016-06-27 21:00 | 313 | 311
2016-06-27 21:30 | 290 | 288
2016-06-27 22:00 | 287 | 285
2016-06-27 22:30 | 273 | 272
2016-06-27 23:00 | 256 | 256
2016-06-27 23:30 | 240 | 240
2016-06-28 | 223 | 223
2016-06-28 00:30 | 211 | 211
2016-06-28 01:00 | 202 | 202
2016-06-28 01:30 | 193 | 193
2016-06-28 02:00 | 187 | 187
2016-06-28 02:30 | 183 | 182
2016-06-28 03:00 | 180 | 180
2016-06-28 03:30 | 181 | 181
2016-06-28 04:00 | 187 | 187
2016-06-28 04:30 | 195 | 195
2016-06-28 05:00 | 212 | 212
2016-06-28 05:30 | 232 | 232
2016-06-28 06:00 | 261 | 260
2016-06-28 06:30 | 288 | 288
2016-06-28 07:00 | 308 | 307
2016-06-28 07:30 | 324 | 324
2016-06-28 08:00 | 323 | 322
2016-06-28 08:30 | 312 | 311
2016-06-28 09:00 | 298 | 298
2016-06-28 09:30 | 281 | 281
2016-06-28 10:00 | 270 | 270
2016-06-28 10:30 | 260 | 259
2016-06-28 11:00 | 250 | 250
2016-06-28 11:30 | 244 | 244
2016-06-28 12:00 | 239 | 239
2016-06-28 12:30 | 237 | 236
2016-06-28 13:00 | 236 | 236
2016-06-28 13:30 | 237 | 237
2016-06-28 14:00 | 240 | 240
2016-06-28 14:30 | 245 | 245
2016-06-28 15:00 | 246 | 245
2016-06-28 15:30 | 252 | 252
2016-06-28 16:00 | 270 | 268
2016-06-28 16:30 | 293 | 292
2016-06-28 17:00 | 331 | 331
2016-06-28 17:30 | 353 | 353
2016-06-28 18:00 | 355 | 354
2016-06-28 18:30 | 358 | 358
2016-06-28 19:00 | 349 | 349
2016-06-28 19:30 | 349 | 349
2016-06-28 20:00 | 344 | 344
2016-06-28 20:30 | 327 | 326
2016-06-28 21:00 | 310 | 307
2016-06-28 21:30 | 291 | 290
2016-06-28 22:00 | 279 | 278
2016-06-28 22:30 | 264 | 264
2016-06-28 23:00 | 250 | 250
2016-06-28 23:30 | 233 | 233
2016-06-29 | 214 | 214
2016-06-29 00:30 | 202 | 202
2016-06-29 01:00 | 196 | 196
2016-06-29 01:30 | 187 | 187
2016-06-29 02:00 | 182 | 182
2016-06-29 02:30 | 178 | 178
2016-06-29 03:00 | 176 | 175
2016-06-29 03:30 | 173 | 173
2016-06-29 04:00 | 178 | 178
2016-06-29 04:30 | 184 | 184
2016-06-29 05:00 | 196 | 196
2016-06-29 05:30 | 213 | 212
2016-06-29 06:00 | 243 | 242
2016-06-29 06:30 | 261 | 261
2016-06-29 07:00 | 284 | 282
2016-06-29 07:30 | 291 | 288
2016-06-29 08:00 | 284 | 282
2016-06-29 08:30 | 275 | 274
2016-06-29 09:00 | 265 | 264
2016-06-29 09:30 | 243 | 242
2016-06-29 10:00 | 234 | 234
2016-06-29 10:30 | 240 | 239
2016-06-29 11:00 | 237 | 237
2016-06-29 11:30 | 214 | 214
2016-06-29 12:00 | 227 | 227
2016-06-29 12:30 | 214 | 213
2016-06-29 13:00 | 204 | 203
2016-06-29 13:30 | 208 | 207
2016-06-29 14:00 | 212 | 212
2016-06-29 14:30 | 218 | 218
2016-06-29 15:00 | 227 | 226
2016-06-29 15:30 | 238 | 236
2016-06-29 16:00 | 256 | 252
2016-06-29 16:30 | 288 | 284
2016-06-29 17:00 | 314 | 312
2016-06-29 17:30 | 326 | 324
2016-06-29 18:00 | 327 | 326
2016-06-29 18:30 | 328 | 327
2016-06-29 19:00 | 324 | 323
2016-06-29 19:30 | 323 | 322
2016-06-29 20:00 | 322 | 321
2016-06-29 20:30 | 311 | 309
2016-06-29 21:00 | 288 | 288
2016-06-29 21:30 | 270 | 270
2016-06-29 22:00 | 268 | 267
2016-06-29 22:30 | 256 | 254
2016-06-29 23:00 | 246 | 244
2016-06-29 23:30 | 231 | 229
2016-06-30 | 206 | 205
2016-06-30 00:30 | 193 | 193
2016-06-30 01:00 | 188 | 188
2016-06-30 01:30 | 181 | 181
2016-06-30 02:00 | 175 | 175
2016-06-30 02:30 | 156 | 156
2016-06-30 03:00 | 165 | 165
2016-06-30 03:30 | 157 | 157
2016-06-30 04:00 | 149 | 149
2016-06-30 04:30 | 160 | 160
2016-06-30 05:00 | 176 | 176
2016-06-30 05:30 | 214 | 214
2016-06-30 06:00 | 243 | 243
2016-06-30 06:30 | 276 | 276
2016-06-30 07:00 | 288 | 288
2016-06-30 07:30 | 289 | 289
2016-06-30 08:00 | 286 | 286
2016-06-30 08:30 | 274 | 274
2016-06-30 09:00 | 260 | 260
2016-06-30 09:30 | 245 | 245
2016-06-30 10:00 | 234 | 233
2016-06-30 10:30 | 225 | 225
2016-06-30 11:00 | 220 | 220
2016-06-30 11:30 | 215 | 215
2016-06-30 12:00 | 212 | 212
2016-06-30 12:30 | 213 | 212
2016-06-30 13:00 | 216 | 215
2016-06-30 13:30 | 232 | 232
2016-06-30 14:00 | 239 | 239
2016-06-30 14:30 | 247 | 247
2016-06-30 15:00 | 254 | 253
2016-06-30 15:30 | 262 | 262
2016-06-30 16:00 | 273 | 273
2016-06-30 16:30 | 298 | 298
2016-06-30 17:00 | 317 | 317
2016-06-30 17:30 | 330 | 330
2016-06-30 18:00 | 332 | 332
2016-06-30 18:30 | 334 | 334
2016-06-30 19:00 | 327 | 327
2016-06-30 19:30 | 326 | 326
2016-06-30 20:00 | 323 | 323
2016-06-30 20:30 | 309 | 309
2016-06-30 21:00 | 292 | 292
2016-06-30 21:30 | 272 | 272
2016-06-30 22:00 | 266 | 265
2016-06-30 22:30 | 254 | 254
2016-06-30 23:00 | 236 | 235
2016-06-30 23:30 | 221 | 220
2016-07-01 | 207 | 206
2016-07-01 00:30 | 197 | 195
2016-07-01 01:00 | 188 | 186
2016-07-01 01:30 | 179 | 177
2016-07-01 02:00 | 173 | 171
2016-07-01 02:30 | 168 | 167
2016-07-01 03:00 | 167 | 166
2016-07-01 03:30 | 168 | 167
2016-07-01 04:00 | 172 | 171
2016-07-01 04:30 | 178 | 178
2016-07-01 05:00 | 192 | 191
2016-07-01 05:30 | 204 | 204
2016-07-01 06:00 | 234 | 233
2016-07-01 06:30 | 251 | 251
2016-07-01 07:00 | 275 | 274
2016-07-01 07:30 | 285 | 284
2016-07-01 08:00 | 282 | 281
2016-07-01 08:30 | 275 | 274
2016-07-01 09:00 | 264 | 263
2016-07-01 09:30 | 250 | 250
2016-07-01 10:00 | 242 | 242
2016-07-01 10:30 | 235 | 234
2016-07-01 11:00 | 231 | 230
2016-07-01 11:30 | 226 | 226
2016-07-01 12:00 | 230 | 230
2016-07-01 12:30 | 237 | 237
2016-07-01 13:00 | 233 | 233
2016-07-01 13:30 | 232 | 232
2016-07-01 14:00 | 235 | 235
2016-07-01 14:30 | 237 | 237
2016-07-01 15:00 | 242 | 242
2016-07-01 15:30 | 245 | 245
2016-07-01 16:00 | 260 | 260
2016-07-01 16:30 | 277 | 276
2016-07-01 17:00 | 297 | 295
2016-07-01 17:30 | 312 | 311
2016-07-01 18:00 | 315 | 315
2016-07-01 18:30 | 313 | 313
2016-07-01 19:00 | 306 | 306
2016-07-01 19:30 | 307 | 307
2016-07-01 20:00 | 307 | 307
2016-07-01 20:30 | 296 | 295
2016-07-01 21:00 | 286 | 286
2016-07-01 21:30 | 274 | 273
2016-07-01 22:00 | 267 | 267
2016-07-01 22:30 | 259 | 259
2016-07-01 23:00 | 246 | 246
2016-07-01 23:30 | 233 | 233
2016-07-02 | 216 | 215
2016-07-02 00:30 | 204 | 202
2016-07-02 01:00 | 194 | 193
2016-07-02 01:30 | 184 | 183
2016-07-02 02:00 | 178 | 178
2016-07-02 02:30 | 174 | 174
2016-07-02 03:00 | 172 | 171
2016-07-02 03:30 | 171 | 170
2016-07-02 04:00 | 172 | 172
2016-07-02 04:30 | 178 | 178
2016-07-02 05:00 | 187 | 187
2016-07-02 05:30 | 197 | 197
2016-07-02 06:00 | 213 | 213
2016-07-02 06:30 | 230 | 230
2016-07-02 07:00 | 250 | 249
2016-07-02 07:30 | 264 | 263
2016-07-02 08:00 | 274 | 271
2016-07-02 08:30 | 273 | 270
2016-07-02 09:00 | 265 | 263
2016-07-02 09:30 | 251 | 250
2016-07-02 10:00 | 238 | 238
2016-07-02 10:30 | 228 | 228
2016-07-02 11:00 | 216 | 216
2016-07-02 11:30 | 207 | 207
2016-07-02 12:00 | 202 | 202
2016-07-02 12:30 | 198 | 198
2016-07-02 13:00 | 199 | 199
2016-07-02 13:30 | 203 | 203
2016-07-02 14:00 | 207 | 207
2016-07-02 14:30 | 214 | 214
2016-07-02 15:00 | 223 | 223
2016-07-02 15:30 | 236 | 236
2016-07-02 16:00 | 251 | 251
2016-07-02 16:30 | 271 | 271
2016-07-02 17:00 | 297 | 297
2016-07-02 17:30 | 315 | 315
2016-07-02 18:00 | 317 | 316
2016-07-02 18:30 | 315 | 315
2016-07-02 19:00 | 309 | 309
2016-07-02 19:30 | 307 | 307
2016-07-02 20:00 | 305 | 305
2016-07-02 20:30 | 295 | 294
2016-07-02 21:00 | 286 | 286
2016-07-02 21:30 | 277 | 276
2016-07-02 22:00 | 272 | 272
2016-07-02 22:30 | 264 | 264
2016-07-02 23:00 | 252 | 251
2016-07-02 23:30 | 237 | 236
2016-07-03 | 219 | 218
2016-07-03 00:30 | 207 | 206
2016-07-03 01:00 | 195 | 195
2016-07-03 01:30 | 185 | 185
2016-07-03 02:00 | 178 | 178
2016-07-03 02:30 | 173 | 173
2016-07-03 03:00 | 171 | 171
2016-07-03 03:30 | 171 | 171
2016-07-03 04:00 | 175 | 174
2016-07-03 04:30 | 176 | 175
2016-07-03 05:00 | 175 | 174
2016-07-03 05:30 | 180 | 179
2016-07-03 06:00 | 190 | 190
2016-07-03 06:30 | 203 | 203
2016-07-03 07:00 | 223 | 223
2016-07-03 07:30 | 240 | 240
2016-07-03 08:00 | 251 | 250
2016-07-03 08:30 | 251 | 251
2016-07-03 09:00 | 247 | 247
2016-07-03 09:30 | 239 | 239
2016-07-03 10:00 | 229 | 229
2016-07-03 10:30 | 219 | 219
2016-07-03 11:00 | 214 | 214
2016-07-03 11:30 | 214 | 214
2016-07-03 12:00 | 209 | 209
2016-07-03 12:30 | 208 | 208
2016-07-03 13:00 | 203 | 203
2016-07-03 13:30 | 200 | 200
2016-07-03 14:00 | 204 | 204
2016-07-03 14:30 | 217 | 217
2016-07-03 15:00 | 227 | 227
2016-07-03 15:30 | 236 | 236
2016-07-03 16:00 | 248 | 248
2016-07-03 16:30 | 268 | 268
2016-07-03 17:00 | 289 | 289
2016-07-03 17:30 | 307 | 307
2016-07-03 18:00 | 308 | 308
2016-07-03 18:30 | 308 | 307
2016-07-03 19:00 | 304 | 304
2016-07-03 19:30 | 302 | 302
2016-07-03 20:00 | 301 | 301
2016-07-03 20:30 | 286 | 286
2016-07-03 21:00 | 276 | 275
2016-07-03 21:30 | 264 | 264
2016-07-03 22:00 | 257 | 257
2016-07-03 22:30 | 248 | 248
2016-07-03 23:00 | 238 | 238
2016-07-03 23:30 | 222 | 222
2016-07-04 | 206 | 206
2016-07-04 00:30 | 193 | 193
2016-07-04 01:00 | 186 | 186
2016-07-04 01:30 | 178 | 178
2016-07-04 02:00 | 173 | 173
2016-07-04 02:30 | 168 | 168
2016-07-04 03:00 | 165 | 165
2016-07-04 03:30 | 166 | 166
2016-07-04 04:00 | 171 | 171
2016-07-04 04:30 | 179 | 179
2016-07-04 05:00 | 195 | 195
2016-07-04 05:30 | 215 | 215
2016-07-04 06:00 | 241 | 241
2016-07-04 06:30 | 264 | 264
2016-07-04 07:00 | 282 | 282
2016-07-04 07:30 | 292 | 292
2016-07-04 08:00 | 292 | 291
2016-07-04 08:30 | 287 | 286
2016-07-04 09:00 | 279 | 279
2016-07-04 09:30 | 268 | 268
2016-07-04 10:00 | 268 | 268
2016-07-04 10:30 | 264 | 264
2016-07-04 11:00 | 255 | 253
2016-07-04 11:30 | 249 | 248
2016-07-04 12:00 | 246 | 245
2016-07-04 12:30 | 241 | 241
2016-07-04 13:00 | 240 | 239
2016-07-04 13:30 | 242 | 241
2016-07-04 14:00 | 246 | 245
2016-07-04 14:30 | 251 | 250
2016-07-04 15:00 | 255 | 255
2016-07-04 15:30 | 258 | 258
2016-07-04 16:00 | 269 | 267
2016-07-04 16:30 | 289 | 287
2016-07-04 17:00 | 323 | 321
2016-07-04 17:30 | 342 | 341
2016-07-04 18:00 | 340 | 338
2016-07-04 18:30 | 335 | 334
2016-07-04 19:00 | 321 | 321
2016-07-04 19:30 | 314 | 314
2016-07-04 20:00 | 313 | 312
2016-07-04 20:30 | 299 | 299
2016-07-04 21:00 | 282 | 282
2016-07-04 21:30 | 269 | 269
2016-07-04 22:00 | 260 | 260
2016-07-04 22:30 | 250 | 249
2016-07-04 23:00 | 241 | 240
2016-07-04 23:30 | 226 | 225
2016-07-05 | 211 | 210
2016-07-05 00:30 | 200 | 199
2016-07-05 01:00 | 191 | 189
2016-07-05 01:30 | 183 | 181
2016-07-05 02:00 | 176 | 175
2016-07-05 02:30 | 171 | 171
2016-07-05 03:00 | 166 | 165
2016-07-05 03:30 | 165 | 165
2016-07-05 04:00 | 171 | 171
2016-07-05 04:30 | 178 | 177
2016-07-05 05:00 | 192 | 192
2016-07-05 05:30 | 207 | 207
2016-07-05 06:00 | 229 | 228
2016-07-05 06:30 | 251 | 250
2016-07-05 07:00 | 275 | 274
2016-07-05 07:30 | 293 | 292
2016-07-05 08:00 | 300 | 299
2016-07-05 08:30 | 307 | 305
2016-07-05 09:00 | 315 | 311
2016-07-05 09:30 | 316 | 313
2016-07-05 10:00 | 309 | 306
2016-07-05 10:30 | 298 | 296
2016-07-05 11:00 | 291 | 290
2016-07-05 11:30 | 285 | 284
2016-07-05 12:00 | 284 | 283
2016-07-05 12:30 | 280 | 279
2016-07-05 13:00 | 279 | 278
2016-07-05 13:30 | 281 | 280
2016-07-05 14:00 | 281 | 280
2016-07-05 14:30 | 275 | 274
2016-07-05 15:00 | 272 | 270
2016-07-05 15:30 | 277 | 275
2016-07-05 16:00 | 284 | 282
2016-07-05 16:30 | 300 | 299
2016-07-05 17:00 | 323 | 321
2016-07-05 17:30 | 335 | 333
2016-07-05 18:00 | 330 | 330
2016-07-05 18:30 | 327 | 327
2016-07-05 19:00 | 321 | 320
2016-07-05 19:30 | 314 | 313
2016-07-05 20:00 | 313 | 312
2016-07-05 20:30 | 305 | 303
2016-07-05 21:00 | 285 | 284
2016-07-05 21:30 | 267 | 266
2016-07-05 22:00 | 268 | 267
2016-07-05 22:30 | 261 | 260
2016-07-05 23:00 | 246 | 246
2016-07-05 23:30 | 224 | 224
2016-07-06 | 205 | 204
2016-07-06 00:30 | 188 | 188
2016-07-06 01:00 | 175 | 174
2016-07-06 01:30 | 167 | 166
2016-07-06 02:00 | 165 | 164
2016-07-06 02:30 | 163 | 162
2016-07-06 03:00 | 162 | 161
2016-07-06 03:30 | 162 | 161
2016-07-06 04:00 | 166 | 165
2016-07-06 04:30 | 167 | 166
2016-07-06 05:00 | 176 | 175
2016-07-06 05:30 | 197 | 195
2016-07-06 06:00 | 244 | 241
2016-07-06 06:30 | 272 | 272
2016-07-06 07:00 | 290 | 290
2016-07-06 07:30 | 306 | 304
2016-07-06 08:00 | 307 | 305
2016-07-06 08:30 | 300 | 299
2016-07-06 09:00 | 290 | 288
2016-07-06 09:30 | 278 | 276
2016-07-06 10:00 | 269 | 266
2016-07-06 10:30 | 256 | 255
2016-07-06 11:00 | 249 | 248
2016-07-06 11:30 | 244 | 243
2016-07-06 12:00 | 239 | 238
2016-07-06 12:30 | 232 | 232
2016-07-06 13:00 | 233 | 233
2016-07-06 13:30 | 236 | 236
2016-07-06 14:00 | 242 | 242
2016-07-06 14:30 | 251 | 251
2016-07-06 15:00 | 257 | 257
2016-07-06 15:30 | 271 | 271
2016-07-06 16:00 | 285 | 284
2016-07-06 16:30 | 305 | 304
2016-07-06 17:00 | 340 | 338
2016-07-06 17:30 | 359 | 357
2016-07-06 18:00 | 360 | 359
2016-07-06 18:30 | 361 | 361
2016-07-06 19:00 | 355 | 354
2016-07-06 19:30 | 351 | 351
2016-07-06 20:00 | 349 | 349
2016-07-06 20:30 | 335 | 335
2016-07-06 21:00 | 312 | 312
2016-07-06 21:30 | 294 | 293
2016-07-06 22:00 | 287 | 286
2016-07-06 22:30 | 278 | 278
2016-07-06 23:00 | 260 | 260
2016-07-06 23:30 | 246 | 246
2016-07-07 | 229 | 229
2016-07-07 00:30 | 219 | 219
2016-07-07 01:00 | 207 | 207
2016-07-07 01:30 | 197 | 197
2016-07-07 02:00 | 188 | 188
2016-07-07 02:30 | 181 | 181
2016-07-07 03:00 | 182 | 182
2016-07-07 03:30 | 182 | 182
2016-07-07 04:00 | 184 | 184
2016-07-07 04:30 | 188 | 188
2016-07-07 05:00 | 200 | 200
2016-07-07 05:30 | 219 | 219
2016-07-07 06:00 | 253 | 253
2016-07-07 06:30 | 274 | 274
2016-07-07 07:00 | 294 | 293
2016-07-07 07:30 | 303 | 303
2016-07-07 08:00 | 307 | 307
2016-07-07 08:30 | 301 | 300
2016-07-07 09:00 | 296 | 296
2016-07-07 09:30 | 287 | 287
2016-07-07 10:00 | 273 | 273
2016-07-07 10:30 | 258 | 257
2016-07-07 11:00 | 250 | 250
2016-07-07 11:30 | 247 | 247
2016-07-07 12:00 | 246 | 246
2016-07-07 12:30 | 243 | 243
2016-07-07 13:00 | 242 | 242
2016-07-07 13:30 | 245 | 244
2016-07-07 14:00 | 248 | 248
2016-07-07 14:30 | 252 | 252
2016-07-07 15:00 | 254 | 254
2016-07-07 15:30 | 267 | 267
2016-07-07 16:00 | 279 | 279
2016-07-07 16:30 | 293 | 293
2016-07-07 17:00 | 309 | 309
2016-07-07 17:30 | 328 | 328
2016-07-07 18:00 | 330 | 330
2016-07-07 18:30 | 326 | 326
2016-07-07 19:00 | 322 | 322
2016-07-07 19:30 | 318 | 318
2016-07-07 20:00 | 319 | 318
2016-07-07 20:30 | 311 | 311
2016-07-07 21:00 | 294 | 294
2016-07-07 21:30 | 278 | 277
2016-07-07 22:00 | 272 | 272
2016-07-07 22:30 | 267 | 267
2016-07-07 23:00 | 258 | 258
2016-07-07 23:30 | 244 | 244
2016-07-08 | 225 | 225
2016-07-08 00:30 | 210 | 210
2016-07-08 01:00 | 200 | 200
2016-07-08 01:30 | 190 | 190
2016-07-08 02:00 | 181 | 181
2016-07-08 02:30 | 175 | 175
2016-07-08 03:00 | 169 | 169
2016-07-08 03:30 | 171 | 171
2016-07-08 04:00 | 173 | 173
2016-07-08 04:30 | 176 | 176
2016-07-08 05:00 | 190 | 190
2016-07-08 05:30 | 209 | 209
2016-07-08 06:00 | 235 | 234
2016-07-08 06:30 | 255 | 254
2016-07-08 07:00 | 270 | 270
2016-07-08 07:30 | 279 | 279
2016-07-08 08:00 | 283 | 283
2016-07-08 08:30 | 275 | 275
2016-07-08 09:00 | 268 | 268
2016-07-08 09:30 | 268 | 268
2016-07-08 10:00 | 263 | 263
2016-07-08 10:30 | 250 | 250
2016-07-08 11:00 | 241 | 241
2016-07-08 11:30 | 238 | 238
2016-07-08 12:00 | 235 | 235
2016-07-08 12:30 | 232 | 232
2016-07-08 13:00 | 233 | 233
2016-07-08 13:30 | 237 | 237
2016-07-08 14:00 | 239 | 239
2016-07-08 14:30 | 234 | 234
2016-07-08 15:00 | 236 | 236
2016-07-08 15:30 | 241 | 241
2016-07-08 16:00 | 254 | 254
2016-07-08 16:30 | 264 | 264
2016-07-08 17:00 | 280 | 280
2016-07-08 17:30 | 294 | 293
2016-07-08 18:00 | 294 | 294
2016-07-08 18:30 | 292 | 292
2016-07-08 19:00 | 286 | 286
2016-07-08 19:30 | 290 | 290
2016-07-08 20:00 | 291 | 290
2016-07-08 20:30 | 285 | 284
2016-07-08 21:00 | 271 | 270
2016-07-08 21:30 | 258 | 257
2016-07-08 22:00 | 256 | 256
2016-07-08 22:30 | 254 | 253
2016-07-08 23:00 | 243 | 242
2016-07-08 23:30 | 230 | 229
2016-07-09 | 214 | 214
2016-07-09 00:30 | 202 | 202
2016-07-09 01:00 | 192 | 192
2016-07-09 01:30 | 180 | 180
2016-07-09 02:00 | 172 | 172
2016-07-09 02:30 | 169 | 169
2016-07-09 03:00 | 169 | 169
2016-07-09 03:30 | 167 | 167
2016-07-09 04:00 | 170 | 170
2016-07-09 04:30 | 178 | 178
2016-07-09 05:00 | 183 | 183
2016-07-09 05:30 | 193 | 193
2016-07-09 06:00 | 208 | 208
2016-07-09 06:30 | 219 | 219
2016-07-09 07:00 | 239 | 239
2016-07-09 07:30 | 256 | 255
2016-07-09 08:00 | 265 | 264
2016-07-09 08:30 | 263 | 263
2016-07-09 09:00 | 261 | 260
2016-07-09 09:30 | 255 | 255
2016-07-09 10:00 | 250 | 250
2016-07-09 10:30 | 240 | 239
2016-07-09 11:00 | 231 | 230
2016-07-09 11:30 | 227 | 227
2016-07-09 12:00 | 223 | 222
2016-07-09 12:30 | 220 | 219
2016-07-09 13:00 | 223 | 222
2016-07-09 13:30 | 225 | 224
2016-07-09 14:00 | 229 | 228
2016-07-09 14:30 | 229 | 228
2016-07-09 15:00 | 234 | 233
2016-07-09 15:30 | 240 | 239
2016-07-09 16:00 | 250 | 249
2016-07-09 16:30 | 270 | 269
2016-07-09 17:00 | 287 | 287
2016-07-09 17:30 | 296 | 296
2016-07-09 18:00 | 296 | 296
2016-07-09 18:30 | 295 | 295
2016-07-09 19:00 | 288 | 288
2016-07-09 19:30 | 283 | 283
2016-07-09 20:00 | 279 | 279
2016-07-09 20:30 | 280 | 279
2016-07-09 21:00 | 270 | 269
2016-07-09 21:30 | 258 | 257
2016-07-09 22:00 | 256 | 255
2016-07-09 22:30 | 250 | 249
2016-07-09 23:00 | 240 | 240
2016-07-09 23:30 | 230 | 230
2016-07-10 | 213 | 213
2016-07-10 00:30 | 200 | 200
2016-07-10 01:00 | 192 | 191
2016-07-10 01:30 | 186 | 185
2016-07-10 02:00 | 182 | 181
2016-07-10 02:30 | 177 | 176
2016-07-10 03:00 | 175 | 174
2016-07-10 03:30 | 177 | 176
2016-07-10 04:00 | 179 | 178
2016-07-10 04:30 | 181 | 180
2016-07-10 05:00 | 184 | 183
2016-07-10 05:30 | 189 | 188
2016-07-10 06:00 | 205 | 204
2016-07-10 06:30 | 215 | 214
2016-07-10 07:00 | 225 | 225
2016-07-10 07:30 | 237 | 237
2016-07-10 08:00 | 245 | 245
2016-07-10 08:30 | 249 | 249
2016-07-10 09:00 | 245 | 244
2016-07-10 09:30 | 239 | 239
2016-07-10 10:00 | 234 | 234
2016-07-10 10:30 | 227 | 227
2016-07-10 11:00 | 220 | 220
2016-07-10 11:30 | 218 | 218
2016-07-10 12:00 | 215 | 215
2016-07-10 12:30 | 209 | 209
2016-07-10 13:00 | 209 | 209
2016-07-10 13:30 | 211 | 211
2016-07-10 14:00 | 213 | 213
2016-07-10 14:30 | 217 | 217
2016-07-10 15:00 | 225 | 225
2016-07-10 15:30 | 232 | 232
2016-07-10 16:00 | 240 | 240
2016-07-10 16:30 | 256 | 256
2016-07-10 17:00 | 278 | 278
2016-07-10 17:30 | 296 | 296
2016-07-10 18:00 | 296 | 296
2016-07-10 18:30 | 293 | 293
2016-07-10 19:00 | 284 | 284
2016-07-10 19:30 | 282 | 282
2016-07-10 20:00 | 281 | 281
2016-07-10 20:30 | 265 | 265
2016-07-10 21:00 | 251 | 251
2016-07-10 21:30 | 241 | 240
2016-07-10 22:00 | 242 | 241
2016-07-10 22:30 | 236 | 235
2016-07-10 23:00 | 228 | 228
2016-07-10 23:30 | 218 | 218
2016-07-11 | 196 | 196
2016-07-11 00:30 | 189 | 189
2016-07-11 01:00 | 186 | 186
2016-07-11 01:30 | 182 | 182
2016-07-11 02:00 | 178 | 178
2016-07-11 02:30 | 170 | 170
2016-07-11 03:00 | 164 | 164
2016-07-11 03:30 | 157 | 156
2016-07-11 04:00 | 156 | 156
2016-07-11 04:30 | 176 | 176
2016-07-11 05:00 | 194 | 194
2016-07-11 05:30 | 210 | 209
2016-07-11 06:00 | 225 | 225
2016-07-11 06:30 | 244 | 244
2016-07-11 07:00 | 262 | 262
2016-07-11 07:30 | 276 | 276
2016-07-11 08:00 | 280 | 280
2016-07-11 08:30 | 277 | 277
2016-07-11 09:00 | 272 | 272
2016-07-11 09:30 | 260 | 260
2016-07-11 10:00 | 253 | 252
2016-07-11 10:30 | 241 | 240
2016-07-11 11:00 | 239 | 238
2016-07-11 11:30 | 245 | 245
2016-07-11 12:00 | 248 | 248
2016-07-11 12:30 | 249 | 249
2016-07-11 13:00 | 244 | 243
2016-07-11 13:30 | 242 | 241
2016-07-11 14:00 | 236 | 235
2016-07-11 14:30 | 236 | 235
2016-07-11 15:00 | 242 | 242
2016-07-11 15:30 | 251 | 250
2016-07-11 16:00 | 261 | 261
2016-07-11 16:30 | 281 | 281
2016-07-11 17:00 | 312 | 312
2016-07-11 17:30 | 326 | 325
2016-07-11 18:00 | 328 | 328
2016-07-11 18:30 | 326 | 326
2016-07-11 19:00 | 321 | 320
2016-07-11 19:30 | 310 | 310
2016-07-11 20:00 | 298 | 298
2016-07-11 20:30 | 279 | 279
2016-07-11 21:00 | 256 | 256
2016-07-11 21:30 | 243 | 243
2016-07-11 22:00 | 241 | 241
2016-07-11 22:30 | 232 | 231
2016-07-11 23:00 | 223 | 223
2016-07-11 23:30 | 195 | 195
2016-07-12 | 179 | 179
2016-07-12 00:30 | 191 | 190
2016-07-12 01:00 | 190 | 189
2016-07-12 01:30 | 190 | 190
2016-07-12 02:00 | 174 | 173
2016-07-12 02:30 | 173 | 173
2016-07-12 03:00 | 171 | 171
2016-07-12 03:30 | 170 | 170
2016-07-12 04:00 | 170 | 170
2016-07-12 04:30 | 178 | 178
2016-07-12 05:00 | 190 | 190
2016-07-12 05:30 | 201 | 201
2016-07-12 06:00 | 223 | 222
2016-07-12 06:30 | 244 | 244
2016-07-12 07:00 | 262 | 262
2016-07-12 07:30 | 281 | 280
2016-07-12 08:00 | 279 | 277
2016-07-12 08:30 | 273 | 272
2016-07-12 09:00 | 272 | 271
2016-07-12 09:30 | 259 | 258
2016-07-12 10:00 | 257 | 255
2016-07-12 10:30 | 257 | 256
2016-07-12 11:00 | 258 | 257
2016-07-12 11:30 | 253 | 252
2016-07-12 12:00 | 250 | 249
2016-07-12 12:30 | 242 | 241
2016-07-12 13:00 | 244 | 243
2016-07-12 13:30 | 239 | 238
2016-07-12 14:00 | 239 | 237
2016-07-12 14:30 | 244 | 243
2016-07-12 15:00 | 243 | 241
2016-07-12 15:30 | 229 | 228
2016-07-12 16:00 | 254 | 252
2016-07-12 16:30 | 278 | 276
2016-07-12 17:00 | 303 | 302
2016-07-12 17:30 | 317 | 317
2016-07-12 18:00 | 315 | 315
2016-07-12 18:30 | 317 | 317
2016-07-12 19:00 | 314 | 314
2016-07-12 19:30 | 314 | 313
2016-07-12 20:00 | 311 | 311
2016-07-12 20:30 | 283 | 283
2016-07-12 21:00 | 263 | 263
2016-07-12 21:30 | 248 | 248
2016-07-12 22:00 | 242 | 242
2016-07-12 22:30 | 232 | 232
2016-07-12 23:00 | 226 | 226
2016-07-12 23:30 | 219 | 219
2016-07-13 | 208 | 208
2016-07-13 00:30 | 198 | 197
2016-07-13 01:00 | 187 | 187
2016-07-13 01:30 | 181 | 180
2016-07-13 02:00 | 181 | 180
2016-07-13 02:30 | 176 | 175
2016-07-13 03:00 | 175 | 174
2016-07-13 03:30 | 175 | 174
2016-07-13 04:00 | 175 | 175
2016-07-13 04:30 | 174 | 173
2016-07-13 05:00 | 184 | 184
2016-07-13 05:30 | 201 | 200
2016-07-13 06:00 | 229 | 229
2016-07-13 06:30 | 255 | 255
2016-07-13 07:00 | 279 | 278
2016-07-13 07:30 | 290 | 290
2016-07-13 08:00 | 292 | 291
2016-07-13 08:30 | 293 | 293
2016-07-13 09:00 | 277 | 277
2016-07-13 09:30 | 272 | 272
2016-07-13 10:00 | 264 | 264
2016-07-13 10:30 | 255 | 254
2016-07-13 11:00 | 249 | 248
2016-07-13 11:30 | 242 | 241
2016-07-13 12:00 | 238 | 237
2016-07-13 12:30 | 238 | 238
2016-07-13 13:00 | 240 | 239
2016-07-13 13:30 | 244 | 243
2016-07-13 14:00 | 240 | 240
2016-07-13 14:30 | 244 | 243
2016-07-13 15:00 | 249 | 248
2016-07-13 15:30 | 255 | 255
2016-07-13 16:00 | 266 | 265
2016-07-13 16:30 | 288 | 288
2016-07-13 17:00 | 314 | 313
2016-07-13 17:30 | 332 | 330
2016-07-13 18:00 | 331 | 329
2016-07-13 18:30 | 329 | 327
2016-07-13 19:00 | 326 | 324
2016-07-13 19:30 | 328 | 326
2016-07-13 20:00 | 327 | 325
2016-07-13 20:30 | 313 | 310
2016-07-13 21:00 | 299 | 296
2016-07-13 21:30 | 279 | 277
2016-07-13 22:00 | 272 | 269
2016-07-13 22:30 | 263 | 261
2016-07-13 23:00 | 247 | 245
2016-07-13 23:30 | 233 | 231
2016-07-14 | 216 | 216
2016-07-14 00:30 | 204 | 203
2016-07-14 01:00 | 197 | 197
2016-07-14 01:30 | 195 | 194
2016-07-14 02:00 | 190 | 189
2016-07-14 02:30 | 182 | 181
2016-07-14 03:00 | 180 | 179
2016-07-14 03:30 | 179 | 179
2016-07-14 04:00 | 183 | 182
2016-07-14 04:30 | 191 | 191
2016-07-14 05:00 | 209 | 209
2016-07-14 05:30 | 223 | 220
2016-07-14 06:00 | 240 | 238
2016-07-14 06:30 | 266 | 264
2016-07-14 07:00 | 287 | 286
2016-07-14 07:30 | 304 | 303
2016-07-14 08:00 | 309 | 307
2016-07-14 08:30 | 303 | 299
2016-07-14 09:00 | 285 | 282
2016-07-14 09:30 | 278 | 274
2016-07-14 10:00 | 270 | 266
2016-07-14 10:30 | 242 | 241
2016-07-14 11:00 | 243 | 242
2016-07-14 11:30 | 247 | 246
2016-07-14 12:00 | 250 | 250
2016-07-14 12:30 | 252 | 252
2016-07-14 13:00 | 252 | 251
2016-07-14 13:30 | 255 | 254
2016-07-14 14:00 | 260 | 260
2016-07-14 14:30 | 261 | 260
2016-07-14 15:00 | 265 | 264
2016-07-14 15:30 | 272 | 272
2016-07-14 16:00 | 284 | 283
2016-07-14 16:30 | 299 | 299
2016-07-14 17:00 | 337 | 335
2016-07-14 17:30 | 356 | 355
2016-07-14 18:00 | 355 | 354
2016-07-14 18:30 | 355 | 354
2016-07-14 19:00 | 350 | 349
2016-07-14 19:30 | 345 | 343
2016-07-14 20:00 | 344 | 342
2016-07-14 20:30 | 331 | 330
2016-07-14 21:00 | 312 | 311
2016-07-14 21:30 | 285 | 284
2016-07-14 22:00 | 268 | 267
2016-07-14 22:30 | 259 | 257
2016-07-14 23:00 | 245 | 244
2016-07-14 23:30 | 235 | 235
2016-07-15 | 218 | 217
2016-07-15 00:30 | 209 | 208
2016-07-15 01:00 | 195 | 195
2016-07-15 01:30 | 183 | 182
2016-07-15 02:00 | 176 | 175
2016-07-15 02:30 | 173 | 172
2016-07-15 03:00 | 173 | 172
2016-07-15 03:30 | 173 | 172
2016-07-15 04:00 | 175 | 174
2016-07-15 04:30 | 186 | 185
2016-07-15 05:00 | 197 | 197
2016-07-15 05:30 | 216 | 216
2016-07-15 06:00 | 239 | 239
2016-07-15 06:30 | 276 | 274
2016-07-15 07:00 | 306 | 305
2016-07-15 07:30 | 318 | 318
2016-07-15 08:00 | 316 | 315
2016-07-15 08:30 | 307 | 307
2016-07-15 09:00 | 295 | 294
2016-07-15 09:30 | 279 | 279
2016-07-15 10:00 | 280 | 280
2016-07-15 10:30 | 275 | 275
2016-07-15 11:00 | 266 | 265
2016-07-15 11:30 | 262 | 262
2016-07-15 12:00 | 258 | 258
2016-07-15 12:30 | 253 | 252
2016-07-15 13:00 | 251 | 250
2016-07-15 13:30 | 254 | 253
2016-07-15 14:00 | 254 | 253
2016-07-15 14:30 | 253 | 252
2016-07-15 15:00 | 256 | 255
2016-07-15 15:30 | 264 | 263
2016-07-15 16:00 | 276 | 275
2016-07-15 16:30 | 307 | 305
2016-07-15 17:00 | 328 | 327
2016-07-15 17:30 | 342 | 340
2016-07-15 18:00 | 345 | 340
2016-07-15 18:30 | 344 | 339
2016-07-15 19:00 | 338 | 334
2016-07-15 19:30 | 333 | 332
2016-07-15 20:00 | 332 | 332
2016-07-15 20:30 | 319 | 318
2016-07-15 21:00 | 300 | 298
2016-07-15 21:30 | 284 | 281
2016-07-15 22:00 | 276 | 275
2016-07-15 22:30 | 268 | 268
2016-07-15 23:00 | 250 | 249
2016-07-15 23:30 | 231 | 230
2016-07-16 | 219 | 218
2016-07-16 00:30 | 207 | 207
2016-07-16 01:00 | 196 | 195
2016-07-16 01:30 | 187 | 187
2016-07-16 02:00 | 178 | 177
2016-07-16 02:30 | 171 | 170
2016-07-16 03:00 | 170 | 168
2016-07-16 03:30 | 170 | 169
2016-07-16 04:00 | 170 | 169
2016-07-16 04:30 | 171 | 170
2016-07-16 05:00 | 177 | 176
2016-07-16 05:30 | 184 | 184
2016-07-16 06:00 | 201 | 201
2016-07-16 06:30 | 218 | 218
2016-07-16 07:00 | 237 | 237
2016-07-16 07:30 | 251 | 251
2016-07-16 08:00 | 267 | 266
2016-07-16 08:30 | 274 | 273
2016-07-16 09:00 | 274 | 274
2016-07-16 09:30 | 266 | 265
2016-07-16 10:00 | 255 | 253
2016-07-16 10:30 | 248 | 247
2016-07-16 11:00 | 245 | 244
2016-07-16 11:30 | 244 | 242
2016-07-16 12:00 | 245 | 243
2016-07-16 12:30 | 249 | 247
2016-07-16 13:00 | 249 | 248
2016-07-16 13:30 | 251 | 250
2016-07-16 14:00 | 252 | 251
2016-07-16 14:30 | 253 | 251
2016-07-16 15:00 | 254 | 253
2016-07-16 15:30 | 259 | 258
2016-07-16 16:00 | 266 | 265
2016-07-16 16:30 | 284 | 283
2016-07-16 17:00 | 306 | 306
2016-07-16 17:30 | 312 | 312
2016-07-16 18:00 | 309 | 309
2016-07-16 18:30 | 305 | 305
2016-07-16 19:00 | 299 | 298
2016-07-16 19:30 | 299 | 298
2016-07-16 20:00 | 288 | 288
2016-07-16 20:30 | 277 | 277
2016-07-16 21:00 | 266 | 266
2016-07-16 21:30 | 259 | 259
2016-07-16 22:00 | 249 | 249
2016-07-16 22:30 | 243 | 243
2016-07-16 23:00 | 234 | 233
2016-07-16 23:30 | 224 | 223
2016-07-17 | 207 | 206
2016-07-17 00:30 | 193 | 192
2016-07-17 01:00 | 182 | 181
2016-07-17 01:30 | 172 | 172
2016-07-17 02:00 | 167 | 167
2016-07-17 02:30 | 164 | 164
2016-07-17 03:00 | 163 | 162
2016-07-17 03:30 | 158 | 157
2016-07-17 04:00 | 154 | 154
2016-07-17 04:30 | 154 | 153
2016-07-17 05:00 | 159 | 158
2016-07-17 05:30 | 168 | 167
2016-07-17 06:00 | 183 | 183
2016-07-17 06:30 | 199 | 198
2016-07-17 07:00 | 210 | 209
2016-07-17 07:30 | 230 | 228
2016-07-17 08:00 | 246 | 245
2016-07-17 08:30 | 255 | 255
2016-07-17 09:00 | 256 | 256
2016-07-17 09:30 | 260 | 260
2016-07-17 10:00 | 258 | 258
2016-07-17 10:30 | 246 | 246
2016-07-17 11:00 | 237 | 237
2016-07-17 11:30 | 234 | 234
2016-07-17 12:00 | 229 | 229
2016-07-17 12:30 | 220 | 220
2016-07-17 13:00 | 218 | 218
2016-07-17 13:30 | 218 | 218
2016-07-17 14:00 | 216 | 215
2016-07-17 14:30 | 220 | 220
2016-07-17 15:00 | 222 | 222
2016-07-17 15:30 | 230 | 230
2016-07-17 16:00 | 238 | 238
2016-07-17 16:30 | 253 | 253
2016-07-17 17:00 | 277 | 276
2016-07-17 17:30 | 288 | 288
2016-07-17 18:00 | 288 | 287
2016-07-17 18:30 | 286 | 286
2016-07-17 19:00 | 279 | 279
2016-07-17 19:30 | 277 | 277
2016-07-17 20:00 | 275 | 275
2016-07-17 20:30 | 270 | 270
2016-07-17 21:00 | 253 | 253
2016-07-17 21:30 | 243 | 242
2016-07-17 22:00 | 236 | 235
2016-07-17 22:30 | 228 | 227
2016-07-17 23:00 | 213 | 213
2016-07-17 23:30 | 203 | 203
2016-07-18 | 193 | 193
2016-07-18 00:30 | 183 | 183
2016-07-18 01:00 | 176 | 176
2016-07-18 01:30 | 169 | 169
2016-07-18 02:00 | 161 | 161
2016-07-18 02:30 | 153 | 153
2016-07-18 03:00 | 141 | 141
2016-07-18 03:30 | 138 | 138
2016-07-18 04:00 | 154 | 153
2016-07-18 04:30 | 159 | 158
2016-07-18 05:00 | 169 | 169
2016-07-18 05:30 | 194 | 192
2016-07-18 06:00 | 215 | 213
2016-07-18 06:30 | 236 | 235
2016-07-18 07:00 | 260 | 260
2016-07-18 07:30 | 267 | 267
2016-07-18 08:00 | 259 | 259
2016-07-18 08:30 | 253 | 253
2016-07-18 09:00 | 249 | 249
2016-07-18 09:30 | 245 | 245
2016-07-18 10:00 | 247 | 247
2016-07-18 10:30 | 233 | 233
2016-07-18 11:00 | 234 | 234
2016-07-18 11:30 | 238 | 238
2016-07-18 12:00 | 230 | 230
2016-07-18 12:30 | 225 | 225
2016-07-18 13:00 | 224 | 224
2016-07-18 13:30 | 228 | 228
2016-07-18 14:00 | 226 | 226
2016-07-18 14:30 | 226 | 226
2016-07-18 15:00 | 232 | 232
2016-07-18 15:30 | 239 | 239
2016-07-18 16:00 | 250 | 250
2016-07-18 16:30 | 264 | 264
2016-07-18 17:00 | 284 | 284
2016-07-18 17:30 | 307 | 305
2016-07-18 18:00 | 304 | 303
2016-07-18 18:30 | 303 | 301
2016-07-18 19:00 | 292 | 290
2016-07-18 19:30 | 288 | 285
2016-07-18 20:00 | 282 | 279
2016-07-18 20:30 | 265 | 264
2016-07-18 21:00 | 254 | 252
2016-07-18 21:30 | 237 | 235
2016-07-18 22:00 | 230 | 230
2016-07-18 22:30 | 222 | 222
2016-07-18 23:00 | 210 | 210
2016-07-18 23:30 | 195 | 195
2016-07-19 | 178 | 178
2016-07-19 00:30 | 168 | 168
2016-07-19 01:00 | 159 | 159
2016-07-19 01:30 | 151 | 150
2016-07-19 02:00 | 144 | 144
2016-07-19 02:30 | 140 | 139
2016-07-19 03:00 | 139 | 139
2016-07-19 03:30 | 140 | 140
2016-07-19 04:00 | 144 | 144
2016-07-19 04:30 | 151 | 150
2016-07-19 05:00 | 163 | 163
2016-07-19 05:30 | 181 | 181
2016-07-19 06:00 | 208 | 208
2016-07-19 06:30 | 232 | 232
2016-07-19 07:00 | 266 | 266
2016-07-19 07:30 | 271 | 270
2016-07-19 08:00 | 268 | 268
2016-07-19 08:30 | 258 | 258
2016-07-19 09:00 | 250 | 250
2016-07-19 09:30 | 243 | 242
2016-07-19 10:00 | 239 | 239
2016-07-19 10:30 | 233 | 233
2016-07-19 11:00 | 229 | 229
2016-07-19 11:30 | 227 | 226
2016-07-19 12:00 | 225 | 225
2016-07-19 12:30 | 224 | 224
2016-07-19 13:00 | 226 | 226
2016-07-19 13:30 | 230 | 230
2016-07-19 14:00 | 235 | 234
2016-07-19 14:30 | 239 | 239
2016-07-19 15:00 | 244 | 244
2016-07-19 15:30 | 246 | 246
2016-07-19 16:00 | 257 | 256
2016-07-19 16:30 | 270 | 269
2016-07-19 17:00 | 285 | 285
2016-07-19 17:30 | 306 | 304
2016-07-19 18:00 | 305 | 303
2016-07-19 18:30 | 304 | 302
2016-07-19 19:00 | 291 | 290
2016-07-19 19:30 | 286 | 286
2016-07-19 20:00 | 282 | 282
2016-07-19 20:30 | 269 | 269
2016-07-19 21:00 | 256 | 255
2016-07-19 21:30 | 244 | 243
2016-07-19 22:00 | 239 | 238
2016-07-19 22:30 | 226 | 225
2016-07-19 23:00 | 215 | 215
2016-07-19 23:30 | 201 | 200
2016-07-20 | 184 | 184
2016-07-20 00:30 | 175 | 174
2016-07-20 01:00 | 167 | 167
2016-07-20 01:30 | 158 | 158
2016-07-20 02:00 | 152 | 152
2016-07-20 02:30 | 147 | 147
2016-07-20 03:00 | 143 | 143
2016-07-20 03:30 | 142 | 141
2016-07-20 04:00 | 145 | 145
2016-07-20 04:30 | 151 | 151
2016-07-20 05:00 | 166 | 165
2016-07-20 05:30 | 181 | 181
2016-07-20 06:00 | 206 | 206
2016-07-20 06:30 | 228 | 228
2016-07-20 07:00 | 251 | 251
2016-07-20 07:30 | 254 | 254
2016-07-20 08:00 | 246 | 245
2016-07-20 08:30 | 240 | 239
2016-07-20 09:00 | 232 | 231
2016-07-20 09:30 | 226 | 225
2016-07-20 10:00 | 228 | 227
2016-07-20 10:30 | 218 | 216
2016-07-20 11:00 | 217 | 215
2016-07-20 11:30 | 217 | 215
2016-07-20 12:00 | 215 | 213
2016-07-20 12:30 | 222 | 220
2016-07-20 13:00 | 224 | 222
2016-07-20 13:30 | 219 | 217
2016-07-20 14:00 | 223 | 221
2016-07-20 14:30 | 226 | 225
2016-07-20 15:00 | 231 | 230
2016-07-20 15:30 | 239 | 238
2016-07-20 16:00 | 249 | 248
2016-07-20 16:30 | 261 | 261
2016-07-20 17:00 | 275 | 274
2016-07-20 17:30 | 291 | 291
2016-07-20 18:00 | 291 | 291
2016-07-20 18:30 | 289 | 289
2016-07-20 19:00 | 279 | 279
2016-07-20 19:30 | 275 | 274
2016-07-20 20:00 | 271 | 271
2016-07-20 20:30 | 259 | 258
2016-07-20 21:00 | 247 | 246
2016-07-20 21:30 | 232 | 232
2016-07-20 22:00 | 228 | 228
2016-07-20 22:30 | 220 | 220
2016-07-20 23:00 | 210 | 209
2016-07-20 23:30 | 196 | 195
2016-07-21 | 177 | 176
2016-07-21 00:30 | 168 | 168
2016-07-21 01:00 | 160 | 160
2016-07-21 01:30 | 153 | 153
2016-07-21 02:00 | 147 | 147
2016-07-21 02:30 | 144 | 144
2016-07-21 03:00 | 142 | 142
2016-07-21 03:30 | 144 | 143
2016-07-21 04:00 | 148 | 148
2016-07-21 04:30 | 153 | 153
2016-07-21 05:00 | 167 | 167
2016-07-21 05:30 | 183 | 182
2016-07-21 06:00 | 206 | 205
2016-07-21 06:30 | 228 | 228
2016-07-21 07:00 | 250 | 250
2016-07-21 07:30 | 255 | 255
2016-07-21 08:00 | 254 | 254
2016-07-21 08:30 | 251 | 251
2016-07-21 09:00 | 251 | 251
2016-07-21 09:30 | 248 | 247
2016-07-21 10:00 | 235 | 235
2016-07-21 10:30 | 232 | 232
2016-07-21 11:00 | 231 | 230
2016-07-21 11:30 | 234 | 233
2016-07-21 12:00 | 218 | 217
2016-07-21 12:30 | 216 | 216
2016-07-21 13:00 | 221 | 220
2016-07-21 13:30 | 224 | 223
2016-07-21 14:00 | 231 | 231
2016-07-21 14:30 | 238 | 238
2016-07-21 15:00 | 242 | 242
2016-07-21 15:30 | 245 | 245
2016-07-21 16:00 | 252 | 252
2016-07-21 16:30 | 263 | 263
2016-07-21 17:00 | 275 | 275
2016-07-21 17:30 | 288 | 288
2016-07-21 18:00 | 288 | 288
2016-07-21 18:30 | 287 | 287
2016-07-21 19:00 | 279 | 279
2016-07-21 19:30 | 274 | 274
2016-07-21 20:00 | 270 | 270
2016-07-21 20:30 | 257 | 257
2016-07-21 21:00 | 243 | 243
2016-07-21 21:30 | 230 | 230
2016-07-21 22:00 | 224 | 223
2016-07-21 22:30 | 216 | 216
2016-07-21 23:00 | 205 | 205
2016-07-21 23:30 | 190 | 190
2016-07-22 | 174 | 174
2016-07-22 00:30 | 163 | 163
2016-07-22 01:00 | 155 | 155
2016-07-22 01:30 | 147 | 147
2016-07-22 02:00 | 142 | 141
2016-07-22 02:30 | 139 | 138
2016-07-22 03:00 | 138 | 138
2016-07-22 03:30 | 138 | 138
2016-07-22 04:00 | 142 | 142
2016-07-22 04:30 | 148 | 148
2016-07-22 05:00 | 160 | 160
2016-07-22 05:30 | 176 | 176
2016-07-22 06:00 | 198 | 198
2016-07-22 06:30 | 220 | 220
2016-07-22 07:00 | 243 | 243
2016-07-22 07:30 | 248 | 248
2016-07-22 08:00 | 251 | 251
2016-07-22 08:30 | 248 | 248
2016-07-22 09:00 | 244 | 244
2016-07-22 09:30 | 238 | 238
2016-07-22 10:00 | 232 | 232
2016-07-22 10:30 | 225 | 225
2016-07-22 11:00 | 222 | 222
2016-07-22 11:30 | 221 | 221
2016-07-22 12:00 | 218 | 218
2016-07-22 12:30 | 217 | 217
2016-07-22 13:00 | 219 | 219
2016-07-22 13:30 | 224 | 224
2016-07-22 14:00 | 228 | 228
2016-07-22 14:30 | 231 | 231
2016-07-22 15:00 | 237 | 237
2016-07-22 15:30 | 244 | 244
2016-07-22 16:00 | 252 | 252
2016-07-22 16:30 | 260 | 260
2016-07-22 17:00 | 267 | 267
2016-07-22 17:30 | 276 | 276
2016-07-22 18:00 | 272 | 272
2016-07-22 18:30 | 270 | 270
2016-07-22 19:00 | 262 | 262
2016-07-22 19:30 | 260 | 260
2016-07-22 20:00 | 255 | 255
2016-07-22 20:30 | 244 | 244
2016-07-22 21:00 | 233 | 233
2016-07-22 21:30 | 221 | 220
2016-07-22 22:00 | 220 | 220
2016-07-22 22:30 | 216 | 216
2016-07-22 23:00 | 206 | 206
2016-07-22 23:30 | 192 | 192
2016-07-23 | 176 | 176
2016-07-23 00:30 | 166 | 166
2016-07-23 01:00 | 158 | 158
2016-07-23 01:30 | 149 | 149
2016-07-23 02:00 | 144 | 143
2016-07-23 02:30 | 142 | 142
2016-07-23 03:00 | 142 | 141
2016-07-23 03:30 | 140 | 140
2016-07-23 04:00 | 141 | 141
2016-07-23 04:30 | 144 | 143
2016-07-23 05:00 | 149 | 149
2016-07-23 05:30 | 156 | 155
2016-07-23 06:00 | 164 | 164
2016-07-23 06:30 | 176 | 176
2016-07-23 07:00 | 192 | 192
2016-07-23 07:30 | 204 | 204
2016-07-23 08:00 | 212 | 211
2016-07-23 08:30 | 217 | 216
2016-07-23 09:00 | 217 | 216
2016-07-23 09:30 | 214 | 213
2016-07-23 10:00 | 211 | 210
2016-07-23 10:30 | 208 | 207
2016-07-23 11:00 | 204 | 202
2016-07-23 11:30 | 198 | 196
2016-07-23 12:00 | 196 | 194
2016-07-23 12:30 | 194 | 192
2016-07-23 13:00 | 194 | 193
2016-07-23 13:30 | 197 | 196
2016-07-23 14:00 | 201 | 199
2016-07-23 14:30 | 208 | 206
2016-07-23 15:00 | 215 | 214
2016-07-23 15:30 | 223 | 222
2016-07-23 16:00 | 230 | 229
2016-07-23 16:30 | 239 | 238
2016-07-23 17:00 | 246 | 246
2016-07-23 17:30 | 254 | 254
2016-07-23 18:00 | 251 | 251
2016-07-23 18:30 | 250 | 250
2016-07-23 19:00 | 239 | 239
2016-07-23 19:30 | 237 | 237
2016-07-23 20:00 | 231 | 231
2016-07-23 20:30 | 221 | 221
2016-07-23 21:00 | 214 | 214
2016-07-23 21:30 | 207 | 207
2016-07-23 22:00 | 210 | 210
2016-07-23 22:30 | 207 | 207
2016-07-23 23:00 | 200 | 200
2016-07-23 23:30 | 187 | 187
2016-07-24 | 171 | 171
2016-07-24 00:30 | 161 | 160
2016-07-24 01:00 | 152 | 152
2016-07-24 01:30 | 145 | 145
2016-07-24 02:00 | 140 | 139
2016-07-24 02:30 | 137 | 136
2016-07-24 03:00 | 136 | 135
2016-07-24 03:30 | 135 | 134
2016-07-24 04:00 | 135 | 135
2016-07-24 04:30 | 136 | 136
2016-07-24 05:00 | 140 | 140
2016-07-24 05:30 | 145 | 145
2016-07-24 06:00 | 152 | 152
2016-07-24 06:30 | 159 | 159
2016-07-24 07:00 | 173 | 173
2016-07-24 07:30 | 184 | 184
2016-07-24 08:00 | 186 | 185
2016-07-24 08:30 | 191 | 190
2016-07-24 09:00 | 192 | 191
2016-07-24 09:30 | 191 | 189
2016-07-24 10:00 | 187 | 185
2016-07-24 10:30 | 180 | 179
2016-07-24 11:00 | 174 | 172
2016-07-24 11:30 | 169 | 168
2016-07-24 12:00 | 169 | 167
2016-07-24 12:30 | 172 | 170
2016-07-24 13:00 | 170 | 168
2016-07-24 13:30 | 169 | 168
2016-07-24 14:00 | 173 | 172
2016-07-24 14:30 | 180 | 178
2016-07-24 15:00 | 189 | 187
2016-07-24 15:30 | 199 | 198
2016-07-24 16:00 | 210 | 210
2016-07-24 16:30 | 224 | 224
2016-07-24 17:00 | 243 | 243
2016-07-24 17:30 | 261 | 261
2016-07-24 18:00 | 265 | 265
2016-07-24 18:30 | 264 | 264
2016-07-24 19:00 | 254 | 254
2016-07-24 19:30 | 251 | 251
2016-07-24 20:00 | 248 | 248
2016-07-24 20:30 | 236 | 235
2016-07-24 21:00 | 221 | 221
2016-07-24 21:30 | 210 | 210
2016-07-24 22:00 | 210 | 210
2016-07-24 22:30 | 205 | 205
2016-07-24 23:00 | 196 | 196
2016-07-24 23:30 | 183 | 183
2016-07-25 | 169 | 169
2016-07-25 00:30 | 160 | 160
2016-07-25 01:00 | 153 | 152
2016-07-25 01:30 | 146 | 145
2016-07-25 02:00 | 140 | 140
2016-07-25 02:30 | 138 | 138
2016-07-25 03:00 | 138 | 138
2016-07-25 03:30 | 139 | 139
2016-07-25 04:00 | 143 | 143
2016-07-25 04:30 | 150 | 150
2016-07-25 05:00 | 163 | 163
2016-07-25 05:30 | 181 | 181
2016-07-25 06:00 | 204 | 204
2016-07-25 06:30 | 223 | 222
2016-07-25 07:00 | 248 | 248
2016-07-25 07:30 | 249 | 248
2016-07-25 08:00 | 240 | 239
2016-07-25 08:30 | 229 | 228
2016-07-25 09:00 | 224 | 223
2016-07-25 09:30 | 216 | 215
2016-07-25 10:00 | 211 | 210
2016-07-25 10:30 | 204 | 203
2016-07-25 11:00 | 200 | 199
2016-07-25 11:30 | 199 | 197
2016-07-25 12:00 | 196 | 194
2016-07-25 12:30 | 196 | 195
2016-07-25 13:00 | 210 | 208
2016-07-25 13:30 | 209 | 208
2016-07-25 14:00 | 208 | 207
2016-07-25 14:30 | 209 | 208
2016-07-25 15:00 | 216 | 215
2016-07-25 15:30 | 225 | 225
2016-07-25 16:00 | 236 | 235
2016-07-25 16:30 | 253 | 253
2016-07-25 17:00 | 271 | 271
2016-07-25 17:30 | 294 | 294
2016-07-25 18:00 | 295 | 294
2016-07-25 18:30 | 294 | 294
2016-07-25 19:00 | 284 | 283
2016-07-25 19:30 | 281 | 280
2016-07-25 20:00 | 275 | 274
2016-07-25 20:30 | 259 | 259
2016-07-25 21:00 | 245 | 245
2016-07-25 21:30 | 231 | 231
2016-07-25 22:00 | 222 | 222
2016-07-25 22:30 | 213 | 213
2016-07-25 23:00 | 204 | 204
2016-07-25 23:30 | 190 | 190
2016-07-26 | 175 | 174
2016-07-26 00:30 | 165 | 165
2016-07-26 01:00 | 157 | 157
2016-07-26 01:30 | 149 | 149
2016-07-26 02:00 | 145 | 144
2016-07-26 02:30 | 141 | 140
2016-07-26 03:00 | 140 | 139
2016-07-26 03:30 | 140 | 139
2016-07-26 04:00 | 144 | 144
2016-07-26 04:30 | 151 | 150
2016-07-26 05:00 | 165 | 165
2016-07-26 05:30 | 183 | 183
2016-07-26 06:00 | 208 | 208
2016-07-26 06:30 | 235 | 235
2016-07-26 07:00 | 261 | 261
2016-07-26 07:30 | 269 | 269
2016-07-26 08:00 | 271 | 271
2016-07-26 08:30 | 253 | 253
2016-07-26 09:00 | 247 | 247
2016-07-26 09:30 | 241 | 241
2016-07-26 10:00 | 244 | 244
2016-07-26 10:30 | 232 | 232
2016-07-26 11:00 | 220 | 220
2016-07-26 11:30 | 210 | 210
2016-07-26 12:00 | 210 | 210
2016-07-26 12:30 | 212 | 212
2016-07-26 13:00 | 220 | 220
2016-07-26 13:30 | 214 | 214
2016-07-26 14:00 | 214 | 214
2016-07-26 14:30 | 225 | 225
2016-07-26 15:00 | 233 | 233
2016-07-26 15:30 | 242 | 242
2016-07-26 16:00 | 257 | 256
2016-07-26 16:30 | 275 | 275
2016-07-26 17:00 | 297 | 297
2016-07-26 17:30 | 317 | 317
2016-07-26 18:00 | 317 | 317
2016-07-26 18:30 | 317 | 317
2016-07-26 19:00 | 307 | 307
2016-07-26 19:30 | 302 | 301
2016-07-26 20:00 | 297 | 296
2016-07-26 20:30 | 280 | 279
2016-07-26 21:00 | 264 | 263
2016-07-26 21:30 | 246 | 246
2016-07-26 22:00 | 240 | 240
2016-07-26 22:30 | 229 | 229
2016-07-26 23:00 | 215 | 214
2016-07-26 23:30 | 199 | 198
2016-07-27 | 182 | 182
2016-07-27 00:30 | 172 | 171
2016-07-27 01:00 | 162 | 161
2016-07-27 01:30 | 153 | 153
2016-07-27 02:00 | 148 | 148
2016-07-27 02:30 | 144 | 144
2016-07-27 03:00 | 143 | 143
2016-07-27 03:30 | 144 | 144
2016-07-27 04:00 | 149 | 149
2016-07-27 04:30 | 155 | 155
2016-07-27 05:00 | 169 | 169
2016-07-27 05:30 | 188 | 188
2016-07-27 06:00 | 217 | 217
2016-07-27 06:30 | 242 | 242
2016-07-27 07:00 | 274 | 274
2016-07-27 07:30 | 285 | 285
2016-07-27 08:00 | 283 | 283
2016-07-27 08:30 | 277 | 277
2016-07-27 09:00 | 276 | 276
2016-07-27 09:30 | 268 | 268
2016-07-27 10:00 | 268 | 268
2016-07-27 10:30 | 261 | 261
2016-07-27 11:00 | 259 | 259
2016-07-27 11:30 | 245 | 245
2016-07-27 12:00 | 242 | 242
2016-07-27 12:30 | 245 | 245
2016-07-27 13:00 | 243 | 243
2016-07-27 13:30 | 240 | 240
2016-07-27 14:00 | 236 | 236
2016-07-27 14:30 | 234 | 234
2016-07-27 15:00 | 233 | 233
2016-07-27 15:30 | 241 | 241
2016-07-27 16:00 | 251 | 251
2016-07-27 16:30 | 268 | 267
2016-07-27 17:00 | 290 | 289
2016-07-27 17:30 | 316 | 316
2016-07-27 18:00 | 327 | 326
2016-07-27 18:30 | 331 | 330
2016-07-27 19:00 | 325 | 324
2016-07-27 19:30 | 322 | 321
2016-07-27 20:00 | 318 | 317
2016-07-27 20:30 | 304 | 304
2016-07-27 21:00 | 287 | 286
2016-07-27 21:30 | 268 | 267
2016-07-27 22:00 | 256 | 255
2016-07-27 22:30 | 243 | 243
2016-07-27 23:00 | 231 | 230
2016-07-27 23:30 | 213 | 213
2016-07-28 | 196 | 195
2016-07-28 00:30 | 182 | 181
2016-07-28 01:00 | 173 | 173
2016-07-28 01:30 | 164 | 164
2016-07-28 02:00 | 157 | 157
2016-07-28 02:30 | 153 | 153
2016-07-28 03:00 | 152 | 152
2016-07-28 03:30 | 153 | 153
2016-07-28 04:00 | 159 | 159
2016-07-28 04:30 | 166 | 166
2016-07-28 05:00 | 183 | 183
2016-07-28 05:30 | 207 | 206
2016-07-28 06:00 | 242 | 242
2016-07-28 06:30 | 278 | 276
2016-07-28 07:00 | 303 | 303
2016-07-28 07:30 | 301 | 300
2016-07-28 08:00 | 283 | 283
2016-07-28 08:30 | 263 | 263
2016-07-28 09:00 | 250 | 250
2016-07-28 09:30 | 234 | 234
2016-07-28 10:00 | 225 | 225
2016-07-28 10:30 | 215 | 215
2016-07-28 11:00 | 210 | 210
2016-07-28 11:30 | 206 | 206
2016-07-28 12:00 | 203 | 203
2016-07-28 12:30 | 203 | 203
2016-07-28 13:00 | 204 | 204
2016-07-28 13:30 | 207 | 207
2016-07-28 14:00 | 212 | 212
2016-07-28 14:30 | 222 | 222
2016-07-28 15:00 | 230 | 230
2016-07-28 15:30 | 240 | 240
2016-07-28 16:00 | 254 | 254
2016-07-28 16:30 | 271 | 271
2016-07-28 17:00 | 288 | 288
2016-07-28 17:30 | 314 | 314
2016-07-28 18:00 | 323 | 323
2016-07-28 18:30 | 327 | 326
2016-07-28 19:00 | 321 | 320
2016-07-28 19:30 | 318 | 317
2016-07-28 20:00 | 315 | 314
2016-07-28 20:30 | 302 | 301
2016-07-28 21:00 | 286 | 285
2016-07-28 21:30 | 270 | 268
2016-07-28 22:00 | 273 | 272
2016-07-28 22:30 | 256 | 254
2016-07-28 23:00 | 229 | 229
2016-07-28 23:30 | 209 | 209
2016-07-29 | 193 | 193
2016-07-29 00:30 | 184 | 184
2016-07-29 01:00 | 176 | 176
2016-07-29 01:30 | 169 | 168
2016-07-29 02:00 | 163 | 162
2016-07-29 02:30 | 160 | 159
2016-07-29 03:00 | 159 | 158
2016-07-29 03:30 | 160 | 159
2016-07-29 04:00 | 165 | 164
2016-07-29 04:30 | 173 | 173
2016-07-29 05:00 | 187 | 187
2016-07-29 05:30 | 207 | 207
2016-07-29 06:00 | 236 | 236
2016-07-29 06:30 | 269 | 269
2016-07-29 07:00 | 292 | 292
2016-07-29 07:30 | 292 | 292
2016-07-29 08:00 | 276 | 276
2016-07-29 08:30 | 259 | 259
2016-07-29 09:00 | 247 | 247
2016-07-29 09:30 | 235 | 235
2016-07-29 10:00 | 226 | 226
2016-07-29 10:30 | 216 | 216
2016-07-29 11:00 | 210 | 208
2016-07-29 11:30 | 206 | 205
2016-07-29 12:00 | 203 | 202
2016-07-29 12:30 | 201 | 200
2016-07-29 13:00 | 201 | 200
2016-07-29 13:30 | 205 | 204
2016-07-29 14:00 | 208 | 207
2016-07-29 14:30 | 213 | 212
2016-07-29 15:00 | 220 | 219
2016-07-29 15:30 | 229 | 228
2016-07-29 16:00 | 242 | 241
2016-07-29 16:30 | 256 | 256
2016-07-29 17:00 | 270 | 269
2016-07-29 17:30 | 288 | 288
2016-07-29 18:00 | 290 | 290
2016-07-29 18:30 | 293 | 293
2016-07-29 19:00 | 287 | 287
2016-07-29 19:30 | 285 | 284
2016-07-29 20:00 | 282 | 282
2016-07-29 20:30 | 272 | 272
2016-07-29 21:00 | 261 | 261
2016-07-29 21:30 | 251 | 251
2016-07-29 22:00 | 258 | 258
2016-07-29 22:30 | 243 | 243
2016-07-29 23:00 | 220 | 220
2016-07-29 23:30 | 202 | 202
2016-07-30 | 188 | 187
2016-07-30 00:30 | 178 | 178
2016-07-30 01:00 | 169 | 169
2016-07-30 01:30 | 161 | 161
2016-07-30 02:00 | 154 | 154
2016-07-30 02:30 | 151 | 151
2016-07-30 03:00 | 150 | 150
2016-07-30 03:30 | 149 | 149
2016-07-30 04:00 | 151 | 151
2016-07-30 04:30 | 155 | 155
2016-07-30 05:00 | 163 | 163
2016-07-30 05:30 | 173 | 173
2016-07-30 06:00 | 189 | 189
2016-07-30 06:30 | 207 | 207
2016-07-30 07:00 | 228 | 228
2016-07-30 07:30 | 238 | 238
2016-07-30 08:00 | 241 | 241
2016-07-30 08:30 | 236 | 236
2016-07-30 09:00 | 228 | 228
2016-07-30 09:30 | 218 | 218
2016-07-30 10:00 | 209 | 207
2016-07-30 10:30 | 199 | 197
2016-07-30 11:00 | 191 | 189
2016-07-30 11:30 | 184 | 182
2016-07-30 12:00 | 180 | 178
2016-07-30 12:30 | 179 | 177
2016-07-30 13:00 | 185 | 183
2016-07-30 13:30 | 192 | 190
2016-07-30 14:00 | 191 | 190
2016-07-30 14:30 | 195 | 194
2016-07-30 15:00 | 203 | 202
2016-07-30 15:30 | 213 | 212
2016-07-30 16:00 | 227 | 227
2016-07-30 16:30 | 242 | 242
2016-07-30 17:00 | 257 | 257
2016-07-30 17:30 | 275 | 275
2016-07-30 18:00 | 279 | 278
2016-07-30 18:30 | 280 | 279
2016-07-30 19:00 | 273 | 272
2016-07-30 19:30 | 269 | 269
2016-07-30 20:00 | 266 | 266
2016-07-30 20:30 | 257 | 257
2016-07-30 21:00 | 248 | 248
2016-07-30 21:30 | 243 | 243
2016-07-30 22:00 | 240 | 240
2016-07-30 22:30 | 226 | 226
2016-07-30 23:00 | 207 | 207
2016-07-30 23:30 | 192 | 191
2016-07-31 | 178 | 178
2016-07-31 00:30 | 170 | 170
2016-07-31 01:00 | 162 | 162
2016-07-31 01:30 | 154 | 154
2016-07-31 02:00 | 150 | 150
2016-07-31 02:30 | 148 | 148
2016-07-31 03:00 | 147 | 147
2016-07-31 03:30 | 146 | 146
2016-07-31 04:00 | 147 | 147
2016-07-31 04:30 | 149 | 149
2016-07-31 05:00 | 154 | 154
2016-07-31 05:30 | 162 | 161
2016-07-31 06:00 | 171 | 171
2016-07-31 06:30 | 183 | 182
2016-07-31 07:00 | 198 | 198
2016-07-31 07:30 | 206 | 205
2016-07-31 08:00 | 213 | 212
2016-07-31 08:30 | 214 | 213
2016-07-31 09:00 | 212 | 210
2016-07-31 09:30 | 206 | 205
2016-07-31 10:00 | 199 | 199
2016-07-31 10:30 | 192 | 192
2016-07-31 11:00 | 191 | 191
2016-07-31 11:30 | 186 | 185
2016-07-31 12:00 | 182 | 182
2016-07-31 12:30 | 179 | 179
2016-07-31 13:00 | 179 | 178
2016-07-31 13:30 | 182 | 180
2016-07-31 14:00 | 187 | 186
2016-07-31 14:30 | 194 | 192
2016-07-31 15:00 | 198 | 197
2016-07-31 15:30 | 208 | 207
2016-07-31 16:00 | 221 | 219
2016-07-31 16:30 | 235 | 234
2016-07-31 17:00 | 254 | 254
2016-07-31 17:30 | 276 | 276
2016-07-31 18:00 | 283 | 282
2016-07-31 18:30 | 283 | 282
2016-07-31 19:00 | 274 | 274
2016-07-31 19:30 | 271 | 270
2016-07-31 20:00 | 268 | 266
2016-07-31 20:30 | 253 | 253
2016-07-31 21:00 | 241 | 241
2016-07-31 21:30 | 231 | 231
2016-07-31 22:00 | 239 | 239
2016-07-31 22:30 | 230 | 229
2016-07-31 23:00 | 210 | 210
2016-07-31 23:30 | 191 | 191
2016-08-01 | 177 | 177
2016-08-01 00:30 | 169 | 168
2016-08-01 01:00 | 161 | 161
2016-08-01 01:30 | 154 | 154
2016-08-01 02:00 | 150 | 150
2016-08-01 02:30 | 147 | 147
2016-08-01 03:00 | 147 | 147
2016-08-01 03:30 | 146 | 146
2016-08-01 04:00 | 149 | 149
2016-08-01 04:30 | 155 | 155
2016-08-01 05:00 | 172 | 172
2016-08-01 05:30 | 192 | 191
2016-08-01 06:00 | 223 | 221
2016-08-01 06:30 | 250 | 248
2016-08-01 07:00 | 272 | 272
2016-08-01 07:30 | 273 | 273
2016-08-01 08:00 | 260 | 260
2016-08-01 08:30 | 244 | 244
2016-08-01 09:00 | 232 | 232
2016-08-01 09:30 | 222 | 222
2016-08-01 10:00 | 214 | 214
2016-08-01 10:30 | 208 | 208
2016-08-01 11:00 | 202 | 202
2016-08-01 11:30 | 198 | 198
2016-08-01 12:00 | 196 | 196
2016-08-01 12:30 | 195 | 195
2016-08-01 13:00 | 197 | 197
2016-08-01 13:30 | 201 | 201
2016-08-01 14:00 | 205 | 205
2016-08-01 14:30 | 210 | 210
2016-08-01 15:00 | 217 | 217
2016-08-01 15:30 | 227 | 227
2016-08-01 16:00 | 239 | 238
2016-08-01 16:30 | 254 | 254
2016-08-01 17:00 | 275 | 275
2016-08-01 17:30 | 304 | 304
2016-08-01 18:00 | 307 | 307
2016-08-01 18:30 | 299 | 298
2016-08-01 19:00 | 285 | 284
2016-08-01 19:30 | 270 | 270
2016-08-01 20:00 | 261 | 260
2016-08-01 20:30 | 255 | 255
2016-08-01 21:00 | 247 | 247
2016-08-01 21:30 | 234 | 234
2016-08-01 22:00 | 242 | 242
2016-08-01 22:30 | 228 | 228
2016-08-01 23:00 | 208 | 207
2016-08-01 23:30 | 191 | 191
2016-08-02 | 175 | 175
2016-08-02 00:30 | 165 | 164
2016-08-02 01:00 | 156 | 156
2016-08-02 01:30 | 149 | 148
2016-08-02 02:00 | 143 | 143
2016-08-02 02:30 | 140 | 140
2016-08-02 03:00 | 139 | 138
2016-08-02 03:30 | 140 | 139
2016-08-02 04:00 | 144 | 143
2016-08-02 04:30 | 151 | 150
2016-08-02 05:00 | 165 | 165
2016-08-02 05:30 | 183 | 182
2016-08-02 06:00 | 208 | 208
2016-08-02 06:30 | 236 | 236
2016-08-02 07:00 | 265 | 264
2016-08-02 07:30 | 275 | 275
2016-08-02 08:00 | 272 | 271
2016-08-02 08:30 | 263 | 262
2016-08-02 09:00 | 248 | 247
2016-08-02 09:30 | 228 | 228
2016-08-02 10:00 | 221 | 221
2016-08-02 10:30 | 216 | 216
2016-08-02 11:00 | 216 | 216
2016-08-02 11:30 | 219 | 219
2016-08-02 12:00 | 230 | 230
2016-08-02 12:30 | 231 | 231
2016-08-02 13:00 | 234 | 234
2016-08-02 13:30 | 241 | 241
2016-08-02 14:00 | 242 | 242
2016-08-02 14:30 | 237 | 237
2016-08-02 15:00 | 236 | 236
2016-08-02 15:30 | 234 | 234
2016-08-02 16:00 | 244 | 244
2016-08-02 16:30 | 257 | 257
2016-08-02 17:00 | 276 | 276
2016-08-02 17:30 | 294 | 293
2016-08-02 18:00 | 295 | 295
2016-08-02 18:30 | 295 | 294
2016-08-02 19:00 | 285 | 284
2016-08-02 19:30 | 279 | 279
2016-08-02 20:00 | 273 | 272
2016-08-02 20:30 | 257 | 256
2016-08-02 21:00 | 243 | 243
2016-08-02 21:30 | 230 | 229
2016-08-02 22:00 | 237 | 236
2016-08-02 22:30 | 226 | 224
2016-08-02 23:00 | 202 | 201
2016-08-02 23:30 | 183 | 183
2016-08-03 | 169 | 169
2016-08-03 00:30 | 160 | 160
2016-08-03 01:00 | 153 | 153
2016-08-03 01:30 | 147 | 146
2016-08-03 02:00 | 142 | 142
2016-08-03 02:30 | 138 | 137
2016-08-03 03:00 | 138 | 137
2016-08-03 03:30 | 138 | 137
2016-08-03 04:00 | 142 | 141
2016-08-03 04:30 | 148 | 148
2016-08-03 05:00 | 162 | 162
2016-08-03 05:30 | 179 | 179
2016-08-03 06:00 | 204 | 204
2016-08-03 06:30 | 229 | 229
2016-08-03 07:00 | 256 | 256
2016-08-03 07:30 | 270 | 269
2016-08-03 08:00 | 280 | 278
2016-08-03 08:30 | 270 | 270
2016-08-03 09:00 | 257 | 257
2016-08-03 09:30 | 245 | 245
2016-08-03 10:00 | 238 | 238
2016-08-03 10:30 | 237 | 237
2016-08-03 11:00 | 235 | 235
2016-08-03 11:30 | 226 | 226
2016-08-03 12:00 | 221 | 221
2016-08-03 12:30 | 218 | 218
2016-08-03 13:00 | 216 | 215
2016-08-03 13:30 | 216 | 216
2016-08-03 14:00 | 219 | 219
2016-08-03 14:30 | 223 | 223
2016-08-03 15:00 | 230 | 230
2016-08-03 15:30 | 240 | 240
2016-08-03 16:00 | 255 | 254
2016-08-03 16:30 | 274 | 273
2016-08-03 17:00 | 294 | 294
2016-08-03 17:30 | 322 | 322
2016-08-03 18:00 | 333 | 332
2016-08-03 18:30 | 335 | 334
2016-08-03 19:00 | 326 | 325
2016-08-03 19:30 | 321 | 320
2016-08-03 20:00 | 317 | 316
2016-08-03 20:30 | 301 | 300
2016-08-03 21:00 | 286 | 286
2016-08-03 21:30 | 271 | 270
2016-08-03 22:00 | 274 | 273
2016-08-03 22:30 | 255 | 255
2016-08-03 23:00 | 230 | 230
2016-08-03 23:30 | 210 | 210
2016-08-04 | 195 | 194
2016-08-04 00:30 | 184 | 183
2016-08-04 01:00 | 174 | 173
2016-08-04 01:30 | 166 | 165
2016-08-04 02:00 | 160 | 159
2016-08-04 02:30 | 157 | 156
2016-08-04 03:00 | 157 | 157
2016-08-04 03:30 | 157 | 156
2016-08-04 04:00 | 162 | 161
2016-08-04 04:30 | 167 | 166
2016-08-04 05:00 | 184 | 183
2016-08-04 05:30 | 205 | 205
2016-08-04 06:00 | 230 | 230
2016-08-04 06:30 | 261 | 260
2016-08-04 07:00 | 296 | 295
2016-08-04 07:30 | 309 | 309
2016-08-04 08:00 | 302 | 302
2016-08-04 08:30 | 279 | 278
2016-08-04 09:00 | 266 | 265
2016-08-04 09:30 | 258 | 257
2016-08-04 10:00 | 244 | 244
2016-08-04 10:30 | 233 | 232
2016-08-04 11:00 | 237 | 236
2016-08-04 11:30 | 238 | 237
2016-08-04 12:00 | 235 | 234
2016-08-04 12:30 | 239 | 239
2016-08-04 13:00 | 240 | 239
2016-08-04 13:30 | 251 | 250
2016-08-04 14:00 | 244 | 243
2016-08-04 14:30 | 240 | 239
2016-08-04 15:00 | 242 | 241
2016-08-04 15:30 | 243 | 242
2016-08-04 16:00 | 257 | 257
2016-08-04 16:30 | 278 | 278
2016-08-04 17:00 | 305 | 304
2016-08-04 17:30 | 327 | 326
2016-08-04 18:00 | 336 | 336
2016-08-04 18:30 | 336 | 335
2016-08-04 19:00 | 324 | 323
2016-08-04 19:30 | 324 | 324
2016-08-04 20:00 | 318 | 316
2016-08-04 20:30 | 312 | 310
2016-08-04 21:00 | 292 | 290
2016-08-04 21:30 | 268 | 265
2016-08-04 22:00 | 251 | 251
2016-08-04 22:30 | 244 | 244
2016-08-04 23:00 | 231 | 230
2016-08-04 23:30 | 215 | 214
2016-08-05 | 201 | 201
2016-08-05 00:30 | 194 | 194
2016-08-05 01:00 | 190 | 190
2016-08-05 01:30 | 187 | 187
2016-08-05 02:00 | 182 | 182
2016-08-05 02:30 | 178 | 178
2016-08-05 03:00 | 176 | 176
2016-08-05 03:30 | 176 | 176
2016-08-05 04:00 | 179 | 179
2016-08-05 04:30 | 186 | 186
2016-08-05 05:00 | 195 | 195
2016-08-05 05:30 | 204 | 203
2016-08-05 06:00 | 220 | 219
2016-08-05 06:30 | 246 | 246
2016-08-05 07:00 | 273 | 273
2016-08-05 07:30 | 285 | 285
2016-08-05 08:00 | 281 | 281
2016-08-05 08:30 | 272 | 272
2016-08-05 09:00 | 264 | 264
2016-08-05 09:30 | 257 | 257
2016-08-05 10:00 | 252 | 252
2016-08-05 10:30 | 239 | 239
2016-08-05 11:00 | 231 | 231
2016-08-05 11:30 | 225 | 225
2016-08-05 12:00 | 223 | 223
2016-08-05 12:30 | 222 | 222
2016-08-05 13:00 | 223 | 222
2016-08-05 13:30 | 227 | 227
2016-08-05 14:00 | 232 | 231
2016-08-05 14:30 | 235 | 235
2016-08-05 15:00 | 239 | 239
2016-08-05 15:30 | 242 | 242
2016-08-05 16:00 | 252 | 252
2016-08-05 16:30 | 262 | 262
2016-08-05 17:00 | 292 | 291
2016-08-05 17:30 | 307 | 306
2016-08-05 18:00 | 310 | 310
2016-08-05 18:30 | 310 | 310
2016-08-05 19:00 | 304 | 303
2016-08-05 19:30 | 303 | 303
2016-08-05 20:00 | 301 | 301
2016-08-05 20:30 | 289 | 288
2016-08-05 21:00 | 279 | 278
2016-08-05 21:30 | 268 | 267
2016-08-05 22:00 | 256 | 255
2016-08-05 22:30 | 248 | 247
2016-08-05 23:00 | 237 | 237
2016-08-05 23:30 | 225 | 225
2016-08-06 | 205 | 205
2016-08-06 00:30 | 196 | 196
2016-08-06 01:00 | 190 | 190
2016-08-06 01:30 | 180 | 180
2016-08-06 02:00 | 173 | 173
2016-08-06 02:30 | 168 | 168
2016-08-06 03:00 | 166 | 166
2016-08-06 03:30 | 168 | 167
2016-08-06 04:00 | 168 | 167
2016-08-06 04:30 | 171 | 170
2016-08-06 05:00 | 176 | 176
2016-08-06 05:30 | 186 | 186
2016-08-06 06:00 | 196 | 196
2016-08-06 06:30 | 206 | 206
2016-08-06 07:00 | 222 | 222
2016-08-06 07:30 | 238 | 238
2016-08-06 08:00 | 247 | 247
2016-08-06 08:30 | 248 | 248
2016-08-06 09:00 | 245 | 244
2016-08-06 09:30 | 239 | 238
2016-08-06 10:00 | 232 | 231
2016-08-06 10:30 | 227 | 226
2016-08-06 11:00 | 225 | 224
2016-08-06 11:30 | 219 | 219
2016-08-06 12:00 | 213 | 213
2016-08-06 12:30 | 215 | 215
2016-08-06 13:00 | 214 | 214
2016-08-06 13:30 | 214 | 214
2016-08-06 14:00 | 217 | 217
2016-08-06 14:30 | 223 | 223
2016-08-06 15:00 | 232 | 232
2016-08-06 15:30 | 237 | 237
2016-08-06 16:00 | 244 | 244
2016-08-06 16:30 | 257 | 256
2016-08-06 17:00 | 280 | 277
2016-08-06 17:30 | 301 | 299
2016-08-06 18:00 | 305 | 303
2016-08-06 18:30 | 303 | 301
2016-08-06 19:00 | 296 | 293
2016-08-06 19:30 | 290 | 286
2016-08-06 20:00 | 282 | 278
2016-08-06 20:30 | 266 | 263
2016-08-06 21:00 | 254 | 253
2016-08-06 21:30 | 251 | 249
2016-08-06 22:00 | 247 | 244
2016-08-06 22:30 | 238 | 234
2016-08-06 23:00 | 232 | 227
2016-08-06 23:30 | 225 | 219
2016-08-07 | 211 | 203
2016-08-07 00:30 | 205 | 196
2016-08-07 01:00 | 197 | 187
2016-08-07 01:30 | 188 | 178
2016-08-07 02:00 | 179 | 172
2016-08-07 02:30 | 176 | 168
2016-08-07 03:00 | 175 | 166
2016-08-07 03:30 | 174 | 165
2016-08-07 04:00 | 175 | 167
2016-08-07 04:30 | 176 | 167
2016-08-07 05:00 | 181 | 173
2016-08-07 05:30 | 187 | 180
2016-08-07 06:00 | 197 | 190
2016-08-07 06:30 | 207 | 201
2016-08-07 07:00 | 221 | 216
2016-08-07 07:30 | 228 | 224
2016-08-07 08:00 | 231 | 228
2016-08-07 08:30 | 232 | 229
2016-08-07 09:00 | 233 | 230
2016-08-07 09:30 | 228 | 227
2016-08-07 10:00 | 221 | 219
2016-08-07 10:30 | 211 | 209
2016-08-07 11:00 | 204 | 202
2016-08-07 11:30 | 202 | 200
2016-08-07 12:00 | 206 | 204
2016-08-07 12:30 | 204 | 202
2016-08-07 13:00 | 203 | 200
2016-08-07 13:30 | 208 | 206
2016-08-07 14:00 | 215 | 212
2016-08-07 14:30 | 221 | 219
2016-08-07 15:00 | 229 | 227
2016-08-07 15:30 | 238 | 236
2016-08-07 16:00 | 245 | 242
2016-08-07 16:30 | 255 | 250
2016-08-07 17:00 | 272 | 269
2016-08-07 17:30 | 291 | 289
2016-08-07 18:00 | 296 | 294
2016-08-07 18:30 | 292 | 291
2016-08-07 19:00 | 287 | 285
2016-08-07 19:30 | 285 | 282
2016-08-07 20:00 | 280 | 277
2016-08-07 20:30 | 267 | 263
2016-08-07 21:00 | 249 | 245
2016-08-07 21:30 | 236 | 234
2016-08-07 22:00 | 228 | 226
2016-08-07 22:30 | 226 | 223
2016-08-07 23:00 | 218 | 215
2016-08-07 23:30 | 213 | 209
2016-08-08 | 199 | 194
2016-08-08 00:30 | 192 | 186
2016-08-08 01:00 | 187 | 180
2016-08-08 01:30 | 179 | 172
2016-08-08 02:00 | 174 | 167
2016-08-08 02:30 | 171 | 163
2016-08-08 03:00 | 170 | 162
2016-08-08 03:30 | 172 | 164
2016-08-08 04:00 | 176 | 168
2016-08-08 04:30 | 182 | 175
2016-08-08 05:00 | 194 | 189
2016-08-08 05:30 | 202 | 198
2016-08-08 06:00 | 217 | 214
2016-08-08 06:30 | 245 | 243
2016-08-08 07:00 | 268 | 264
2016-08-08 07:30 | 272 | 269
2016-08-08 08:00 | 258 | 255
2016-08-08 08:30 | 241 | 238
2016-08-08 09:00 | 233 | 229
2016-08-08 09:30 | 222 | 218
2016-08-08 10:00 | 216 | 212
2016-08-08 10:30 | 208 | 205
2016-08-08 11:00 | 206 | 205
2016-08-08 11:30 | 216 | 215
2016-08-08 12:00 | 223 | 222
2016-08-08 12:30 | 223 | 222
2016-08-08 13:00 | 237 | 235
2016-08-08 13:30 | 235 | 231
2016-08-08 14:00 | 237 | 233
2016-08-08 14:30 | 235 | 231
2016-08-08 15:00 | 239 | 235
2016-08-08 15:30 | 240 | 236
2016-08-08 16:00 | 248 | 244
2016-08-08 16:30 | 256 | 253
2016-08-08 17:00 | 279 | 277
2016-08-08 17:30 | 301 | 299
2016-08-08 18:00 | 305 | 303
2016-08-08 18:30 | 305 | 303
2016-08-08 19:00 | 301 | 299
2016-08-08 19:30 | 300 | 298
2016-08-08 20:00 | 293 | 290
2016-08-08 20:30 | 279 | 275
2016-08-08 21:00 | 265 | 261
2016-08-08 21:30 | 259 | 255
2016-08-08 22:00 | 244 | 239
2016-08-08 22:30 | 232 | 229
2016-08-08 23:00 | 218 | 215
2016-08-08 23:30 | 209 | 205
2016-08-09 | 199 | 193
2016-08-09 00:30 | 193 | 187
2016-08-09 01:00 | 190 | 183
2016-08-09 01:30 | 183 | 176
2016-08-09 02:00 | 178 | 170
2016-08-09 02:30 | 175 | 167
2016-08-09 03:00 | 174 | 166
2016-08-09 03:30 | 175 | 168
2016-08-09 04:00 | 179 | 172
2016-08-09 04:30 | 186 | 180
2016-08-09 05:00 | 201 | 196
2016-08-09 05:30 | 212 | 209
2016-08-09 06:00 | 225 | 223
2016-08-09 06:30 | 253 | 251
2016-08-09 07:00 | 272 | 272
2016-08-09 07:30 | 280 | 280
2016-08-09 08:00 | 271 | 271
2016-08-09 08:30 | 252 | 252
2016-08-09 09:00 | 241 | 240
2016-08-09 09:30 | 235 | 234
2016-08-09 10:00 | 232 | 231
2016-08-09 10:30 | 225 | 224
2016-08-09 11:00 | 222 | 221
2016-08-09 11:30 | 220 | 219
2016-08-09 12:00 | 218 | 217
2016-08-09 12:30 | 217 | 216
2016-08-09 13:00 | 218 | 217
2016-08-09 13:30 | 221 | 220
2016-08-09 14:00 | 225 | 224
2016-08-09 14:30 | 228 | 227
2016-08-09 15:00 | 231 | 231
2016-08-09 15:30 | 237 | 237
2016-08-09 16:00 | 245 | 245
2016-08-09 16:30 | 254 | 253
2016-08-09 17:00 | 272 | 272
2016-08-09 17:30 | 296 | 296
2016-08-09 18:00 | 303 | 302
2016-08-09 18:30 | 302 | 301
2016-08-09 19:00 | 293 | 292
2016-08-09 19:30 | 291 | 289
2016-08-09 20:00 | 280 | 279
2016-08-09 20:30 | 267 | 266
2016-08-09 21:00 | 255 | 254
2016-08-09 21:30 | 251 | 250
2016-08-09 22:00 | 231 | 229
2016-08-09 22:30 | 219 | 218
2016-08-09 23:00 | 194 | 194
2016-08-09 23:30 | 201 | 201
2016-08-10 | 178 | 178
2016-08-10 00:30 | 166 | 166
2016-08-10 01:00 | 179 | 179
2016-08-10 01:30 | 173 | 173
2016-08-10 02:00 | 168 | 168
2016-08-10 02:30 | 165 | 165
2016-08-10 03:00 | 164 | 164
2016-08-10 03:30 | 165 | 165
2016-08-10 04:00 | 169 | 169
2016-08-10 04:30 | 175 | 175
2016-08-10 05:00 | 190 | 190
2016-08-10 05:30 | 200 | 199
2016-08-10 06:00 | 214 | 214
2016-08-10 06:30 | 234 | 234
2016-08-10 07:00 | 245 | 245
2016-08-10 07:30 | 261 | 261
2016-08-10 08:00 | 249 | 249
2016-08-10 08:30 | 235 | 235
2016-08-10 09:00 | 225 | 225
2016-08-10 09:30 | 216 | 216
2016-08-10 10:00 | 210 | 210
2016-08-10 10:30 | 203 | 203
2016-08-10 11:00 | 200 | 200
2016-08-10 11:30 | 196 | 196
2016-08-10 12:00 | 201 | 201
2016-08-10 12:30 | 196 | 196
2016-08-10 13:00 | 197 | 197
2016-08-10 13:30 | 201 | 201
2016-08-10 14:00 | 207 | 207
2016-08-10 14:30 | 213 | 213
2016-08-10 15:00 | 219 | 219
2016-08-10 15:30 | 227 | 227
2016-08-10 16:00 | 239 | 238
2016-08-10 16:30 | 252 | 252
2016-08-10 17:00 | 265 | 264
2016-08-10 17:30 | 282 | 281
2016-08-10 18:00 | 284 | 284
2016-08-10 18:30 | 282 | 282
2016-08-10 19:00 | 275 | 275
2016-08-10 19:30 | 274 | 273
2016-08-10 20:00 | 270 | 269
2016-08-10 20:30 | 260 | 259
2016-08-10 21:00 | 244 | 244
2016-08-10 21:30 | 241 | 241
2016-08-10 22:00 | 231 | 231
2016-08-10 22:30 | 224 | 224
2016-08-10 23:00 | 209 | 208
2016-08-10 23:30 | 198 | 198
2016-08-11 | 186 | 185
2016-08-11 00:30 | 182 | 181
2016-08-11 01:00 | 172 | 172
2016-08-11 01:30 | 170 | 170
2016-08-11 02:00 | 166 | 166
2016-08-11 02:30 | 163 | 163
2016-08-11 03:00 | 163 | 162
2016-08-11 03:30 | 151 | 150
2016-08-11 04:00 | 159 | 158
2016-08-11 04:30 | 175 | 174
2016-08-11 05:00 | 189 | 189
2016-08-11 05:30 | 200 | 200
2016-08-11 06:00 | 214 | 214
2016-08-11 06:30 | 236 | 236
2016-08-11 07:00 | 256 | 255
2016-08-11 07:30 | 264 | 264
2016-08-11 08:00 | 259 | 259
2016-08-11 08:30 | 246 | 246
2016-08-11 09:00 | 240 | 240
2016-08-11 09:30 | 233 | 233
2016-08-11 10:00 | 230 | 230
2016-08-11 10:30 | 228 | 228
2016-08-11 11:00 | 227 | 227
2016-08-11 11:30 | 230 | 229
2016-08-11 12:00 | 224 | 224
2016-08-11 12:30 | 230 | 229
2016-08-11 13:00 | 232 | 232
2016-08-11 13:30 | 230 | 230
2016-08-11 14:00 | 240 | 240
2016-08-11 14:30 | 241 | 241
2016-08-11 15:00 | 243 | 243
2016-08-11 15:30 | 248 | 248
2016-08-11 16:00 | 253 | 252
2016-08-11 16:30 | 264 | 264
2016-08-11 17:00 | 281 | 281
2016-08-11 17:30 | 293 | 293
2016-08-11 18:00 | 295 | 295
2016-08-11 18:30 | 295 | 295
2016-08-11 19:00 | 289 | 289
2016-08-11 19:30 | 286 | 286
2016-08-11 20:00 | 285 | 285
2016-08-11 20:30 | 275 | 275
2016-08-11 21:00 | 260 | 260
2016-08-11 21:30 | 253 | 253
2016-08-11 22:00 | 246 | 245
2016-08-11 22:30 | 232 | 232
2016-08-11 23:00 | 213 | 213
2016-08-11 23:30 | 203 | 203
2016-08-12 | 191 | 191
2016-08-12 00:30 | 184 | 183
2016-08-12 01:00 | 177 | 176
2016-08-12 01:30 | 170 | 170
2016-08-12 02:00 | 165 | 164
2016-08-12 02:30 | 163 | 162
2016-08-12 03:00 | 163 | 162
2016-08-12 03:30 | 162 | 162
2016-08-12 04:00 | 166 | 166
2016-08-12 04:30 | 173 | 172
2016-08-12 05:00 | 186 | 186
2016-08-12 05:30 | 203 | 203
2016-08-12 06:00 | 220 | 220
2016-08-12 06:30 | 243 | 243
2016-08-12 07:00 | 263 | 263
2016-08-12 07:30 | 271 | 271
2016-08-12 08:00 | 265 | 265
2016-08-12 08:30 | 254 | 253
2016-08-12 09:00 | 247 | 247
2016-08-12 09:30 | 240 | 240
2016-08-12 10:00 | 238 | 238
2016-08-12 10:30 | 240 | 240
2016-08-12 11:00 | 239 | 239
2016-08-12 11:30 | 227 | 227
2016-08-12 12:00 | 228 | 228
2016-08-12 12:30 | 224 | 224
2016-08-12 13:00 | 226 | 226
2016-08-12 13:30 | 227 | 227
2016-08-12 14:00 | 223 | 223
2016-08-12 14:30 | 224 | 224
2016-08-12 15:00 | 231 | 231
2016-08-12 15:30 | 236 | 236
2016-08-12 16:00 | 242 | 241
2016-08-12 16:30 | 256 | 256
2016-08-12 17:00 | 277 | 277
2016-08-12 17:30 | 294 | 293
2016-08-12 18:00 | 298 | 297
2016-08-12 18:30 | 298 | 298
2016-08-12 19:00 | 292 | 291
2016-08-12 19:30 | 290 | 289
2016-08-12 20:00 | 287 | 286
2016-08-12 20:30 | 275 | 274
2016-08-12 21:00 | 258 | 258
2016-08-12 21:30 | 250 | 250
2016-08-12 22:00 | 240 | 239
2016-08-12 22:30 | 238 | 237
2016-08-12 23:00 | 220 | 220
2016-08-12 23:30 | 208 | 208
2016-08-13 | 195 | 195
2016-08-13 00:30 | 177 | 177
2016-08-13 01:00 | 182 | 182
2016-08-13 01:30 | 174 | 174
2016-08-13 02:00 | 170 | 169
2016-08-13 02:30 | 166 | 166
2016-08-13 03:00 | 165 | 164
2016-08-13 03:30 | 163 | 163
2016-08-13 04:00 | 165 | 165
2016-08-13 04:30 | 168 | 168
2016-08-13 05:00 | 175 | 175
2016-08-13 05:30 | 186 | 186
2016-08-13 06:00 | 194 | 194
2016-08-13 06:30 | 204 | 204
2016-08-13 07:00 | 217 | 217
2016-08-13 07:30 | 229 | 228
2016-08-13 08:00 | 237 | 236
2016-08-13 08:30 | 238 | 238
2016-08-13 09:00 | 230 | 230
2016-08-13 09:30 | 224 | 224
2016-08-13 10:00 | 222 | 221
2016-08-13 10:30 | 218 | 217
2016-08-13 11:00 | 211 | 210
2016-08-13 11:30 | 208 | 207
2016-08-13 12:00 | 200 | 199
2016-08-13 12:30 | 191 | 191
2016-08-13 13:00 | 191 | 191
2016-08-13 13:30 | 197 | 197
2016-08-13 14:00 | 201 | 201
2016-08-13 14:30 | 206 | 206
2016-08-13 15:00 | 209 | 209
2016-08-13 15:30 | 214 | 214
2016-08-13 16:00 | 223 | 223
2016-08-13 16:30 | 231 | 231
2016-08-13 17:00 | 240 | 239
2016-08-13 17:30 | 260 | 260
2016-08-13 18:00 | 271 | 271
2016-08-13 18:30 | 277 | 276
2016-08-13 19:00 | 274 | 272
2016-08-13 19:30 | 270 | 267
2016-08-13 20:00 | 264 | 262
2016-08-13 20:30 | 252 | 252
2016-08-13 21:00 | 244 | 244
2016-08-13 21:30 | 237 | 237
2016-08-13 22:00 | 226 | 226
2016-08-13 22:30 | 224 | 224
2016-08-13 23:00 | 214 | 213
2016-08-13 23:30 | 205 | 205
2016-08-14 | 193 | 193
2016-08-14 00:30 | 186 | 186
2016-08-14 01:00 | 180 | 180
2016-08-14 01:30 | 172 | 172
2016-08-14 02:00 | 166 | 166
2016-08-14 02:30 | 164 | 164
2016-08-14 03:00 | 162 | 162
2016-08-14 03:30 | 162 | 161
2016-08-14 04:00 | 163 | 162
2016-08-14 04:30 | 164 | 164
2016-08-14 05:00 | 170 | 170
2016-08-14 05:30 | 176 | 176
2016-08-14 06:00 | 185 | 184
2016-08-14 06:30 | 196 | 196
2016-08-14 07:00 | 206 | 206
2016-08-14 07:30 | 217 | 217
2016-08-14 08:00 | 224 | 224
2016-08-14 08:30 | 225 | 225
2016-08-14 09:00 | 223 | 223
2016-08-14 09:30 | 218 | 217
2016-08-14 10:00 | 211 | 211
2016-08-14 10:30 | 205 | 204
2016-08-14 11:00 | 199 | 198
2016-08-14 11:30 | 192 | 192
2016-08-14 12:00 | 189 | 189
2016-08-14 12:30 | 189 | 188
2016-08-14 13:00 | 187 | 187
2016-08-14 13:30 | 190 | 190
2016-08-14 14:00 | 195 | 194
2016-08-14 14:30 | 200 | 200
2016-08-14 15:00 | 208 | 207
2016-08-14 15:30 | 214 | 214
2016-08-14 16:00 | 221 | 220
2016-08-14 16:30 | 233 | 232
2016-08-14 17:00 | 253 | 252
2016-08-14 17:30 | 273 | 273
2016-08-14 18:00 | 285 | 284
2016-08-14 18:30 | 285 | 284
2016-08-14 19:00 | 278 | 277
2016-08-14 19:30 | 274 | 273
2016-08-14 20:00 | 268 | 267
2016-08-14 20:30 | 256 | 256
2016-08-14 21:00 | 247 | 247
2016-08-14 21:30 | 236 | 236
2016-08-14 22:00 | 224 | 224
2016-08-14 22:30 | 224 | 224
2016-08-14 23:00 | 212 | 212
2016-08-14 23:30 | 203 | 203
2016-08-15 | 189 | 189
2016-08-15 00:30 | 180 | 180
2016-08-15 01:00 | 173 | 173
2016-08-15 01:30 | 166 | 165
2016-08-15 02:00 | 161 | 161
2016-08-15 02:30 | 159 | 158
2016-08-15 03:00 | 159 | 158
2016-08-15 03:30 | 160 | 159
2016-08-15 04:00 | 165 | 164
2016-08-15 04:30 | 171 | 171
2016-08-15 05:00 | 186 | 185
2016-08-15 05:30 | 200 | 200
2016-08-15 06:00 | 216 | 216
2016-08-15 06:30 | 241 | 241
2016-08-15 07:00 | 264 | 264
2016-08-15 07:30 | 268 | 267
2016-08-15 08:00 | 265 | 264
2016-08-15 08:30 | 254 | 253
2016-08-15 09:00 | 235 | 235
2016-08-15 09:30 | 229 | 227
2016-08-15 10:00 | 227 | 225
2016-08-15 10:30 | 227 | 225
2016-08-15 11:00 | 234 | 231
2016-08-15 11:30 | 227 | 224
2016-08-15 12:00 | 232 | 229
2016-08-15 12:30 | 233 | 231
2016-08-15 13:00 | 226 | 223
2016-08-15 13:30 | 226 | 223
2016-08-15 14:00 | 227 | 224
2016-08-15 14:30 | 226 | 223
2016-08-15 15:00 | 233 | 229
2016-08-15 15:30 | 241 | 238
2016-08-15 16:00 | 247 | 243
2016-08-15 16:30 | 255 | 252
2016-08-15 17:00 | 279 | 276
2016-08-15 17:30 | 301 | 300
2016-08-15 18:00 | 306 | 306
2016-08-15 18:30 | 308 | 308
2016-08-15 19:00 | 301 | 301
2016-08-15 19:30 | 298 | 298
2016-08-15 20:00 | 288 | 288
2016-08-15 20:30 | 273 | 273
2016-08-15 21:00 | 260 | 259
2016-08-15 21:30 | 248 | 247
2016-08-15 22:00 | 233 | 232
2016-08-15 22:30 | 229 | 229
2016-08-15 23:00 | 219 | 219
2016-08-15 23:30 | 210 | 210
2016-08-16 | 197 | 197
2016-08-16 00:30 | 190 | 189
2016-08-16 01:00 | 183 | 183
2016-08-16 01:30 | 175 | 175
2016-08-16 02:00 | 170 | 169
2016-08-16 02:30 | 167 | 167
2016-08-16 03:00 | 166 | 166
2016-08-16 03:30 | 169 | 169
2016-08-16 04:00 | 175 | 175
2016-08-16 04:30 | 182 | 181
2016-08-16 05:00 | 187 | 187
2016-08-16 05:30 | 201 | 201
2016-08-16 06:00 | 222 | 222
2016-08-16 06:30 | 244 | 244
2016-08-16 07:00 | 274 | 274
2016-08-16 07:30 | 275 | 275
2016-08-16 08:00 | 261 | 261
2016-08-16 08:30 | 255 | 254
2016-08-16 09:00 | 263 | 263
2016-08-16 09:30 | 260 | 260
2016-08-16 10:00 | 256 | 256
2016-08-16 10:30 | 250 | 250
2016-08-16 11:00 | 247 | 247
2016-08-16 11:30 | 237 | 237
2016-08-16 12:00 | 235 | 235
2016-08-16 12:30 | 227 | 226
2016-08-16 13:00 | 223 | 223
2016-08-16 13:30 | 237 | 236
2016-08-16 14:00 | 238 | 238
2016-08-16 14:30 | 239 | 239
2016-08-16 15:00 | 246 | 246
2016-08-16 15:30 | 250 | 250
2016-08-16 16:00 | 260 | 259
2016-08-16 16:30 | 267 | 267
2016-08-16 17:00 | 291 | 291
2016-08-16 17:30 | 319 | 318
2016-08-16 18:00 | 329 | 327
2016-08-16 18:30 | 330 | 328
2016-08-16 19:00 | 319 | 318
2016-08-16 19:30 | 319 | 318
2016-08-16 20:00 | 314 | 313
2016-08-16 20:30 | 299 | 299
2016-08-16 21:00 | 283 | 283
2016-08-16 21:30 | 269 | 268
2016-08-16 22:00 | 255 | 255
2016-08-16 22:30 | 254 | 252
2016-08-16 23:00 | 243 | 241
2016-08-16 23:30 | 227 | 227
2016-08-17 | 214 | 214
2016-08-17 00:30 | 209 | 209
2016-08-17 01:00 | 204 | 203
2016-08-17 01:30 | 195 | 195
2016-08-17 02:00 | 189 | 189
2016-08-17 02:30 | 185 | 185
2016-08-17 03:00 | 183 | 182
2016-08-17 03:30 | 185 | 184
2016-08-17 04:00 | 191 | 190
2016-08-17 04:30 | 197 | 197
2016-08-17 05:00 | 213 | 213
2016-08-17 05:30 | 226 | 226
2016-08-17 06:00 | 242 | 242
2016-08-17 06:30 | 275 | 274
2016-08-17 07:00 | 295 | 295
2016-08-17 07:30 | 300 | 299
2016-08-17 08:00 | 290 | 289
2016-08-17 08:30 | 274 | 274
2016-08-17 09:00 | 265 | 264
2016-08-17 09:30 | 268 | 268
2016-08-17 10:00 | 261 | 261
2016-08-17 10:30 | 247 | 246
2016-08-17 11:00 | 245 | 245
2016-08-17 11:30 | 247 | 247
2016-08-17 12:00 | 243 | 243
2016-08-17 12:30 | 237 | 237
2016-08-17 13:00 | 236 | 235
2016-08-17 13:30 | 239 | 239
2016-08-17 14:00 | 245 | 245
2016-08-17 14:30 | 247 | 247
2016-08-17 15:00 | 250 | 250
2016-08-17 15:30 | 256 | 256
2016-08-17 16:00 | 261 | 260
2016-08-17 16:30 | 272 | 272
2016-08-17 17:00 | 290 | 289
2016-08-17 17:30 | 310 | 310
2016-08-17 18:00 | 322 | 320
2016-08-17 18:30 | 323 | 320
2016-08-17 19:00 | 323 | 320
2016-08-17 19:30 | 315 | 314
2016-08-17 20:00 | 309 | 308
2016-08-17 20:30 | 295 | 295
2016-08-17 21:00 | 283 | 283
2016-08-17 21:30 | 271 | 270
2016-08-17 22:00 | 259 | 258
2016-08-17 22:30 | 254 | 252
2016-08-17 23:00 | 221 | 218
2016-08-17 23:30 | 211 | 211
2016-08-18 | 197 | 197
2016-08-18 00:30 | 193 | 192
2016-08-18 01:00 | 193 | 192
2016-08-18 01:30 | 189 | 189
2016-08-18 02:00 | 170 | 169
2016-08-18 02:30 | 167 | 166
2016-08-18 03:00 | 155 | 154
2016-08-18 03:30 | 155 | 155
2016-08-18 04:00 | 172 | 172
2016-08-18 04:30 | 164 | 164
2016-08-18 05:00 | 178 | 178
2016-08-18 05:30 | 210 | 209
2016-08-18 06:00 | 233 | 233
2016-08-18 06:30 | 263 | 263
2016-08-18 07:00 | 279 | 278
2016-08-18 07:30 | 289 | 289
2016-08-18 08:00 | 277 | 277
2016-08-18 08:30 | 253 | 253
2016-08-18 09:00 | 247 | 247
2016-08-18 09:30 | 251 | 251
2016-08-18 10:00 | 256 | 256
2016-08-18 10:30 | 258 | 258
2016-08-18 11:00 | 255 | 255
2016-08-18 11:30 | 255 | 255
2016-08-18 12:00 | 247 | 246
2016-08-18 12:30 | 246 | 245
2016-08-18 13:00 | 243 | 243
2016-08-18 13:30 | 249 | 249
2016-08-18 14:00 | 257 | 257
2016-08-18 14:30 | 260 | 260
2016-08-18 15:00 | 261 | 261
2016-08-18 15:30 | 260 | 260
2016-08-18 16:00 | 262 | 262
2016-08-18 16:30 | 261 | 261
2016-08-18 17:00 | 291 | 291
2016-08-18 17:30 | 307 | 307
2016-08-18 18:00 | 317 | 317
2016-08-18 18:30 | 319 | 318
2016-08-18 19:00 | 305 | 304
2016-08-18 19:30 | 306 | 306
2016-08-18 20:00 | 295 | 294
2016-08-18 20:30 | 291 | 289
2016-08-18 21:00 | 275 | 275
2016-08-18 21:30 | 265 | 265
2016-08-18 22:00 | 255 | 254
2016-08-18 22:30 | 246 | 246
2016-08-18 23:00 | 244 | 244
2016-08-18 23:30 | 230 | 229
2016-08-19 | 216 | 214
2016-08-19 00:30 | 206 | 206
2016-08-19 01:00 | 202 | 202
2016-08-19 01:30 | 195 | 195
2016-08-19 02:00 | 189 | 189
2016-08-19 02:30 | 185 | 185
2016-08-19 03:00 | 184 | 184
2016-08-19 03:30 | 184 | 184
2016-08-19 04:00 | 188 | 188
2016-08-19 04:30 | 197 | 197
2016-08-19 05:00 | 210 | 210
2016-08-19 05:30 | 221 | 221
2016-08-19 06:00 | 235 | 235
2016-08-19 06:30 | 251 | 251
2016-08-19 07:00 | 256 | 256
2016-08-19 07:30 | 268 | 268
2016-08-19 08:00 | 261 | 261
2016-08-19 08:30 | 259 | 259
2016-08-19 09:00 | 257 | 257
2016-08-19 09:30 | 264 | 263
2016-08-19 10:00 | 258 | 258
2016-08-19 10:30 | 250 | 250
2016-08-19 11:00 | 254 | 254
2016-08-19 11:30 | 252 | 252
2016-08-19 12:00 | 253 | 253
2016-08-19 12:30 | 246 | 246
2016-08-19 13:00 | 240 | 239
2016-08-19 13:30 | 224 | 224
2016-08-19 14:00 | 214 | 214
2016-08-19 14:30 | 218 | 218
2016-08-19 15:00 | 224 | 224
2016-08-19 15:30 | 230 | 230
2016-08-19 16:00 | 239 | 238
2016-08-19 16:30 | 246 | 246
2016-08-19 17:00 | 257 | 256
2016-08-19 17:30 | 269 | 269
2016-08-19 18:00 | 275 | 275
2016-08-19 18:30 | 274 | 274
2016-08-19 19:00 | 267 | 267
2016-08-19 19:30 | 264 | 264
2016-08-19 20:00 | 261 | 261
2016-08-19 20:30 | 255 | 254
2016-08-19 21:00 | 247 | 246
2016-08-19 21:30 | 236 | 236
2016-08-19 22:00 | 225 | 225
2016-08-19 22:30 | 214 | 214
2016-08-19 23:00 | 206 | 206
2016-08-19 23:30 | 192 | 192
2016-08-20 | 184 | 183
2016-08-20 00:30 | 175 | 174
2016-08-20 01:00 | 176 | 175
2016-08-20 01:30 | 173 | 172
2016-08-20 02:00 | 167 | 166
2016-08-20 02:30 | 163 | 163
2016-08-20 03:00 | 161 | 160
2016-08-20 03:30 | 160 | 159
2016-08-20 04:00 | 161 | 161
2016-08-20 04:30 | 164 | 164
2016-08-20 05:00 | 156 | 156
2016-08-20 05:30 | 153 | 153
2016-08-20 06:00 | 184 | 184
2016-08-20 06:30 | 191 | 191
2016-08-20 07:00 | 201 | 201
2016-08-20 07:30 | 209 | 209
2016-08-20 08:00 | 216 | 216
2016-08-20 08:30 | 218 | 218
2016-08-20 09:00 | 218 | 218
2016-08-20 09:30 | 208 | 207
2016-08-20 10:00 | 202 | 202
2016-08-20 10:30 | 196 | 195
2016-08-20 11:00 | 194 | 193
2016-08-20 11:30 | 188 | 187
2016-08-20 12:00 | 190 | 189
2016-08-20 12:30 | 195 | 194
2016-08-20 13:00 | 196 | 195
2016-08-20 13:30 | 200 | 199
2016-08-20 14:00 | 202 | 201
2016-08-20 14:30 | 197 | 196
2016-08-20 15:00 | 201 | 201
2016-08-20 15:30 | 214 | 213
2016-08-20 16:00 | 219 | 219
2016-08-20 16:30 | 228 | 227
2016-08-20 17:00 | 238 | 238
2016-08-20 17:30 | 254 | 253
2016-08-20 18:00 | 262 | 262
2016-08-20 18:30 | 261 | 261
2016-08-20 19:00 | 245 | 245
2016-08-20 19:30 | 237 | 237
2016-08-20 20:00 | 231 | 231
2016-08-20 20:30 | 224 | 223
2016-08-20 21:00 | 218 | 218
2016-08-20 21:30 | 213 | 213
2016-08-20 22:00 | 197 | 197
2016-08-20 22:30 | 197 | 197
2016-08-20 23:00 | 190 | 190
2016-08-20 23:30 | 189 | 189
2016-08-21 | 177 | 177
2016-08-21 00:30 | 166 | 166
2016-08-21 01:00 | 162 | 161
2016-08-21 01:30 | 159 | 158
2016-08-21 02:00 | 160 | 159
2016-08-21 02:30 | 161 | 160
2016-08-21 03:00 | 159 | 158
2016-08-21 03:30 | 160 | 159
2016-08-21 04:00 | 161 | 160
2016-08-21 04:30 | 163 | 162
2016-08-21 05:00 | 165 | 165
2016-08-21 05:30 | 170 | 169
2016-08-21 06:00 | 173 | 173
2016-08-21 06:30 | 183 | 182
2016-08-21 07:00 | 190 | 189
2016-08-21 07:30 | 199 | 199
2016-08-21 08:00 | 207 | 207
2016-08-21 08:30 | 209 | 209
2016-08-21 09:00 | 207 | 207
2016-08-21 09:30 | 206 | 205
2016-08-21 10:00 | 202 | 202
2016-08-21 10:30 | 196 | 196
2016-08-21 11:00 | 190 | 190
2016-08-21 11:30 | 183 | 183
2016-08-21 12:00 | 181 | 181
2016-08-21 12:30 | 177 | 177
2016-08-21 13:00 | 175 | 175
2016-08-21 13:30 | 182 | 182
2016-08-21 14:00 | 183 | 183
2016-08-21 14:30 | 190 | 190
2016-08-21 15:00 | 202 | 202
2016-08-21 15:30 | 213 | 213
2016-08-21 16:00 | 227 | 227
2016-08-21 16:30 | 240 | 240
2016-08-21 17:00 | 246 | 246
2016-08-21 17:30 | 267 | 267
2016-08-21 18:00 | 280 | 277
2016-08-21 18:30 | 279 | 276
2016-08-21 19:00 | 274 | 271
2016-08-21 19:30 | 264 | 263
2016-08-21 20:00 | 255 | 254
2016-08-21 20:30 | 233 | 232
2016-08-21 21:00 | 221 | 221
2016-08-21 21:30 | 218 | 218
2016-08-21 22:00 | 196 | 196
2016-08-21 22:30 | 194 | 194
2016-08-21 23:00 | 194 | 194
2016-08-21 23:30 | 187 | 187
2016-08-22 | 173 | 173
2016-08-22 00:30 | 166 | 165
2016-08-22 01:00 | 163 | 162
2016-08-22 01:30 | 162 | 161
2016-08-22 02:00 | 160 | 159
2016-08-22 02:30 | 159 | 158
2016-08-22 03:00 | 160 | 159
2016-08-22 03:30 | 161 | 160
2016-08-22 04:00 | 162 | 161
2016-08-22 04:30 | 166 | 165
2016-08-22 05:00 | 173 | 173
2016-08-22 05:30 | 186 | 186
2016-08-22 06:00 | 211 | 211
2016-08-22 06:30 | 234 | 234
2016-08-22 07:00 | 252 | 252
2016-08-22 07:30 | 259 | 258
2016-08-22 08:00 | 253 | 252
2016-08-22 08:30 | 243 | 243
2016-08-22 09:00 | 239 | 239
2016-08-22 09:30 | 235 | 235
2016-08-22 10:00 | 234 | 234
2016-08-22 10:30 | 234 | 234
2016-08-22 11:00 | 238 | 237
2016-08-22 11:30 | 238 | 238
2016-08-22 12:00 | 239 | 239
2016-08-22 12:30 | 239 | 239
2016-08-22 13:00 | 234 | 234
2016-08-22 13:30 | 234 | 234
2016-08-22 14:00 | 237 | 237
2016-08-22 14:30 | 237 | 236
2016-08-22 15:00 | 236 | 236
2016-08-22 15:30 | 241 | 240
2016-08-22 16:00 | 247 | 246
2016-08-22 16:30 | 255 | 255
2016-08-22 17:00 | 267 | 267
2016-08-22 17:30 | 288 | 288
2016-08-22 18:00 | 294 | 294
2016-08-22 18:30 | 294 | 294
2016-08-22 19:00 | 282 | 282
2016-08-22 19:30 | 281 | 281
2016-08-22 20:00 | 279 | 278
2016-08-22 20:30 | 264 | 264
2016-08-22 21:00 | 247 | 247
2016-08-22 21:30 | 227 | 227
2016-08-22 22:00 | 220 | 220
2016-08-22 22:30 | 222 | 222
2016-08-22 23:00 | 211 | 211
2016-08-22 23:30 | 197 | 197
2016-08-23 | 186 | 185
2016-08-23 00:30 | 179 | 178
2016-08-23 01:00 | 169 | 169
2016-08-23 01:30 | 163 | 163
2016-08-23 02:00 | 160 | 159
2016-08-23 02:30 | 158 | 157
2016-08-23 03:00 | 157 | 156
2016-08-23 03:30 | 159 | 158
2016-08-23 04:00 | 162 | 162
2016-08-23 04:30 | 166 | 165
2016-08-23 05:00 | 175 | 175
2016-08-23 05:30 | 189 | 189
2016-08-23 06:00 | 216 | 216
2016-08-23 06:30 | 235 | 235
2016-08-23 07:00 | 251 | 251
2016-08-23 07:30 | 256 | 255
2016-08-23 08:00 | 261 | 261
2016-08-23 08:30 | 261 | 261
2016-08-23 09:00 | 269 | 268
2016-08-23 09:30 | 260 | 260
2016-08-23 10:00 | 257 | 257
2016-08-23 10:30 | 261 | 261
2016-08-23 11:00 | 260 | 260
2016-08-23 11:30 | 245 | 245
2016-08-23 12:00 | 228 | 228
2016-08-23 12:30 | 223 | 223
2016-08-23 13:00 | 223 | 223
2016-08-23 13:30 | 218 | 218
2016-08-23 14:00 | 230 | 230
2016-08-23 14:30 | 229 | 229
2016-08-23 15:00 | 228 | 228
2016-08-23 15:30 | 241 | 241
2016-08-23 16:00 | 254 | 254
2016-08-23 16:30 | 265 | 265
2016-08-23 17:00 | 278 | 278
2016-08-23 17:30 | 291 | 290
2016-08-23 18:00 | 292 | 291
2016-08-23 18:30 | 291 | 290
2016-08-23 19:00 | 286 | 285
2016-08-23 19:30 | 289 | 288
2016-08-23 20:00 | 283 | 282
2016-08-23 20:30 | 266 | 266
2016-08-23 21:00 | 248 | 248
2016-08-23 21:30 | 239 | 239
2016-08-23 22:00 | 233 | 233
2016-08-23 22:30 | 234 | 234
2016-08-23 23:00 | 219 | 219
2016-08-23 23:30 | 206 | 206
2016-08-24 | 191 | 191
2016-08-24 00:30 | 180 | 180
2016-08-24 01:00 | 175 | 174
2016-08-24 01:30 | 169 | 168
2016-08-24 02:00 | 165 | 165
2016-08-24 02:30 | 163 | 163
2016-08-24 03:00 | 161 | 160
2016-08-24 03:30 | 161 | 161
2016-08-24 04:00 | 164 | 164
2016-08-24 04:30 | 170 | 170
2016-08-24 05:00 | 179 | 179
2016-08-24 05:30 | 189 | 189
2016-08-24 06:00 | 208 | 208
2016-08-24 06:30 | 237 | 237
2016-08-24 07:00 | 259 | 258
2016-08-24 07:30 | 270 | 270
2016-08-24 08:00 | 275 | 275
2016-08-24 08:30 | 272 | 272
2016-08-24 09:00 | 277 | 277
2016-08-24 09:30 | 283 | 283
2016-08-24 10:00 | 290 | 290
2016-08-24 10:30 | 289 | 289
2016-08-24 11:00 | 281 | 281
2016-08-24 11:30 | 282 | 282
2016-08-24 12:00 | 283 | 283
2016-08-24 12:30 | 283 | 283
2016-08-24 13:00 | 287 | 287
2016-08-24 13:30 | 290 | 290
2016-08-24 14:00 | 281 | 281
2016-08-24 14:30 | 272 | 272
2016-08-24 15:00 | 274 | 274
2016-08-24 15:30 | 281 | 280
2016-08-24 16:00 | 289 | 289
2016-08-24 16:30 | 295 | 295
2016-08-24 17:00 | 310 | 310
2016-08-24 17:30 | 320 | 320
2016-08-24 18:00 | 322 | 322
2016-08-24 18:30 | 320 | 320
2016-08-24 19:00 | 310 | 309
2016-08-24 19:30 | 307 | 306
2016-08-24 20:00 | 301 | 300
2016-08-24 20:30 | 284 | 283
2016-08-24 21:00 | 264 | 264
2016-08-24 21:30 | 248 | 248
2016-08-24 22:00 | 242 | 242
2016-08-24 22:30 | 237 | 237
2016-08-24 23:00 | 218 | 218
2016-08-24 23:30 | 205 | 204
2016-08-25 | 194 | 193
2016-08-25 00:30 | 185 | 185
2016-08-25 01:00 | 177 | 177
2016-08-25 01:30 | 170 | 170
2016-08-25 02:00 | 164 | 164
2016-08-25 02:30 | 161 | 161
2016-08-25 03:00 | 160 | 160
2016-08-25 03:30 | 161 | 161
2016-08-25 04:00 | 164 | 164
2016-08-25 04:30 | 172 | 171
2016-08-25 05:00 | 183 | 183
2016-08-25 05:30 | 194 | 194
2016-08-25 06:00 | 219 | 219
2016-08-25 06:30 | 251 | 251
2016-08-25 07:00 | 273 | 273
2016-08-25 07:30 | 271 | 271
2016-08-25 08:00 | 259 | 259
2016-08-25 08:30 | 246 | 245
2016-08-25 09:00 | 237 | 236
2016-08-25 09:30 | 232 | 232
2016-08-25 10:00 | 222 | 221
2016-08-25 10:30 | 212 | 212
2016-08-25 11:00 | 201 | 200
2016-08-25 11:30 | 196 | 195
2016-08-25 12:00 | 193 | 193
2016-08-25 12:30 | 192 | 192
2016-08-25 13:00 | 191 | 191
2016-08-25 13:30 | 192 | 192
2016-08-25 14:00 | 197 | 197
2016-08-25 14:30 | 201 | 201
2016-08-25 15:00 | 206 | 206
2016-08-25 15:30 | 216 | 216
2016-08-25 16:00 | 229 | 229
2016-08-25 16:30 | 245 | 245
2016-08-25 17:00 | 257 | 257
2016-08-25 17:30 | 276 | 276
2016-08-25 18:00 | 288 | 288
2016-08-25 18:30 | 292 | 292
2016-08-25 19:00 | 291 | 291
2016-08-25 19:30 | 287 | 287
2016-08-25 20:00 | 285 | 285
2016-08-25 20:30 | 274 | 274
2016-08-25 21:00 | 264 | 263
2016-08-25 21:30 | 250 | 249
2016-08-25 22:00 | 243 | 243
2016-08-25 22:30 | 238 | 238
2016-08-25 23:00 | 220 | 220
2016-08-25 23:30 | 206 | 206
2016-08-26 | 191 | 191
2016-08-26 00:30 | 184 | 184
2016-08-26 01:00 | 178 | 178
2016-08-26 01:30 | 167 | 166
2016-08-26 02:00 | 161 | 160
2016-08-26 02:30 | 160 | 159
2016-08-26 03:00 | 162 | 161
2016-08-26 03:30 | 165 | 164
2016-08-26 04:00 | 167 | 167
2016-08-26 04:30 | 171 | 170
2016-08-26 05:00 | 174 | 174
2016-08-26 05:30 | 187 | 187
2016-08-26 06:00 | 200 | 199
2016-08-26 06:30 | 217 | 216
2016-08-26 07:00 | 227 | 227
2016-08-26 07:30 | 236 | 236
2016-08-26 08:00 | 236 | 236
2016-08-26 08:30 | 228 | 228
2016-08-26 09:00 | 229 | 229
2016-08-26 09:30 | 224 | 224
2016-08-26 10:00 | 211 | 211
2016-08-26 10:30 | 202 | 202
2016-08-26 11:00 | 195 | 195
2016-08-26 11:30 | 191 | 191
2016-08-26 12:00 | 193 | 193
2016-08-26 12:30 | 193 | 193
2016-08-26 13:00 | 192 | 192
2016-08-26 13:30 | 195 | 195
2016-08-26 14:00 | 197 | 197
2016-08-26 14:30 | 202 | 202
2016-08-26 15:00 | 207 | 207
2016-08-26 15:30 | 209 | 209
2016-08-26 16:00 | 212 | 212
2016-08-26 16:30 | 226 | 226
2016-08-26 17:00 | 242 | 242
2016-08-26 17:30 | 264 | 264
2016-08-26 18:00 | 274 | 273
2016-08-26 18:30 | 272 | 272
2016-08-26 19:00 | 266 | 266
2016-08-26 19:30 | 266 | 266
2016-08-26 20:00 | 265 | 265
2016-08-26 20:30 | 255 | 255
2016-08-26 21:00 | 246 | 246
2016-08-26 21:30 | 230 | 230
2016-08-26 22:00 | 225 | 224
2016-08-26 22:30 | 220 | 220
2016-08-26 23:00 | 205 | 205
2016-08-26 23:30 | 193 | 193
2016-08-27 | 185 | 184
2016-08-27 00:30 | 173 | 172
2016-08-27 01:00 | 168 | 168
2016-08-27 01:30 | 165 | 165
2016-08-27 02:00 | 165 | 164
2016-08-27 02:30 | 160 | 159
2016-08-27 03:00 | 160 | 159
2016-08-27 03:30 | 157 | 156
2016-08-27 04:00 | 154 | 153
2016-08-27 04:30 | 153 | 152
2016-08-27 05:00 | 158 | 157
2016-08-27 05:30 | 169 | 169
2016-08-27 06:00 | 182 | 182
2016-08-27 06:30 | 190 | 190
2016-08-27 07:00 | 201 | 201
2016-08-27 07:30 | 208 | 208
2016-08-27 08:00 | 216 | 216
2016-08-27 08:30 | 213 | 213
2016-08-27 09:00 | 211 | 211
2016-08-27 09:30 | 206 | 206
2016-08-27 10:00 | 199 | 199
2016-08-27 10:30 | 189 | 189
2016-08-27 11:00 | 179 | 179
2016-08-27 11:30 | 173 | 173
2016-08-27 12:00 | 171 | 171
2016-08-27 12:30 | 177 | 177
2016-08-27 13:00 | 177 | 177
2016-08-27 13:30 | 181 | 181
2016-08-27 14:00 | 181 | 181
2016-08-27 14:30 | 181 | 181
2016-08-27 15:00 | 194 | 194
2016-08-27 15:30 | 204 | 204
2016-08-27 16:00 | 208 | 208
2016-08-27 16:30 | 216 | 216
2016-08-27 17:00 | 230 | 230
2016-08-27 17:30 | 250 | 250
2016-08-27 18:00 | 263 | 263
2016-08-27 18:30 | 265 | 265
2016-08-27 19:00 | 258 | 257
2016-08-27 19:30 | 254 | 253
2016-08-27 20:00 | 249 | 248
2016-08-27 20:30 | 235 | 234
2016-08-27 21:00 | 228 | 228
2016-08-27 21:30 | 222 | 221
2016-08-27 22:00 | 211 | 211
2016-08-27 22:30 | 213 | 213
2016-08-27 23:00 | 200 | 200
2016-08-27 23:30 | 191 | 191
2016-08-28 | 176 | 176
2016-08-28 00:30 | 169 | 168
2016-08-28 01:00 | 164 | 164
2016-08-28 01:30 | 158 | 157
2016-08-28 02:00 | 151 | 150
2016-08-28 02:30 | 148 | 147
2016-08-28 03:00 | 147 | 147
2016-08-28 03:30 | 146 | 146
2016-08-28 04:00 | 147 | 146
2016-08-28 04:30 | 148 | 148
2016-08-28 05:00 | 150 | 150
2016-08-28 05:30 | 158 | 158
2016-08-28 06:00 | 170 | 170
2016-08-28 06:30 | 176 | 176
2016-08-28 07:00 | 184 | 184
2016-08-28 07:30 | 196 | 196
2016-08-28 08:00 | 200 | 200
2016-08-28 08:30 | 200 | 199
2016-08-28 09:00 | 199 | 199
2016-08-28 09:30 | 196 | 195
2016-08-28 10:00 | 192 | 191
2016-08-28 10:30 | 183 | 183
2016-08-28 11:00 | 178 | 177
2016-08-28 11:30 | 178 | 177
2016-08-28 12:00 | 177 | 176
2016-08-28 12:30 | 176 | 175
2016-08-28 13:00 | 182 | 181
2016-08-28 13:30 | 186 | 186
2016-08-28 14:00 | 187 | 186
2016-08-28 14:30 | 189 | 189
2016-08-28 15:00 | 191 | 190
2016-08-28 15:30 | 198 | 198
2016-08-28 16:00 | 204 | 204
2016-08-28 16:30 | 217 | 217
2016-08-28 17:00 | 239 | 238
2016-08-28 17:30 | 257 | 257
2016-08-28 18:00 | 271 | 271
2016-08-28 18:30 | 276 | 275
2016-08-28 19:00 | 271 | 270
2016-08-28 19:30 | 265 | 265
2016-08-28 20:00 | 257 | 257
2016-08-28 20:30 | 245 | 245
2016-08-28 21:00 | 235 | 234
2016-08-28 21:30 | 224 | 223
2016-08-28 22:00 | 216 | 216
2016-08-28 22:30 | 217 | 217
2016-08-28 23:00 | 203 | 203
2016-08-28 23:30 | 185 | 185
2016-08-29 | 170 | 170
2016-08-29 00:30 | 160 | 160
2016-08-29 01:00 | 153 | 152
2016-08-29 01:30 | 146 | 145
2016-08-29 02:00 | 141 | 140
2016-08-29 02:30 | 139 | 138
2016-08-29 03:00 | 139 | 138
2016-08-29 03:30 | 138 | 138
2016-08-29 04:00 | 143 | 143
2016-08-29 04:30 | 151 | 151
2016-08-29 05:00 | 164 | 164
2016-08-29 05:30 | 181 | 181
2016-08-29 06:00 | 207 | 207
2016-08-29 06:30 | 231 | 231
2016-08-29 07:00 | 250 | 250
2016-08-29 07:30 | 251 | 250
2016-08-29 08:00 | 241 | 240
2016-08-29 08:30 | 235 | 235
2016-08-29 09:00 | 225 | 225
2016-08-29 09:30 | 211 | 210
2016-08-29 10:00 | 206 | 205
2016-08-29 10:30 | 201 | 200
2016-08-29 11:00 | 198 | 196
2016-08-29 11:30 | 196 | 195
2016-08-29 12:00 | 195 | 194
2016-08-29 12:30 | 195 | 194
2016-08-29 13:00 | 197 | 196
2016-08-29 13:30 | 202 | 201
2016-08-29 14:00 | 207 | 206
2016-08-29 14:30 | 211 | 211
2016-08-29 15:00 | 217 | 217
2016-08-29 15:30 | 225 | 225
2016-08-29 16:00 | 233 | 233
2016-08-29 16:30 | 248 | 248
2016-08-29 17:00 | 264 | 264
2016-08-29 17:30 | 281 | 281
2016-08-29 18:00 | 289 | 289
2016-08-29 18:30 | 289 | 288
2016-08-29 19:00 | 277 | 276
2016-08-29 19:30 | 274 | 273
2016-08-29 20:00 | 269 | 268
2016-08-29 20:30 | 253 | 252
2016-08-29 21:00 | 239 | 239
2016-08-29 21:30 | 226 | 226
2016-08-29 22:00 | 221 | 221
2016-08-29 22:30 | 220 | 220
2016-08-29 23:00 | 204 | 204
2016-08-29 23:30 | 186 | 186
2016-08-30 | 171 | 171
2016-08-30 00:30 | 161 | 161
2016-08-30 01:00 | 154 | 153
2016-08-30 01:30 | 147 | 147
2016-08-30 02:00 | 142 | 141
2016-08-30 02:30 | 139 | 138
2016-08-30 03:00 | 138 | 137
2016-08-30 03:30 | 139 | 138
2016-08-30 04:00 | 143 | 143
2016-08-30 04:30 | 149 | 149
2016-08-30 05:00 | 163 | 163
2016-08-30 05:30 | 181 | 181
2016-08-30 06:00 | 202 | 202
2016-08-30 06:30 | 224 | 224
2016-08-30 07:00 | 245 | 245
2016-08-30 07:30 | 252 | 252
2016-08-30 08:00 | 242 | 242
2016-08-30 08:30 | 229 | 229
2016-08-30 09:00 | 222 | 222
2016-08-30 09:30 | 218 | 217
2016-08-30 10:00 | 213 | 212
2016-08-30 10:30 | 207 | 206
2016-08-30 11:00 | 203 | 201
2016-08-30 11:30 | 200 | 199
2016-08-30 12:00 | 199 | 197
2016-08-30 12:30 | 196 | 195
2016-08-30 13:00 | 197 | 196
2016-08-30 13:30 | 203 | 201
2016-08-30 14:00 | 205 | 204
2016-08-30 14:30 | 208 | 207
2016-08-30 15:00 | 214 | 213
2016-08-30 15:30 | 221 | 220
2016-08-30 16:00 | 231 | 231
2016-08-30 16:30 | 244 | 243
2016-08-30 17:00 | 257 | 257
2016-08-30 17:30 | 274 | 274
2016-08-30 18:00 | 287 | 287
2016-08-30 18:30 | 286 | 285
2016-08-30 19:00 | 277 | 276
2016-08-30 19:30 | 270 | 270
2016-08-30 20:00 | 266 | 266
2016-08-30 20:30 | 254 | 254
2016-08-30 21:00 | 241 | 240
2016-08-30 21:30 | 228 | 228
2016-08-30 22:00 | 222 | 222
2016-08-30 22:30 | 220 | 220
2016-08-30 23:00 | 204 | 204
2016-08-30 23:30 | 185 | 185
2016-08-31 | 170 | 170
2016-08-31 00:30 | 161 | 160
2016-08-31 01:00 | 154 | 153
2016-08-31 01:30 | 146 | 146
2016-08-31 02:00 | 142 | 141
2016-08-31 02:30 | 139 | 138
2016-08-31 03:00 | 138 | 137
2016-08-31 03:30 | 138 | 138
2016-08-31 04:00 | 143 | 142
2016-08-31 04:30 | 149 | 149
2016-08-31 05:00 | 164 | 164
2016-08-31 05:30 | 182 | 182
2016-08-31 06:00 | 205 | 205
2016-08-31 06:30 | 227 | 227
2016-08-31 07:00 | 249 | 248
2016-08-31 07:30 | 250 | 250
2016-08-31 08:00 | 243 | 243
2016-08-31 08:30 | 232 | 232
2016-08-31 09:00 | 231 | 231
2016-08-31 09:30 | 225 | 225
2016-08-31 10:00 | 217 | 217
2016-08-31 10:30 | 223 | 223
2016-08-31 11:00 | 215 | 215
2016-08-31 11:30 | 230 | 230
2016-08-31 12:00 | 223 | 223
2016-08-31 12:30 | 216 | 216
2016-08-31 13:00 | 216 | 216
2016-08-31 13:30 | 224 | 224
2016-08-31 14:00 | 226 | 226
2016-08-31 14:30 | 229 | 229
2016-08-31 15:00 | 230 | 230
2016-08-31 15:30 | 233 | 233
2016-08-31 16:00 | 240 | 240
2016-08-31 16:30 | 255 | 255
2016-08-31 17:00 | 267 | 267
2016-08-31 17:30 | 284 | 284
2016-08-31 18:00 | 296 | 296
2016-08-31 18:30 | 296 | 295
2016-08-31 19:00 | 286 | 285
2016-08-31 19:30 | 276 | 275
2016-08-31 20:00 | 269 | 267
2016-08-31 20:30 | 252 | 252
2016-08-31 21:00 | 240 | 240
2016-08-31 21:30 | 227 | 227
2016-08-31 22:00 | 223 | 223
2016-08-31 22:30 | 223 | 223
2016-08-31 23:00 | 207 | 206
2016-08-31 23:30 | 185 | 185
2016-09-01 | 170 | 170
2016-09-01 00:30 | 162 | 162
2016-09-01 01:00 | 155 | 155
2016-09-01 01:30 | 146 | 146
2016-09-01 02:00 | 141 | 141
2016-09-01 02:30 | 137 | 137
2016-09-01 03:00 | 136 | 136
2016-09-01 03:30 | 137 | 137
2016-09-01 04:00 | 142 | 142
2016-09-01 04:30 | 148 | 148
2016-09-01 05:00 | 162 | 162
2016-09-01 05:30 | 178 | 178
2016-09-01 06:00 | 198 | 198
2016-09-01 06:30 | 220 | 220
2016-09-01 07:00 | 240 | 240
2016-09-01 07:30 | 248 | 248
2016-09-01 08:00 | 238 | 238
2016-09-01 08:30 | 229 | 229
2016-09-01 09:00 | 225 | 225
2016-09-01 09:30 | 222 | 222
2016-09-01 10:00 | 224 | 224
2016-09-01 10:30 | 223 | 223
2016-09-01 11:00 | 215 | 215
2016-09-01 11:30 | 217 | 217
2016-09-01 12:00 | 214 | 214
2016-09-01 12:30 | 218 | 218
2016-09-01 13:00 | 219 | 219
2016-09-01 13:30 | 232 | 232
2016-09-01 14:00 | 234 | 234
2016-09-01 14:30 | 236 | 236
2016-09-01 15:00 | 236 | 236
2016-09-01 15:30 | 245 | 245
2016-09-01 16:00 | 248 | 248
2016-09-01 16:30 | 254 | 254
2016-09-01 17:00 | 264 | 264
2016-09-01 17:30 | 284 | 283
2016-09-01 18:00 | 288 | 287
2016-09-01 18:30 | 287 | 287
2016-09-01 19:00 | 280 | 280
2016-09-01 19:30 | 276 | 276
2016-09-01 20:00 | 268 | 268
2016-09-01 20:30 | 250 | 250
2016-09-01 21:00 | 234 | 234
2016-09-01 21:30 | 220 | 220
2016-09-01 22:00 | 225 | 225
2016-09-01 22:30 | 224 | 224
2016-09-01 23:00 | 209 | 208
2016-09-01 23:30 | 192 | 192
2016-09-02 | 173 | 173
2016-09-02 00:30 | 165 | 165
2016-09-02 01:00 | 162 | 162
2016-09-02 01:30 | 159 | 159
2016-09-02 02:00 | 154 | 154
2016-09-02 02:30 | 150 | 150
2016-09-02 03:00 | 150 | 150
2016-09-02 03:30 | 150 | 150
2016-09-02 04:00 | 151 | 151
2016-09-02 04:30 | 157 | 157
2016-09-02 05:00 | 167 | 167
2016-09-02 05:30 | 176 | 176
2016-09-02 06:00 | 206 | 205
2016-09-02 06:30 | 230 | 230
2016-09-02 07:00 | 249 | 249
2016-09-02 07:30 | 262 | 261
2016-09-02 08:00 | 262 | 262
2016-09-02 08:30 | 251 | 251
2016-09-02 09:00 | 256 | 256
2016-09-02 09:30 | 250 | 250
2016-09-02 10:00 | 255 | 255
2016-09-02 10:30 | 253 | 253
2016-09-02 11:00 | 242 | 242
2016-09-02 11:30 | 246 | 246
2016-09-02 12:00 | 246 | 246
2016-09-02 12:30 | 241 | 241
2016-09-02 13:00 | 235 | 235
2016-09-02 13:30 | 228 | 228
2016-09-02 14:00 | 226 | 226
2016-09-02 14:30 | 228 | 228
2016-09-02 15:00 | 228 | 228
2016-09-02 15:30 | 236 | 236
2016-09-02 16:00 | 243 | 242
2016-09-02 16:30 | 250 | 250
2016-09-02 17:00 | 257 | 257
2016-09-02 17:30 | 264 | 264
2016-09-02 18:00 | 266 | 266
2016-09-02 18:30 | 266 | 266
2016-09-02 19:00 | 260 | 259
2016-09-02 19:30 | 258 | 258
2016-09-02 20:00 | 252 | 252
2016-09-02 20:30 | 240 | 240
2016-09-02 21:00 | 219 | 218
2016-09-02 21:30 | 200 | 200
2016-09-02 22:00 | 211 | 211
2016-09-02 22:30 | 200 | 200
2016-09-02 23:00 | 188 | 188
2016-09-02 23:30 | 181 | 181
2016-09-03 | 159 | 159
2016-09-03 00:30 | 162 | 161
2016-09-03 01:00 | 153 | 152
2016-09-03 01:30 | 143 | 142
2016-09-03 02:00 | 139 | 139
2016-09-03 02:30 | 136 | 136
2016-09-03 03:00 | 137 | 136
2016-09-03 03:30 | 138 | 138
2016-09-03 04:00 | 138 | 138
2016-09-03 04:30 | 138 | 138
2016-09-03 05:00 | 143 | 143
2016-09-03 05:30 | 147 | 147
2016-09-03 06:00 | 161 | 161
2016-09-03 06:30 | 172 | 172
2016-09-03 07:00 | 183 | 183
2016-09-03 07:30 | 192 | 191
2016-09-03 08:00 | 208 | 208
2016-09-03 08:30 | 214 | 214
2016-09-03 09:00 | 212 | 212
2016-09-03 09:30 | 203 | 202
2016-09-03 10:00 | 195 | 194
2016-09-03 10:30 | 187 | 187
2016-09-03 11:00 | 183 | 183
2016-09-03 11:30 | 179 | 178
2016-09-03 12:00 | 178 | 177
2016-09-03 12:30 | 176 | 175
2016-09-03 13:00 | 174 | 174
2016-09-03 13:30 | 177 | 176
2016-09-03 14:00 | 178 | 178
2016-09-03 14:30 | 181 | 181
2016-09-03 15:00 | 186 | 185
2016-09-03 15:30 | 193 | 193
2016-09-03 16:00 | 197 | 197
2016-09-03 16:30 | 195 | 195
2016-09-03 17:00 | 216 | 216
2016-09-03 17:30 | 232 | 232
2016-09-03 18:00 | 249 | 249
2016-09-03 18:30 | 250 | 249
2016-09-03 19:00 | 243 | 242
2016-09-03 19:30 | 236 | 235
2016-09-03 20:00 | 224 | 224
2016-09-03 20:30 | 214 | 214
2016-09-03 21:00 | 206 | 206
2016-09-03 21:30 | 205 | 205
2016-09-03 22:00 | 198 | 198
2016-09-03 22:30 | 192 | 192
2016-09-03 23:00 | 182 | 182
2016-09-03 23:30 | 171 | 170
2016-09-04 | 159 | 159
2016-09-04 00:30 | 156 | 156
2016-09-04 01:00 | 153 | 153
2016-09-04 01:30 | 150 | 150
2016-09-04 02:00 | 147 | 147
2016-09-04 02:30 | 146 | 146
2016-09-04 03:00 | 143 | 143
2016-09-04 03:30 | 140 | 140
2016-09-04 04:00 | 140 | 140
2016-09-04 04:30 | 141 | 141
2016-09-04 05:00 | 145 | 145
2016-09-04 05:30 | 152 | 152
2016-09-04 06:00 | 158 | 158
2016-09-04 06:30 | 165 | 165
2016-09-04 07:00 | 177 | 177
2016-09-04 07:30 | 186 | 186
2016-09-04 08:00 | 191 | 190
2016-09-04 08:30 | 191 | 191
2016-09-04 09:00 | 192 | 191
2016-09-04 09:30 | 190 | 189
2016-09-04 10:00 | 187 | 186
2016-09-04 10:30 | 181 | 180
2016-09-04 11:00 | 174 | 173
2016-09-04 11:30 | 169 | 168
2016-09-04 12:00 | 165 | 164
2016-09-04 12:30 | 163 | 162
2016-09-04 13:00 | 163 | 162
2016-09-04 13:30 | 166 | 165
2016-09-04 14:00 | 169 | 168
2016-09-04 14:30 | 174 | 173
2016-09-04 15:00 | 181 | 180
2016-09-04 15:30 | 191 | 190
2016-09-04 16:00 | 198 | 198
2016-09-04 16:30 | 203 | 203
2016-09-04 17:00 | 215 | 215
2016-09-04 17:30 | 237 | 237
2016-09-04 18:00 | 251 | 251
2016-09-04 18:30 | 250 | 250
2016-09-04 19:00 | 245 | 244
2016-09-04 19:30 | 245 | 244
2016-09-04 20:00 | 244 | 243
2016-09-04 20:30 | 235 | 234
2016-09-04 21:00 | 226 | 225
2016-09-04 21:30 | 214 | 213
2016-09-04 22:00 | 204 | 204
2016-09-04 22:30 | 201 | 201
2016-09-04 23:00 | 183 | 183
2016-09-04 23:30 | 172 | 172
2016-09-05 | 159 | 158
2016-09-05 00:30 | 155 | 155
2016-09-05 01:00 | 152 | 152
2016-09-05 01:30 | 148 | 148
2016-09-05 02:00 | 145 | 145
2016-09-05 02:30 | 143 | 143
2016-09-05 03:00 | 144 | 144
2016-09-05 03:30 | 144 | 144
2016-09-05 04:00 | 150 | 150
2016-09-05 04:30 | 157 | 157
2016-09-05 05:00 | 162 | 162
2016-09-05 05:30 | 176 | 175
2016-09-05 06:00 | 195 | 194
2016-09-05 06:30 | 222 | 221
2016-09-05 07:00 | 235 | 235
2016-09-05 07:30 | 239 | 239
2016-09-05 08:00 | 231 | 231
2016-09-05 08:30 | 218 | 218
2016-09-05 09:00 | 209 | 209
2016-09-05 09:30 | 192 | 191
2016-09-05 10:00 | 188 | 188
2016-09-05 10:30 | 185 | 185
2016-09-05 11:00 | 190 | 190
2016-09-05 11:30 | 196 | 196
2016-09-05 12:00 | 195 | 195
2016-09-05 12:30 | 196 | 196
2016-09-05 13:00 | 196 | 196
2016-09-05 13:30 | 197 | 197
2016-09-05 14:00 | 200 | 200
2016-09-05 14:30 | 203 | 203
2016-09-05 15:00 | 205 | 205
2016-09-05 15:30 | 205 | 205
2016-09-05 16:00 | 215 | 215
2016-09-05 16:30 | 227 | 227
2016-09-05 17:00 | 243 | 243
2016-09-05 17:30 | 268 | 268
2016-09-05 18:00 | 278 | 277
2016-09-05 18:30 | 283 | 282
2016-09-05 19:00 | 269 | 269
2016-09-05 19:30 | 263 | 263
2016-09-05 20:00 | 255 | 255
2016-09-05 20:30 | 245 | 245
2016-09-05 21:00 | 229 | 228
2016-09-05 21:30 | 212 | 212
2016-09-05 22:00 | 210 | 210
2016-09-05 22:30 | 200 | 200
2016-09-05 23:00 | 182 | 181
2016-09-05 23:30 | 178 | 178
2016-09-06 | 166 | 166
2016-09-06 00:30 | 163 | 163
2016-09-06 01:00 | 158 | 158
2016-09-06 01:30 | 156 | 156
2016-09-06 02:00 | 155 | 155
2016-09-06 02:30 | 153 | 153
2016-09-06 03:00 | 149 | 149
2016-09-06 03:30 | 148 | 148
2016-09-06 04:00 | 153 | 153
2016-09-06 04:30 | 155 | 155
2016-09-06 05:00 | 160 | 160
2016-09-06 05:30 | 164 | 164
2016-09-06 06:00 | 186 | 186
2016-09-06 06:30 | 222 | 222
2016-09-06 07:00 | 245 | 245
2016-09-06 07:30 | 244 | 244
2016-09-06 08:00 | 234 | 234
2016-09-06 08:30 | 225 | 225
2016-09-06 09:00 | 222 | 222
2016-09-06 09:30 | 211 | 211
2016-09-06 10:00 | 204 | 204
2016-09-06 10:30 | 209 | 209
2016-09-06 11:00 | 206 | 206
2016-09-06 11:30 | 206 | 206
2016-09-06 12:00 | 204 | 204
2016-09-06 12:30 | 202 | 202
2016-09-06 13:00 | 199 | 199
2016-09-06 13:30 | 201 | 201
2016-09-06 14:00 | 206 | 206
2016-09-06 14:30 | 208 | 208
2016-09-06 15:00 | 212 | 212
2016-09-06 15:30 | 217 | 216
2016-09-06 16:00 | 225 | 225
2016-09-06 16:30 | 231 | 231
2016-09-06 17:00 | 242 | 242
2016-09-06 17:30 | 262 | 262
2016-09-06 18:00 | 277 | 276
2016-09-06 18:30 | 278 | 277
2016-09-06 19:00 | 264 | 264
2016-09-06 19:30 | 253 | 252
2016-09-06 20:00 | 242 | 240
2016-09-06 20:30 | 232 | 230
2016-09-06 21:00 | 219 | 217
2016-09-06 21:30 | 208 | 208
2016-09-06 22:00 | 195 | 195
2016-09-06 22:30 | 191 | 190
2016-09-06 23:00 | 182 | 182
2016-09-06 23:30 | 179 | 179
2016-09-07 | 168 | 168
2016-09-07 00:30 | 162 | 162
2016-09-07 01:00 | 159 | 158
2016-09-07 01:30 | 152 | 151
2016-09-07 02:00 | 146 | 145
2016-09-07 02:30 | 149 | 149
2016-09-07 03:00 | 149 | 148
2016-09-07 03:30 | 150 | 149
2016-09-07 04:00 | 141 | 140
2016-09-07 04:30 | 142 | 141
2016-09-07 05:00 | 160 | 159
2016-09-07 05:30 | 166 | 166
2016-09-07 06:00 | 191 | 191
2016-09-07 06:30 | 209 | 209
2016-09-07 07:00 | 219 | 218
2016-09-07 07:30 | 234 | 233
2016-09-07 08:00 | 224 | 223
2016-09-07 08:30 | 210 | 210
2016-09-07 09:00 | 200 | 199
2016-09-07 09:30 | 206 | 206
2016-09-07 10:00 | 212 | 212
2016-09-07 10:30 | 204 | 204
2016-09-07 11:00 | 205 | 204
2016-09-07 11:30 | 207 | 207
2016-09-07 12:00 | 211 | 211
2016-09-07 12:30 | 209 | 208
2016-09-07 13:00 | 208 | 207
2016-09-07 13:30 | 211 | 211
2016-09-07 14:00 | 214 | 213
2016-09-07 14:30 | 213 | 212
2016-09-07 15:00 | 197 | 197
2016-09-07 15:30 | 194 | 194
2016-09-07 16:00 | 202 | 201
2016-09-07 16:30 | 213 | 213
2016-09-07 17:00 | 225 | 224
2016-09-07 17:30 | 236 | 235
2016-09-07 18:00 | 246 | 246
2016-09-07 18:30 | 246 | 246
2016-09-07 19:00 | 236 | 236
2016-09-07 19:30 | 229 | 229
2016-09-07 20:00 | 222 | 222
2016-09-07 20:30 | 211 | 211
2016-09-07 21:00 | 199 | 199
2016-09-07 21:30 | 198 | 198
2016-09-07 22:00 | 194 | 194
2016-09-07 22:30 | 186 | 186
2016-09-07 23:00 | 169 | 169
2016-09-07 23:30 | 170 | 170
2016-09-08 | 150 | 149
2016-09-08 00:30 | 149 | 149
2016-09-08 01:00 | 140 | 139
2016-09-08 01:30 | 142 | 141
2016-09-08 02:00 | 152 | 151
2016-09-08 02:30 | 138 | 137
2016-09-08 03:00 | 137 | 136
2016-09-08 03:30 | 113 | 112
2016-09-08 04:00 | 133 | 132
2016-09-08 04:30 | 129 | 128
2016-09-08 05:00 | 143 | 143
2016-09-08 05:30 | 157 | 157
2016-09-08 06:00 | 166 | 166
2016-09-08 06:30 | 188 | 188
2016-09-08 07:00 | 203 | 202
2016-09-08 07:30 | 209 | 209
2016-09-08 08:00 | 214 | 213
2016-09-08 08:30 | 202 | 201
2016-09-08 09:00 | 203 | 201
2016-09-08 09:30 | 206 | 204
2016-09-08 10:00 | 195 | 194
2016-09-08 10:30 | 201 | 199
2016-09-08 11:00 | 200 | 198
2016-09-08 11:30 | 200 | 199
2016-09-08 12:00 | 199 | 198
2016-09-08 12:30 | 197 | 197
2016-09-08 13:00 | 199 | 199
2016-09-08 13:30 | 196 | 196
2016-09-08 14:00 | 191 | 191
2016-09-08 14:30 | 189 | 189
2016-09-08 15:00 | 191 | 191
2016-09-08 15:30 | 199 | 198
2016-09-08 16:00 | 208 | 208
2016-09-08 16:30 | 218 | 218
2016-09-08 17:00 | 227 | 227
2016-09-08 17:30 | 245 | 245
2016-09-08 18:00 | 254 | 254
2016-09-08 18:30 | 255 | 255
2016-09-08 19:00 | 248 | 248
2016-09-08 19:30 | 243 | 243
2016-09-08 20:00 | 233 | 233
2016-09-08 20:30 | 219 | 219
2016-09-08 21:00 | 203 | 203
2016-09-08 21:30 | 200 | 200
2016-09-08 22:00 | 190 | 190
2016-09-08 22:30 | 183 | 183
2016-09-08 23:00 | 177 | 177
2016-09-08 23:30 | 182 | 182
2016-09-09 | 167 | 166
2016-09-09 00:30 | 162 | 161
2016-09-09 01:00 | 151 | 150
2016-09-09 01:30 | 146 | 145
2016-09-09 02:00 | 150 | 149
2016-09-09 02:30 | 149 | 148
2016-09-09 03:00 | 148 | 147
2016-09-09 03:30 | 148 | 147
2016-09-09 04:00 | 151 | 151
2016-09-09 04:30 | 154 | 154
2016-09-09 05:00 | 153 | 153
2016-09-09 05:30 | 145 | 144
2016-09-09 06:00 | 161 | 161
2016-09-09 06:30 | 176 | 176
2016-09-09 07:00 | 190 | 190
2016-09-09 07:30 | 213 | 213
2016-09-09 08:00 | 222 | 222
2016-09-09 08:30 | 214 | 214
2016-09-09 09:00 | 203 | 203
2016-09-09 09:30 | 192 | 192
2016-09-09 10:00 | 181 | 180
2016-09-09 10:30 | 185 | 183
2016-09-09 11:00 | 193 | 192
2016-09-09 11:30 | 194 | 193
2016-09-09 12:00 | 194 | 193
2016-09-09 12:30 | 189 | 188
2016-09-09 13:00 | 180 | 179
2016-09-09 13:30 | 187 | 186
2016-09-09 14:00 | 192 | 192
2016-09-09 14:30 | 195 | 194
2016-09-09 15:00 | 199 | 199
2016-09-09 15:30 | 209 | 209
2016-09-09 16:00 | 206 | 206
2016-09-09 16:30 | 221 | 221
2016-09-09 17:00 | 234 | 233
2016-09-09 17:30 | 246 | 245
2016-09-09 18:00 | 239 | 239
2016-09-09 18:30 | 234 | 234
2016-09-09 19:00 | 224 | 224
2016-09-09 19:30 | 221 | 220
2016-09-09 20:00 | 216 | 215
2016-09-09 20:30 | 208 | 208
2016-09-09 21:00 | 200 | 200
2016-09-09 21:30 | 208 | 208
2016-09-09 22:00 | 218 | 218
2016-09-09 22:30 | 198 | 198
2016-09-09 23:00 | 183 | 182
2016-09-09 23:30 | 184 | 183
2016-09-10 | 170 | 169
2016-09-10 00:30 | 164 | 164
2016-09-10 01:00 | 158 | 157
2016-09-10 01:30 | 154 | 153
2016-09-10 02:00 | 151 | 150
2016-09-10 02:30 | 147 | 147
2016-09-10 03:00 | 146 | 146
2016-09-10 03:30 | 146 | 146
2016-09-10 04:00 | 147 | 147
2016-09-10 04:30 | 148 | 148
2016-09-10 05:00 | 152 | 152
2016-09-10 05:30 | 155 | 155
2016-09-10 06:00 | 166 | 166
2016-09-10 06:30 | 177 | 177
2016-09-10 07:00 | 192 | 192
2016-09-10 07:30 | 206 | 206
2016-09-10 08:00 | 220 | 220
2016-09-10 08:30 | 226 | 226
2016-09-10 09:00 | 225 | 225
2016-09-10 09:30 | 222 | 222
2016-09-10 10:00 | 229 | 229
2016-09-10 10:30 | 229 | 228
2016-09-10 11:00 | 220 | 220
2016-09-10 11:30 | 213 | 212
2016-09-10 12:00 | 219 | 218
2016-09-10 12:30 | 219 | 218
2016-09-10 13:00 | 214 | 213
2016-09-10 13:30 | 206 | 206
2016-09-10 14:00 | 204 | 203
2016-09-10 14:30 | 212 | 211
2016-09-10 15:00 | 195 | 194
2016-09-10 15:30 | 188 | 188
2016-09-10 16:00 | 194 | 194
2016-09-10 16:30 | 204 | 204
2016-09-10 17:00 | 227 | 227
2016-09-10 17:30 | 244 | 244
2016-09-10 18:00 | 245 | 245
2016-09-10 18:30 | 241 | 240
2016-09-10 19:00 | 236 | 236
2016-09-10 19:30 | 238 | 238
2016-09-10 20:00 | 215 | 215
2016-09-10 20:30 | 208 | 208
2016-09-10 21:00 | 202 | 201
2016-09-10 21:30 | 196 | 196
2016-09-10 22:00 | 175 | 175
2016-09-10 22:30 | 180 | 180
2016-09-10 23:00 | 178 | 178
2016-09-10 23:30 | 179 | 179
2016-09-11 | 167 | 167
2016-09-11 00:30 | 161 | 160
2016-09-11 01:00 | 155 | 155
2016-09-11 01:30 | 155 | 155
2016-09-11 02:00 | 153 | 153
2016-09-11 02:30 | 154 | 154
2016-09-11 03:00 | 155 | 155
2016-09-11 03:30 | 157 | 157
2016-09-11 04:00 | 160 | 160
2016-09-11 04:30 | 168 | 168
2016-09-11 05:00 | 171 | 171
2016-09-11 05:30 | 171 | 171
2016-09-11 06:00 | 174 | 174
2016-09-11 06:30 | 177 | 177
2016-09-11 07:00 | 185 | 185
2016-09-11 07:30 | 193 | 193
2016-09-11 08:00 | 202 | 202
2016-09-11 08:30 | 203 | 203
2016-09-11 09:00 | 202 | 201
2016-09-11 09:30 | 199 | 198
2016-09-11 10:00 | 196 | 195
2016-09-11 10:30 | 190 | 189
2016-09-11 11:00 | 188 | 187
2016-09-11 11:30 | 190 | 189
2016-09-11 12:00 | 189 | 188
2016-09-11 12:30 | 189 | 188
2016-09-11 13:00 | 190 | 188
2016-09-11 13:30 | 189 | 188
2016-09-11 14:00 | 194 | 193
2016-09-11 14:30 | 200 | 199
2016-09-11 15:00 | 208 | 208
2016-09-11 15:30 | 217 | 216
2016-09-11 16:00 | 221 | 221
2016-09-11 16:30 | 229 | 228
2016-09-11 17:00 | 239 | 238
2016-09-11 17:30 | 254 | 254
2016-09-11 18:00 | 267 | 266
2016-09-11 18:30 | 267 | 267
2016-09-11 19:00 | 258 | 258
2016-09-11 19:30 | 253 | 253
2016-09-11 20:00 | 243 | 243
2016-09-11 20:30 | 232 | 232
2016-09-11 21:00 | 225 | 225
2016-09-11 21:30 | 218 | 218
2016-09-11 22:00 | 212 | 212
2016-09-11 22:30 | 214 | 214
2016-09-11 23:00 | 200 | 200
2016-09-11 23:30 | 184 | 184
2016-09-12 | 171 | 171
2016-09-12 00:30 | 162 | 161
2016-09-12 01:00 | 157 | 156
2016-09-12 01:30 | 155 | 154
2016-09-12 02:00 | 149 | 149
2016-09-12 02:30 | 148 | 148
2016-09-12 03:00 | 150 | 150
2016-09-12 03:30 | 144 | 144
2016-09-12 04:00 | 155 | 155
2016-09-12 04:30 | 161 | 161
2016-09-12 05:00 | 172 | 172
2016-09-12 05:30 | 186 | 186
2016-09-12 06:00 | 203 | 203
2016-09-12 06:30 | 225 | 225
2016-09-12 07:00 | 232 | 232
2016-09-12 07:30 | 243 | 243
2016-09-12 08:00 | 242 | 241
2016-09-12 08:30 | 234 | 234
2016-09-12 09:00 | 232 | 231
2016-09-12 09:30 | 226 | 226
2016-09-12 10:00 | 223 | 223
2016-09-12 10:30 | 218 | 217
2016-09-12 11:00 | 218 | 218
2016-09-12 11:30 | 214 | 214
2016-09-12 12:00 | 216 | 216
2016-09-12 12:30 | 214 | 214
2016-09-12 13:00 | 215 | 215
2016-09-12 13:30 | 216 | 216
2016-09-12 14:00 | 220 | 220
2016-09-12 14:30 | 222 | 222
2016-09-12 15:00 | 226 | 226
2016-09-12 15:30 | 235 | 235
2016-09-12 16:00 | 241 | 241
2016-09-12 16:30 | 256 | 256
2016-09-12 17:00 | 264 | 264
2016-09-12 17:30 | 279 | 279
2016-09-12 18:00 | 295 | 293
2016-09-12 18:30 | 292 | 290
2016-09-12 19:00 | 274 | 272
2016-09-12 19:30 | 269 | 266
2016-09-12 20:00 | 263 | 259
2016-09-12 20:30 | 249 | 244
2016-09-12 21:00 | 236 | 231
2016-09-12 21:30 | 221 | 221
2016-09-12 22:00 | 219 | 219
2016-09-12 22:30 | 209 | 209
2016-09-12 23:00 | 199 | 199
2016-09-12 23:30 | 188 | 188
2016-09-13 | 177 | 176
2016-09-13 00:30 | 171 | 170
2016-09-13 01:00 | 163 | 162
2016-09-13 01:30 | 159 | 158
2016-09-13 02:00 | 160 | 159
2016-09-13 02:30 | 159 | 158
2016-09-13 03:00 | 158 | 157
2016-09-13 03:30 | 160 | 159
2016-09-13 04:00 | 163 | 162
2016-09-13 04:30 | 166 | 165
2016-09-13 05:00 | 173 | 172
2016-09-13 05:30 | 182 | 181
2016-09-13 06:00 | 202 | 202
2016-09-13 06:30 | 229 | 229
2016-09-13 07:00 | 247 | 247
2016-09-13 07:30 | 263 | 263
2016-09-13 08:00 | 265 | 264
2016-09-13 08:30 | 253 | 253
2016-09-13 09:00 | 247 | 247
2016-09-13 09:30 | 238 | 238
2016-09-13 10:00 | 233 | 233
2016-09-13 10:30 | 226 | 226
2016-09-13 11:00 | 227 | 227
2016-09-13 11:30 | 229 | 229
2016-09-13 12:00 | 229 | 229
2016-09-13 12:30 | 226 | 226
2016-09-13 13:00 | 228 | 227
2016-09-13 13:30 | 240 | 240
2016-09-13 14:00 | 242 | 242
2016-09-13 14:30 | 239 | 239
2016-09-13 15:00 | 240 | 240
2016-09-13 15:30 | 249 | 249
2016-09-13 16:00 | 253 | 253
2016-09-13 16:30 | 274 | 274
2016-09-13 17:00 | 281 | 281
2016-09-13 17:30 | 279 | 279
2016-09-13 18:00 | 283 | 283
2016-09-13 18:30 | 283 | 283
2016-09-13 19:00 | 273 | 273
2016-09-13 19:30 | 273 | 273
2016-09-13 20:00 | 268 | 268
2016-09-13 20:30 | 253 | 253
2016-09-13 21:00 | 235 | 234
2016-09-13 21:30 | 227 | 226
2016-09-13 22:00 | 225 | 225
2016-09-13 22:30 | 218 | 217
2016-09-13 23:00 | 205 | 204
2016-09-13 23:30 | 190 | 188
2016-09-14 | 175 | 172
2016-09-14 00:30 | 167 | 163
2016-09-14 01:00 | 160 | 156
2016-09-14 01:30 | 157 | 154
2016-09-14 02:00 | 155 | 150
2016-09-14 02:30 | 155 | 151
2016-09-14 03:00 | 156 | 152
2016-09-14 03:30 | 156 | 153
2016-09-14 04:00 | 156 | 155
2016-09-14 04:30 | 159 | 158
2016-09-14 05:00 | 169 | 169
2016-09-14 05:30 | 183 | 183
2016-09-14 06:00 | 202 | 202
2016-09-14 06:30 | 218 | 218
2016-09-14 07:00 | 236 | 236
2016-09-14 07:30 | 250 | 249
2016-09-14 08:00 | 254 | 253
2016-09-14 08:30 | 247 | 247
2016-09-14 09:00 | 248 | 248
2016-09-14 09:30 | 246 | 246
2016-09-14 10:00 | 240 | 240
2016-09-14 10:30 | 232 | 232
2016-09-14 11:00 | 228 | 228
2016-09-14 11:30 | 227 | 227
2016-09-14 12:00 | 225 | 225
2016-09-14 12:30 | 225 | 225
2016-09-14 13:00 | 229 | 229
2016-09-14 13:30 | 239 | 239
2016-09-14 14:00 | 244 | 244
2016-09-14 14:30 | 244 | 244
2016-09-14 15:00 | 241 | 241
2016-09-14 15:30 | 244 | 244
2016-09-14 16:00 | 250 | 250
2016-09-14 16:30 | 263 | 263
2016-09-14 17:00 | 271 | 270
2016-09-14 17:30 | 275 | 275
2016-09-14 18:00 | 281 | 281
2016-09-14 18:30 | 283 | 283
2016-09-14 19:00 | 272 | 272
2016-09-14 19:30 | 271 | 270
2016-09-14 20:00 | 263 | 262
2016-09-14 20:30 | 248 | 248
2016-09-14 21:00 | 233 | 233
2016-09-14 21:30 | 221 | 220
2016-09-14 22:00 | 228 | 227
2016-09-14 22:30 | 219 | 219
2016-09-14 23:00 | 200 | 199
2016-09-14 23:30 | 187 | 186
2016-09-15 | 173 | 171
2016-09-15 00:30 | 163 | 159
2016-09-15 01:00 | 160 | 156
2016-09-15 01:30 | 157 | 153
2016-09-15 02:00 | 152 | 149
2016-09-15 02:30 | 146 | 144
2016-09-15 03:00 | 144 | 142
2016-09-15 03:30 | 146 | 144
2016-09-15 04:00 | 151 | 149
2016-09-15 04:30 | 154 | 153
2016-09-15 05:00 | 169 | 168
2016-09-15 05:30 | 177 | 177
2016-09-15 06:00 | 185 | 185
2016-09-15 06:30 | 215 | 215
2016-09-15 07:00 | 241 | 240
2016-09-15 07:30 | 255 | 254
2016-09-15 08:00 | 257 | 256
2016-09-15 08:30 | 247 | 246
2016-09-15 09:00 | 242 | 242
2016-09-15 09:30 | 232 | 231
2016-09-15 10:00 | 223 | 222
2016-09-15 10:30 | 232 | 232
2016-09-15 11:00 | 240 | 240
2016-09-15 11:30 | 234 | 234
2016-09-15 12:00 | 217 | 217
2016-09-15 12:30 | 217 | 217
2016-09-15 13:00 | 222 | 222
2016-09-15 13:30 | 227 | 227
2016-09-15 14:00 | 229 | 229
2016-09-15 14:30 | 235 | 235
2016-09-15 15:00 | 237 | 237
2016-09-15 15:30 | 242 | 242
2016-09-15 16:00 | 251 | 251
2016-09-15 16:30 | 258 | 258
2016-09-15 17:00 | 260 | 260
2016-09-15 17:30 | 266 | 266
2016-09-15 18:00 | 269 | 269
2016-09-15 18:30 | 275 | 275
2016-09-15 19:00 | 264 | 264
2016-09-15 19:30 | 262 | 261
2016-09-15 20:00 | 259 | 259
2016-09-15 20:30 | 253 | 252
2016-09-15 21:00 | 242 | 242
2016-09-15 21:30 | 233 | 232
2016-09-15 22:00 | 233 | 233
2016-09-15 22:30 | 232 | 232
2016-09-15 23:00 | 215 | 215
2016-09-15 23:30 | 202 | 202
2016-09-16 | 191 | 190
2016-09-16 00:30 | 185 | 184
2016-09-16 01:00 | 181 | 180
2016-09-16 01:30 | 172 | 171
2016-09-16 02:00 | 166 | 165
2016-09-16 02:30 | 163 | 161
2016-09-16 03:00 | 165 | 163
2016-09-16 03:30 | 166 | 164
2016-09-16 04:00 | 168 | 167
2016-09-16 04:30 | 170 | 169
2016-09-16 05:00 | 176 | 175
2016-09-16 05:30 | 186 | 185
2016-09-16 06:00 | 212 | 212
2016-09-16 06:30 | 230 | 230
2016-09-16 07:00 | 244 | 244
2016-09-16 07:30 | 256 | 255
2016-09-16 08:00 | 250 | 249
2016-09-16 08:30 | 242 | 241
2016-09-16 09:00 | 244 | 243
2016-09-16 09:30 | 254 | 253
2016-09-16 10:00 | 259 | 259
2016-09-16 10:30 | 250 | 249
2016-09-16 11:00 | 242 | 242
2016-09-16 11:30 | 239 | 239
2016-09-16 12:00 | 221 | 221
2016-09-16 12:30 | 223 | 223
2016-09-16 13:00 | 225 | 224
2016-09-16 13:30 | 222 | 222
2016-09-16 14:00 | 226 | 225
2016-09-16 14:30 | 224 | 223
2016-09-16 15:00 | 228 | 228
2016-09-16 15:30 | 231 | 231
2016-09-16 16:00 | 237 | 237
2016-09-16 16:30 | 245 | 244
2016-09-16 17:00 | 255 | 254
2016-09-16 17:30 | 265 | 264
2016-09-16 18:00 | 270 | 270
2016-09-16 18:30 | 272 | 271
2016-09-16 19:00 | 266 | 265
2016-09-16 19:30 | 261 | 260
2016-09-16 20:00 | 256 | 255
2016-09-16 20:30 | 248 | 247
2016-09-16 21:00 | 240 | 238
2016-09-16 21:30 | 231 | 229
2016-09-16 22:00 | 234 | 232
2016-09-16 22:30 | 229 | 227
2016-09-16 23:00 | 208 | 205
2016-09-16 23:30 | 196 | 192
2016-09-17 | 180 | 177
2016-09-17 00:30 | 173 | 170
2016-09-17 01:00 | 167 | 163
2016-09-17 01:30 | 163 | 158
2016-09-17 02:00 | 157 | 151
2016-09-17 02:30 | 155 | 150
2016-09-17 03:00 | 157 | 151
2016-09-17 03:30 | 157 | 151
2016-09-17 04:00 | 157 | 152
2016-09-17 04:30 | 158 | 153
2016-09-17 05:00 | 160 | 155
2016-09-17 05:30 | 165 | 160
2016-09-17 06:00 | 175 | 170
2016-09-17 06:30 | 183 | 179
2016-09-17 07:00 | 192 | 190
2016-09-17 07:30 | 201 | 200
2016-09-17 08:00 | 209 | 208
2016-09-17 08:30 | 211 | 211
2016-09-17 09:00 | 210 | 210
2016-09-17 09:30 | 210 | 210
2016-09-17 10:00 | 204 | 204
2016-09-17 10:30 | 200 | 200
2016-09-17 11:00 | 194 | 194
2016-09-17 11:30 | 197 | 197
2016-09-17 12:00 | 192 | 192
2016-09-17 12:30 | 192 | 192
2016-09-17 13:00 | 194 | 194
2016-09-17 13:30 | 202 | 202
2016-09-17 14:00 | 212 | 212
2016-09-17 14:30 | 222 | 221
2016-09-17 15:00 | 235 | 234
2016-09-17 15:30 | 243 | 239
2016-09-17 16:00 | 246 | 242
2016-09-17 16:30 | 242 | 240
2016-09-17 17:00 | 247 | 245
2016-09-17 17:30 | 256 | 255
2016-09-17 18:00 | 263 | 262
2016-09-17 18:30 | 265 | 264
2016-09-17 19:00 | 255 | 254
2016-09-17 19:30 | 251 | 249
2016-09-17 20:00 | 247 | 245
2016-09-17 20:30 | 238 | 237
2016-09-17 21:00 | 233 | 232
2016-09-17 21:30 | 225 | 224
2016-09-17 22:00 | 220 | 219
2016-09-17 22:30 | 221 | 220
2016-09-17 23:00 | 212 | 211
2016-09-17 23:30 | 200 | 198
2016-09-18 | 184 | 181
2016-09-18 00:30 | 175 | 171
2016-09-18 01:00 | 173 | 169
2016-09-18 01:30 | 169 | 165
2016-09-18 02:00 | 168 | 164
2016-09-18 02:30 | 169 | 165
2016-09-18 03:00 | 166 | 162
2016-09-18 03:30 | 166 | 162
2016-09-18 04:00 | 167 | 163
2016-09-18 04:30 | 169 | 165
2016-09-18 05:00 | 172 | 168
2016-09-18 05:30 | 176 | 173
2016-09-18 06:00 | 180 | 176
2016-09-18 06:30 | 189 | 185
2016-09-18 07:00 | 198 | 195
2016-09-18 07:30 | 214 | 212
2016-09-18 08:00 | 225 | 224
2016-09-18 08:30 | 236 | 235
2016-09-18 09:00 | 248 | 247
2016-09-18 09:30 | 249 | 249
2016-09-18 10:00 | 239 | 239
2016-09-18 10:30 | 240 | 240
2016-09-18 11:00 | 238 | 238
2016-09-18 11:30 | 234 | 234
2016-09-18 12:00 | 238 | 238
2016-09-18 12:30 | 239 | 239
2016-09-18 13:00 | 240 | 240
2016-09-18 13:30 | 234 | 234
2016-09-18 14:00 | 229 | 228
2016-09-18 14:30 | 229 | 229
2016-09-18 15:00 | 229 | 229
2016-09-18 15:30 | 234 | 234
2016-09-18 16:00 | 238 | 238
2016-09-18 16:30 | 248 | 247
2016-09-18 17:00 | 258 | 257
2016-09-18 17:30 | 266 | 265
2016-09-18 18:00 | 272 | 271
2016-09-18 18:30 | 273 | 272
2016-09-18 19:00 | 266 | 264
2016-09-18 19:30 | 265 | 264
2016-09-18 20:00 | 260 | 259
2016-09-18 20:30 | 252 | 251
2016-09-18 21:00 | 246 | 244
2016-09-18 21:30 | 235 | 233
2016-09-18 22:00 | 228 | 226
2016-09-18 22:30 | 224 | 222
2016-09-18 23:00 | 208 | 204
2016-09-18 23:30 | 193 | 189
2016-09-19 | 179 | 176
2016-09-19 00:30 | 173 | 169
2016-09-19 01:00 | 169 | 165
2016-09-19 01:30 | 167 | 163
2016-09-19 02:00 | 167 | 162
2016-09-19 02:30 | 165 | 160
2016-09-19 03:00 | 165 | 160
2016-09-19 03:30 | 167 | 163
2016-09-19 04:00 | 170 | 165
2016-09-19 04:30 | 172 | 168
2016-09-19 05:00 | 175 | 174
2016-09-19 05:30 | 184 | 183
2016-09-19 06:00 | 204 | 204
2016-09-19 06:30 | 222 | 222
2016-09-19 07:00 | 238 | 238
2016-09-19 07:30 | 253 | 253
2016-09-19 08:00 | 259 | 259
2016-09-19 08:30 | 258 | 257
2016-09-19 09:00 | 253 | 253
2016-09-19 09:30 | 250 | 249
2016-09-19 10:00 | 245 | 244
2016-09-19 10:30 | 244 | 243
2016-09-19 11:00 | 236 | 235
2016-09-19 11:30 | 230 | 229
2016-09-19 12:00 | 230 | 229
2016-09-19 12:30 | 230 | 229
2016-09-19 13:00 | 232 | 231
2016-09-19 13:30 | 232 | 231
2016-09-19 14:00 | 237 | 236
2016-09-19 14:30 | 240 | 239
2016-09-19 15:00 | 235 | 234
2016-09-19 15:30 | 244 | 244
2016-09-19 16:00 | 245 | 245
2016-09-19 16:30 | 259 | 259
2016-09-19 17:00 | 270 | 270
2016-09-19 17:30 | 276 | 276
2016-09-19 18:00 | 284 | 284
2016-09-19 18:30 | 286 | 286
2016-09-19 19:00 | 280 | 280
2016-09-19 19:30 | 276 | 276
2016-09-19 20:00 | 268 | 268
2016-09-19 20:30 | 255 | 255
2016-09-19 21:00 | 246 | 245
2016-09-19 21:30 | 234 | 231
2016-09-19 22:00 | 228 | 226
2016-09-19 22:30 | 229 | 227
2016-09-19 23:00 | 218 | 217
2016-09-19 23:30 | 201 | 200
2016-09-20 | 183 | 182
2016-09-20 00:30 | 173 | 172
2016-09-20 01:00 | 170 | 170
2016-09-20 01:30 | 167 | 166
2016-09-20 02:00 | 164 | 163
2016-09-20 02:30 | 165 | 164
2016-09-20 03:00 | 165 | 164
2016-09-20 03:30 | 165 | 164
2016-09-20 04:00 | 169 | 168
2016-09-20 04:30 | 173 | 172
2016-09-20 05:00 | 177 | 176
2016-09-20 05:30 | 183 | 182
2016-09-20 06:00 | 202 | 201
2016-09-20 06:30 | 221 | 219
2016-09-20 07:00 | 230 | 229
2016-09-20 07:30 | 239 | 239
2016-09-20 08:00 | 237 | 237
2016-09-20 08:30 | 231 | 231
2016-09-20 09:00 | 226 | 226
2016-09-20 09:30 | 224 | 224
2016-09-20 10:00 | 221 | 221
2016-09-20 10:30 | 215 | 215
2016-09-20 11:00 | 209 | 209
2016-09-20 11:30 | 205 | 205
2016-09-20 12:00 | 203 | 203
2016-09-20 12:30 | 205 | 205
2016-09-20 13:00 | 210 | 210
2016-09-20 13:30 | 221 | 220
2016-09-20 14:00 | 234 | 234
2016-09-20 14:30 | 238 | 238
2016-09-20 15:00 | 240 | 240
2016-09-20 15:30 | 244 | 244
2016-09-20 16:00 | 251 | 251
2016-09-20 16:30 | 260 | 260
2016-09-20 17:00 | 269 | 269
2016-09-20 17:30 | 283 | 283
2016-09-20 18:00 | 289 | 289
2016-09-20 18:30 | 290 | 290
2016-09-20 19:00 | 279 | 279
2016-09-20 19:30 | 276 | 276
2016-09-20 20:00 | 269 | 269
2016-09-20 20:30 | 255 | 255
2016-09-20 21:00 | 245 | 244
2016-09-20 21:30 | 231 | 231
2016-09-20 22:00 | 230 | 230
2016-09-20 22:30 | 226 | 226
2016-09-20 23:00 | 213 | 213
2016-09-20 23:30 | 200 | 200
2016-09-21 | 187 | 187
2016-09-21 00:30 | 177 | 177
2016-09-21 01:00 | 174 | 174
2016-09-21 01:30 | 173 | 173
2016-09-21 02:00 | 170 | 170
2016-09-21 02:30 | 171 | 171
2016-09-21 03:00 | 172 | 172
2016-09-21 03:30 | 173 | 173
2016-09-21 04:00 | 174 | 174
2016-09-21 04:30 | 179 | 179
2016-09-21 05:00 | 185 | 185
2016-09-21 05:30 | 189 | 189
2016-09-21 06:00 | 209 | 208
2016-09-21 06:30 | 232 | 231
2016-09-21 07:00 | 249 | 248
2016-09-21 07:30 | 264 | 264
2016-09-21 08:00 | 282 | 281
2016-09-21 08:30 | 299 | 299
2016-09-21 09:00 | 299 | 299
2016-09-21 09:30 | 301 | 301
2016-09-21 10:00 | 297 | 297
2016-09-21 10:30 | 291 | 291
2016-09-21 11:00 | 288 | 288
2016-09-21 11:30 | 280 | 280
2016-09-21 12:00 | 278 | 278
2016-09-21 12:30 | 274 | 274
2016-09-21 13:00 | 279 | 278
2016-09-21 13:30 | 281 | 281
2016-09-21 14:00 | 292 | 292
2016-09-21 14:30 | 291 | 291
2016-09-21 15:00 | 294 | 294
2016-09-21 15:30 | 305 | 305
2016-09-21 16:00 | 308 | 308
2016-09-21 16:30 | 308 | 308
2016-09-21 17:00 | 312 | 312
2016-09-21 17:30 | 320 | 320
2016-09-21 18:00 | 335 | 334
2016-09-21 18:30 | 339 | 338
2016-09-21 19:00 | 330 | 328
2016-09-21 19:30 | 333 | 333
2016-09-21 20:00 | 327 | 327
2016-09-21 20:30 | 308 | 307
2016-09-21 21:00 | 291 | 290
2016-09-21 21:30 | 278 | 277
2016-09-21 22:00 | 276 | 275
2016-09-21 22:30 | 272 | 271
2016-09-21 23:00 | 253 | 252
2016-09-21 23:30 | 239 | 239
2016-09-22 | 231 | 231
2016-09-22 00:30 | 213 | 213
2016-09-22 01:00 | 205 | 205
2016-09-22 01:30 | 204 | 203
2016-09-22 02:00 | 200 | 200
2016-09-22 02:30 | 198 | 198
2016-09-22 03:00 | 198 | 197
2016-09-22 03:30 | 198 | 198
2016-09-22 04:00 | 203 | 202
2016-09-22 04:30 | 208 | 207
2016-09-22 05:00 | 212 | 211
2016-09-22 05:30 | 221 | 221
2016-09-22 06:00 | 253 | 253
2016-09-22 06:30 | 266 | 266
2016-09-22 07:00 | 272 | 271
2016-09-22 07:30 | 278 | 277
2016-09-22 08:00 | 280 | 280
2016-09-22 08:30 | 226 | 226
2016-09-22 09:00 | 184 | 184
2016-09-22 09:30 | 182 | 182
2016-09-22 10:00 | 177 | 177
2016-09-22 10:30 | 174 | 174
2016-09-22 11:00 | 175 | 175
2016-09-22 11:30 | 175 | 175
2016-09-22 12:00 | 179 | 179
2016-09-22 12:30 | 168 | 168
2016-09-22 13:00 | 163 | 163
2016-09-22 13:30 | 165 | 165
2016-09-22 14:00 | 166 | 166
2016-09-22 14:30 | 167 | 167
2016-09-22 15:00 | 170 | 170
2016-09-22 15:30 | 172 | 172
2016-09-22 16:00 | 176 | 176
2016-09-22 16:30 | 180 | 180
2016-09-22 17:00 | 184 | 184
2016-09-22 17:30 | 190 | 189
2016-09-22 18:00 | 198 | 198
2016-09-22 18:30 | 193 | 193
2016-09-22 19:00 | 190 | 190
2016-09-22 19:30 | 192 | 192
2016-09-22 20:00 | 192 | 192
2016-09-22 20:30 | 186 | 186
2016-09-22 21:00 | 178 | 178
2016-09-22 21:30 | 171 | 171
2016-09-22 22:00 | 168 | 168
2016-09-22 22:30 | 167 | 167
2016-09-22 23:00 | 154 | 154
2016-09-22 23:30 | 145 | 145
2016-09-23 | 133 | 133
2016-09-23 00:30 | 128 | 128
2016-09-23 01:00 | 124 | 124
2016-09-23 01:30 | 123 | 123
2016-09-23 02:00 | 122 | 122
2016-09-23 02:30 | 121 | 121
2016-09-23 03:00 | 120 | 120
2016-09-23 03:30 | 120 | 120
2016-09-23 04:00 | 122 | 122
2016-09-23 04:30 | 124 | 124
2016-09-23 05:00 | 127 | 127
2016-09-23 05:30 | 133 | 133
2016-09-23 06:00 | 146 | 146
2016-09-23 06:30 | 161 | 160
2016-09-23 07:00 | 162 | 162
2016-09-23 07:30 | 165 | 165
2016-09-23 08:00 | 166 | 166
2016-09-23 08:30 | 165 | 165
2016-09-23 09:00 | 163 | 163
2016-09-23 09:30 | 162 | 162
2016-09-23 10:00 | 162 | 162
2016-09-23 10:30 | 159 | 159
2016-09-23 11:00 | 156 | 156
2016-09-23 11:30 | 154 | 154
2016-09-23 12:00 | 151 | 151
2016-09-23 12:30 | 150 | 150
2016-09-23 13:00 | 149 | 149
2016-09-23 13:30 | 151 | 151
2016-09-23 14:00 | 154 | 154
2016-09-23 14:30 | 161 | 161
2016-09-23 15:00 | 164 | 164
2016-09-23 15:30 | 168 | 168
2016-09-23 16:00 | 174 | 174
2016-09-23 16:30 | 176 | 176
2016-09-23 17:00 | 178 | 177
2016-09-23 17:30 | 180 | 179
2016-09-23 18:00 | 183 | 183
2016-09-23 18:30 | 187 | 187
2016-09-23 19:00 | 182 | 182
2016-09-23 19:30 | 182 | 181
2016-09-23 20:00 | 178 | 178
2016-09-23 20:30 | 172 | 172
2016-09-23 21:00 | 168 | 168
2016-09-23 21:30 | 162 | 162
2016-09-23 22:00 | 161 | 161
2016-09-23 22:30 | 161 | 161
2016-09-23 23:00 | 154 | 154
2016-09-23 23:30 | 147 | 146
2016-09-24 | 132 | 132
2016-09-24 00:30 | 124 | 123
2016-09-24 01:00 | 122 | 122
2016-09-24 01:30 | 119 | 119
2016-09-24 02:00 | 118 | 118
2016-09-24 02:30 | 116 | 116
2016-09-24 03:00 | 116 | 116
2016-09-24 03:30 | 114 | 114
2016-09-24 04:00 | 115 | 115
2016-09-24 04:30 | 118 | 118
2016-09-24 05:00 | 120 | 120
2016-09-24 05:30 | 123 | 123
2016-09-24 06:00 | 129 | 129
2016-09-24 06:30 | 135 | 135
2016-09-24 07:00 | 142 | 142
2016-09-24 07:30 | 166 | 166
2016-09-24 08:00 | 171 | 171
2016-09-24 08:30 | 158 | 158
2016-09-24 09:00 | 153 | 153
2016-09-24 09:30 | 152 | 152
2016-09-24 10:00 | 150 | 150
2016-09-24 10:30 | 143 | 143
2016-09-24 11:00 | 141 | 140
2016-09-24 11:30 | 139 | 139
2016-09-24 12:00 | 137 | 136
2016-09-24 12:30 | 136 | 136
2016-09-24 13:00 | 142 | 142
2016-09-24 13:30 | 143 | 143
2016-09-24 14:00 | 144 | 144
2016-09-24 14:30 | 162 | 162
2016-09-24 15:00 | 211 | 211
2016-09-24 15:30 | 221 | 221
2016-09-24 16:00 | 224 | 224
2016-09-24 16:30 | 230 | 230
2016-09-24 17:00 | 235 | 235
2016-09-24 17:30 | 243 | 243
2016-09-24 18:00 | 252 | 252
2016-09-24 18:30 | 257 | 257
2016-09-24 19:00 | 249 | 249
2016-09-24 19:30 | 245 | 245
2016-09-24 20:00 | 241 | 240
2016-09-24 20:30 | 236 | 236
2016-09-24 21:00 | 228 | 228
2016-09-24 21:30 | 224 | 224
2016-09-24 22:00 | 223 | 223
2016-09-24 22:30 | 220 | 220
2016-09-24 23:00 | 212 | 212
2016-09-24 23:30 | 200 | 200
2016-09-25 | 181 | 181
2016-09-25 00:30 | 176 | 176
2016-09-25 01:00 | 166 | 166
2016-09-25 01:30 | 163 | 163
2016-09-25 02:00 | 160 | 160
2016-09-25 02:30 | 157 | 157
2016-09-25 03:00 | 157 | 157
2016-09-25 03:30 | 153 | 153
2016-09-25 04:00 | 161 | 161
2016-09-25 04:30 | 166 | 166
2016-09-25 05:00 | 170 | 170
2016-09-25 05:30 | 172 | 172
2016-09-25 06:00 | 181 | 181
2016-09-25 06:30 | 187 | 187
2016-09-25 07:00 | 198 | 198
2016-09-25 07:30 | 214 | 214
2016-09-25 08:00 | 222 | 222
2016-09-25 08:30 | 229 | 229
2016-09-25 09:00 | 223 | 223
2016-09-25 09:30 | 219 | 219
2016-09-25 10:00 | 209 | 208
2016-09-25 10:30 | 208 | 207
2016-09-25 11:00 | 213 | 212
2016-09-25 11:30 | 210 | 208
2016-09-25 12:00 | 201 | 200
2016-09-25 12:30 | 205 | 204
2016-09-25 13:00 | 203 | 202
2016-09-25 13:30 | 201 | 200
2016-09-25 14:00 | 206 | 205
2016-09-25 14:30 | 199 | 199
2016-09-25 15:00 | 205 | 204
2016-09-25 15:30 | 216 | 214
2016-09-25 16:00 | 223 | 222
2016-09-25 16:30 | 233 | 232
2016-09-25 17:00 | 242 | 242
2016-09-25 17:30 | 255 | 255
2016-09-25 18:00 | 267 | 267
2016-09-25 18:30 | 271 | 271
2016-09-25 19:00 | 264 | 264
2016-09-25 19:30 | 257 | 257
2016-09-25 20:00 | 252 | 250
2016-09-25 20:30 | 245 | 244
2016-09-25 21:00 | 240 | 239
2016-09-25 21:30 | 231 | 230
2016-09-25 22:00 | 220 | 220
2016-09-25 22:30 | 219 | 219
2016-09-25 23:00 | 206 | 206
2016-09-25 23:30 | 196 | 196
2016-09-26 | 181 | 181
2016-09-26 00:30 | 178 | 178
2016-09-26 01:00 | 175 | 175
2016-09-26 01:30 | 172 | 172
2016-09-26 02:00 | 172 | 172
2016-09-26 02:30 | 171 | 171
2016-09-26 03:00 | 171 | 171
2016-09-26 03:30 | 174 | 174
2016-09-26 04:00 | 175 | 175
2016-09-26 04:30 | 184 | 184
2016-09-26 05:00 | 185 | 185
2016-09-26 05:30 | 190 | 190
2016-09-26 06:00 | 204 | 204
2016-09-26 06:30 | 216 | 216
2016-09-26 07:00 | 230 | 230
2016-09-26 07:30 | 239 | 239
2016-09-26 08:00 | 237 | 237
2016-09-26 08:30 | 237 | 236
2016-09-26 09:00 | 232 | 231
2016-09-26 09:30 | 226 | 225
2016-09-26 10:00 | 227 | 226
2016-09-26 10:30 | 220 | 219
2016-09-26 11:00 | 216 | 215
2016-09-26 11:30 | 216 | 214
2016-09-26 12:00 | 214 | 213
2016-09-26 12:30 | 214 | 212
2016-09-26 13:00 | 217 | 216
2016-09-26 13:30 | 219 | 218
2016-09-26 14:00 | 221 | 220
2016-09-26 14:30 | 222 | 221
2016-09-26 15:00 | 226 | 225
2016-09-26 15:30 | 232 | 232
2016-09-26 16:00 | 241 | 241
2016-09-26 16:30 | 258 | 258
2016-09-26 17:00 | 267 | 267
2016-09-26 17:30 | 276 | 276
2016-09-26 18:00 | 287 | 287
2016-09-26 18:30 | 286 | 286
2016-09-26 19:00 | 278 | 278
2016-09-26 19:30 | 274 | 274
2016-09-26 20:00 | 271 | 271
2016-09-26 20:30 | 264 | 264
2016-09-26 21:00 | 248 | 248
2016-09-26 21:30 | 237 | 237
2016-09-26 22:00 | 229 | 229
2016-09-26 22:30 | 223 | 222
2016-09-26 23:00 | 214 | 214
2016-09-26 23:30 | 201 | 201
2016-09-27 | 186 | 186
2016-09-27 00:30 | 179 | 179
2016-09-27 01:00 | 178 | 178
2016-09-27 01:30 | 176 | 176
2016-09-27 02:00 | 174 | 174
2016-09-27 02:30 | 169 | 169
2016-09-27 03:00 | 170 | 170
2016-09-27 03:30 | 174 | 174
2016-09-27 04:00 | 178 | 178
2016-09-27 04:30 | 179 | 179
2016-09-27 05:00 | 186 | 186
2016-09-27 05:30 | 190 | 190
2016-09-27 06:00 | 210 | 209
2016-09-27 06:30 | 231 | 230
2016-09-27 07:00 | 238 | 238
2016-09-27 07:30 | 226 | 225
2016-09-27 08:00 | 227 | 226
2016-09-27 08:30 | 224 | 222
2016-09-27 09:00 | 207 | 205
2016-09-27 09:30 | 205 | 202
2016-09-27 10:00 | 202 | 199
2016-09-27 10:30 | 193 | 191
2016-09-27 11:00 | 192 | 189
2016-09-27 11:30 | 190 | 187
2016-09-27 12:00 | 188 | 185
2016-09-27 12:30 | 188 | 185
2016-09-27 13:00 | 191 | 188
2016-09-27 13:30 | 196 | 193
2016-09-27 14:00 | 201 | 198
2016-09-27 14:30 | 207 | 205
2016-09-27 15:00 | 215 | 214
2016-09-27 15:30 | 223 | 223
2016-09-27 16:00 | 234 | 233
2016-09-27 16:30 | 255 | 255
2016-09-27 17:00 | 260 | 259
2016-09-27 17:30 | 269 | 268
2016-09-27 18:00 | 282 | 282
2016-09-27 18:30 | 287 | 287
2016-09-27 19:00 | 283 | 283
2016-09-27 19:30 | 280 | 280
2016-09-27 20:00 | 274 | 273
2016-09-27 20:30 | 265 | 265
2016-09-27 21:00 | 255 | 254
2016-09-27 21:30 | 239 | 239
2016-09-27 22:00 | 227 | 227
2016-09-27 22:30 | 225 | 225
2016-09-27 23:00 | 210 | 210
2016-09-27 23:30 | 199 | 199
2016-09-28 | 188 | 188
2016-09-28 00:30 | 176 | 176
2016-09-28 01:00 | 169 | 169
2016-09-28 01:30 | 167 | 167
2016-09-28 02:00 | 164 | 164
2016-09-28 02:30 | 163 | 162
2016-09-28 03:00 | 163 | 163
2016-09-28 03:30 | 165 | 165
2016-09-28 04:00 | 167 | 167
2016-09-28 04:30 | 170 | 170
2016-09-28 05:00 | 175 | 175
2016-09-28 05:30 | 184 | 184
2016-09-28 06:00 | 200 | 200
2016-09-28 06:30 | 220 | 220
2016-09-28 07:00 | 229 | 228
2016-09-28 07:30 | 218 | 218
2016-09-28 08:00 | 215 | 215
2016-09-28 08:30 | 212 | 212
2016-09-28 09:00 | 209 | 209
2016-09-28 09:30 | 205 | 205
2016-09-28 10:00 | 203 | 203
2016-09-28 10:30 | 199 | 199
2016-09-28 11:00 | 196 | 196
2016-09-28 11:30 | 192 | 192
2016-09-28 12:00 | 191 | 191
2016-09-28 12:30 | 191 | 191
2016-09-28 13:00 | 193 | 193
2016-09-28 13:30 | 198 | 198
2016-09-28 14:00 | 203 | 203
2016-09-28 14:30 | 211 | 211
2016-09-28 15:00 | 219 | 219
2016-09-28 15:30 | 228 | 228
2016-09-28 16:00 | 235 | 235
2016-09-28 16:30 | 232 | 232
2016-09-28 17:00 | 239 | 239
2016-09-28 17:30 | 243 | 243
2016-09-28 18:00 | 253 | 253
2016-09-28 18:30 | 253 | 253
2016-09-28 19:00 | 250 | 250
2016-09-28 19:30 | 254 | 254
2016-09-28 20:00 | 248 | 248
2016-09-28 20:30 | 237 | 237
2016-09-28 21:00 | 222 | 222
2016-09-28 21:30 | 225 | 224
2016-09-28 22:00 | 225 | 225
2016-09-28 22:30 | 215 | 215
2016-09-28 23:00 | 198 | 198
2016-09-28 23:30 | 194 | 194
2016-09-29 | 176 | 176
2016-09-29 00:30 | 167 | 167
2016-09-29 01:00 | 162 | 162
2016-09-29 01:30 | 162 | 162
2016-09-29 02:00 | 161 | 161
2016-09-29 02:30 | 160 | 160
2016-09-29 03:00 | 160 | 160
2016-09-29 03:30 | 152 | 152
2016-09-29 04:00 | 164 | 164
2016-09-29 04:30 | 169 | 169
2016-09-29 05:00 | 175 | 175
2016-09-29 05:30 | 180 | 180
2016-09-29 06:00 | 198 | 198
2016-09-29 06:30 | 223 | 223
2016-09-29 07:00 | 241 | 240
2016-09-29 07:30 | 255 | 255
2016-09-29 08:00 | 261 | 261
2016-09-29 08:30 | 261 | 260
2016-09-29 09:00 | 255 | 254
2016-09-29 09:30 | 262 | 261
2016-09-29 10:00 | 255 | 254
2016-09-29 10:30 | 239 | 239
2016-09-29 11:00 | 244 | 244
2016-09-29 11:30 | 250 | 250
2016-09-29 12:00 | 240 | 240
2016-09-29 12:30 | 237 | 237
2016-09-29 13:00 | 231 | 231
2016-09-29 13:30 | 233 | 233
2016-09-29 14:00 | 234 | 234
2016-09-29 14:30 | 240 | 240
2016-09-29 15:00 | 227 | 227
2016-09-29 15:30 | 241 | 241
2016-09-29 16:00 | 246 | 246
2016-09-29 16:30 | 255 | 254
2016-09-29 17:00 | 257 | 257
2016-09-29 17:30 | 266 | 266
2016-09-29 18:00 | 275 | 274
2016-09-29 18:30 | 282 | 282
2016-09-29 19:00 | 274 | 273
2016-09-29 19:30 | 270 | 270
2016-09-29 20:00 | 269 | 269
2016-09-29 20:30 | 256 | 255
2016-09-29 21:00 | 246 | 245
2016-09-29 21:30 | 238 | 237
2016-09-29 22:00 | 240 | 239
2016-09-29 22:30 | 236 | 235
2016-09-29 23:00 | 209 | 209
2016-09-29 23:30 | 202 | 202
2016-09-30 | 187 | 187
2016-09-30 00:30 | 177 | 177
2016-09-30 01:00 | 175 | 175
2016-09-30 01:30 | 163 | 163
2016-09-30 02:00 | 147 | 147
2016-09-30 02:30 | 166 | 165
2016-09-30 03:00 | 166 | 165
2016-09-30 03:30 | 154 | 153
2016-09-30 04:00 | 143 | 143
2016-09-30 04:30 | 155 | 154
2016-09-30 05:00 | 178 | 178
2016-09-30 05:30 | 184 | 184
2016-09-30 06:00 | 198 | 197
2016-09-30 06:30 | 207 | 206
2016-09-30 07:00 | 217 | 216
2016-09-30 07:30 | 226 | 226
2016-09-30 08:00 | 225 | 225
2016-09-30 08:30 | 224 | 222
2016-09-30 09:00 | 224 | 222
2016-09-30 09:30 | 220 | 217
2016-09-30 10:00 | 217 | 214
2016-09-30 10:30 | 211 | 208
2016-09-30 11:00 | 204 | 201
2016-09-30 11:30 | 199 | 197
2016-09-30 12:00 | 197 | 194
2016-09-30 12:30 | 194 | 192
2016-09-30 13:00 | 193 | 190
2016-09-30 13:30 | 190 | 187
2016-09-30 14:00 | 183 | 179
2016-09-30 14:30 | 205 | 202
2016-09-30 15:00 | 209 | 207
2016-09-30 15:30 | 214 | 212
2016-09-30 16:00 | 223 | 221
2016-09-30 16:30 | 234 | 234
2016-09-30 17:00 | 234 | 234
2016-09-30 17:30 | 242 | 242
2016-09-30 18:00 | 254 | 254
2016-09-30 18:30 | 256 | 256
2016-09-30 19:00 | 248 | 248
2016-09-30 19:30 | 246 | 246
2016-09-30 20:00 | 241 | 239
2016-09-30 20:30 | 234 | 232
2016-09-30 21:00 | 217 | 216
2016-09-30 21:30 | 214 | 213
2016-09-30 22:00 | 214 | 214
2016-09-30 22:30 | 208 | 208
2016-09-30 23:00 | 202 | 202
2016-09-30 23:30 | 190 | 190
2016-10-01 | 177 | 177
2016-10-01 00:30 | 135 | 135
2016-10-01 01:00 | 141 | 141
2016-10-01 01:30 | 148 | 148
2016-10-01 02:00 | 150 | 150
2016-10-01 02:30 | 150 | 149
2016-10-01 03:00 | 150 | 149
2016-10-01 03:30 | 150 | 150
2016-10-01 04:00 | 150 | 150
2016-10-01 04:30 | 151 | 151
2016-10-01 05:00 | 152 | 152
2016-10-01 05:30 | 157 | 157
2016-10-01 06:00 | 164 | 164
2016-10-01 06:30 | 171 | 171
2016-10-01 07:00 | 179 | 178
2016-10-01 07:30 | 188 | 186
2016-10-01 08:00 | 195 | 193
2016-10-01 08:30 | 198 | 195
2016-10-01 09:00 | 201 | 199
2016-10-01 09:30 | 188 | 187
2016-10-01 10:00 | 178 | 176
2016-10-01 10:30 | 191 | 190
2016-10-01 11:00 | 189 | 187
2016-10-01 11:30 | 165 | 163
2016-10-01 12:00 | 175 | 173
2016-10-01 12:30 | 186 | 185
2016-10-01 13:00 | 182 | 181
2016-10-01 13:30 | 182 | 181
2016-10-01 14:00 | 178 | 176
2016-10-01 14:30 | 160 | 157
2016-10-01 15:00 | 191 | 189
2016-10-01 15:30 | 211 | 209
2016-10-01 16:00 | 192 | 190
2016-10-01 16:30 | 217 | 216
2016-10-01 17:00 | 204 | 202
2016-10-01 17:30 | 203 | 202
2016-10-01 18:00 | 231 | 231
2016-10-01 18:30 | 239 | 239
2016-10-01 19:00 | 233 | 233
2016-10-01 19:30 | 230 | 230
2016-10-01 20:00 | 229 | 229
2016-10-01 20:30 | 197 | 197
2016-10-01 21:00 | 186 | 185
2016-10-01 21:30 | 180 | 180
2016-10-01 22:00 | 187 | 186
2016-10-01 22:30 | 197 | 196
2016-10-01 23:00 | 190 | 190
2016-10-01 23:30 | 176 | 176
2016-10-02 | 164 | 164
2016-10-02 00:30 | 155 | 155
2016-10-02 01:00 | 137 | 137
2016-10-02 01:30 | 121 | 120
2016-10-02 02:00 | 134 | 134
2016-10-02 02:30 | 124 | 124
2016-10-02 03:00 | 130 | 130
2016-10-02 03:30 | 137 | 137
2016-10-02 04:00 | 149 | 148
2016-10-02 04:30 | 114 | 114
2016-10-02 05:00 | 134 | 134
2016-10-02 05:30 | 149 | 149
2016-10-02 06:00 | 152 | 152
2016-10-02 06:30 | 147 | 147
2016-10-02 07:00 | 144 | 143
2016-10-02 07:30 | 138 | 137
2016-10-02 08:00 | 160 | 159
2016-10-02 08:30 | 182 | 181
2016-10-02 09:00 | 186 | 183
2016-10-02 09:30 | 160 | 156
2016-10-02 10:00 | 145 | 141
2016-10-02 10:30 | 151 | 147
2016-10-02 11:00 | 169 | 165
2016-10-02 11:30 | 159 | 155
2016-10-02 12:00 | 157 | 153
2016-10-02 12:30 | 157 | 153
2016-10-02 13:00 | 159 | 155
2016-10-02 13:30 | 157 | 153
2016-10-02 14:00 | 185 | 180
2016-10-02 14:30 | 195 | 190
2016-10-02 15:00 | 200 | 199
2016-10-02 15:30 | 207 | 207
2016-10-02 16:00 | 198 | 198
2016-10-02 16:30 | 195 | 195
2016-10-02 17:00 | 218 | 218
2016-10-02 17:30 | 219 | 219
2016-10-02 18:00 | 215 | 215
2016-10-02 18:30 | 216 | 216
2016-10-02 19:00 | 209 | 208
2016-10-02 19:30 | 219 | 219
2016-10-02 20:00 | 212 | 212
2016-10-02 20:30 | 207 | 206
2016-10-02 21:00 | 202 | 201
2016-10-02 21:30 | 191 | 190
2016-10-02 22:00 | 183 | 183
2016-10-02 22:30 | 188 | 188
2016-10-02 23:00 | 169 | 169
2016-10-02 23:30 | 177 | 177
2016-10-03 | 163 | 162
2016-10-03 00:30 | 148 | 148
2016-10-03 01:00 | 143 | 143
2016-10-03 01:30 | 145 | 145
2016-10-03 02:00 | 140 | 140
2016-10-03 02:30 | 134 | 134
2016-10-03 03:00 | 113 | 113
2016-10-03 03:30 | 122 | 122
2016-10-03 04:00 | 122 | 122
2016-10-03 04:30 | 144 | 144
2016-10-03 05:00 | 148 | 148
2016-10-03 05:30 | 151 | 151
2016-10-03 06:00 | 145 | 145
2016-10-03 06:30 | 167 | 167
2016-10-03 07:00 | 174 | 174
2016-10-03 07:30 | 195 | 195
2016-10-03 08:00 | 205 | 204
2016-10-03 08:30 | 208 | 207
2016-10-03 09:00 | 215 | 215
2016-10-03 09:30 | 214 | 214
2016-10-03 10:00 | 221 | 221
2016-10-03 10:30 | 222 | 222
2016-10-03 11:00 | 226 | 226
2016-10-03 11:30 | 220 | 220
2016-10-03 12:00 | 216 | 216
2016-10-03 12:30 | 221 | 221
2016-10-03 13:00 | 214 | 214
2016-10-03 13:30 | 215 | 215
2016-10-03 14:00 | 219 | 219
2016-10-03 14:30 | 219 | 219
2016-10-03 15:00 | 216 | 216
2016-10-03 15:30 | 222 | 222
2016-10-03 16:00 | 223 | 223
2016-10-03 16:30 | 238 | 238
2016-10-03 17:00 | 241 | 241
2016-10-03 17:30 | 253 | 252
2016-10-03 18:00 | 255 | 255
2016-10-03 18:30 | 246 | 246
2016-10-03 19:00 | 239 | 239
2016-10-03 19:30 | 228 | 228
2016-10-03 20:00 | 221 | 221
2016-10-03 20:30 | 208 | 208
2016-10-03 21:00 | 203 | 203
2016-10-03 21:30 | 204 | 204
2016-10-03 22:00 | 208 | 208
2016-10-03 22:30 | 210 | 210
2016-10-03 23:00 | 188 | 188
2016-10-03 23:30 | 188 | 187
2016-10-04 | 167 | 166
2016-10-04 00:30 | 139 | 139
2016-10-04 01:00 | 144 | 144
2016-10-04 01:30 | 156 | 156
2016-10-04 02:00 | 130 | 130
2016-10-04 02:30 | 125 | 125
2016-10-04 03:00 | 118 | 118
2016-10-04 03:30 | 122 | 122
2016-10-04 04:00 | 129 | 129
2016-10-04 04:30 | 153 | 153
2016-10-04 05:00 | 152 | 152
2016-10-04 05:30 | 187 | 187
2016-10-04 06:00 | 202 | 202
2016-10-04 06:30 | 212 | 212
2016-10-04 07:00 | 217 | 216
2016-10-04 07:30 | 218 | 216
2016-10-04 08:00 | 212 | 210
2016-10-04 08:30 | 204 | 202
2016-10-04 09:00 | 200 | 197
2016-10-04 09:30 | 196 | 192
2016-10-04 10:00 | 194 | 190
2016-10-04 10:30 | 189 | 187
2016-10-04 11:00 | 186 | 184
2016-10-04 11:30 | 186 | 184
2016-10-04 12:00 | 184 | 183
2016-10-04 12:30 | 186 | 184
2016-10-04 13:00 | 188 | 187
2016-10-04 13:30 | 194 | 192
2016-10-04 14:00 | 199 | 197
2016-10-04 14:30 | 205 | 203
2016-10-04 15:00 | 211 | 210
2016-10-04 15:30 | 216 | 215
2016-10-04 16:00 | 211 | 210
2016-10-04 16:30 | 224 | 224
2016-10-04 17:00 | 242 | 241
2016-10-04 17:30 | 251 | 251
2016-10-04 18:00 | 256 | 256
2016-10-04 18:30 | 268 | 268
2016-10-04 19:00 | 258 | 258
2016-10-04 19:30 | 256 | 256
2016-10-04 20:00 | 245 | 244
2016-10-04 20:30 | 237 | 236
2016-10-04 21:00 | 224 | 223
2016-10-04 21:30 | 213 | 213
2016-10-04 22:00 | 215 | 215
2016-10-04 22:30 | 205 | 205
2016-10-04 23:00 | 192 | 192
2016-10-04 23:30 | 165 | 165
2016-10-05 | 154 | 154
2016-10-05 00:30 | 145 | 145
2016-10-05 01:00 | 154 | 154
2016-10-05 01:30 | 150 | 150
2016-10-05 02:00 | 148 | 148
2016-10-05 02:30 | 153 | 153
2016-10-05 03:00 | 152 | 152
2016-10-05 03:30 | 153 | 153
2016-10-05 04:00 | 160 | 160
2016-10-05 04:30 | 167 | 167
2016-10-05 05:00 | 179 | 179
2016-10-05 05:30 | 191 | 191
2016-10-05 06:00 | 207 | 207
2016-10-05 06:30 | 208 | 208
2016-10-05 07:00 | 216 | 216
2016-10-05 07:30 | 217 | 217
2016-10-05 08:00 | 212 | 212
2016-10-05 08:30 | 206 | 206
2016-10-05 09:00 | 203 | 203
2016-10-05 09:30 | 200 | 199
2016-10-05 10:00 | 199 | 198
2016-10-05 10:30 | 194 | 194
2016-10-05 11:00 | 193 | 192
2016-10-05 11:30 | 194 | 193
2016-10-05 12:00 | 194 | 193
2016-10-05 12:30 | 193 | 193
2016-10-05 13:00 | 195 | 195
2016-10-05 13:30 | 200 | 200
2016-10-05 14:00 | 205 | 205
2016-10-05 14:30 | 210 | 210
2016-10-05 15:00 | 217 | 216
2016-10-05 15:30 | 228 | 227
2016-10-05 16:00 | 242 | 242
2016-10-05 16:30 | 252 | 252
2016-10-05 17:00 | 252 | 252
2016-10-05 17:30 | 261 | 261
2016-10-05 18:00 | 272 | 272
2016-10-05 18:30 | 280 | 280
2016-10-05 19:00 | 278 | 277
2016-10-05 19:30 | 278 | 277
2016-10-05 20:00 | 272 | 270
2016-10-05 20:30 | 256 | 253
2016-10-05 21:00 | 239 | 237
2016-10-05 21:30 | 226 | 224
2016-10-05 22:00 | 227 | 227
2016-10-05 22:30 | 227 | 227
2016-10-05 23:00 | 212 | 212
2016-10-05 23:30 | 199 | 199
2016-10-06 | 184 | 184
2016-10-06 00:30 | 174 | 174
2016-10-06 01:00 | 167 | 166
2016-10-06 01:30 | 162 | 161
2016-10-06 02:00 | 158 | 158
2016-10-06 02:30 | 157 | 156
2016-10-06 03:00 | 157 | 156
2016-10-06 03:30 | 158 | 157
2016-10-06 04:00 | 163 | 162
2016-10-06 04:30 | 169 | 168
2016-10-06 05:00 | 181 | 180
2016-10-06 05:30 | 194 | 193
2016-10-06 06:00 | 211 | 210
2016-10-06 06:30 | 211 | 210
2016-10-06 07:00 | 218 | 217
2016-10-06 07:30 | 217 | 217
2016-10-06 08:00 | 211 | 211
2016-10-06 08:30 | 204 | 204
2016-10-06 09:00 | 200 | 200
2016-10-06 09:30 | 195 | 195
2016-10-06 10:00 | 194 | 194
2016-10-06 10:30 | 191 | 191
2016-10-06 11:00 | 188 | 188
2016-10-06 11:30 | 189 | 189
2016-10-06 12:00 | 189 | 189
2016-10-06 12:30 | 191 | 191
2016-10-06 13:00 | 194 | 194
2016-10-06 13:30 | 199 | 199
2016-10-06 14:00 | 207 | 207
2016-10-06 14:30 | 194 | 194
2016-10-06 15:00 | 211 | 211
2016-10-06 15:30 | 229 | 229
2016-10-06 16:00 | 236 | 236
2016-10-06 16:30 | 256 | 256
2016-10-06 17:00 | 263 | 263
2016-10-06 17:30 | 261 | 261
2016-10-06 18:00 | 244 | 244
2016-10-06 18:30 | 251 | 251
2016-10-06 19:00 | 246 | 245
2016-10-06 19:30 | 263 | 263
2016-10-06 20:00 | 243 | 243
2016-10-06 20:30 | 229 | 229
2016-10-06 21:00 | 231 | 231
2016-10-06 21:30 | 224 | 224
2016-10-06 22:00 | 224 | 224
2016-10-06 22:30 | 223 | 223
2016-10-06 23:00 | 205 | 205
2016-10-06 23:30 | 187 | 186
2016-10-07 | 174 | 173
2016-10-07 00:30 | 167 | 165
2016-10-07 01:00 | 163 | 161
2016-10-07 01:30 | 155 | 153
2016-10-07 02:00 | 152 | 150
2016-10-07 02:30 | 151 | 150
2016-10-07 03:00 | 151 | 150
2016-10-07 03:30 | 152 | 150
2016-10-07 04:00 | 161 | 160
2016-10-07 04:30 | 166 | 165
2016-10-07 05:00 | 176 | 175
2016-10-07 05:30 | 186 | 185
2016-10-07 06:00 | 203 | 203
2016-10-07 06:30 | 208 | 207
2016-10-07 07:00 | 215 | 214
2016-10-07 07:30 | 215 | 215
2016-10-07 08:00 | 228 | 228
2016-10-07 08:30 | 224 | 224
2016-10-07 09:00 | 222 | 222
2016-10-07 09:30 | 218 | 218
2016-10-07 10:00 | 217 | 217
2016-10-07 10:30 | 236 | 236
2016-10-07 11:00 | 237 | 236
2016-10-07 11:30 | 234 | 234
2016-10-07 12:00 | 231 | 231
2016-10-07 12:30 | 226 | 226
2016-10-07 13:00 | 233 | 233
2016-10-07 13:30 | 228 | 228
2016-10-07 14:00 | 194 | 194
2016-10-07 14:30 | 189 | 189
2016-10-07 15:00 | 199 | 199
2016-10-07 15:30 | 217 | 217
2016-10-07 16:00 | 230 | 230
2016-10-07 16:30 | 229 | 229
2016-10-07 17:00 | 238 | 238
2016-10-07 17:30 | 239 | 239
2016-10-07 18:00 | 240 | 240
2016-10-07 18:30 | 226 | 226
2016-10-07 19:00 | 241 | 241
2016-10-07 19:30 | 239 | 239
2016-10-07 20:00 | 224 | 224
2016-10-07 20:30 | 235 | 235
2016-10-07 21:00 | 223 | 222
2016-10-07 21:30 | 220 | 220
2016-10-07 22:00 | 216 | 216
2016-10-07 22:30 | 205 | 205
2016-10-07 23:00 | 198 | 198
2016-10-07 23:30 | 186 | 186
2016-10-08 | 181 | 180
2016-10-08 00:30 | 172 | 171
2016-10-08 01:00 | 166 | 165
2016-10-08 01:30 | 167 | 166
2016-10-08 02:00 | 166 | 165
2016-10-08 02:30 | 164 | 163
2016-10-08 03:00 | 164 | 163
2016-10-08 03:30 | 163 | 162
2016-10-08 04:00 | 163 | 161
2016-10-08 04:30 | 163 | 162
2016-10-08 05:00 | 164 | 163
2016-10-08 05:30 | 170 | 168
2016-10-08 06:00 | 175 | 174
2016-10-08 06:30 | 182 | 181
2016-10-08 07:00 | 195 | 195
2016-10-08 07:30 | 202 | 202
2016-10-08 08:00 | 215 | 215
2016-10-08 08:30 | 208 | 208
2016-10-08 09:00 | 206 | 206
2016-10-08 09:30 | 206 | 205
2016-10-08 10:00 | 210 | 210
2016-10-08 10:30 | 197 | 197
2016-10-08 11:00 | 197 | 197
2016-10-08 11:30 | 198 | 198
2016-10-08 12:00 | 195 | 195
2016-10-08 12:30 | 193 | 193
2016-10-08 13:00 | 199 | 199
2016-10-08 13:30 | 213 | 213
2016-10-08 14:00 | 225 | 225
2016-10-08 14:30 | 217 | 217
2016-10-08 15:00 | 219 | 219
2016-10-08 15:30 | 226 | 226
2016-10-08 16:00 | 232 | 232
2016-10-08 16:30 | 239 | 239
2016-10-08 17:00 | 244 | 244
2016-10-08 17:30 | 221 | 221
2016-10-08 18:00 | 228 | 228
2016-10-08 18:30 | 234 | 233
2016-10-08 19:00 | 226 | 224
2016-10-08 19:30 | 219 | 219
2016-10-08 20:00 | 235 | 235
2016-10-08 20:30 | 227 | 227
2016-10-08 21:00 | 220 | 220
2016-10-08 21:30 | 212 | 212
2016-10-08 22:00 | 199 | 198
2016-10-08 22:30 | 182 | 182
2016-10-08 23:00 | 173 | 173
2016-10-08 23:30 | 154 | 154
2016-10-09 | 155 | 155
2016-10-09 00:30 | 147 | 147
2016-10-09 01:00 | 140 | 140
2016-10-09 01:30 | 135 | 135
2016-10-09 02:00 | 132 | 132
2016-10-09 02:30 | 130 | 130
2016-10-09 03:00 | 129 | 129
2016-10-09 03:30 | 129 | 129
2016-10-09 04:00 | 130 | 130
2016-10-09 04:30 | 131 | 131
2016-10-09 05:00 | 132 | 132
2016-10-09 05:30 | 135 | 135
2016-10-09 06:00 | 140 | 139
2016-10-09 06:30 | 145 | 144
2016-10-09 07:00 | 154 | 154
2016-10-09 07:30 | 163 | 163
2016-10-09 08:00 | 180 | 180
2016-10-09 08:30 | 188 | 188
2016-10-09 09:00 | 189 | 189
2016-10-09 09:30 | 192 | 192
2016-10-09 10:00 | 192 | 192
2016-10-09 10:30 | 212 | 212
2016-10-09 11:00 | 190 | 189
2016-10-09 11:30 | 199 | 199
2016-10-09 12:00 | 200 | 199
2016-10-09 12:30 | 199 | 198
2016-10-09 13:00 | 194 | 193
2016-10-09 13:30 | 197 | 196
2016-10-09 14:00 | 199 | 198
2016-10-09 14:30 | 199 | 198
2016-10-09 15:00 | 199 | 198
2016-10-09 15:30 | 201 | 200
2016-10-09 16:00 | 205 | 204
2016-10-09 16:30 | 213 | 213
2016-10-09 17:00 | 227 | 226
2016-10-09 17:30 | 229 | 229
2016-10-09 18:00 | 224 | 224
2016-10-09 18:30 | 224 | 224
2016-10-09 19:00 | 215 | 215
2016-10-09 19:30 | 213 | 213
2016-10-09 20:00 | 207 | 207
2016-10-09 20:30 | 196 | 196
2016-10-09 21:00 | 190 | 190
2016-10-09 21:30 | 187 | 187
2016-10-09 22:00 | 189 | 189
2016-10-09 22:30 | 176 | 176
2016-10-09 23:00 | 169 | 168
2016-10-09 23:30 | 162 | 161
2016-10-10 | 138 | 137
2016-10-10 00:30 | 138 | 136
2016-10-10 01:00 | 126 | 125
2016-10-10 01:30 | 120 | 118
2016-10-10 02:00 | 113 | 111
2016-10-10 02:30 | 106 | 104
2016-10-10 03:00 | 103 | 101
2016-10-10 03:30 | 113 | 111
2016-10-10 04:00 | 124 | 122
2016-10-10 04:30 | 130 | 129
2016-10-10 05:00 | 141 | 140
2016-10-10 05:30 | 153 | 152
2016-10-10 06:00 | 180 | 180
2016-10-10 06:30 | 187 | 187
2016-10-10 07:00 | 204 | 204
2016-10-10 07:30 | 231 | 231
2016-10-10 08:00 | 234 | 233
2016-10-10 08:30 | 228 | 228
2016-10-10 09:00 | 220 | 220
2016-10-10 09:30 | 217 | 217
2016-10-10 10:00 | 216 | 216
2016-10-10 10:30 | 214 | 214
2016-10-10 11:00 | 213 | 213
2016-10-10 11:30 | 219 | 219
2016-10-10 12:00 | 219 | 218
2016-10-10 12:30 | 229 | 228
2016-10-10 13:00 | 228 | 227
2016-10-10 13:30 | 225 | 225
2016-10-10 14:00 | 232 | 231
2016-10-10 14:30 | 234 | 234
2016-10-10 15:00 | 244 | 243
2016-10-10 15:30 | 248 | 247
2016-10-10 16:00 | 256 | 255
2016-10-10 16:30 | 265 | 264
2016-10-10 17:00 | 269 | 268
2016-10-10 17:30 | 274 | 272
2016-10-10 18:00 | 284 | 283
2016-10-10 18:30 | 293 | 290
2016-10-10 19:00 | 283 | 279
2016-10-10 19:30 | 277 | 274
2016-10-10 20:00 | 270 | 267
2016-10-10 20:30 | 255 | 253
2016-10-10 21:00 | 244 | 243
2016-10-10 21:30 | 228 | 226
2016-10-10 22:00 | 208 | 207
2016-10-10 22:30 | 213 | 213
2016-10-10 23:00 | 196 | 195
2016-10-10 23:30 | 192 | 190
2016-10-11 | 165 | 164
2016-10-11 00:30 | 152 | 151
2016-10-11 01:00 | 153 | 152
2016-10-11 01:30 | 138 | 136
2016-10-11 02:00 | 135 | 133
2016-10-11 02:30 | 144 | 143
2016-10-11 03:00 | 144 | 143
2016-10-11 03:30 | 145 | 144
2016-10-11 04:00 | 158 | 157
2016-10-11 04:30 | 174 | 173
2016-10-11 05:00 | 187 | 186
2016-10-11 05:30 | 207 | 206
2016-10-11 06:00 | 233 | 232
2016-10-11 06:30 | 243 | 242
2016-10-11 07:00 | 249 | 248
2016-10-11 07:30 | 246 | 246
2016-10-11 08:00 | 243 | 243
2016-10-11 08:30 | 246 | 246
2016-10-11 09:00 | 250 | 250
2016-10-11 09:30 | 250 | 249
2016-10-11 10:00 | 258 | 257
2016-10-11 10:30 | 256 | 255
2016-10-11 11:00 | 250 | 248
2016-10-11 11:30 | 248 | 247
2016-10-11 12:00 | 245 | 244
2016-10-11 12:30 | 246 | 244
2016-10-11 13:00 | 252 | 250
2016-10-11 13:30 | 257 | 255
2016-10-11 14:00 | 261 | 258
2016-10-11 14:30 | 257 | 255
2016-10-11 15:00 | 226 | 223
2016-10-11 15:30 | 232 | 230
2016-10-11 16:00 | 255 | 252
2016-10-11 16:30 | 277 | 273
2016-10-11 17:00 | 269 | 265
2016-10-11 17:30 | 272 | 268
2016-10-11 18:00 | 276 | 274
2016-10-11 18:30 | 284 | 282
2016-10-11 19:00 | 283 | 280
2016-10-11 19:30 | 283 | 280
2016-10-11 20:00 | 277 | 273
2016-10-11 20:30 | 257 | 257
2016-10-11 21:00 | 247 | 247
2016-10-11 21:30 | 237 | 236
2016-10-11 22:00 | 238 | 238
2016-10-11 22:30 | 232 | 231
2016-10-11 23:00 | 202 | 201
2016-10-11 23:30 | 200 | 198
2016-10-12 | 191 | 189
2016-10-12 00:30 | 182 | 181
2016-10-12 01:00 | 173 | 173
2016-10-12 01:30 | 167 | 166
2016-10-12 02:00 | 166 | 165
2016-10-12 02:30 | 163 | 162
2016-10-12 03:00 | 163 | 162
2016-10-12 03:30 | 165 | 164
2016-10-12 04:00 | 170 | 169
2016-10-12 04:30 | 182 | 181
2016-10-12 05:00 | 192 | 191
2016-10-12 05:30 | 203 | 203
2016-10-12 06:00 | 223 | 223
2016-10-12 06:30 | 237 | 237
2016-10-12 07:00 | 246 | 246
2016-10-12 07:30 | 246 | 244
2016-10-12 08:00 | 248 | 247
2016-10-12 08:30 | 247 | 246
2016-10-12 09:00 | 246 | 245
2016-10-12 09:30 | 244 | 243
2016-10-12 10:00 | 243 | 242
2016-10-12 10:30 | 239 | 239
2016-10-12 11:00 | 241 | 241
2016-10-12 11:30 | 242 | 241
2016-10-12 12:00 | 236 | 235
2016-10-12 12:30 | 232 | 231
2016-10-12 13:00 | 234 | 233
2016-10-12 13:30 | 241 | 241
2016-10-12 14:00 | 239 | 238
2016-10-12 14:30 | 240 | 239
2016-10-12 15:00 | 245 | 245
2016-10-12 15:30 | 253 | 253
2016-10-12 16:00 | 257 | 256
2016-10-12 16:30 | 263 | 262
2016-10-12 17:00 | 274 | 273
2016-10-12 17:30 | 283 | 282
2016-10-12 18:00 | 282 | 282
2016-10-12 18:30 | 284 | 283
2016-10-12 19:00 | 277 | 276
2016-10-12 19:30 | 278 | 277
2016-10-12 20:00 | 268 | 266
2016-10-12 20:30 | 254 | 251
2016-10-12 21:00 | 245 | 242
2016-10-12 21:30 | 235 | 233
2016-10-12 22:00 | 233 | 233
2016-10-12 22:30 | 236 | 236
2016-10-12 23:00 | 221 | 221
2016-10-12 23:30 | 207 | 207
2016-10-13 | 196 | 196
2016-10-13 00:30 | 186 | 185
2016-10-13 01:00 | 177 | 177
2016-10-13 01:30 | 172 | 171
2016-10-13 02:00 | 168 | 167
2016-10-13 02:30 | 166 | 165
2016-10-13 03:00 | 165 | 164
2016-10-13 03:30 | 168 | 167
2016-10-13 04:00 | 178 | 177
2016-10-13 04:30 | 186 | 186
2016-10-13 05:00 | 196 | 196
2016-10-13 05:30 | 213 | 213
2016-10-13 06:00 | 230 | 230
2016-10-13 06:30 | 247 | 246
2016-10-13 07:00 | 251 | 251
2016-10-13 07:30 | 249 | 249
2016-10-13 08:00 | 246 | 246
2016-10-13 08:30 | 245 | 245
2016-10-13 09:00 | 245 | 245
2016-10-13 09:30 | 241 | 240
2016-10-13 10:00 | 238 | 238
2016-10-13 10:30 | 240 | 240
2016-10-13 11:00 | 243 | 243
2016-10-13 11:30 | 240 | 240
2016-10-13 12:00 | 239 | 238
2016-10-13 12:30 | 229 | 228
2016-10-13 13:00 | 223 | 222
2016-10-13 13:30 | 224 | 222
2016-10-13 14:00 | 228 | 226
2016-10-13 14:30 | 236 | 234
2016-10-13 15:00 | 247 | 245
2016-10-13 15:30 | 250 | 248
2016-10-13 16:00 | 254 | 252
2016-10-13 16:30 | 263 | 261
2016-10-13 17:00 | 271 | 268
2016-10-13 17:30 | 275 | 272
2016-10-13 18:00 | 285 | 284
2016-10-13 18:30 | 290 | 289
2016-10-13 19:00 | 292 | 290
2016-10-13 19:30 | 286 | 286
2016-10-13 20:00 | 275 | 275
2016-10-13 20:30 | 258 | 258
2016-10-13 21:00 | 245 | 245
2016-10-13 21:30 | 231 | 231
2016-10-13 22:00 | 241 | 241
2016-10-13 22:30 | 241 | 241
2016-10-13 23:00 | 220 | 219
2016-10-13 23:30 | 206 | 205
2016-10-14 | 195 | 195
2016-10-14 00:30 | 187 | 186
2016-10-14 01:00 | 177 | 176
2016-10-14 01:30 | 170 | 169
2016-10-14 02:00 | 167 | 165
2016-10-14 02:30 | 165 | 164
2016-10-14 03:00 | 164 | 162
2016-10-14 03:30 | 166 | 165
2016-10-14 04:00 | 172 | 171
2016-10-14 04:30 | 180 | 179
2016-10-14 05:00 | 193 | 192
2016-10-14 05:30 | 208 | 208
2016-10-14 06:00 | 228 | 228
2016-10-14 06:30 | 250 | 248
2016-10-14 07:00 | 254 | 253
2016-10-14 07:30 | 250 | 249
2016-10-14 08:00 | 238 | 237
2016-10-14 08:30 | 224 | 222
2016-10-14 09:00 | 224 | 223
2016-10-14 09:30 | 220 | 219
2016-10-14 10:00 | 219 | 218
2016-10-14 10:30 | 217 | 217
2016-10-14 11:00 | 213 | 213
2016-10-14 11:30 | 204 | 204
2016-10-14 12:00 | 203 | 203
2016-10-14 12:30 | 205 | 205
2016-10-14 13:00 | 204 | 204
2016-10-14 13:30 | 206 | 206
2016-10-14 14:00 | 202 | 202
2016-10-14 14:30 | 206 | 206
2016-10-14 15:00 | 209 | 209
2016-10-14 15:30 | 216 | 216
2016-10-14 16:00 | 224 | 224
2016-10-14 16:30 | 230 | 230
2016-10-14 17:00 | 232 | 232
2016-10-14 17:30 | 236 | 236
2016-10-14 18:00 | 249 | 249
2016-10-14 18:30 | 261 | 261
2016-10-14 19:00 | 254 | 254
2016-10-14 19:30 | 248 | 248
2016-10-14 20:00 | 241 | 241
2016-10-14 20:30 | 235 | 235
2016-10-14 21:00 | 230 | 230
2016-10-14 21:30 | 222 | 222
2016-10-14 22:00 | 227 | 227
2016-10-14 22:30 | 232 | 232
2016-10-14 23:00 | 210 | 209
2016-10-14 23:30 | 182 | 181
2016-10-15 | 170 | 170
2016-10-15 00:30 | 170 | 170
2016-10-15 01:00 | 160 | 160
2016-10-15 01:30 | 144 | 143
2016-10-15 02:00 | 140 | 140
2016-10-15 02:30 | 140 | 140
2016-10-15 03:00 | 131 | 130
2016-10-15 03:30 | 150 | 150
2016-10-15 04:00 | 157 | 157
2016-10-15 04:30 | 136 | 136
2016-10-15 05:00 | 170 | 169
2016-10-15 05:30 | 170 | 169
2016-10-15 06:00 | 164 | 164
2016-10-15 06:30 | 191 | 191
2016-10-15 07:00 | 195 | 195
2016-10-15 07:30 | 198 | 198
2016-10-15 08:00 | 199 | 198
2016-10-15 08:30 | 197 | 196
2016-10-15 09:00 | 194 | 194
2016-10-15 09:30 | 192 | 192
2016-10-15 10:00 | 193 | 193
2016-10-15 10:30 | 189 | 189
2016-10-15 11:00 | 196 | 196
2016-10-15 11:30 | 185 | 185
2016-10-15 12:00 | 189 | 189
2016-10-15 12:30 | 188 | 188
2016-10-15 13:00 | 189 | 188
2016-10-15 13:30 | 190 | 190
2016-10-15 14:00 | 176 | 176
2016-10-15 14:30 | 178 | 178
2016-10-15 15:00 | 196 | 196
2016-10-15 15:30 | 207 | 207
2016-10-15 16:00 | 215 | 215
2016-10-15 16:30 | 225 | 225
2016-10-15 17:00 | 225 | 225
2016-10-15 17:30 | 226 | 226
2016-10-15 18:00 | 235 | 235
2016-10-15 18:30 | 244 | 243
2016-10-15 19:00 | 235 | 235
2016-10-15 19:30 | 230 | 230
2016-10-15 20:00 | 228 | 228
2016-10-15 20:30 | 220 | 220
2016-10-15 21:00 | 209 | 209
2016-10-15 21:30 | 208 | 208
2016-10-15 22:00 | 177 | 177
2016-10-15 22:30 | 192 | 192
2016-10-15 23:00 | 167 | 167
2016-10-15 23:30 | 151 | 150
2016-10-16 | 137 | 137
2016-10-16 00:30 | 139 | 138
2016-10-16 01:00 | 121 | 119
2016-10-16 01:30 | 115 | 113
2016-10-16 02:00 | 112 | 109
2016-10-16 02:30 | 109 | 107
2016-10-16 03:00 | 109 | 107
2016-10-16 03:30 | 109 | 107
2016-10-16 04:00 | 126 | 124
2016-10-16 04:30 | 115 | 113
2016-10-16 05:00 | 119 | 116
2016-10-16 05:30 | 125 | 123
2016-10-16 06:00 | 155 | 153
2016-10-16 06:30 | 166 | 165
2016-10-16 07:00 | 178 | 177
2016-10-16 07:30 | 180 | 180
2016-10-16 08:00 | 186 | 186
2016-10-16 08:30 | 190 | 189
2016-10-16 09:00 | 192 | 192
2016-10-16 09:30 | 188 | 188
2016-10-16 10:00 | 188 | 188
2016-10-16 10:30 | 185 | 184
2016-10-16 11:00 | 178 | 178
2016-10-16 11:30 | 177 | 177
2016-10-16 12:00 | 176 | 176
2016-10-16 12:30 | 170 | 169
2016-10-16 13:00 | 173 | 173
2016-10-16 13:30 | 179 | 179
2016-10-16 14:00 | 187 | 187
2016-10-16 14:30 | 194 | 193
2016-10-16 15:00 | 200 | 200
2016-10-16 15:30 | 207 | 207
2016-10-16 16:00 | 211 | 211
2016-10-16 16:30 | 225 | 225
2016-10-16 17:00 | 229 | 229
2016-10-16 17:30 | 239 | 239
2016-10-16 18:00 | 252 | 251
2016-10-16 18:30 | 257 | 257
2016-10-16 19:00 | 253 | 252
2016-10-16 19:30 | 248 | 247
2016-10-16 20:00 | 237 | 237
2016-10-16 20:30 | 221 | 221
2016-10-16 21:00 | 211 | 211
2016-10-16 21:30 | 205 | 205
2016-10-16 22:00 | 203 | 203
2016-10-16 22:30 | 203 | 203
2016-10-16 23:00 | 188 | 188
2016-10-16 23:30 | 177 | 177
2016-10-17 | 166 | 166
2016-10-17 00:30 | 162 | 161
2016-10-17 01:00 | 159 | 158
2016-10-17 01:30 | 155 | 155
2016-10-17 02:00 | 153 | 153
2016-10-17 02:30 | 149 | 149
2016-10-17 03:00 | 149 | 149
2016-10-17 03:30 | 147 | 147
2016-10-17 04:00 | 156 | 156
2016-10-17 04:30 | 163 | 163
2016-10-17 05:00 | 171 | 171
2016-10-17 05:30 | 184 | 184
2016-10-17 06:00 | 206 | 206
2016-10-17 06:30 | 226 | 225
2016-10-17 07:00 | 232 | 231
2016-10-17 07:30 | 237 | 237
2016-10-17 08:00 | 234 | 233
2016-10-17 08:30 | 236 | 235
2016-10-17 09:00 | 238 | 236
2016-10-17 09:30 | 237 | 237
2016-10-17 10:00 | 241 | 240
2016-10-17 10:30 | 234 | 234
2016-10-17 11:00 | 241 | 240
2016-10-17 11:30 | 237 | 236
2016-10-17 12:00 | 236 | 235
2016-10-17 12:30 | 241 | 241
2016-10-17 13:00 | 242 | 242
2016-10-17 13:30 | 239 | 239
2016-10-17 14:00 | 238 | 238
2016-10-17 14:30 | 245 | 245
2016-10-17 15:00 | 248 | 247
2016-10-17 15:30 | 245 | 244
2016-10-17 16:00 | 254 | 253
2016-10-17 16:30 | 262 | 261
2016-10-17 17:00 | 275 | 275
2016-10-17 17:30 | 280 | 279
2016-10-17 18:00 | 275 | 274
2016-10-17 18:30 | 275 | 274
2016-10-17 19:00 | 268 | 267
2016-10-17 19:30 | 261 | 261
2016-10-17 20:00 | 248 | 248
2016-10-17 20:30 | 234 | 234
2016-10-17 21:00 | 225 | 225
2016-10-17 21:30 | 216 | 216
2016-10-17 22:00 | 209 | 209
2016-10-17 22:30 | 209 | 209
2016-10-17 23:00 | 185 | 185
2016-10-17 23:30 | 183 | 182
2016-10-18 | 171 | 171
2016-10-18 00:30 | 161 | 161
2016-10-18 01:00 | 158 | 157
2016-10-18 01:30 | 156 | 156
2016-10-18 02:00 | 152 | 152
2016-10-18 02:30 | 141 | 141
2016-10-18 03:00 | 144 | 144
2016-10-18 03:30 | 131 | 131
2016-10-18 04:00 | 160 | 160
2016-10-18 04:30 | 166 | 166
2016-10-18 05:00 | 180 | 180
2016-10-18 05:30 | 198 | 198
2016-10-18 06:00 | 208 | 208
2016-10-18 06:30 | 225 | 225
2016-10-18 07:00 | 221 | 219
2016-10-18 07:30 | 217 | 217
2016-10-18 08:00 | 214 | 213
2016-10-18 08:30 | 213 | 213
2016-10-18 09:00 | 211 | 211
2016-10-18 09:30 | 208 | 208
2016-10-18 10:00 | 204 | 204
2016-10-18 10:30 | 204 | 203
2016-10-18 11:00 | 200 | 199
2016-10-18 11:30 | 199 | 198
2016-10-18 12:00 | 196 | 195
2016-10-18 12:30 | 186 | 185
2016-10-18 13:00 | 179 | 178
2016-10-18 13:30 | 208 | 207
2016-10-18 14:00 | 213 | 212
2016-10-18 14:30 | 218 | 218
2016-10-18 15:00 | 225 | 225
2016-10-18 15:30 | 237 | 237
2016-10-18 16:00 | 244 | 244
2016-10-18 16:30 | 256 | 256
2016-10-18 17:00 | 262 | 261
2016-10-18 17:30 | 264 | 264
2016-10-18 18:00 | 270 | 270
2016-10-18 18:30 | 274 | 274
2016-10-18 19:00 | 267 | 267
2016-10-18 19:30 | 263 | 263
2016-10-18 20:00 | 256 | 256
2016-10-18 20:30 | 243 | 242
2016-10-18 21:00 | 231 | 231
2016-10-18 21:30 | 216 | 216
2016-10-18 22:00 | 218 | 218
2016-10-18 22:30 | 219 | 219
2016-10-18 23:00 | 203 | 203
2016-10-18 23:30 | 195 | 195
2016-10-19 | 182 | 182
2016-10-19 00:30 | 174 | 174
2016-10-19 01:00 | 167 | 166
2016-10-19 01:30 | 164 | 163
2016-10-19 02:00 | 164 | 163
2016-10-19 02:30 | 164 | 163
2016-10-19 03:00 | 163 | 163
2016-10-19 03:30 | 165 | 164
2016-10-19 04:00 | 174 | 174
2016-10-19 04:30 | 186 | 185
2016-10-19 05:00 | 201 | 201
2016-10-19 05:30 | 211 | 211
2016-10-19 06:00 | 217 | 217
2016-10-19 06:30 | 228 | 228
2016-10-19 07:00 | 236 | 236
2016-10-19 07:30 | 240 | 239
2016-10-19 08:00 | 237 | 237
2016-10-19 08:30 | 232 | 231
2016-10-19 09:00 | 222 | 222
2016-10-19 09:30 | 202 | 202
2016-10-19 10:00 | 200 | 200
2016-10-19 10:30 | 202 | 202
2016-10-19 11:00 | 227 | 226
2016-10-19 11:30 | 228 | 228
2016-10-19 12:00 | 228 | 228
2016-10-19 12:30 | 225 | 225
2016-10-19 13:00 | 226 | 226
2016-10-19 13:30 | 229 | 229
2016-10-19 14:00 | 232 | 232
2016-10-19 14:30 | 226 | 226
2016-10-19 15:00 | 230 | 230
2016-10-19 15:30 | 243 | 243
2016-10-19 16:00 | 249 | 249
2016-10-19 16:30 | 259 | 258
2016-10-19 17:00 | 264 | 264
2016-10-19 17:30 | 270 | 270
2016-10-19 18:00 | 274 | 274
2016-10-19 18:30 | 281 | 281
2016-10-19 19:00 | 278 | 278
2016-10-19 19:30 | 276 | 276
2016-10-19 20:00 | 267 | 267
2016-10-19 20:30 | 252 | 252
2016-10-19 21:00 | 240 | 239
2016-10-19 21:30 | 225 | 224
2016-10-19 22:00 | 226 | 226
2016-10-19 22:30 | 228 | 228
2016-10-19 23:00 | 220 | 220
2016-10-19 23:30 | 206 | 206
2016-10-20 | 191 | 190
2016-10-20 00:30 | 182 | 181
2016-10-20 01:00 | 176 | 175
2016-10-20 01:30 | 166 | 165
2016-10-20 02:00 | 162 | 160
2016-10-20 02:30 | 159 | 158
2016-10-20 03:00 | 156 | 155
2016-10-20 03:30 | 157 | 157
2016-10-20 04:00 | 162 | 162
2016-10-20 04:30 | 170 | 170
2016-10-20 05:00 | 187 | 187
2016-10-20 05:30 | 200 | 200
2016-10-20 06:00 | 216 | 215
2016-10-20 06:30 | 229 | 229
2016-10-20 07:00 | 231 | 231
2016-10-20 07:30 | 234 | 234
2016-10-20 08:00 | 232 | 232
2016-10-20 08:30 | 231 | 231
2016-10-20 09:00 | 235 | 234
2016-10-20 09:30 | 235 | 234
2016-10-20 10:00 | 240 | 240
2016-10-20 10:30 | 224 | 224
2016-10-20 11:00 | 225 | 225
2016-10-20 11:30 | 236 | 236
2016-10-20 12:00 | 237 | 236
2016-10-20 12:30 | 227 | 227
2016-10-20 13:00 | 239 | 239
2016-10-20 13:30 | 238 | 238
2016-10-20 14:00 | 241 | 241
2016-10-20 14:30 | 254 | 254
2016-10-20 15:00 | 255 | 255
2016-10-20 15:30 | 262 | 262
2016-10-20 16:00 | 270 | 270
2016-10-20 16:30 | 273 | 273
2016-10-20 17:00 | 282 | 281
2016-10-20 17:30 | 283 | 283
2016-10-20 18:00 | 287 | 287
2016-10-20 18:30 | 267 | 267
2016-10-20 19:00 | 265 | 265
2016-10-20 19:30 | 265 | 264
2016-10-20 20:00 | 246 | 246
2016-10-20 20:30 | 229 | 229
2016-10-20 21:00 | 233 | 232
2016-10-20 21:30 | 223 | 223
2016-10-20 22:00 | 225 | 225
2016-10-20 22:30 | 200 | 200
2016-10-20 23:00 | 210 | 210
2016-10-20 23:30 | 182 | 182
2016-10-21 | 186 | 186
2016-10-21 00:30 | 170 | 169
2016-10-21 01:00 | 156 | 156
2016-10-21 01:30 | 144 | 144
2016-10-21 02:00 | 126 | 126
2016-10-21 02:30 | 142 | 142
2016-10-21 03:00 | 146 | 146
2016-10-21 03:30 | 153 | 152
2016-10-21 04:00 | 160 | 160
2016-10-21 04:30 | 172 | 172
2016-10-21 05:00 | 185 | 185
2016-10-21 05:30 | 200 | 200
2016-10-21 06:00 | 211 | 211
2016-10-21 06:30 | 226 | 225
2016-10-21 07:00 | 229 | 229
2016-10-21 07:30 | 237 | 237
2016-10-21 08:00 | 235 | 235
2016-10-21 08:30 | 231 | 231
2016-10-21 09:00 | 231 | 231
2016-10-21 09:30 | 231 | 231
2016-10-21 10:00 | 234 | 234
2016-10-21 10:30 | 232 | 232
2016-10-21 11:00 | 231 | 231
2016-10-21 11:30 | 229 | 229
2016-10-21 12:00 | 227 | 227
2016-10-21 12:30 | 226 | 226
2016-10-21 13:00 | 225 | 225
2016-10-21 13:30 | 236 | 236
2016-10-21 14:00 | 230 | 230
2016-10-21 14:30 | 238 | 238
2016-10-21 15:00 | 247 | 247
2016-10-21 15:30 | 245 | 245
2016-10-21 16:00 | 254 | 254
2016-10-21 16:30 | 261 | 261
2016-10-21 17:00 | 260 | 260
2016-10-21 17:30 | 261 | 260
2016-10-21 18:00 | 268 | 268
2016-10-21 18:30 | 271 | 271
2016-10-21 19:00 | 271 | 271
2016-10-21 19:30 | 268 | 267
2016-10-21 20:00 | 261 | 260
2016-10-21 20:30 | 246 | 245
2016-10-21 21:00 | 232 | 232
2016-10-21 21:30 | 226 | 226
2016-10-21 22:00 | 229 | 229
2016-10-21 22:30 | 230 | 230
2016-10-21 23:00 | 206 | 206
2016-10-21 23:30 | 196 | 195
2016-10-22 | 182 | 182
2016-10-22 00:30 | 172 | 171
2016-10-22 01:00 | 161 | 160
2016-10-22 01:30 | 158 | 158
2016-10-22 02:00 | 155 | 155
2016-10-22 02:30 | 152 | 152
2016-10-22 03:00 | 153 | 153
2016-10-22 03:30 | 154 | 154
2016-10-22 04:00 | 154 | 154
2016-10-22 04:30 | 155 | 154
2016-10-22 05:00 | 158 | 157
2016-10-22 05:30 | 165 | 165
2016-10-22 06:00 | 179 | 179
2016-10-22 06:30 | 199 | 199
2016-10-22 07:00 | 205 | 205
2016-10-22 07:30 | 221 | 221
2016-10-22 08:00 | 236 | 235
2016-10-22 08:30 | 242 | 242
2016-10-22 09:00 | 235 | 235
2016-10-22 09:30 | 229 | 229
2016-10-22 10:00 | 219 | 219
2016-10-22 10:30 | 212 | 212
2016-10-22 11:00 | 216 | 216
2016-10-22 11:30 | 213 | 213
2016-10-22 12:00 | 204 | 204
2016-10-22 12:30 | 207 | 207
2016-10-22 13:00 | 205 | 205
2016-10-22 13:30 | 216 | 216
2016-10-22 14:00 | 233 | 233
2016-10-22 14:30 | 237 | 237
2016-10-22 15:00 | 241 | 241
2016-10-22 15:30 | 238 | 238
2016-10-22 16:00 | 241 | 240
2016-10-22 16:30 | 247 | 247
2016-10-22 17:00 | 248 | 248
2016-10-22 17:30 | 255 | 255
2016-10-22 18:00 | 262 | 261
2016-10-22 18:30 | 264 | 264
2016-10-22 19:00 | 257 | 257
2016-10-22 19:30 | 254 | 254
2016-10-22 20:00 | 249 | 248
2016-10-22 20:30 | 241 | 241
2016-10-22 21:00 | 230 | 230
2016-10-22 21:30 | 221 | 221
2016-10-22 22:00 | 225 | 225
2016-10-22 22:30 | 224 | 224
2016-10-22 23:00 | 206 | 206
2016-10-22 23:30 | 196 | 196
2016-10-23 | 190 | 190
2016-10-23 00:30 | 183 | 182
2016-10-23 01:00 | 179 | 179
2016-10-23 01:30 | 174 | 174
2016-10-23 02:00 | 170 | 170
2016-10-23 02:30 | 164 | 164
2016-10-23 03:00 | 162 | 162
2016-10-23 03:30 | 165 | 165
2016-10-23 04:00 | 167 | 167
2016-10-23 04:30 | 169 | 169
2016-10-23 05:00 | 170 | 170
2016-10-23 05:30 | 174 | 174
2016-10-23 06:00 | 181 | 181
2016-10-23 06:30 | 186 | 186
2016-10-23 07:00 | 199 | 199
2016-10-23 07:30 | 208 | 208
2016-10-23 08:00 | 226 | 226
2016-10-23 08:30 | 231 | 230
2016-10-23 09:00 | 228 | 228
2016-10-23 09:30 | 229 | 228
2016-10-23 10:00 | 231 | 230
2016-10-23 10:30 | 235 | 234
2016-10-23 11:00 | 233 | 233
2016-10-23 11:30 | 229 | 228
2016-10-23 12:00 | 223 | 223
2016-10-23 12:30 | 224 | 224
2016-10-23 13:00 | 226 | 225
2016-10-23 13:30 | 224 | 223
2016-10-23 14:00 | 214 | 214
2016-10-23 14:30 | 206 | 206
2016-10-23 15:00 | 213 | 212
2016-10-23 15:30 | 216 | 216
2016-10-23 16:00 | 220 | 220
2016-10-23 16:30 | 232 | 231
2016-10-23 17:00 | 246 | 245
2016-10-23 17:30 | 259 | 259
2016-10-23 18:00 | 265 | 265
2016-10-23 18:30 | 276 | 276
2016-10-23 19:00 | 271 | 270
2016-10-23 19:30 | 266 | 265
2016-10-23 20:00 | 263 | 262
2016-10-23 20:30 | 250 | 250
2016-10-23 21:00 | 238 | 238
2016-10-23 21:30 | 230 | 229
2016-10-23 22:00 | 230 | 230
2016-10-23 22:30 | 230 | 230
2016-10-23 23:00 | 216 | 216
2016-10-23 23:30 | 202 | 201
2016-10-24 | 189 | 188
2016-10-24 00:30 | 179 | 179
2016-10-24 01:00 | 173 | 172
2016-10-24 01:30 | 167 | 167
2016-10-24 02:00 | 165 | 164
2016-10-24 02:30 | 164 | 164
2016-10-24 03:00 | 165 | 165
2016-10-24 03:30 | 167 | 167
2016-10-24 04:00 | 172 | 172
2016-10-24 04:30 | 177 | 177
2016-10-24 05:00 | 187 | 187
2016-10-24 05:30 | 198 | 198
2016-10-24 06:00 | 215 | 215
2016-10-24 06:30 | 229 | 229
2016-10-24 07:00 | 236 | 236
2016-10-24 07:30 | 236 | 236
2016-10-24 08:00 | 234 | 234
2016-10-24 08:30 | 226 | 226
2016-10-24 09:00 | 224 | 223
2016-10-24 09:30 | 224 | 223
2016-10-24 10:00 | 222 | 221
2016-10-24 10:30 | 219 | 219
2016-10-24 11:00 | 219 | 218
2016-10-24 11:30 | 219 | 218
2016-10-24 12:00 | 215 | 214
2016-10-24 12:30 | 210 | 210
2016-10-24 13:00 | 214 | 213
2016-10-24 13:30 | 215 | 214
2016-10-24 14:00 | 214 | 214
2016-10-24 14:30 | 219 | 218
2016-10-24 15:00 | 223 | 222
2016-10-24 15:30 | 232 | 232
2016-10-24 16:00 | 238 | 237
2016-10-24 16:30 | 248 | 248
2016-10-24 17:00 | 256 | 256
2016-10-24 17:30 | 263 | 263
2016-10-24 18:00 | 269 | 269
2016-10-24 18:30 | 278 | 278
2016-10-24 19:00 | 273 | 273
2016-10-24 19:30 | 270 | 270
2016-10-24 20:00 | 264 | 264
2016-10-24 20:30 | 248 | 248
2016-10-24 21:00 | 235 | 235
2016-10-24 21:30 | 220 | 220
2016-10-24 22:00 | 224 | 224
2016-10-24 22:30 | 219 | 219
2016-10-24 23:00 | 210 | 210
2016-10-24 23:30 | 203 | 203
2016-10-25 | 186 | 185
2016-10-25 00:30 | 174 | 173
2016-10-25 01:00 | 164 | 163
2016-10-25 01:30 | 159 | 159
2016-10-25 02:00 | 157 | 157
2016-10-25 02:30 | 159 | 159
2016-10-25 03:00 | 155 | 155
2016-10-25 03:30 | 157 | 157
2016-10-25 04:00 | 171 | 170
2016-10-25 04:30 | 172 | 172
2016-10-25 05:00 | 186 | 185
2016-10-25 05:30 | 199 | 199
2016-10-25 06:00 | 212 | 212
2016-10-25 06:30 | 221 | 221
2016-10-25 07:00 | 225 | 225
2016-10-25 07:30 | 223 | 222
2016-10-25 08:00 | 222 | 221
2016-10-25 08:30 | 218 | 218
2016-10-25 09:00 | 215 | 214
2016-10-25 09:30 | 217 | 216
2016-10-25 10:00 | 219 | 218
2016-10-25 10:30 | 213 | 213
2016-10-25 11:00 | 212 | 212
2016-10-25 11:30 | 213 | 212
2016-10-25 12:00 | 211 | 211
2016-10-25 12:30 | 211 | 211
2016-10-25 13:00 | 213 | 213
2016-10-25 13:30 | 217 | 217
2016-10-25 14:00 | 219 | 219
2016-10-25 14:30 | 221 | 221
2016-10-25 15:00 | 227 | 227
2016-10-25 15:30 | 232 | 232
2016-10-25 16:00 | 241 | 241
2016-10-25 16:30 | 250 | 249
2016-10-25 17:00 | 256 | 255
2016-10-25 17:30 | 260 | 260
2016-10-25 18:00 | 266 | 266
2016-10-25 18:30 | 276 | 276
2016-10-25 19:00 | 271 | 271
2016-10-25 19:30 | 264 | 264
2016-10-25 20:00 | 251 | 251
2016-10-25 20:30 | 250 | 249
2016-10-25 21:00 | 233 | 233
2016-10-25 21:30 | 219 | 219
2016-10-25 22:00 | 222 | 222
2016-10-25 22:30 | 224 | 224
2016-10-25 23:00 | 210 | 209
2016-10-25 23:30 | 198 | 198
2016-10-26 | 189 | 189
2016-10-26 00:30 | 173 | 173
2016-10-26 01:00 | 172 | 172
2016-10-26 01:30 | 169 | 169
2016-10-26 02:00 | 169 | 169
2016-10-26 02:30 | 168 | 168
2016-10-26 03:00 | 168 | 168
2016-10-26 03:30 | 170 | 170
2016-10-26 04:00 | 173 | 172
2016-10-26 04:30 | 178 | 178
2016-10-26 05:00 | 189 | 189
2016-10-26 05:30 | 200 | 200
2016-10-26 06:00 | 217 | 217
2016-10-26 06:30 | 232 | 232
2016-10-26 07:00 | 237 | 236
2016-10-26 07:30 | 237 | 236
2016-10-26 08:00 | 236 | 235
2016-10-26 08:30 | 234 | 233
2016-10-26 09:00 | 236 | 235
2016-10-26 09:30 | 237 | 237
2016-10-26 10:00 | 236 | 236
2016-10-26 10:30 | 238 | 237
2016-10-26 11:00 | 239 | 239
2016-10-26 11:30 | 236 | 236
2016-10-26 12:00 | 235 | 235
2016-10-26 12:30 | 239 | 239
2016-10-26 13:00 | 237 | 237
2016-10-26 13:30 | 243 | 243
2016-10-26 14:00 | 252 | 252
2016-10-26 14:30 | 250 | 250
2016-10-26 15:00 | 247 | 247
2016-10-26 15:30 | 254 | 254
2016-10-26 16:00 | 263 | 263
2016-10-26 16:30 | 269 | 269
2016-10-26 17:00 | 265 | 265
2016-10-26 17:30 | 263 | 263
2016-10-26 18:00 | 269 | 269
2016-10-26 18:30 | 275 | 275
2016-10-26 19:00 | 271 | 271
2016-10-26 19:30 | 271 | 271
2016-10-26 20:00 | 261 | 261
2016-10-26 20:30 | 249 | 248
2016-10-26 21:00 | 233 | 233
2016-10-26 21:30 | 224 | 224
2016-10-26 22:00 | 222 | 222
2016-10-26 22:30 | 219 | 219
2016-10-26 23:00 | 209 | 209
2016-10-26 23:30 | 197 | 197
2016-10-27 | 183 | 183
2016-10-27 00:30 | 179 | 179
2016-10-27 01:00 | 170 | 170
2016-10-27 01:30 | 167 | 167
2016-10-27 02:00 | 167 | 167
2016-10-27 02:30 | 164 | 164
2016-10-27 03:00 | 162 | 162
2016-10-27 03:30 | 164 | 164
2016-10-27 04:00 | 172 | 172
2016-10-27 04:30 | 177 | 177
2016-10-27 05:00 | 188 | 188
2016-10-27 05:30 | 202 | 202
2016-10-27 06:00 | 208 | 208
2016-10-27 06:30 | 232 | 232
2016-10-27 07:00 | 242 | 241
2016-10-27 07:30 | 229 | 228
2016-10-27 08:00 | 237 | 237
2016-10-27 08:30 | 227 | 226
2016-10-27 09:00 | 229 | 228
2016-10-27 09:30 | 231 | 230
2016-10-27 10:00 | 231 | 229
2016-10-27 10:30 | 231 | 229
2016-10-27 11:00 | 233 | 232
2016-10-27 11:30 | 232 | 231
2016-10-27 12:00 | 234 | 234
2016-10-27 12:30 | 240 | 240
2016-10-27 13:00 | 237 | 237
2016-10-27 13:30 | 241 | 241
2016-10-27 14:00 | 244 | 244
2016-10-27 14:30 | 250 | 250
2016-10-27 15:00 | 257 | 257
2016-10-27 15:30 | 264 | 263
2016-10-27 16:00 | 266 | 266
2016-10-27 16:30 | 271 | 271
2016-10-27 17:00 | 270 | 269
2016-10-27 17:30 | 270 | 270
2016-10-27 18:00 | 268 | 268
2016-10-27 18:30 | 266 | 266
2016-10-27 19:00 | 256 | 256
2016-10-27 19:30 | 256 | 255
2016-10-27 20:00 | 255 | 255
2016-10-27 20:30 | 250 | 250
2016-10-27 21:00 | 238 | 238
2016-10-27 21:30 | 228 | 228
2016-10-27 22:00 | 228 | 228
2016-10-27 22:30 | 223 | 223
2016-10-27 23:00 | 208 | 208
2016-10-27 23:30 | 196 | 196
2016-10-28 | 185 | 184
2016-10-28 00:30 | 177 | 176
2016-10-28 01:00 | 168 | 168
2016-10-28 01:30 | 165 | 165
2016-10-28 02:00 | 164 | 164
2016-10-28 02:30 | 168 | 168
2016-10-28 03:00 | 171 | 171
2016-10-28 03:30 | 172 | 172
2016-10-28 04:00 | 172 | 172
2016-10-28 04:30 | 175 | 175
2016-10-28 05:00 | 187 | 187
2016-10-28 05:30 | 201 | 201
2016-10-28 06:00 | 217 | 217
2016-10-28 06:30 | 233 | 233
2016-10-28 07:00 | 264 | 263
2016-10-28 07:30 | 271 | 270
2016-10-28 08:00 | 281 | 281
2016-10-28 08:30 | 276 | 276
2016-10-28 09:00 | 264 | 264
2016-10-28 09:30 | 258 | 258
2016-10-28 10:00 | 261 | 261
2016-10-28 10:30 | 264 | 264
2016-10-28 11:00 | 265 | 265
2016-10-28 11:30 | 274 | 274
2016-10-28 12:00 | 257 | 257
2016-10-28 12:30 | 247 | 247
2016-10-28 13:00 | 242 | 242
2016-10-28 13:30 | 241 | 241
2016-10-28 14:00 | 242 | 242
2016-10-28 14:30 | 251 | 251
2016-10-28 15:00 | 251 | 251
2016-10-28 15:30 | 257 | 257
2016-10-28 16:00 | 264 | 264
2016-10-28 16:30 | 267 | 267
2016-10-28 17:00 | 264 | 264
2016-10-28 17:30 | 255 | 255
2016-10-28 18:00 | 255 | 254
2016-10-28 18:30 | 266 | 265
2016-10-28 19:00 | 263 | 262
2016-10-28 19:30 | 266 | 265
2016-10-28 20:00 | 257 | 257
2016-10-28 20:30 | 246 | 246
2016-10-28 21:00 | 234 | 234
2016-10-28 21:30 | 228 | 228
2016-10-28 22:00 | 231 | 231
2016-10-28 22:30 | 229 | 229
2016-10-28 23:00 | 211 | 211
2016-10-28 23:30 | 196 | 195
2016-10-29 | 184 | 183
2016-10-29 00:30 | 175 | 175
2016-10-29 01:00 | 171 | 170
2016-10-29 01:30 | 167 | 167
2016-10-29 02:00 | 165 | 165
2016-10-29 02:30 | 164 | 164
2016-10-29 03:00 | 164 | 164
2016-10-29 03:30 | 164 | 164
2016-10-29 04:00 | 163 | 163
2016-10-29 04:30 | 165 | 165
2016-10-29 05:00 | 165 | 165
2016-10-29 05:30 | 173 | 173
2016-10-29 06:00 | 183 | 183
2016-10-29 06:30 | 194 | 194
2016-10-29 07:00 | 198 | 197
2016-10-29 07:30 | 210 | 209
2016-10-29 08:00 | 226 | 226
2016-10-29 08:30 | 223 | 222
2016-10-29 09:00 | 225 | 225
2016-10-29 09:30 | 225 | 225
2016-10-29 10:00 | 220 | 220
2016-10-29 10:30 | 220 | 220
2016-10-29 11:00 | 220 | 220
2016-10-29 11:30 | 222 | 221
2016-10-29 12:00 | 222 | 222
2016-10-29 12:30 | 214 | 214
2016-10-29 13:00 | 213 | 213
2016-10-29 13:30 | 216 | 216
2016-10-29 14:00 | 218 | 218
2016-10-29 14:30 | 224 | 224
2016-10-29 15:00 | 231 | 231
2016-10-29 15:30 | 240 | 239
2016-10-29 16:00 | 237 | 237
2016-10-29 16:30 | 247 | 247
2016-10-29 17:00 | 249 | 248
2016-10-29 17:30 | 244 | 243
2016-10-29 18:00 | 245 | 245
2016-10-29 18:30 | 253 | 253
2016-10-29 19:00 | 245 | 245
2016-10-29 19:30 | 243 | 243
2016-10-29 20:00 | 233 | 233
2016-10-29 20:30 | 230 | 229
2016-10-29 21:00 | 224 | 224
2016-10-29 21:30 | 215 | 215
2016-10-29 22:00 | 203 | 203
2016-10-29 22:30 | 189 | 189
2016-10-29 23:00 | 180 | 180
2016-10-29 23:30 | 186 | 186
2016-10-30 | 161 | 161
2016-10-30 00:30 | 163 | 163
2016-10-30 01:00 | 138 | 138
2016-10-30 01:30 | 143 | 143
2016-10-30 02:00 | 135 | 134
2016-10-30 02:30 | 126 | 125
2016-10-30 03:00 | 125 | 125
2016-10-30 03:30 | 134 | 134
2016-10-30 04:00 | 125 | 125
2016-10-30 04:30 | 124 | 124
2016-10-30 05:00 | 149 | 149
2016-10-30 05:30 | 150 | 150
2016-10-30 06:00 | 172 | 172
2016-10-30 06:30 | 180 | 180
2016-10-30 07:00 | 190 | 189
2016-10-30 07:30 | 197 | 196
2016-10-30 08:00 | 203 | 202
2016-10-30 08:30 | 183 | 181
2016-10-30 09:00 | 190 | 189
2016-10-30 09:30 | 189 | 188
2016-10-30 10:00 | 198 | 198
2016-10-30 10:30 | 196 | 195
2016-10-30 11:00 | 190 | 189
2016-10-30 11:30 | 178 | 177
2016-10-30 12:00 | 192 | 191
2016-10-30 12:30 | 176 | 175
2016-10-30 13:00 | 186 | 185
2016-10-30 13:30 | 180 | 179
2016-10-30 14:00 | 184 | 183
2016-10-30 14:30 | 209 | 208
2016-10-30 15:00 | 204 | 203
2016-10-30 15:30 | 222 | 221
2016-10-30 16:00 | 232 | 231
2016-10-30 16:30 | 242 | 242
2016-10-30 17:00 | 241 | 240
2016-10-30 17:30 | 239 | 238
2016-10-30 18:00 | 245 | 245
2016-10-30 18:30 | 246 | 246
2016-10-30 19:00 | 243 | 243
2016-10-30 19:30 | 239 | 239
2016-10-30 20:00 | 233 | 233
2016-10-30 20:30 | 225 | 225
2016-10-30 21:00 | 216 | 216
2016-10-30 21:30 | 213 | 213
2016-10-30 22:00 | 193 | 193
2016-10-30 22:30 | 184 | 184
2016-10-30 23:00 | 195 | 195
2016-10-30 23:30 | 182 | 181
2016-10-31 | 171 | 171
2016-10-31 00:30 | 166 | 166
2016-10-31 01:00 | 162 | 162
2016-10-31 01:30 | 161 | 161
2016-10-31 02:00 | 160 | 160
2016-10-31 02:30 | 163 | 163
2016-10-31 03:00 | 161 | 161
2016-10-31 03:30 | 162 | 162
2016-10-31 04:00 | 171 | 171
2016-10-31 04:30 | 174 | 174
2016-10-31 05:00 | 177 | 177
2016-10-31 05:30 | 190 | 190
2016-10-31 06:00 | 210 | 209
2016-10-31 06:30 | 231 | 230
2016-10-31 07:00 | 241 | 240
2016-10-31 07:30 | 256 | 256
2016-10-31 08:00 | 258 | 258
2016-10-31 08:30 | 254 | 254
2016-10-31 09:00 | 261 | 261
2016-10-31 09:30 | 260 | 260
2016-10-31 10:00 | 255 | 255
2016-10-31 10:30 | 253 | 253
2016-10-31 11:00 | 247 | 247
2016-10-31 11:30 | 246 | 246
2016-10-31 12:00 | 240 | 240
2016-10-31 12:30 | 228 | 228
2016-10-31 13:00 | 243 | 243
2016-10-31 13:30 | 232 | 232
2016-10-31 14:00 | 228 | 228
2016-10-31 14:30 | 237 | 237
2016-10-31 15:00 | 238 | 238
2016-10-31 15:30 | 249 | 249
2016-10-31 16:00 | 248 | 248
2016-10-31 16:30 | 257 | 257
2016-10-31 17:00 | 259 | 259
2016-10-31 17:30 | 259 | 259
2016-10-31 18:00 | 258 | 258
2016-10-31 18:30 | 266 | 266
2016-10-31 19:00 | 269 | 269
2016-10-31 19:30 | 268 | 268
2016-10-31 20:00 | 263 | 263
2016-10-31 20:30 | 249 | 249
2016-10-31 21:00 | 237 | 237
2016-10-31 21:30 | 230 | 230
2016-10-31 22:00 | 234 | 233
2016-10-31 22:30 | 232 | 232
2016-10-31 23:00 | 216 | 216
2016-10-31 23:30 | 204 | 204
2016-11-01 | 190 | 190
2016-11-01 00:30 | 181 | 180
2016-11-01 01:00 | 176 | 175
2016-11-01 01:30 | 170 | 170
2016-11-01 02:00 | 165 | 165
2016-11-01 02:30 | 164 | 164
2016-11-01 03:00 | 162 | 162
2016-11-01 03:30 | 165 | 165
2016-11-01 04:00 | 172 | 172
2016-11-01 04:30 | 175 | 175
2016-11-01 05:00 | 187 | 187
2016-11-01 05:30 | 202 | 202
2016-11-01 06:00 | 219 | 218
2016-11-01 06:30 | 234 | 233
2016-11-01 07:00 | 256 | 256
2016-11-01 07:30 | 274 | 274
2016-11-01 08:00 | 280 | 280
2016-11-01 08:30 | 286 | 286
2016-11-01 09:00 | 289 | 289
2016-11-01 09:30 | 289 | 289
2016-11-01 10:00 | 292 | 292
2016-11-01 10:30 | 292 | 292
2016-11-01 11:00 | 266 | 266
2016-11-01 11:30 | 253 | 253
2016-11-01 12:00 | 262 | 262
2016-11-01 12:30 | 255 | 255
2016-11-01 13:00 | 253 | 253
2016-11-01 13:30 | 241 | 241
2016-11-01 14:00 | 242 | 242
2016-11-01 14:30 | 250 | 250
2016-11-01 15:00 | 255 | 255
2016-11-01 15:30 | 257 | 256
2016-11-01 16:00 | 255 | 255
2016-11-01 16:30 | 270 | 270
2016-11-01 17:00 | 270 | 269
2016-11-01 17:30 | 268 | 268
2016-11-01 18:00 | 273 | 273
2016-11-01 18:30 | 281 | 281
2016-11-01 19:00 | 278 | 278
2016-11-01 19:30 | 275 | 275
2016-11-01 20:00 | 270 | 270
2016-11-01 20:30 | 260 | 260
2016-11-01 21:00 | 251 | 250
2016-11-01 21:30 | 242 | 241
2016-11-01 22:00 | 235 | 233
2016-11-01 22:30 | 230 | 230
2016-11-01 23:00 | 210 | 210
2016-11-01 23:30 | 195 | 195
2016-11-02 | 185 | 184
2016-11-02 00:30 | 180 | 180
2016-11-02 01:00 | 175 | 174
2016-11-02 01:30 | 172 | 172
2016-11-02 02:00 | 171 | 170
2016-11-02 02:30 | 171 | 171
2016-11-02 03:00 | 171 | 170
2016-11-02 03:30 | 175 | 174
2016-11-02 04:00 | 177 | 177
2016-11-02 04:30 | 180 | 179
2016-11-02 05:00 | 186 | 185
2016-11-02 05:30 | 198 | 198
2016-11-02 06:00 | 212 | 212
2016-11-02 06:30 | 226 | 226
2016-11-02 07:00 | 238 | 238
2016-11-02 07:30 | 243 | 243
2016-11-02 08:00 | 241 | 241
2016-11-02 08:30 | 245 | 245
2016-11-02 09:00 | 236 | 236
2016-11-02 09:30 | 231 | 231
2016-11-02 10:00 | 236 | 236
2016-11-02 10:30 | 235 | 235
2016-11-02 11:00 | 240 | 240
2016-11-02 11:30 | 231 | 231
2016-11-02 12:00 | 226 | 226
2016-11-02 12:30 | 227 | 227
2016-11-02 13:00 | 224 | 224
2016-11-02 13:30 | 226 | 226
2016-11-02 14:00 | 236 | 236
2016-11-02 14:30 | 234 | 234
2016-11-02 15:00 | 242 | 241
2016-11-02 15:30 | 249 | 249
2016-11-02 16:00 | 259 | 259
2016-11-02 16:30 | 269 | 268
2016-11-02 17:00 | 271 | 270
2016-11-02 17:30 | 272 | 271
2016-11-02 18:00 | 274 | 274
2016-11-02 18:30 | 279 | 279
2016-11-02 19:00 | 279 | 279
2016-11-02 19:30 | 277 | 277
2016-11-02 20:00 | 271 | 271
2016-11-02 20:30 | 260 | 260
2016-11-02 21:00 | 247 | 246
2016-11-02 21:30 | 231 | 231
2016-11-02 22:00 | 234 | 234
2016-11-02 22:30 | 236 | 236
2016-11-02 23:00 | 222 | 222
2016-11-02 23:30 | 206 | 206
2016-11-03 | 190 | 189
2016-11-03 00:30 | 180 | 179
2016-11-03 01:00 | 177 | 176
2016-11-03 01:30 | 175 | 174
2016-11-03 02:00 | 173 | 172
2016-11-03 02:30 | 172 | 171
2016-11-03 03:00 | 172 | 171
2016-11-03 03:30 | 173 | 172
2016-11-03 04:00 | 179 | 178
2016-11-03 04:30 | 181 | 180
2016-11-03 05:00 | 189 | 188
2016-11-03 05:30 | 202 | 201
2016-11-03 06:00 | 216 | 215
2016-11-03 06:30 | 234 | 234
2016-11-03 07:00 | 249 | 249
2016-11-03 07:30 | 256 | 256
2016-11-03 08:00 | 256 | 256
2016-11-03 08:30 | 254 | 254
2016-11-03 09:00 | 255 | 255
2016-11-03 09:30 | 253 | 253
2016-11-03 10:00 | 254 | 254
2016-11-03 10:30 | 252 | 252
2016-11-03 11:00 | 251 | 251
2016-11-03 11:30 | 247 | 247
2016-11-03 12:00 | 248 | 248
2016-11-03 12:30 | 252 | 252
2016-11-03 13:00 | 258 | 258
2016-11-03 13:30 | 253 | 253
2016-11-03 14:00 | 258 | 258
2016-11-03 14:30 | 257 | 257
2016-11-03 15:00 | 260 | 260
2016-11-03 15:30 | 267 | 267
2016-11-03 16:00 | 274 | 274
2016-11-03 16:30 | 276 | 276
2016-11-03 17:00 | 280 | 279
2016-11-03 17:30 | 287 | 286
2016-11-03 18:00 | 289 | 289
2016-11-03 18:30 | 302 | 302
2016-11-03 19:00 | 303 | 301
2016-11-03 19:30 | 296 | 296
2016-11-03 20:00 | 289 | 289
2016-11-03 20:30 | 278 | 278
2016-11-03 21:00 | 262 | 261
2016-11-03 21:30 | 245 | 244
2016-11-03 22:00 | 239 | 239
2016-11-03 22:30 | 235 | 235
2016-11-03 23:00 | 221 | 221
2016-11-03 23:30 | 209 | 209
2016-11-04 | 195 | 195
2016-11-04 00:30 | 187 | 186
2016-11-04 01:00 | 180 | 179
2016-11-04 01:30 | 177 | 176
2016-11-04 02:00 | 176 | 175
2016-11-04 02:30 | 175 | 174
2016-11-04 03:00 | 173 | 172
2016-11-04 03:30 | 174 | 174
2016-11-04 04:00 | 178 | 178
2016-11-04 04:30 | 181 | 181
2016-11-04 05:00 | 189 | 189
2016-11-04 05:30 | 201 | 201
2016-11-04 06:00 | 215 | 215
2016-11-04 06:30 | 233 | 233
2016-11-04 07:00 | 242 | 242
2016-11-04 07:30 | 248 | 247
2016-11-04 08:00 | 249 | 249
2016-11-04 08:30 | 250 | 249
2016-11-04 09:00 | 250 | 249
2016-11-04 09:30 | 252 | 251
2016-11-04 10:00 | 253 | 252
2016-11-04 10:30 | 255 | 255
2016-11-04 11:00 | 253 | 252
2016-11-04 11:30 | 248 | 248
2016-11-04 12:00 | 253 | 253
2016-11-04 12:30 | 246 | 246
2016-11-04 13:00 | 253 | 253
2016-11-04 13:30 | 238 | 238
2016-11-04 14:00 | 252 | 252
2016-11-04 14:30 | 257 | 257
2016-11-04 15:00 | 263 | 262
2016-11-04 15:30 | 271 | 270
2016-11-04 16:00 | 277 | 277
2016-11-04 16:30 | 281 | 280
2016-11-04 17:00 | 277 | 277
2016-11-04 17:30 | 269 | 269
2016-11-04 18:00 | 266 | 266
2016-11-04 18:30 | 277 | 277
2016-11-04 19:00 | 271 | 271
2016-11-04 19:30 | 267 | 267
2016-11-04 20:00 | 262 | 262
2016-11-04 20:30 | 250 | 249
2016-11-04 21:00 | 243 | 243
2016-11-04 21:30 | 232 | 232
2016-11-04 22:00 | 221 | 221
2016-11-04 22:30 | 202 | 202
2016-11-04 23:00 | 200 | 200
2016-11-04 23:30 | 195 | 195
2016-11-05 | 163 | 162
2016-11-05 00:30 | 182 | 181
2016-11-05 01:00 | 178 | 177
2016-11-05 01:30 | 171 | 171
2016-11-05 02:00 | 166 | 166
2016-11-05 02:30 | 172 | 172
2016-11-05 03:00 | 155 | 154
2016-11-05 03:30 | 136 | 136
2016-11-05 04:00 | 164 | 164
2016-11-05 04:30 | 163 | 162
2016-11-05 05:00 | 161 | 161
2016-11-05 05:30 | 170 | 170
2016-11-05 06:00 | 181 | 180
2016-11-05 06:30 | 194 | 194
2016-11-05 07:00 | 204 | 203
2016-11-05 07:30 | 212 | 212
2016-11-05 08:00 | 214 | 214
2016-11-05 08:30 | 213 | 213
2016-11-05 09:00 | 218 | 217
2016-11-05 09:30 | 219 | 219
2016-11-05 10:00 | 225 | 224
2016-11-05 10:30 | 225 | 224
2016-11-05 11:00 | 224 | 223
2016-11-05 11:30 | 224 | 223
2016-11-05 12:00 | 227 | 226
2016-11-05 12:30 | 232 | 231
2016-11-05 13:00 | 235 | 235
2016-11-05 13:30 | 241 | 241
2016-11-05 14:00 | 246 | 246
2016-11-05 14:30 | 248 | 248
2016-11-05 15:00 | 242 | 242
2016-11-05 15:30 | 260 | 260
2016-11-05 16:00 | 274 | 274
2016-11-05 16:30 | 279 | 279
2016-11-05 17:00 | 278 | 278
2016-11-05 17:30 | 268 | 268
2016-11-05 18:00 | 270 | 270
2016-11-05 18:30 | 275 | 275
2016-11-05 19:00 | 275 | 275
2016-11-05 19:30 | 275 | 275
2016-11-05 20:00 | 269 | 269
2016-11-05 20:30 | 252 | 252
2016-11-05 21:00 | 243 | 243
2016-11-05 21:30 | 234 | 234
2016-11-05 22:00 | 232 | 232
2016-11-05 22:30 | 228 | 228
2016-11-05 23:00 | 200 | 199
2016-11-05 23:30 | 182 | 182
2016-11-06 | 180 | 179
2016-11-06 00:30 | 174 | 174
2016-11-06 01:00 | 171 | 171
2016-11-06 01:30 | 157 | 157
2016-11-06 02:00 | 155 | 155
2016-11-06 02:30 | 147 | 147
2016-11-06 03:00 | 134 | 133
2016-11-06 03:30 | 142 | 142
2016-11-06 04:00 | 132 | 132
2016-11-06 04:30 | 141 | 140
2016-11-06 05:00 | 162 | 162
2016-11-06 05:30 | 155 | 155
2016-11-06 06:00 | 170 | 170
2016-11-06 06:30 | 180 | 180
2016-11-06 07:00 | 192 | 192
2016-11-06 07:30 | 198 | 197
2016-11-06 08:00 | 203 | 203
2016-11-06 08:30 | 208 | 207
2016-11-06 09:00 | 209 | 208
2016-11-06 09:30 | 211 | 210
2016-11-06 10:00 | 215 | 214
2016-11-06 10:30 | 214 | 212
2016-11-06 11:00 | 212 | 212
2016-11-06 11:30 | 206 | 205
2016-11-06 12:00 | 187 | 186
2016-11-06 12:30 | 173 | 172
2016-11-06 13:00 | 177 | 176
2016-11-06 13:30 | 190 | 189
2016-11-06 14:00 | 215 | 214
2016-11-06 14:30 | 222 | 221
2016-11-06 15:00 | 229 | 228
2016-11-06 15:30 | 235 | 234
2016-11-06 16:00 | 241 | 240
2016-11-06 16:30 | 247 | 246
2016-11-06 17:00 | 251 | 250
2016-11-06 17:30 | 254 | 253
2016-11-06 18:00 | 259 | 258
2016-11-06 18:30 | 268 | 268
2016-11-06 19:00 | 268 | 268
2016-11-06 19:30 | 265 | 264
2016-11-06 20:00 | 255 | 254
2016-11-06 20:30 | 242 | 241
2016-11-06 21:00 | 236 | 235
2016-11-06 21:30 | 223 | 222
2016-11-06 22:00 | 213 | 213
2016-11-06 22:30 | 210 | 210
2016-11-06 23:00 | 172 | 172
2016-11-06 23:30 | 183 | 183
2016-11-07 | 148 | 148
2016-11-07 00:30 | 139 | 139
2016-11-07 01:00 | 133 | 133
2016-11-07 01:30 | 132 | 132
2016-11-07 02:00 | 125 | 125
2016-11-07 02:30 | 120 | 120
2016-11-07 03:00 | 117 | 117
2016-11-07 03:30 | 140 | 140
2016-11-07 04:00 | 132 | 132
2016-11-07 04:30 | 162 | 161
2016-11-07 05:00 | 177 | 177
2016-11-07 05:30 | 190 | 189
2016-11-07 06:00 | 206 | 206
2016-11-07 06:30 | 229 | 229
2016-11-07 07:00 | 242 | 242
2016-11-07 07:30 | 250 | 250
2016-11-07 08:00 | 233 | 233
2016-11-07 08:30 | 218 | 218
2016-11-07 09:00 | 240 | 240
2016-11-07 09:30 | 247 | 247
2016-11-07 10:00 | 247 | 247
2016-11-07 10:30 | 244 | 244
2016-11-07 11:00 | 243 | 243
2016-11-07 11:30 | 246 | 246
2016-11-07 12:00 | 247 | 247
2016-11-07 12:30 | 251 | 251
2016-11-07 13:00 | 255 | 255
2016-11-07 13:30 | 266 | 266
2016-11-07 14:00 | 277 | 276
2016-11-07 14:30 | 280 | 280
2016-11-07 15:00 | 287 | 287
2016-11-07 15:30 | 291 | 291
2016-11-07 16:00 | 300 | 300
2016-11-07 16:30 | 310 | 310
2016-11-07 17:00 | 309 | 308
2016-11-07 17:30 | 306 | 305
2016-11-07 18:00 | 301 | 301
2016-11-07 18:30 | 311 | 311
2016-11-07 19:00 | 306 | 306
2016-11-07 19:30 | 297 | 297
2016-11-07 20:00 | 285 | 285
2016-11-07 20:30 | 269 | 269
2016-11-07 21:00 | 256 | 256
2016-11-07 21:30 | 246 | 246
2016-11-07 22:00 | 244 | 244
2016-11-07 22:30 | 242 | 242
2016-11-07 23:00 | 224 | 224
2016-11-07 23:30 | 203 | 203
2016-11-08 | 193 | 193
2016-11-08 00:30 | 184 | 184
2016-11-08 01:00 | 185 | 185
2016-11-08 01:30 | 182 | 182
2016-11-08 02:00 | 181 | 181
2016-11-08 02:30 | 181 | 181
2016-11-08 03:00 | 182 | 182
2016-11-08 03:30 | 184 | 184
2016-11-08 04:00 | 191 | 191
2016-11-08 04:30 | 194 | 194
2016-11-08 05:00 | 203 | 203
2016-11-08 05:30 | 216 | 216
2016-11-08 06:00 | 238 | 238
2016-11-08 06:30 | 259 | 259
2016-11-08 07:00 | 273 | 273
2016-11-08 07:30 | 284 | 283
2016-11-08 08:00 | 288 | 288
2016-11-08 08:30 | 286 | 286
2016-11-08 09:00 | 292 | 292
2016-11-08 09:30 | 296 | 296
2016-11-08 10:00 | 302 | 302
2016-11-08 10:30 | 300 | 300
2016-11-08 11:00 | 304 | 304
2016-11-08 11:30 | 310 | 310
2016-11-08 12:00 | 317 | 317
2016-11-08 12:30 | 325 | 325
2016-11-08 13:00 | 327 | 327
2016-11-08 13:30 | 335 | 335
2016-11-08 14:00 | 341 | 340
2016-11-08 14:30 | 348 | 348
2016-11-08 15:00 | 348 | 347
2016-11-08 15:30 | 345 | 344
2016-11-08 16:00 | 346 | 345
2016-11-08 16:30 | 346 | 344
2016-11-08 17:00 | 337 | 336
2016-11-08 17:30 | 332 | 332
2016-11-08 18:00 | 327 | 327
2016-11-08 18:30 | 327 | 327
2016-11-08 19:00 | 320 | 320
2016-11-08 19:30 | 314 | 314
2016-11-08 20:00 | 306 | 306
2016-11-08 20:30 | 293 | 293
2016-11-08 21:00 | 275 | 275
2016-11-08 21:30 | 252 | 252
2016-11-08 22:00 | 257 | 257
2016-11-08 22:30 | 250 | 249
2016-11-08 23:00 | 233 | 232
2016-11-08 23:30 | 215 | 215
2016-11-09 | 206 | 205
2016-11-09 00:30 | 194 | 193
2016-11-09 01:00 | 186 | 185
2016-11-09 01:30 | 181 | 180
2016-11-09 02:00 | 180 | 179
2016-11-09 02:30 | 181 | 180
2016-11-09 03:00 | 183 | 182
2016-11-09 03:30 | 186 | 185
2016-11-09 04:00 | 187 | 186
2016-11-09 04:30 | 190 | 189
2016-11-09 05:00 | 201 | 200
2016-11-09 05:30 | 217 | 217
2016-11-09 06:00 | 235 | 234
2016-11-09 06:30 | 257 | 256
2016-11-09 07:00 | 268 | 268
2016-11-09 07:30 | 273 | 273
2016-11-09 08:00 | 280 | 280
2016-11-09 08:30 | 286 | 284
2016-11-09 09:00 | 282 | 281
2016-11-09 09:30 | 288 | 287
2016-11-09 10:00 | 305 | 304
2016-11-09 10:30 | 315 | 314
2016-11-09 11:00 | 317 | 316
2016-11-09 11:30 | 300 | 300
2016-11-09 12:00 | 299 | 298
2016-11-09 12:30 | 301 | 300
2016-11-09 13:00 | 304 | 304
2016-11-09 13:30 | 305 | 305
2016-11-09 14:00 | 309 | 309
2016-11-09 14:30 | 317 | 316
2016-11-09 15:00 | 330 | 330
2016-11-09 15:30 | 334 | 333
2016-11-09 16:00 | 326 | 325
2016-11-09 16:30 | 326 | 324
2016-11-09 17:00 | 319 | 316
2016-11-09 17:30 | 315 | 313
2016-11-09 18:00 | 310 | 309
2016-11-09 18:30 | 313 | 311
2016-11-09 19:00 | 305 | 304
2016-11-09 19:30 | 304 | 302
2016-11-09 20:00 | 299 | 296
2016-11-09 20:30 | 277 | 276
2016-11-09 21:00 | 259 | 259
2016-11-09 21:30 | 241 | 241
2016-11-09 22:00 | 237 | 237
2016-11-09 22:30 | 231 | 231
2016-11-09 23:00 | 213 | 213
2016-11-09 23:30 | 203 | 203
2016-11-10 | 190 | 189
2016-11-10 00:30 | 183 | 183
2016-11-10 01:00 | 175 | 174
2016-11-10 01:30 | 170 | 170
2016-11-10 02:00 | 167 | 167
2016-11-10 02:30 | 167 | 166
2016-11-10 03:00 | 168 | 168
2016-11-10 03:30 | 170 | 170
2016-11-10 04:00 | 174 | 173
2016-11-10 04:30 | 184 | 183
2016-11-10 05:00 | 196 | 194
2016-11-10 05:30 | 215 | 215
2016-11-10 06:00 | 232 | 231
2016-11-10 06:30 | 239 | 238
2016-11-10 07:00 | 252 | 252
2016-11-10 07:30 | 260 | 260
2016-11-10 08:00 | 266 | 266
2016-11-10 08:30 | 271 | 271
2016-11-10 09:00 | 280 | 279
2016-11-10 09:30 | 283 | 283
2016-11-10 10:00 | 284 | 284
2016-11-10 10:30 | 284 | 283
2016-11-10 11:00 | 285 | 285
2016-11-10 11:30 | 290 | 290
2016-11-10 12:00 | 295 | 295
2016-11-10 12:30 | 309 | 308
2016-11-10 13:00 | 307 | 306
2016-11-10 13:30 | 308 | 306
2016-11-10 14:00 | 312 | 311
2016-11-10 14:30 | 318 | 317
2016-11-10 15:00 | 324 | 323
2016-11-10 15:30 | 323 | 322
2016-11-10 16:00 | 328 | 326
2016-11-10 16:30 | 328 | 326
2016-11-10 17:00 | 325 | 323
2016-11-10 17:30 | 321 | 320
2016-11-10 18:00 | 319 | 319
2016-11-10 18:30 | 331 | 330
2016-11-10 19:00 | 324 | 323
2016-11-10 19:30 | 322 | 321
2016-11-10 20:00 | 306 | 306
2016-11-10 20:30 | 284 | 284
2016-11-10 21:00 | 267 | 266
2016-11-10 21:30 | 246 | 245
2016-11-10 22:00 | 246 | 246
2016-11-10 22:30 | 242 | 242
2016-11-10 23:00 | 221 | 221
2016-11-10 23:30 | 200 | 200
2016-11-11 | 186 | 185
2016-11-11 00:30 | 176 | 175
2016-11-11 01:00 | 166 | 166
2016-11-11 01:30 | 161 | 161
2016-11-11 02:00 | 158 | 158
2016-11-11 02:30 | 156 | 156
2016-11-11 03:00 | 156 | 156
2016-11-11 03:30 | 156 | 156
2016-11-11 04:00 | 159 | 159
2016-11-11 04:30 | 162 | 162
2016-11-11 05:00 | 171 | 171
2016-11-11 05:30 | 181 | 181
2016-11-11 06:00 | 197 | 197
2016-11-11 06:30 | 215 | 214
2016-11-11 07:00 | 235 | 233
2016-11-11 07:30 | 244 | 244
2016-11-11 08:00 | 256 | 256
2016-11-11 08:30 | 265 | 264
2016-11-11 09:00 | 268 | 268
2016-11-11 09:30 | 269 | 269
2016-11-11 10:00 | 268 | 267
2016-11-11 10:30 | 265 | 264
2016-11-11 11:00 | 277 | 276
2016-11-11 11:30 | 273 | 272
2016-11-11 12:00 | 281 | 279
2016-11-11 12:30 | 288 | 287
2016-11-11 13:00 | 285 | 284
2016-11-11 13:30 | 289 | 288
2016-11-11 14:00 | 295 | 294
2016-11-11 14:30 | 298 | 297
2016-11-11 15:00 | 301 | 299
2016-11-11 15:30 | 309 | 307
2016-11-11 16:00 | 307 | 306
2016-11-11 16:30 | 307 | 306
2016-11-11 17:00 | 299 | 297
2016-11-11 17:30 | 290 | 287
2016-11-11 18:00 | 281 | 279
2016-11-11 18:30 | 294 | 293
2016-11-11 19:00 | 291 | 289
2016-11-11 19:30 | 286 | 284
2016-11-11 20:00 | 274 | 272
2016-11-11 20:30 | 259 | 257
2016-11-11 21:00 | 252 | 251
2016-11-11 21:30 | 232 | 231
2016-11-11 22:00 | 223 | 222
2016-11-11 22:30 | 228 | 228
2016-11-11 23:00 | 203 | 203
2016-11-11 23:30 | 194 | 194
2016-11-12 | 168 | 168
2016-11-12 00:30 | 157 | 157
2016-11-12 01:00 | 163 | 163
2016-11-12 01:30 | 160 | 160
2016-11-12 02:00 | 159 | 159
2016-11-12 02:30 | 136 | 136
2016-11-12 03:00 | 142 | 142
2016-11-12 03:30 | 132 | 132
2016-11-12 04:00 | 155 | 155
2016-11-12 04:30 | 158 | 158
2016-11-12 05:00 | 162 | 162
2016-11-12 05:30 | 180 | 179
2016-11-12 06:00 | 201 | 200
2016-11-12 06:30 | 208 | 207
2016-11-12 07:00 | 219 | 218
2016-11-12 07:30 | 232 | 230
2016-11-12 08:00 | 218 | 217
2016-11-12 08:30 | 230 | 230
2016-11-12 09:00 | 236 | 236
2016-11-12 09:30 | 238 | 238
2016-11-12 10:00 | 244 | 243
2016-11-12 10:30 | 259 | 259
2016-11-12 11:00 | 256 | 256
2016-11-12 11:30 | 251 | 251
2016-11-12 12:00 | 271 | 270
2016-11-12 12:30 | 300 | 300
2016-11-12 13:00 | 316 | 316
2016-11-12 13:30 | 326 | 326
2016-11-12 14:00 | 329 | 329
2016-11-12 14:30 | 324 | 324
2016-11-12 15:00 | 311 | 310
2016-11-12 15:30 | 296 | 296
2016-11-12 16:00 | 294 | 294
2016-11-12 16:30 | 282 | 281
2016-11-12 17:00 | 286 | 285
2016-11-12 17:30 | 287 | 286
2016-11-12 18:00 | 281 | 280
2016-11-12 18:30 | 286 | 285
2016-11-12 19:00 | 280 | 279
2016-11-12 19:30 | 285 | 284
2016-11-12 20:00 | 280 | 279
2016-11-12 20:30 | 245 | 244
2016-11-12 21:00 | 235 | 235
2016-11-12 21:30 | 227 | 227
2016-11-12 22:00 | 213 | 212
2016-11-12 22:30 | 226 | 225
2016-11-12 23:00 | 196 | 195
2016-11-12 23:30 | 176 | 176
2016-11-13 | 162 | 162
2016-11-13 00:30 | 180 | 180
2016-11-13 01:00 | 175 | 175
2016-11-13 01:30 | 170 | 170
2016-11-13 02:00 | 162 | 162
2016-11-13 02:30 | 159 | 159
2016-11-13 03:00 | 144 | 144
2016-11-13 03:30 | 129 | 129
2016-11-13 04:00 | 151 | 151
2016-11-13 04:30 | 164 | 164
2016-11-13 05:00 | 165 | 165
2016-11-13 05:30 | 166 | 166
2016-11-13 06:00 | 142 | 141
2016-11-13 06:30 | 182 | 181
2016-11-13 07:00 | 197 | 196
2016-11-13 07:30 | 221 | 220
2016-11-13 08:00 | 236 | 235
2016-11-13 08:30 | 241 | 241
2016-11-13 09:00 | 243 | 243
2016-11-13 09:30 | 246 | 246
2016-11-13 10:00 | 251 | 251
2016-11-13 10:30 | 248 | 247
2016-11-13 11:00 | 259 | 259
2016-11-13 11:30 | 267 | 267
2016-11-13 12:00 | 256 | 256
2016-11-13 12:30 | 260 | 260
2016-11-13 13:00 | 258 | 258
2016-11-13 13:30 | 273 | 273
2016-11-13 14:00 | 276 | 276
2016-11-13 14:30 | 289 | 289
2016-11-13 15:00 | 307 | 307
2016-11-13 15:30 | 318 | 318
2016-11-13 16:00 | 311 | 311
2016-11-13 16:30 | 321 | 320
2016-11-13 17:00 | 329 | 328
2016-11-13 17:30 | 324 | 324
2016-11-13 18:00 | 322 | 322
2016-11-13 18:30 | 333 | 333
2016-11-13 19:00 | 329 | 328
2016-11-13 19:30 | 328 | 327
2016-11-13 20:00 | 313 | 313
2016-11-13 20:30 | 295 | 295
2016-11-13 21:00 | 280 | 280
2016-11-13 21:30 | 264 | 264
2016-11-13 22:00 | 229 | 227
2016-11-13 22:30 | 224 | 222
2016-11-13 23:00 | 214 | 213
2016-11-13 23:30 | 213 | 212
2016-11-14 | 201 | 201
2016-11-14 00:30 | 185 | 185
2016-11-14 01:00 | 179 | 179
2016-11-14 01:30 | 175 | 175
2016-11-14 02:00 | 174 | 174
2016-11-14 02:30 | 174 | 174
2016-11-14 03:00 | 172 | 171
2016-11-14 03:30 | 171 | 171
2016-11-14 04:00 | 174 | 174
2016-11-14 04:30 | 176 | 176
2016-11-14 05:00 | 187 | 187
2016-11-14 05:30 | 198 | 198
2016-11-14 06:00 | 213 | 212
2016-11-14 06:30 | 233 | 232
2016-11-14 07:00 | 236 | 236
2016-11-14 07:30 | 244 | 244
2016-11-14 08:00 | 241 | 241
2016-11-14 08:30 | 244 | 244
2016-11-14 09:00 | 247 | 247
2016-11-14 09:30 | 250 | 250
2016-11-14 10:00 | 252 | 252
2016-11-14 10:30 | 250 | 250
2016-11-14 11:00 | 248 | 248
2016-11-14 11:30 | 253 | 253
2016-11-14 12:00 | 257 | 256
2016-11-14 12:30 | 256 | 256
2016-11-14 13:00 | 258 | 257
2016-11-14 13:30 | 255 | 255
2016-11-14 14:00 | 264 | 264
2016-11-14 14:30 | 265 | 265
2016-11-14 15:00 | 267 | 267
2016-11-14 15:30 | 282 | 281
2016-11-14 16:00 | 291 | 290
2016-11-14 16:30 | 296 | 295
2016-11-14 17:00 | 294 | 292
2016-11-14 17:30 | 287 | 286
2016-11-14 18:00 | 281 | 280
2016-11-14 18:30 | 292 | 291
2016-11-14 19:00 | 285 | 284
2016-11-14 19:30 | 289 | 288
2016-11-14 20:00 | 279 | 278
2016-11-14 20:30 | 263 | 263
2016-11-14 21:00 | 254 | 253
2016-11-14 21:30 | 242 | 241
2016-11-14 22:00 | 246 | 246
2016-11-14 22:30 | 247 | 247
2016-11-14 23:00 | 227 | 227
2016-11-14 23:30 | 208 | 208
2016-11-15 | 192 | 192
2016-11-15 00:30 | 188 | 188
2016-11-15 01:00 | 179 | 179
2016-11-15 01:30 | 174 | 174
2016-11-15 02:00 | 167 | 167
2016-11-15 02:30 | 161 | 161
2016-11-15 03:00 | 158 | 158
2016-11-15 03:30 | 166 | 166
2016-11-15 04:00 | 173 | 173
2016-11-15 04:30 | 174 | 174
2016-11-15 05:00 | 184 | 184
2016-11-15 05:30 | 189 | 188
2016-11-15 06:00 | 206 | 205
2016-11-15 06:30 | 220 | 220
2016-11-15 07:00 | 234 | 233
2016-11-15 07:30 | 239 | 238
2016-11-15 08:00 | 244 | 243
2016-11-15 08:30 | 246 | 245
2016-11-15 09:00 | 249 | 249
2016-11-15 09:30 | 243 | 243
2016-11-15 10:00 | 239 | 239
2016-11-15 10:30 | 231 | 231
2016-11-15 11:00 | 231 | 231
2016-11-15 11:30 | 236 | 236
2016-11-15 12:00 | 236 | 236
2016-11-15 12:30 | 233 | 233
2016-11-15 13:00 | 238 | 238
2016-11-15 13:30 | 244 | 244
2016-11-15 14:00 | 245 | 245
2016-11-15 14:30 | 248 | 248
2016-11-15 15:00 | 248 | 248
2016-11-15 15:30 | 245 | 245
2016-11-15 16:00 | 252 | 252
2016-11-15 16:30 | 270 | 270
2016-11-15 17:00 | 269 | 269
2016-11-15 17:30 | 271 | 270
2016-11-15 18:00 | 265 | 265
2016-11-15 18:30 | 280 | 280
2016-11-15 19:00 | 278 | 277
2016-11-15 19:30 | 271 | 271
2016-11-15 20:00 | 257 | 257
2016-11-15 20:30 | 243 | 243
2016-11-15 21:00 | 232 | 232
2016-11-15 21:30 | 224 | 224
2016-11-15 22:00 | 225 | 225
2016-11-15 22:30 | 225 | 225
2016-11-15 23:00 | 205 | 205
2016-11-15 23:30 | 197 | 196
2016-11-16 | 185 | 185
2016-11-16 00:30 | 176 | 176
2016-11-16 01:00 | 169 | 169
2016-11-16 01:30 | 161 | 161
2016-11-16 02:00 | 160 | 160
2016-11-16 02:30 | 160 | 160
2016-11-16 03:00 | 163 | 163
2016-11-16 03:30 | 166 | 166
2016-11-16 04:00 | 173 | 173
2016-11-16 04:30 | 176 | 176
2016-11-16 05:00 | 189 | 189
2016-11-16 05:30 | 201 | 201
2016-11-16 06:00 | 214 | 214
2016-11-16 06:30 | 223 | 223
2016-11-16 07:00 | 239 | 239
2016-11-16 07:30 | 242 | 241
2016-11-16 08:00 | 249 | 248
2016-11-16 08:30 | 252 | 250
2016-11-16 09:00 | 252 | 250
2016-11-16 09:30 | 254 | 254
2016-11-16 10:00 | 253 | 252
2016-11-16 10:30 | 252 | 252
2016-11-16 11:00 | 251 | 251
2016-11-16 11:30 | 252 | 251
2016-11-16 12:00 | 248 | 248
2016-11-16 12:30 | 245 | 245
2016-11-16 13:00 | 244 | 244
2016-11-16 13:30 | 245 | 245
2016-11-16 14:00 | 251 | 250
2016-11-16 14:30 | 252 | 252
2016-11-16 15:00 | 260 | 259
2016-11-16 15:30 | 258 | 258
2016-11-16 16:00 | 263 | 262
2016-11-16 16:30 | 268 | 268
2016-11-16 17:00 | 266 | 266
2016-11-16 17:30 | 267 | 267
2016-11-16 18:00 | 266 | 266
2016-11-16 18:30 | 275 | 274
2016-11-16 19:00 | 273 | 273
2016-11-16 19:30 | 269 | 269
2016-11-16 20:00 | 252 | 252
2016-11-16 20:30 | 245 | 245
2016-11-16 21:00 | 239 | 239
2016-11-16 21:30 | 234 | 234
2016-11-16 22:00 | 232 | 232
2016-11-16 22:30 | 231 | 231
2016-11-16 23:00 | 215 | 215
2016-11-16 23:30 | 202 | 201
2016-11-17 | 188 | 188
2016-11-17 00:30 | 180 | 179
2016-11-17 01:00 | 178 | 177
2016-11-17 01:30 | 176 | 176
2016-11-17 02:00 | 169 | 168
2016-11-17 02:30 | 168 | 167
2016-11-17 03:00 | 166 | 165
2016-11-17 03:30 | 165 | 164
2016-11-17 04:00 | 175 | 174
2016-11-17 04:30 | 180 | 179
2016-11-17 05:00 | 189 | 189
2016-11-17 05:30 | 200 | 200
2016-11-17 06:00 | 218 | 218
2016-11-17 06:30 | 220 | 220
2016-11-17 07:00 | 231 | 231
2016-11-17 07:30 | 235 | 234
2016-11-17 08:00 | 238 | 237
2016-11-17 08:30 | 239 | 238
2016-11-17 09:00 | 257 | 256
2016-11-17 09:30 | 280 | 279
2016-11-17 10:00 | 281 | 281
2016-11-17 10:30 | 276 | 276
2016-11-17 11:00 | 271 | 271
2016-11-17 11:30 | 267 | 267
2016-11-17 12:00 | 265 | 265
2016-11-17 12:30 | 267 | 267
2016-11-17 13:00 | 271 | 271
2016-11-17 13:30 | 273 | 273
2016-11-17 14:00 | 266 | 266
2016-11-17 14:30 | 260 | 260
2016-11-17 15:00 | 258 | 258
2016-11-17 15:30 | 257 | 256
2016-11-17 16:00 | 262 | 261
2016-11-17 16:30 | 267 | 266
2016-11-17 17:00 | 267 | 266
2016-11-17 17:30 | 270 | 269
2016-11-17 18:00 | 269 | 268
2016-11-17 18:30 | 274 | 274
2016-11-17 19:00 | 272 | 272
2016-11-17 19:30 | 271 | 270
2016-11-17 20:00 | 267 | 266
2016-11-17 20:30 | 261 | 259
2016-11-17 21:00 | 255 | 253
2016-11-17 21:30 | 238 | 237
2016-11-17 22:00 | 228 | 228
2016-11-17 22:30 | 231 | 231
2016-11-17 23:00 | 214 | 214
2016-11-17 23:30 | 201 | 201
2016-11-18 | 189 | 188
2016-11-18 00:30 | 178 | 178
2016-11-18 01:00 | 175 | 175
2016-11-18 01:30 | 167 | 166
2016-11-18 02:00 | 164 | 163
2016-11-18 02:30 | 164 | 163
2016-11-18 03:00 | 163 | 162
2016-11-18 03:30 | 161 | 160
2016-11-18 04:00 | 173 | 172
2016-11-18 04:30 | 178 | 177
2016-11-18 05:00 | 189 | 188
2016-11-18 05:30 | 201 | 200
2016-11-18 06:00 | 209 | 209
2016-11-18 06:30 | 222 | 222
2016-11-18 07:00 | 237 | 237
2016-11-18 07:30 | 243 | 243
2016-11-18 08:00 | 242 | 242
2016-11-18 08:30 | 242 | 242
2016-11-18 09:00 | 245 | 245
2016-11-18 09:30 | 245 | 245
2016-11-18 10:00 | 244 | 244
2016-11-18 10:30 | 242 | 242
2016-11-18 11:00 | 241 | 241
2016-11-18 11:30 | 241 | 241
2016-11-18 12:00 | 240 | 240
2016-11-18 12:30 | 241 | 241
2016-11-18 13:00 | 243 | 243
2016-11-18 13:30 | 248 | 248
2016-11-18 14:00 | 252 | 252
2016-11-18 14:30 | 257 | 257
2016-11-18 15:00 | 262 | 262
2016-11-18 15:30 | 271 | 271
2016-11-18 16:00 | 280 | 280
2016-11-18 16:30 | 285 | 285
2016-11-18 17:00 | 281 | 280
2016-11-18 17:30 | 275 | 275
2016-11-18 18:00 | 272 | 272
2016-11-18 18:30 | 282 | 282
2016-11-18 19:00 | 285 | 285
2016-11-18 19:30 | 283 | 283
2016-11-18 20:00 | 276 | 276
2016-11-18 20:30 | 264 | 263
2016-11-18 21:00 | 250 | 250
2016-11-18 21:30 | 237 | 237
2016-11-18 22:00 | 232 | 232
2016-11-18 22:30 | 227 | 226
2016-11-18 23:00 | 209 | 208
2016-11-18 23:30 | 199 | 198
2016-11-19 | 183 | 182
2016-11-19 00:30 | 174 | 173
2016-11-19 01:00 | 169 | 168
2016-11-19 01:30 | 167 | 166
2016-11-19 02:00 | 162 | 160
2016-11-19 02:30 | 158 | 156
2016-11-19 03:00 | 157 | 156
2016-11-19 03:30 | 157 | 155
2016-11-19 04:00 | 161 | 160
2016-11-19 04:30 | 160 | 159
2016-11-19 05:00 | 169 | 169
2016-11-19 05:30 | 177 | 177
2016-11-19 06:00 | 185 | 184
2016-11-19 06:30 | 195 | 195
2016-11-19 07:00 | 211 | 211
2016-11-19 07:30 | 220 | 220
2016-11-19 08:00 | 218 | 218
2016-11-19 08:30 | 230 | 230
2016-11-19 09:00 | 238 | 238
2016-11-19 09:30 | 244 | 244
2016-11-19 10:00 | 241 | 241
2016-11-19 10:30 | 239 | 239
2016-11-19 11:00 | 233 | 233
2016-11-19 11:30 | 225 | 224
2016-11-19 12:00 | 219 | 219
2016-11-19 12:30 | 215 | 215
2016-11-19 13:00 | 221 | 221
2016-11-19 13:30 | 228 | 228
2016-11-19 14:00 | 225 | 225
2016-11-19 14:30 | 223 | 223
2016-11-19 15:00 | 223 | 223
2016-11-19 15:30 | 225 | 225
2016-11-19 16:00 | 236 | 236
2016-11-19 16:30 | 243 | 243
2016-11-19 17:00 | 241 | 241
2016-11-19 17:30 | 239 | 239
2016-11-19 18:00 | 236 | 236
2016-11-19 18:30 | 246 | 245
2016-11-19 19:00 | 242 | 242
2016-11-19 19:30 | 239 | 239
2016-11-19 20:00 | 236 | 235
2016-11-19 20:30 | 229 | 229
2016-11-19 21:00 | 230 | 230
2016-11-19 21:30 | 225 | 225
2016-11-19 22:00 | 220 | 220
2016-11-19 22:30 | 221 | 221
2016-11-19 23:00 | 204 | 204
2016-11-19 23:30 | 189 | 188
2016-11-20 | 180 | 179
2016-11-20 00:30 | 174 | 173
2016-11-20 01:00 | 171 | 170
2016-11-20 01:30 | 166 | 165
2016-11-20 02:00 | 161 | 160
2016-11-20 02:30 | 159 | 158
2016-11-20 03:00 | 157 | 155
2016-11-20 03:30 | 156 | 154
2016-11-20 04:00 | 160 | 159
2016-11-20 04:30 | 165 | 164
2016-11-20 05:00 | 168 | 167
2016-11-20 05:30 | 172 | 172
2016-11-20 06:00 | 177 | 177
2016-11-20 06:30 | 182 | 182
2016-11-20 07:00 | 192 | 192
2016-11-20 07:30 | 202 | 201
2016-11-20 08:00 | 208 | 208
2016-11-20 08:30 | 208 | 208
2016-11-20 09:00 | 212 | 212
2016-11-20 09:30 | 214 | 214
2016-11-20 10:00 | 216 | 216
2016-11-20 10:30 | 215 | 215
2016-11-20 11:00 | 214 | 214
2016-11-20 11:30 | 216 | 215
2016-11-20 12:00 | 214 | 214
2016-11-20 12:30 | 215 | 215
2016-11-20 13:00 | 218 | 218
2016-11-20 13:30 | 221 | 221
2016-11-20 14:00 | 225 | 225
2016-11-20 14:30 | 232 | 230
2016-11-20 15:00 | 237 | 236
2016-11-20 15:30 | 240 | 240
2016-11-20 16:00 | 243 | 243
2016-11-20 16:30 | 251 | 251
2016-11-20 17:00 | 252 | 251
2016-11-20 17:30 | 256 | 255
2016-11-20 18:00 | 258 | 257
2016-11-20 18:30 | 266 | 266
2016-11-20 19:00 | 266 | 265
2016-11-20 19:30 | 262 | 261
2016-11-20 20:00 | 249 | 249
2016-11-20 20:30 | 237 | 237
2016-11-20 21:00 | 235 | 235
2016-11-20 21:30 | 228 | 228
2016-11-20 22:00 | 225 | 225
2016-11-20 22:30 | 224 | 224
2016-11-20 23:00 | 202 | 202
2016-11-20 23:30 | 190 | 189
2016-11-21 | 183 | 183
2016-11-21 00:30 | 179 | 178
2016-11-21 01:00 | 175 | 174
2016-11-21 01:30 | 172 | 170
2016-11-21 02:00 | 171 | 170
2016-11-21 02:30 | 171 | 170
2016-11-21 03:00 | 170 | 169
2016-11-21 03:30 | 166 | 164
2016-11-21 04:00 | 163 | 162
2016-11-21 04:30 | 166 | 164
2016-11-21 05:00 | 171 | 169
2016-11-21 05:30 | 195 | 194
2016-11-21 06:00 | 209 | 209
2016-11-21 06:30 | 205 | 205
2016-11-21 07:00 | 217 | 217
2016-11-21 07:30 | 225 | 225
2016-11-21 08:00 | 228 | 228
2016-11-21 08:30 | 228 | 228
2016-11-21 09:00 | 230 | 230
2016-11-21 09:30 | 230 | 229
2016-11-21 10:00 | 229 | 228
2016-11-21 10:30 | 230 | 229
2016-11-21 11:00 | 229 | 229
2016-11-21 11:30 | 229 | 229
2016-11-21 12:00 | 231 | 231
2016-11-21 12:30 | 233 | 233
2016-11-21 13:00 | 236 | 236
2016-11-21 13:30 | 241 | 241
2016-11-21 14:00 | 247 | 247
2016-11-21 14:30 | 253 | 252
2016-11-21 15:00 | 259 | 258
2016-11-21 15:30 | 268 | 268
2016-11-21 16:00 | 279 | 279
2016-11-21 16:30 | 288 | 288
2016-11-21 17:00 | 280 | 280
2016-11-21 17:30 | 267 | 267
2016-11-21 18:00 | 277 | 277
2016-11-21 18:30 | 283 | 283
2016-11-21 19:00 | 280 | 280
2016-11-21 19:30 | 275 | 274
2016-11-21 20:00 | 264 | 263
2016-11-21 20:30 | 252 | 251
2016-11-21 21:00 | 247 | 246
2016-11-21 21:30 | 234 | 234
2016-11-21 22:00 | 231 | 231
2016-11-21 22:30 | 232 | 232
2016-11-21 23:00 | 211 | 211
2016-11-21 23:30 | 197 | 197
2016-11-22 | 187 | 187
2016-11-22 00:30 | 185 | 184
2016-11-22 01:00 | 179 | 178
2016-11-22 01:30 | 179 | 178
2016-11-22 02:00 | 170 | 170
2016-11-22 02:30 | 168 | 168
2016-11-22 03:00 | 164 | 164
2016-11-22 03:30 | 165 | 165
2016-11-22 04:00 | 172 | 172
2016-11-22 04:30 | 178 | 178
2016-11-22 05:00 | 185 | 185
2016-11-22 05:30 | 195 | 195
2016-11-22 06:00 | 204 | 204
2016-11-22 06:30 | 213 | 213
2016-11-22 07:00 | 231 | 231
2016-11-22 07:30 | 237 | 237
2016-11-22 08:00 | 241 | 241
2016-11-22 08:30 | 240 | 240
2016-11-22 09:00 | 241 | 241
2016-11-22 09:30 | 239 | 239
2016-11-22 10:00 | 238 | 237
2016-11-22 10:30 | 234 | 234
2016-11-22 11:00 | 233 | 233
2016-11-22 11:30 | 233 | 233
2016-11-22 12:00 | 233 | 233
2016-11-22 12:30 | 234 | 234
2016-11-22 13:00 | 237 | 237
2016-11-22 13:30 | 243 | 243
2016-11-22 14:00 | 249 | 249
2016-11-22 14:30 | 260 | 260
2016-11-22 15:00 | 266 | 265
2016-11-22 15:30 | 276 | 276
2016-11-22 16:00 | 279 | 278
2016-11-22 16:30 | 283 | 282
2016-11-22 17:00 | 277 | 277
2016-11-22 17:30 | 271 | 271
2016-11-22 18:00 | 266 | 266
2016-11-22 18:30 | 262 | 262
2016-11-22 19:00 | 258 | 258
2016-11-22 19:30 | 250 | 250
2016-11-22 20:00 | 242 | 242
2016-11-22 20:30 | 227 | 227
2016-11-22 21:00 | 225 | 225
2016-11-22 21:30 | 213 | 212
2016-11-22 22:00 | 212 | 211
2016-11-22 22:30 | 203 | 202
2016-11-22 23:00 | 185 | 183
2016-11-22 23:30 | 181 | 179
2016-11-23 | 169 | 168
2016-11-23 00:30 | 164 | 163
2016-11-23 01:00 | 164 | 162
2016-11-23 01:30 | 161 | 160
2016-11-23 02:00 | 160 | 158
2016-11-23 02:30 | 155 | 154
2016-11-23 03:00 | 154 | 153
2016-11-23 03:30 | 154 | 152
2016-11-23 04:00 | 158 | 156
2016-11-23 04:30 | 166 | 164
2016-11-23 05:00 | 173 | 172
2016-11-23 05:30 | 186 | 185
2016-11-23 06:00 | 198 | 198
2016-11-23 06:30 | 210 | 210
2016-11-23 07:00 | 223 | 223
2016-11-23 07:30 | 228 | 228
2016-11-23 08:00 | 231 | 231
2016-11-23 08:30 | 232 | 231
2016-11-23 09:00 | 226 | 226
2016-11-23 09:30 | 241 | 240
2016-11-23 10:00 | 231 | 231
2016-11-23 10:30 | 235 | 234
2016-11-23 11:00 | 245 | 245
2016-11-23 11:30 | 243 | 242
2016-11-23 12:00 | 243 | 242
2016-11-23 12:30 | 249 | 249
2016-11-23 13:00 | 254 | 253
2016-11-23 13:30 | 259 | 259
2016-11-23 14:00 | 261 | 261
2016-11-23 14:30 | 270 | 269
2016-11-23 15:00 | 259 | 258
2016-11-23 15:30 | 270 | 270
2016-11-23 16:00 | 282 | 281
2016-11-23 16:30 | 288 | 286
2016-11-23 17:00 | 291 | 289
2016-11-23 17:30 | 288 | 286
2016-11-23 18:00 | 279 | 277
2016-11-23 18:30 | 287 | 286
2016-11-23 19:00 | 288 | 287
2016-11-23 19:30 | 285 | 283
2016-11-23 20:00 | 279 | 276
2016-11-23 20:30 | 256 | 255
2016-11-23 21:00 | 245 | 244
2016-11-23 21:30 | 226 | 225
2016-11-23 22:00 | 224 | 223
2016-11-23 22:30 | 228 | 227
2016-11-23 23:00 | 207 | 205
2016-11-23 23:30 | 195 | 194
2016-11-24 | 185 | 183
2016-11-24 00:30 | 181 | 178
2016-11-24 01:00 | 179 | 175
2016-11-24 01:30 | 177 | 174
2016-11-24 02:00 | 175 | 171
2016-11-24 02:30 | 170 | 166
2016-11-24 03:00 | 167 | 166
2016-11-24 03:30 | 168 | 166
2016-11-24 04:00 | 171 | 170
2016-11-24 04:30 | 173 | 172
2016-11-24 05:00 | 183 | 182
2016-11-24 05:30 | 202 | 202
2016-11-24 06:00 | 215 | 215
2016-11-24 06:30 | 228 | 228
2016-11-24 07:00 | 247 | 246
2016-11-24 07:30 | 253 | 250
2016-11-24 08:00 | 257 | 256
2016-11-24 08:30 | 257 | 256
2016-11-24 09:00 | 258 | 257
2016-11-24 09:30 | 261 | 261
2016-11-24 10:00 | 261 | 261
2016-11-24 10:30 | 250 | 250
2016-11-24 11:00 | 259 | 259
2016-11-24 11:30 | 266 | 266
2016-11-24 12:00 | 266 | 265
2016-11-24 12:30 | 263 | 262
2016-11-24 13:00 | 257 | 256
2016-11-24 13:30 | 261 | 261
2016-11-24 14:00 | 267 | 267
2016-11-24 14:30 | 269 | 269
2016-11-24 15:00 | 278 | 278
2016-11-24 15:30 | 278 | 278
2016-11-24 16:00 | 282 | 282
2016-11-24 16:30 | 284 | 284
2016-11-24 17:00 | 273 | 273
2016-11-24 17:30 | 269 | 268
2016-11-24 18:00 | 269 | 268
2016-11-24 18:30 | 273 | 273
2016-11-24 19:00 | 263 | 262
2016-11-24 19:30 | 265 | 265
2016-11-24 20:00 | 262 | 261
2016-11-24 20:30 | 248 | 248
2016-11-24 21:00 | 238 | 238
2016-11-24 21:30 | 230 | 230
2016-11-24 22:00 | 233 | 233
2016-11-24 22:30 | 228 | 228
2016-11-24 23:00 | 203 | 202
2016-11-24 23:30 | 191 | 191
2016-11-25 | 181 | 181
2016-11-25 00:30 | 178 | 178
2016-11-25 01:00 | 173 | 173
2016-11-25 01:30 | 168 | 168
2016-11-25 02:00 | 161 | 161
2016-11-25 02:30 | 159 | 158
2016-11-25 03:00 | 158 | 157
2016-11-25 03:30 | 157 | 157
2016-11-25 04:00 | 167 | 167
2016-11-25 04:30 | 168 | 168
2016-11-25 05:00 | 176 | 176
2016-11-25 05:30 | 180 | 180
2016-11-25 06:00 | 191 | 191
2016-11-25 06:30 | 208 | 208
2016-11-25 07:00 | 218 | 218
2016-11-25 07:30 | 225 | 225
2016-11-25 08:00 | 232 | 232
2016-11-25 08:30 | 236 | 236
2016-11-25 09:00 | 238 | 238
2016-11-25 09:30 | 235 | 235
2016-11-25 10:00 | 230 | 230
2016-11-25 10:30 | 227 | 227
2016-11-25 11:00 | 228 | 228
2016-11-25 11:30 | 229 | 229
2016-11-25 12:00 | 233 | 233
2016-11-25 12:30 | 241 | 241
2016-11-25 13:00 | 249 | 249
2016-11-25 13:30 | 236 | 236
2016-11-25 14:00 | 238 | 238
2016-11-25 14:30 | 242 | 242
2016-11-25 15:00 | 242 | 242
2016-11-25 15:30 | 246 | 246
2016-11-25 16:00 | 254 | 254
2016-11-25 16:30 | 267 | 267
2016-11-25 17:00 | 263 | 262
2016-11-25 17:30 | 260 | 259
2016-11-25 18:00 | 258 | 257
2016-11-25 18:30 | 268 | 267
2016-11-25 19:00 | 267 | 267
2016-11-25 19:30 | 265 | 264
2016-11-25 20:00 | 259 | 258
2016-11-25 20:30 | 243 | 243
2016-11-25 21:00 | 241 | 241
2016-11-25 21:30 | 233 | 233
2016-11-25 22:00 | 235 | 235
2016-11-25 22:30 | 237 | 237
2016-11-25 23:00 | 215 | 215
2016-11-25 23:30 | 201 | 201
2016-11-26 | 192 | 192
2016-11-26 00:30 | 188 | 188
2016-11-26 01:00 | 185 | 184
2016-11-26 01:30 | 183 | 182
2016-11-26 02:00 | 178 | 178
2016-11-26 02:30 | 174 | 174
2016-11-26 03:00 | 172 | 172
2016-11-26 03:30 | 171 | 171
2016-11-26 04:00 | 175 | 175
2016-11-26 04:30 | 177 | 176
2016-11-26 05:00 | 178 | 177
2016-11-26 05:30 | 188 | 188
2016-11-26 06:00 | 195 | 195
2016-11-26 06:30 | 205 | 205
2016-11-26 07:00 | 215 | 215
2016-11-26 07:30 | 224 | 224
2016-11-26 08:00 | 237 | 236
2016-11-26 08:30 | 239 | 238
2016-11-26 09:00 | 238 | 238
2016-11-26 09:30 | 240 | 240
2016-11-26 10:00 | 241 | 241
2016-11-26 10:30 | 238 | 238
2016-11-26 11:00 | 239 | 239
2016-11-26 11:30 | 242 | 242
2016-11-26 12:00 | 240 | 240
2016-11-26 12:30 | 241 | 241
2016-11-26 13:00 | 243 | 243
2016-11-26 13:30 | 247 | 247
2016-11-26 14:00 | 245 | 245
2016-11-26 14:30 | 246 | 246
2016-11-26 15:00 | 251 | 251
2016-11-26 15:30 | 254 | 254
2016-11-26 16:00 | 255 | 255
2016-11-26 16:30 | 254 | 254
2016-11-26 17:00 | 251 | 251
2016-11-26 17:30 | 249 | 249
2016-11-26 18:00 | 250 | 250
2016-11-26 18:30 | 258 | 258
2016-11-26 19:00 | 257 | 257
2016-11-26 19:30 | 258 | 258
2016-11-26 20:00 | 251 | 250
2016-11-26 20:30 | 242 | 240
2016-11-26 21:00 | 238 | 236
2016-11-26 21:30 | 234 | 233
2016-11-26 22:00 | 230 | 229
2016-11-26 22:30 | 232 | 232
2016-11-26 23:00 | 216 | 215
2016-11-26 23:30 | 203 | 203
2016-11-27 | 194 | 194
2016-11-27 00:30 | 189 | 189
2016-11-27 01:00 | 185 | 185
2016-11-27 01:30 | 182 | 182
2016-11-27 02:00 | 178 | 178
2016-11-27 02:30 | 176 | 176
2016-11-27 03:00 | 174 | 174
2016-11-27 03:30 | 173 | 173
2016-11-27 04:00 | 175 | 175
2016-11-27 04:30 | 173 | 173
2016-11-27 05:00 | 174 | 174
2016-11-27 05:30 | 178 | 178
2016-11-27 06:00 | 185 | 185
2016-11-27 06:30 | 194 | 194
2016-11-27 07:00 | 203 | 203
2016-11-27 07:30 | 213 | 212
2016-11-27 08:00 | 224 | 223
2016-11-27 08:30 | 230 | 230
2016-11-27 09:00 | 233 | 233
2016-11-27 09:30 | 232 | 232
2016-11-27 10:00 | 232 | 232
2016-11-27 10:30 | 232 | 232
2016-11-27 11:00 | 234 | 234
2016-11-27 11:30 | 235 | 235
2016-11-27 12:00 | 241 | 241
2016-11-27 12:30 | 255 | 255
2016-11-27 13:00 | 260 | 260
2016-11-27 13:30 | 263 | 263
2016-11-27 14:00 | 259 | 259
2016-11-27 14:30 | 253 | 253
2016-11-27 15:00 | 245 | 244
2016-11-27 15:30 | 243 | 242
2016-11-27 16:00 | 249 | 249
2016-11-27 16:30 | 259 | 258
2016-11-27 17:00 | 260 | 259
2016-11-27 17:30 | 261 | 260
2016-11-27 18:00 | 263 | 262
2016-11-27 18:30 | 268 | 267
2016-11-27 19:00 | 266 | 265
2016-11-27 19:30 | 266 | 266
2016-11-27 20:00 | 261 | 260
2016-11-27 20:30 | 247 | 247
2016-11-27 21:00 | 245 | 245
2016-11-27 21:30 | 238 | 238
2016-11-27 22:00 | 236 | 236
2016-11-27 22:30 | 233 | 233
2016-11-27 23:00 | 212 | 212
2016-11-27 23:30 | 202 | 202
2016-11-28 | 192 | 192
2016-11-28 00:30 | 187 | 187
2016-11-28 01:00 | 183 | 183
2016-11-28 01:30 | 179 | 179
2016-11-28 02:00 | 178 | 177
2016-11-28 02:30 | 177 | 176
2016-11-28 03:00 | 178 | 178
2016-11-28 03:30 | 179 | 178
2016-11-28 04:00 | 182 | 182
2016-11-28 04:30 | 184 | 184
2016-11-28 05:00 | 193 | 193
2016-11-28 05:30 | 204 | 204
2016-11-28 06:00 | 221 | 221
2016-11-28 06:30 | 229 | 229
2016-11-28 07:00 | 246 | 245
2016-11-28 07:30 | 258 | 257
2016-11-28 08:00 | 265 | 265
2016-11-28 08:30 | 273 | 273
2016-11-28 09:00 | 273 | 273
2016-11-28 09:30 | 276 | 275
2016-11-28 10:00 | 275 | 275
2016-11-28 10:30 | 277 | 276
2016-11-28 11:00 | 278 | 278
2016-11-28 11:30 | 278 | 278
2016-11-28 12:00 | 274 | 274
2016-11-28 12:30 | 273 | 273
2016-11-28 13:00 | 273 | 272
2016-11-28 13:30 | 272 | 272
2016-11-28 14:00 | 280 | 280
2016-11-28 14:30 | 288 | 288
2016-11-28 15:00 | 297 | 296
2016-11-28 15:30 | 307 | 306
2016-11-28 16:00 | 311 | 310
2016-11-28 16:30 | 314 | 313
2016-11-28 17:00 | 313 | 313
2016-11-28 17:30 | 311 | 310
2016-11-28 18:00 | 299 | 299
2016-11-28 18:30 | 302 | 302
2016-11-28 19:00 | 296 | 296
2016-11-28 19:30 | 290 | 290
2016-11-28 20:00 | 277 | 277
2016-11-28 20:30 | 265 | 265
2016-11-28 21:00 | 257 | 257
2016-11-28 21:30 | 249 | 248
2016-11-28 22:00 | 242 | 242
2016-11-28 22:30 | 235 | 235
2016-11-28 23:00 | 214 | 214
2016-11-28 23:30 | 204 | 204
2016-11-29 | 196 | 195
2016-11-29 00:30 | 189 | 189
2016-11-29 01:00 | 185 | 184
2016-11-29 01:30 | 183 | 182
2016-11-29 02:00 | 181 | 180
2016-11-29 02:30 | 180 | 180
2016-11-29 03:00 | 179 | 179
2016-11-29 03:30 | 180 | 180
2016-11-29 04:00 | 186 | 186
2016-11-29 04:30 | 188 | 188
2016-11-29 05:00 | 196 | 196
2016-11-29 05:30 | 208 | 208
2016-11-29 06:00 | 225 | 225
2016-11-29 06:30 | 239 | 239
2016-11-29 07:00 | 253 | 253
2016-11-29 07:30 | 261 | 261
2016-11-29 08:00 | 263 | 263
2016-11-29 08:30 | 267 | 267
2016-11-29 09:00 | 271 | 271
2016-11-29 09:30 | 274 | 274
2016-11-29 10:00 | 278 | 278
2016-11-29 10:30 | 287 | 287
2016-11-29 11:00 | 283 | 283
2016-11-29 11:30 | 281 | 281
2016-11-29 12:00 | 283 | 283
2016-11-29 12:30 | 284 | 284
2016-11-29 13:00 | 285 | 285
2016-11-29 13:30 | 283 | 283
2016-11-29 14:00 | 281 | 281
2016-11-29 14:30 | 280 | 280
2016-11-29 15:00 | 285 | 285
2016-11-29 15:30 | 295 | 295
2016-11-29 16:00 | 302 | 302
2016-11-29 16:30 | 309 | 308
2016-11-29 17:00 | 303 | 303
2016-11-29 17:30 | 285 | 284
2016-11-29 18:00 | 283 | 283
2016-11-29 18:30 | 288 | 288
2016-11-29 19:00 | 283 | 283
2016-11-29 19:30 | 280 | 280
2016-11-29 20:00 | 269 | 269
2016-11-29 20:30 | 260 | 259
2016-11-29 21:00 | 250 | 249
2016-11-29 21:30 | 239 | 238
2016-11-29 22:00 | 233 | 233
2016-11-29 22:30 | 231 | 230
2016-11-29 23:00 | 215 | 214
2016-11-29 23:30 | 201 | 201
2016-11-30 | 190 | 190
2016-11-30 00:30 | 188 | 188
2016-11-30 01:00 | 181 | 181
2016-11-30 01:30 | 179 | 179
2016-11-30 02:00 | 179 | 179
2016-11-30 02:30 | 180 | 179
2016-11-30 03:00 | 181 | 181
2016-11-30 03:30 | 181 | 181
2016-11-30 04:00 | 185 | 185
2016-11-30 04:30 | 186 | 185
2016-11-30 05:00 | 197 | 197
2016-11-30 05:30 | 207 | 207
2016-11-30 06:00 | 215 | 215
2016-11-30 06:30 | 234 | 233
2016-11-30 07:00 | 247 | 247
2016-11-30 07:30 | 255 | 255
2016-11-30 08:00 | 262 | 262
2016-11-30 08:30 | 266 | 266
2016-11-30 09:00 | 266 | 266
2016-11-30 09:30 | 275 | 275
2016-11-30 10:00 | 277 | 276
2016-11-30 10:30 | 270 | 269
2016-11-30 11:00 | 268 | 267
2016-11-30 11:30 | 267 | 267
2016-11-30 12:00 | 267 | 267
2016-11-30 12:30 | 273 | 273
2016-11-30 13:00 | 279 | 279
2016-11-30 13:30 | 298 | 298
2016-11-30 14:00 | 310 | 310
2016-11-30 14:30 | 310 | 310
2016-11-30 15:00 | 304 | 304
2016-11-30 15:30 | 299 | 299
2016-11-30 16:00 | 292 | 292
2016-11-30 16:30 | 291 | 291
2016-11-30 17:00 | 290 | 289
2016-11-30 17:30 | 283 | 282
2016-11-30 18:00 | 276 | 275
2016-11-30 18:30 | 284 | 283
2016-11-30 19:00 | 286 | 283
2016-11-30 19:30 | 285 | 283
2016-11-30 20:00 | 275 | 273
2016-11-30 20:30 | 259 | 255
2016-11-30 21:00 | 244 | 242
2016-11-30 21:30 | 232 | 231
2016-11-30 22:00 | 228 | 227
2016-11-30 22:30 | 225 | 224
2016-11-30 23:00 | 208 | 208
2016-11-30 23:30 | 200 | 200
2016-12-01 | 190 | 189
2016-12-01 00:30 | 186 | 184
2016-12-01 01:00 | 187 | 186
2016-12-01 01:30 | 183 | 182
2016-12-01 02:00 | 181 | 180
2016-12-01 02:30 | 174 | 172
2016-12-01 03:00 | 170 | 168
2016-12-01 03:30 | 179 | 178
2016-12-01 04:00 | 161 | 159
2016-12-01 04:30 | 168 | 166
2016-12-01 05:00 | 196 | 195
2016-12-01 05:30 | 204 | 203
2016-12-01 06:00 | 214 | 214
2016-12-01 06:30 | 225 | 224
2016-12-01 07:00 | 241 | 241
2016-12-01 07:30 | 253 | 252
2016-12-01 08:00 | 257 | 257
2016-12-01 08:30 | 265 | 264
2016-12-01 09:00 | 263 | 263
2016-12-01 09:30 | 263 | 263
2016-12-01 10:00 | 255 | 255
2016-12-01 10:30 | 255 | 255
2016-12-01 11:00 | 268 | 268
2016-12-01 11:30 | 273 | 273
2016-12-01 12:00 | 280 | 279
2016-12-01 12:30 | 280 | 279
2016-12-01 13:00 | 273 | 273
2016-12-01 13:30 | 278 | 278
2016-12-01 14:00 | 274 | 273
2016-12-01 14:30 | 290 | 289
2016-12-01 15:00 | 295 | 294
2016-12-01 15:30 | 297 | 296
2016-12-01 16:00 | 299 | 297
2016-12-01 16:30 | 305 | 303
2016-12-01 17:00 | 294 | 291
2016-12-01 17:30 | 287 | 283
2016-12-01 18:00 | 285 | 281
2016-12-01 18:30 | 291 | 288
2016-12-01 19:00 | 288 | 285
2016-12-01 19:30 | 289 | 286
2016-12-01 20:00 | 282 | 278
2016-12-01 20:30 | 265 | 261
2016-12-01 21:00 | 245 | 243
2016-12-01 21:30 | 238 | 237
2016-12-01 22:00 | 232 | 230
2016-12-01 22:30 | 228 | 226
2016-12-01 23:00 | 204 | 204
2016-12-01 23:30 | 194 | 194
2016-12-02 | 188 | 188
2016-12-02 00:30 | 186 | 186
2016-12-02 01:00 | 182 | 182
2016-12-02 01:30 | 179 | 178
2016-12-02 02:00 | 175 | 175
2016-12-02 02:30 | 174 | 173
2016-12-02 03:00 | 173 | 173
2016-12-02 03:30 | 173 | 173
2016-12-02 04:00 | 178 | 177
2016-12-02 04:30 | 181 | 180
2016-12-02 05:00 | 190 | 190
2016-12-02 05:30 | 202 | 202
2016-12-02 06:00 | 220 | 220
2016-12-02 06:30 | 229 | 229
2016-12-02 07:00 | 244 | 244
2016-12-02 07:30 | 258 | 258
2016-12-02 08:00 | 262 | 262
2016-12-02 08:30 | 269 | 269
2016-12-02 09:00 | 268 | 267
2016-12-02 09:30 | 267 | 267
2016-12-02 10:00 | 272 | 272
2016-12-02 10:30 | 274 | 274
2016-12-02 11:00 | 275 | 275
2016-12-02 11:30 | 280 | 280
2016-12-02 12:00 | 279 | 279
2016-12-02 12:30 | 283 | 283
2016-12-02 13:00 | 289 | 289
2016-12-02 13:30 | 296 | 293
2016-12-02 14:00 | 301 | 298
2016-12-02 14:30 | 304 | 302
2016-12-02 15:00 | 325 | 323
2016-12-02 15:30 | 334 | 332
2016-12-02 16:00 | 334 | 331
2016-12-02 16:30 | 341 | 339
2016-12-02 17:00 | 328 | 325
2016-12-02 17:30 | 313 | 310
2016-12-02 18:00 | 306 | 304
2016-12-02 18:30 | 309 | 308
2016-12-02 19:00 | 305 | 304
2016-12-02 19:30 | 298 | 297
2016-12-02 20:00 | 294 | 293
2016-12-02 20:30 | 279 | 277
2016-12-02 21:00 | 272 | 271
2016-12-02 21:30 | 261 | 261
2016-12-02 22:00 | 254 | 254
2016-12-02 22:30 | 247 | 247
2016-12-02 23:00 | 228 | 227
2016-12-02 23:30 | 215 | 213
2016-12-03 | 202 | 202
2016-12-03 00:30 | 198 | 197
2016-12-03 01:00 | 194 | 193
2016-12-03 01:30 | 192 | 191
2016-12-03 02:00 | 191 | 190
2016-12-03 02:30 | 189 | 188
2016-12-03 03:00 | 190 | 189
2016-12-03 03:30 | 189 | 188
2016-12-03 04:00 | 191 | 190
2016-12-03 04:30 | 196 | 195
2016-12-03 05:00 | 199 | 198
2016-12-03 05:30 | 204 | 203
2016-12-03 06:00 | 211 | 210
2016-12-03 06:30 | 219 | 218
2016-12-03 07:00 | 233 | 233
2016-12-03 07:30 | 243 | 243
2016-12-03 08:00 | 251 | 250
2016-12-03 08:30 | 257 | 257
2016-12-03 09:00 | 263 | 263
2016-12-03 09:30 | 264 | 264
2016-12-03 10:00 | 260 | 260
2016-12-03 10:30 | 254 | 254
2016-12-03 11:00 | 254 | 254
2016-12-03 11:30 | 255 | 255
2016-12-03 12:00 | 256 | 256
2016-12-03 12:30 | 257 | 257
2016-12-03 13:00 | 262 | 262
2016-12-03 13:30 | 267 | 267
2016-12-03 14:00 | 283 | 283
2016-12-03 14:30 | 300 | 300
2016-12-03 15:00 | 304 | 302
2016-12-03 15:30 | 301 | 297
2016-12-03 16:00 | 296 | 293
2016-12-03 16:30 | 305 | 303
2016-12-03 17:00 | 298 | 298
2016-12-03 17:30 | 294 | 293
2016-12-03 18:00 | 286 | 285
2016-12-03 18:30 | 276 | 275
2016-12-03 19:00 | 262 | 262
2016-12-03 19:30 | 258 | 258
2016-12-03 20:00 | 257 | 256
2016-12-03 20:30 | 251 | 250
2016-12-03 21:00 | 236 | 234
2016-12-03 21:30 | 238 | 236
2016-12-03 22:00 | 236 | 233
2016-12-03 22:30 | 231 | 227
2016-12-03 23:00 | 216 | 212
2016-12-03 23:30 | 202 | 201
2016-12-04 | 197 | 197
2016-12-04 00:30 | 193 | 193
2016-12-04 01:00 | 187 | 186
2016-12-04 01:30 | 179 | 179
2016-12-04 02:00 | 180 | 179
2016-12-04 02:30 | 178 | 178
2016-12-04 03:00 | 178 | 177
2016-12-04 03:30 | 178 | 177
2016-12-04 04:00 | 178 | 178
2016-12-04 04:30 | 178 | 177
2016-12-04 05:00 | 180 | 178
2016-12-04 05:30 | 180 | 179
2016-12-04 06:00 | 185 | 184
2016-12-04 06:30 | 196 | 196
2016-12-04 07:00 | 207 | 207
2016-12-04 07:30 | 219 | 219
2016-12-04 08:00 | 226 | 225
2016-12-04 08:30 | 231 | 231
2016-12-04 09:00 | 239 | 239
2016-12-04 09:30 | 244 | 244
2016-12-04 10:00 | 247 | 247
2016-12-04 10:30 | 247 | 247
2016-12-04 11:00 | 248 | 248
2016-12-04 11:30 | 249 | 249
2016-12-04 12:00 | 250 | 250
2016-12-04 12:30 | 252 | 252
2016-12-04 13:00 | 250 | 250
2016-12-04 13:30 | 249 | 249
2016-12-04 14:00 | 241 | 241
2016-12-04 14:30 | 244 | 244
2016-12-04 15:00 | 266 | 266
2016-12-04 15:30 | 277 | 277
2016-12-04 16:00 | 282 | 282
2016-12-04 16:30 | 286 | 285
2016-12-04 17:00 | 284 | 284
2016-12-04 17:30 | 286 | 286
2016-12-04 18:00 | 284 | 284
2016-12-04 18:30 | 286 | 286
2016-12-04 19:00 | 287 | 287
2016-12-04 19:30 | 278 | 278
2016-12-04 20:00 | 276 | 276
2016-12-04 20:30 | 258 | 258
2016-12-04 21:00 | 243 | 243
2016-12-04 21:30 | 238 | 238
2016-12-04 22:00 | 229 | 229
2016-12-04 22:30 | 227 | 227
2016-12-04 23:00 | 211 | 211
2016-12-04 23:30 | 199 | 198
2016-12-05 | 191 | 191
2016-12-05 00:30 | 180 | 180
2016-12-05 01:00 | 180 | 180
2016-12-05 01:30 | 166 | 166
2016-12-05 02:00 | 168 | 168
2016-12-05 02:30 | 168 | 168
2016-12-05 03:00 | 180 | 180
2016-12-05 03:30 | 185 | 185
2016-12-05 04:00 | 189 | 189
2016-12-05 04:30 | 191 | 191
2016-12-05 05:00 | 194 | 194
2016-12-05 05:30 | 203 | 202
2016-12-05 06:00 | 214 | 214
2016-12-05 06:30 | 232 | 231
2016-12-05 07:00 | 253 | 253
2016-12-05 07:30 | 264 | 264
2016-12-05 08:00 | 272 | 272
2016-12-05 08:30 | 285 | 285
2016-12-05 09:00 | 286 | 286
2016-12-05 09:30 | 294 | 294
2016-12-05 10:00 | 300 | 300
2016-12-05 10:30 | 309 | 308
2016-12-05 11:00 | 313 | 313
2016-12-05 11:30 | 315 | 315
2016-12-05 12:00 | 318 | 318
2016-12-05 12:30 | 319 | 318
2016-12-05 13:00 | 326 | 326
2016-12-05 13:30 | 336 | 336
2016-12-05 14:00 | 347 | 346
2016-12-05 14:30 | 355 | 355
2016-12-05 15:00 | 354 | 354
2016-12-05 15:30 | 358 | 357
2016-12-05 16:00 | 357 | 357
2016-12-05 16:30 | 357 | 356
2016-12-05 17:00 | 352 | 351
2016-12-05 17:30 | 344 | 343
2016-12-05 18:00 | 331 | 330
2016-12-05 18:30 | 330 | 330
2016-12-05 19:00 | 315 | 315
2016-12-05 19:30 | 304 | 304
2016-12-05 20:00 | 293 | 292
2016-12-05 20:30 | 276 | 274
2016-12-05 21:00 | 258 | 258
2016-12-05 21:30 | 248 | 248
2016-12-05 22:00 | 246 | 246
2016-12-05 22:30 | 232 | 232
2016-12-05 23:00 | 212 | 212
2016-12-05 23:30 | 205 | 205
2016-12-06 | 198 | 198
2016-12-06 00:30 | 193 | 192
2016-12-06 01:00 | 190 | 190
2016-12-06 01:30 | 187 | 187
2016-12-06 02:00 | 184 | 184
2016-12-06 02:30 | 185 | 185
2016-12-06 03:00 | 184 | 184
2016-12-06 03:30 | 188 | 188
2016-12-06 04:00 | 187 | 187
2016-12-06 04:30 | 188 | 187
2016-12-06 05:00 | 194 | 194
2016-12-06 05:30 | 200 | 200
2016-12-06 06:00 | 215 | 215
2016-12-06 06:30 | 226 | 226
2016-12-06 07:00 | 242 | 241
2016-12-06 07:30 | 252 | 252
2016-12-06 08:00 | 263 | 262
2016-12-06 08:30 | 270 | 270
2016-12-06 09:00 | 268 | 267
2016-12-06 09:30 | 266 | 265
2016-12-06 10:00 | 268 | 267
2016-12-06 10:30 | 268 | 268
2016-12-06 11:00 | 266 | 266
2016-12-06 11:30 | 266 | 266
2016-12-06 12:00 | 276 | 276
2016-12-06 12:30 | 291 | 291
2016-12-06 13:00 | 307 | 307
2016-12-06 13:30 | 325 | 325
2016-12-06 14:00 | 340 | 340
2016-12-06 14:30 | 360 | 360
2016-12-06 15:00 | 379 | 379
2016-12-06 15:30 | 398 | 398
2016-12-06 16:00 | 407 | 407
2016-12-06 16:30 | 402 | 402
2016-12-06 17:00 | 387 | 386
2016-12-06 17:30 | 370 | 368
2016-12-06 18:00 | 358 | 357
2016-12-06 18:30 | 364 | 364
2016-12-06 19:00 | 337 | 336
2016-12-06 19:30 | 315 | 314
2016-12-06 20:00 | 296 | 296
2016-12-06 20:30 | 277 | 277
2016-12-06 21:00 | 261 | 261
2016-12-06 21:30 | 244 | 244
2016-12-06 22:00 | 240 | 240
2016-12-06 22:30 | 235 | 235
2016-12-06 23:00 | 209 | 209
2016-12-06 23:30 | 200 | 200
2016-12-07 | 190 | 190
2016-12-07 00:30 | 189 | 189
2016-12-07 01:00 | 186 | 186
2016-12-07 01:30 | 182 | 182
2016-12-07 02:00 | 180 | 179
2016-12-07 02:30 | 181 | 180
2016-12-07 03:00 | 179 | 179
2016-12-07 03:30 | 184 | 184
2016-12-07 04:00 | 189 | 189
2016-12-07 04:30 | 193 | 193
2016-12-07 05:00 | 199 | 199
2016-12-07 05:30 | 207 | 207
2016-12-07 06:00 | 222 | 221
2016-12-07 06:30 | 236 | 235
2016-12-07 07:00 | 246 | 246
2016-12-07 07:30 | 258 | 258
2016-12-07 08:00 | 272 | 272
2016-12-07 08:30 | 273 | 273
2016-12-07 09:00 | 266 | 266
2016-12-07 09:30 | 276 | 276
2016-12-07 10:00 | 288 | 288
2016-12-07 10:30 | 283 | 283
2016-12-07 11:00 | 292 | 291
2016-12-07 11:30 | 296 | 296
2016-12-07 12:00 | 312 | 312
2016-12-07 12:30 | 303 | 303
2016-12-07 13:00 | 312 | 312
2016-12-07 13:30 | 320 | 320
2016-12-07 14:00 | 316 | 316
2016-12-07 14:30 | 309 | 309
2016-12-07 15:00 | 316 | 316
2016-12-07 15:30 | 316 | 316
2016-12-07 16:00 | 313 | 313
2016-12-07 16:30 | 311 | 311
2016-12-07 17:00 | 308 | 308
2016-12-07 17:30 | 306 | 306
2016-12-07 18:00 | 297 | 297
2016-12-07 18:30 | 300 | 300
2016-12-07 19:00 | 290 | 290
2016-12-07 19:30 | 285 | 285
2016-12-07 20:00 | 277 | 277
2016-12-07 20:30 | 267 | 267
2016-12-07 21:00 | 257 | 257
2016-12-07 21:30 | 249 | 248
2016-12-07 22:00 | 241 | 241
2016-12-07 22:30 | 228 | 228
2016-12-07 23:00 | 204 | 204
2016-12-07 23:30 | 199 | 199
2016-12-08 | 187 | 187
2016-12-08 00:30 | 182 | 182
2016-12-08 01:00 | 180 | 180
2016-12-08 01:30 | 178 | 178
2016-12-08 02:00 | 177 | 177
2016-12-08 02:30 | 175 | 175
2016-12-08 03:00 | 176 | 176
2016-12-08 03:30 | 179 | 179
2016-12-08 04:00 | 184 | 184
2016-12-08 04:30 | 186 | 186
2016-12-08 05:00 | 198 | 198
2016-12-08 05:30 | 207 | 207
2016-12-08 06:00 | 218 | 218
2016-12-08 06:30 | 234 | 234
2016-12-08 07:00 | 249 | 248
2016-12-08 07:30 | 262 | 262
2016-12-08 08:00 | 272 | 272
2016-12-08 08:30 | 272 | 272
2016-12-08 09:00 | 289 | 289
2016-12-08 09:30 | 296 | 296
2016-12-08 10:00 | 284 | 284
2016-12-08 10:30 | 291 | 291
2016-12-08 11:00 | 297 | 297
2016-12-08 11:30 | 294 | 294
2016-12-08 12:00 | 290 | 290
2016-12-08 12:30 | 281 | 281
2016-12-08 13:00 | 282 | 282
2016-12-08 13:30 | 301 | 301
2016-12-08 14:00 | 299 | 299
2016-12-08 14:30 | 295 | 295
2016-12-08 15:00 | 288 | 288
2016-12-08 15:30 | 283 | 283
2016-12-08 16:00 | 290 | 290
2016-12-08 16:30 | 311 | 311
2016-12-08 17:00 | 314 | 314
2016-12-08 17:30 | 316 | 316
2016-12-08 18:00 | 307 | 307
2016-12-08 18:30 | 317 | 317
2016-12-08 19:00 | 300 | 300
2016-12-08 19:30 | 297 | 296
2016-12-08 20:00 | 281 | 281
2016-12-08 20:30 | 265 | 265
2016-12-08 21:00 | 248 | 248
2016-12-08 21:30 | 238 | 238
2016-12-08 22:00 | 241 | 240
2016-12-08 22:30 | 227 | 227
2016-12-08 23:00 | 209 | 209
2016-12-08 23:30 | 201 | 200
2016-12-09 | 191 | 191
2016-12-09 00:30 | 185 | 185
2016-12-09 01:00 | 180 | 180
2016-12-09 01:30 | 177 | 176
2016-12-09 02:00 | 173 | 173
2016-12-09 02:30 | 170 | 170
2016-12-09 03:00 | 173 | 173
2016-12-09 03:30 | 175 | 175
2016-12-09 04:00 | 181 | 181
2016-12-09 04:30 | 185 | 185
2016-12-09 05:00 | 196 | 195
2016-12-09 05:30 | 204 | 204
2016-12-09 06:00 | 214 | 214
2016-12-09 06:30 | 241 | 241
2016-12-09 07:00 | 262 | 262
2016-12-09 07:30 | 277 | 277
2016-12-09 08:00 | 290 | 289
2016-12-09 08:30 | 294 | 293
2016-12-09 09:00 | 295 | 295
2016-12-09 09:30 | 297 | 296
2016-12-09 10:00 | 297 | 296
2016-12-09 10:30 | 290 | 290
2016-12-09 11:00 | 289 | 288
2016-12-09 11:30 | 283 | 283
2016-12-09 12:00 | 285 | 285
2016-12-09 12:30 | 293 | 292
2016-12-09 13:00 | 291 | 290
2016-12-09 13:30 | 268 | 268
2016-12-09 14:00 | 263 | 263
2016-12-09 14:30 | 261 | 261
2016-12-09 15:00 | 261 | 261
2016-12-09 15:30 | 268 | 268
2016-12-09 16:00 | 269 | 269
2016-12-09 16:30 | 271 | 271
2016-12-09 17:00 | 274 | 274
2016-12-09 17:30 | 269 | 269
2016-12-09 18:00 | 267 | 267
2016-12-09 18:30 | 269 | 269
2016-12-09 19:00 | 271 | 271
2016-12-09 19:30 | 277 | 277
2016-12-09 20:00 | 269 | 269
2016-12-09 20:30 | 264 | 264
2016-12-09 21:00 | 255 | 255
2016-12-09 21:30 | 249 | 248
2016-12-09 22:00 | 239 | 239
2016-12-09 22:30 | 233 | 233
2016-12-09 23:00 | 212 | 212
2016-12-09 23:30 | 199 | 199
2016-12-10 | 189 | 189
2016-12-10 00:30 | 183 | 183
2016-12-10 01:00 | 179 | 179
2016-12-10 01:30 | 176 | 176
2016-12-10 02:00 | 174 | 174
2016-12-10 02:30 | 172 | 171
2016-12-10 03:00 | 172 | 171
2016-12-10 03:30 | 171 | 170
2016-12-10 04:00 | 172 | 172
2016-12-10 04:30 | 172 | 171
2016-12-10 05:00 | 175 | 174
2016-12-10 05:30 | 181 | 180
2016-12-10 06:00 | 188 | 188
2016-12-10 06:30 | 196 | 196
2016-12-10 07:00 | 207 | 207
2016-12-10 07:30 | 217 | 216
2016-12-10 08:00 | 220 | 219
2016-12-10 08:30 | 223 | 223
2016-12-10 09:00 | 225 | 224
2016-12-10 09:30 | 230 | 230
2016-12-10 10:00 | 232 | 232
2016-12-10 10:30 | 231 | 231
2016-12-10 11:00 | 227 | 227
2016-12-10 11:30 | 225 | 225
2016-12-10 12:00 | 225 | 225
2016-12-10 12:30 | 231 | 231
2016-12-10 13:00 | 228 | 228
2016-12-10 13:30 | 226 | 226
2016-12-10 14:00 | 224 | 224
2016-12-10 14:30 | 225 | 224
2016-12-10 15:00 | 230 | 230
2016-12-10 15:30 | 238 | 238
2016-12-10 16:00 | 237 | 237
2016-12-10 16:30 | 243 | 243
2016-12-10 17:00 | 241 | 241
2016-12-10 17:30 | 240 | 240
2016-12-10 18:00 | 240 | 239
2016-12-10 18:30 | 244 | 244
2016-12-10 19:00 | 243 | 243
2016-12-10 19:30 | 244 | 244
2016-12-10 20:00 | 239 | 238
2016-12-10 20:30 | 232 | 232
2016-12-10 21:00 | 227 | 227
2016-12-10 21:30 | 223 | 223
2016-12-10 22:00 | 219 | 219
2016-12-10 22:30 | 220 | 219
2016-12-10 23:00 | 203 | 202
2016-12-10 23:30 | 189 | 189
2016-12-11 | 181 | 180
2016-12-11 00:30 | 175 | 175
2016-12-11 01:00 | 170 | 170
2016-12-11 01:30 | 165 | 165
2016-12-11 02:00 | 160 | 160
2016-12-11 02:30 | 159 | 159
2016-12-11 03:00 | 160 | 160
2016-12-11 03:30 | 158 | 158
2016-12-11 04:00 | 156 | 156
2016-12-11 04:30 | 154 | 154
2016-12-11 05:00 | 156 | 156
2016-12-11 05:30 | 160 | 160
2016-12-11 06:00 | 161 | 161
2016-12-11 06:30 | 168 | 168
2016-12-11 07:00 | 180 | 180
2016-12-11 07:30 | 197 | 197
2016-12-11 08:00 | 208 | 207
2016-12-11 08:30 | 207 | 206
2016-12-11 09:00 | 205 | 205
2016-12-11 09:30 | 211 | 210
2016-12-11 10:00 | 213 | 212
2016-12-11 10:30 | 210 | 210
2016-12-11 11:00 | 204 | 203
2016-12-11 11:30 | 207 | 207
2016-12-11 12:00 | 201 | 201
2016-12-11 12:30 | 199 | 199
2016-12-11 13:00 | 206 | 206
2016-12-11 13:30 | 212 | 212
2016-12-11 14:00 | 213 | 213
2016-12-11 14:30 | 212 | 212
2016-12-11 15:00 | 225 | 224
2016-12-11 15:30 | 227 | 227
2016-12-11 16:00 | 227 | 227
2016-12-11 16:30 | 233 | 232
2016-12-11 17:00 | 230 | 230
2016-12-11 17:30 | 230 | 230
2016-12-11 18:00 | 232 | 232
2016-12-11 18:30 | 239 | 239
2016-12-11 19:00 | 244 | 244
2016-12-11 19:30 | 244 | 242
2016-12-11 20:00 | 241 | 239
2016-12-11 20:30 | 231 | 229
2016-12-11 21:00 | 226 | 224
2016-12-11 21:30 | 214 | 214
2016-12-11 22:00 | 214 | 214
2016-12-11 22:30 | 215 | 215
2016-12-11 23:00 | 197 | 197
2016-12-11 23:30 | 184 | 184
2016-12-12 | 171 | 171
2016-12-12 00:30 | 166 | 165
2016-12-12 01:00 | 163 | 163
2016-12-12 01:30 | 161 | 160
2016-12-12 02:00 | 157 | 157
2016-12-12 02:30 | 157 | 157
2016-12-12 03:00 | 159 | 159
2016-12-12 03:30 | 161 | 161
2016-12-12 04:00 | 166 | 166
2016-12-12 04:30 | 168 | 168
2016-12-12 05:00 | 177 | 177
2016-12-12 05:30 | 183 | 183
2016-12-12 06:00 | 191 | 191
2016-12-12 06:30 | 202 | 202
2016-12-12 07:00 | 218 | 218
2016-12-12 07:30 | 226 | 226
2016-12-12 08:00 | 233 | 233
2016-12-12 08:30 | 236 | 236
2016-12-12 09:00 | 238 | 238
2016-12-12 09:30 | 240 | 240
2016-12-12 10:00 | 239 | 239
2016-12-12 10:30 | 241 | 241
2016-12-12 11:00 | 241 | 241
2016-12-12 11:30 | 240 | 240
2016-12-12 12:00 | 238 | 238
2016-12-12 12:30 | 241 | 241
2016-12-12 13:00 | 244 | 244
2016-12-12 13:30 | 249 | 248
2016-12-12 14:00 | 258 | 256
2016-12-12 14:30 | 271 | 270
2016-12-12 15:00 | 277 | 276
2016-12-12 15:30 | 283 | 281
2016-12-12 16:00 | 290 | 289
2016-12-12 16:30 | 297 | 295
2016-12-12 17:00 | 292 | 291
2016-12-12 17:30 | 288 | 287
2016-12-12 18:00 | 283 | 282
2016-12-12 18:30 | 284 | 282
2016-12-12 19:00 | 282 | 282
2016-12-12 19:30 | 277 | 276
2016-12-12 20:00 | 264 | 264
2016-12-12 20:30 | 250 | 250
2016-12-12 21:00 | 234 | 234
2016-12-12 21:30 | 227 | 227
2016-12-12 22:00 | 226 | 226
2016-12-12 22:30 | 222 | 222
2016-12-12 23:00 | 204 | 204
2016-12-12 23:30 | 192 | 191
2016-12-13 | 183 | 183
2016-12-13 00:30 | 179 | 179
2016-12-13 01:00 | 172 | 171
2016-12-13 01:30 | 168 | 167
2016-12-13 02:00 | 164 | 164
2016-12-13 02:30 | 160 | 159
2016-12-13 03:00 | 161 | 160
2016-12-13 03:30 | 161 | 161
2016-12-13 04:00 | 170 | 169
2016-12-13 04:30 | 172 | 172
2016-12-13 05:00 | 181 | 180
2016-12-13 05:30 | 191 | 190
2016-12-13 06:00 | 200 | 200
2016-12-13 06:30 | 206 | 206
2016-12-13 07:00 | 217 | 217
2016-12-13 07:30 | 229 | 229
2016-12-13 08:00 | 235 | 235
2016-12-13 08:30 | 236 | 236
2016-12-13 09:00 | 236 | 235
2016-12-13 09:30 | 240 | 240
2016-12-13 10:00 | 243 | 243
2016-12-13 10:30 | 244 | 244
2016-12-13 11:00 | 247 | 246
2016-12-13 11:30 | 247 | 247
2016-12-13 12:00 | 249 | 249
2016-12-13 12:30 | 251 | 250
2016-12-13 13:00 | 253 | 253
2016-12-13 13:30 | 256 | 256
2016-12-13 14:00 | 266 | 266
2016-12-13 14:30 | 272 | 272
2016-12-13 15:00 | 284 | 282
2016-12-13 15:30 | 294 | 292
2016-12-13 16:00 | 296 | 294
2016-12-13 16:30 | 299 | 297
2016-12-13 17:00 | 290 | 290
2016-12-13 17:30 | 285 | 285
2016-12-13 18:00 | 279 | 279
2016-12-13 18:30 | 279 | 279
2016-12-13 19:00 | 282 | 282
2016-12-13 19:30 | 281 | 281
2016-12-13 20:00 | 273 | 273
2016-12-13 20:30 | 259 | 259
2016-12-13 21:00 | 241 | 241
2016-12-13 21:30 | 235 | 235
2016-12-13 22:00 | 234 | 234
2016-12-13 22:30 | 219 | 219
2016-12-13 23:00 | 203 | 203
2016-12-13 23:30 | 192 | 191
2016-12-14 | 185 | 184
2016-12-14 00:30 | 178 | 176
2016-12-14 01:00 | 176 | 176
2016-12-14 01:30 | 172 | 172
2016-12-14 02:00 | 170 | 170
2016-12-14 02:30 | 168 | 168
2016-12-14 03:00 | 168 | 167
2016-12-14 03:30 | 170 | 170
2016-12-14 04:00 | 174 | 174
2016-12-14 04:30 | 176 | 176
2016-12-14 05:00 | 186 | 186
2016-12-14 05:30 | 195 | 195
2016-12-14 06:00 | 202 | 202
2016-12-14 06:30 | 212 | 212
2016-12-14 07:00 | 226 | 225
2016-12-14 07:30 | 241 | 240
2016-12-14 08:00 | 249 | 249
2016-12-14 08:30 | 253 | 253
2016-12-14 09:00 | 256 | 256
2016-12-14 09:30 | 259 | 259
2016-12-14 10:00 | 260 | 260
2016-12-14 10:30 | 253 | 253
2016-12-14 11:00 | 253 | 252
2016-12-14 11:30 | 247 | 247
2016-12-14 12:00 | 249 | 249
2016-12-14 12:30 | 252 | 252
2016-12-14 13:00 | 251 | 251
2016-12-14 13:30 | 256 | 256
2016-12-14 14:00 | 262 | 262
2016-12-14 14:30 | 264 | 264
2016-12-14 15:00 | 269 | 269
2016-12-14 15:30 | 282 | 282
2016-12-14 16:00 | 291 | 291
2016-12-14 16:30 | 301 | 301
2016-12-14 17:00 | 303 | 303
2016-12-14 17:30 | 297 | 297
2016-12-14 18:00 | 285 | 285
2016-12-14 18:30 | 289 | 289
2016-12-14 19:00 | 278 | 278
2016-12-14 19:30 | 270 | 270
2016-12-14 20:00 | 261 | 261
2016-12-14 20:30 | 246 | 246
2016-12-14 21:00 | 235 | 235
2016-12-14 21:30 | 222 | 222
2016-12-14 22:00 | 224 | 223
2016-12-14 22:30 | 217 | 217
2016-12-14 23:00 | 197 | 197
2016-12-14 23:30 | 190 | 190
2016-12-15 | 182 | 182
2016-12-15 00:30 | 176 | 176
2016-12-15 01:00 | 175 | 175
2016-12-15 01:30 | 175 | 175
2016-12-15 02:00 | 171 | 171
2016-12-15 02:30 | 170 | 170
2016-12-15 03:00 | 170 | 170
2016-12-15 03:30 | 172 | 172
2016-12-15 04:00 | 172 | 172
2016-12-15 04:30 | 175 | 174
2016-12-15 05:00 | 179 | 179
2016-12-15 05:30 | 187 | 187
2016-12-15 06:00 | 203 | 203
2016-12-15 06:30 | 211 | 211
2016-12-15 07:00 | 218 | 218
2016-12-15 07:30 | 228 | 228
2016-12-15 08:00 | 230 | 230
2016-12-15 08:30 | 232 | 232
2016-12-15 09:00 | 239 | 239
2016-12-15 09:30 | 250 | 249
2016-12-15 10:00 | 244 | 243
2016-12-15 10:30 | 247 | 246
2016-12-15 11:00 | 252 | 251
2016-12-15 11:30 | 254 | 253
2016-12-15 12:00 | 259 | 259
2016-12-15 12:30 | 264 | 264
2016-12-15 13:00 | 266 | 265
2016-12-15 13:30 | 265 | 264
2016-12-15 14:00 | 268 | 267
2016-12-15 14:30 | 277 | 276
2016-12-15 15:00 | 281 | 280
2016-12-15 15:30 | 289 | 287
2016-12-15 16:00 | 297 | 296
2016-12-15 16:30 | 298 | 296
2016-12-15 17:00 | 295 | 293
2016-12-15 17:30 | 294 | 292
2016-12-15 18:00 | 289 | 287
2016-12-15 18:30 | 294 | 292
2016-12-15 19:00 | 294 | 292
2016-12-15 19:30 | 293 | 291
2016-12-15 20:00 | 285 | 283
2016-12-15 20:30 | 264 | 264
2016-12-15 21:00 | 251 | 251
2016-12-15 21:30 | 243 | 243
2016-12-15 22:00 | 247 | 247
2016-12-15 22:30 | 220 | 220
2016-12-15 23:00 | 195 | 195
2016-12-15 23:30 | 192 | 192
2016-12-16 | 181 | 181
2016-12-16 00:30 | 171 | 171
2016-12-16 01:00 | 174 | 173
2016-12-16 01:30 | 169 | 168
2016-12-16 02:00 | 164 | 163
2016-12-16 02:30 | 164 | 163
2016-12-16 03:00 | 164 | 163
2016-12-16 03:30 | 165 | 164
2016-12-16 04:00 | 164 | 163
2016-12-16 04:30 | 165 | 164
2016-12-16 05:00 | 165 | 164
2016-12-16 05:30 | 177 | 177
2016-12-16 06:00 | 174 | 174
2016-12-16 06:30 | 218 | 218
2016-12-16 07:00 | 232 | 232
2016-12-16 07:30 | 239 | 239
2016-12-16 08:00 | 261 | 261
2016-12-16 08:30 | 270 | 270
2016-12-16 09:00 | 266 | 265
2016-12-16 09:30 | 259 | 258
2016-12-16 10:00 | 270 | 270
2016-12-16 10:30 | 272 | 271
2016-12-16 11:00 | 274 | 274
2016-12-16 11:30 | 265 | 265
2016-12-16 12:00 | 269 | 269
2016-12-16 12:30 | 265 | 265
2016-12-16 13:00 | 249 | 249
2016-12-16 13:30 | 256 | 256
2016-12-16 14:00 | 274 | 271
2016-12-16 14:30 | 276 | 274
2016-12-16 15:00 | 279 | 277
2016-12-16 15:30 | 277 | 275
2016-12-16 16:00 | 279 | 276
2016-12-16 16:30 | 277 | 275
2016-12-16 17:00 | 268 | 266
2016-12-16 17:30 | 264 | 262
2016-12-16 18:00 | 254 | 253
2016-12-16 18:30 | 258 | 258
2016-12-16 19:00 | 260 | 260
2016-12-16 19:30 | 269 | 269
2016-12-16 20:00 | 259 | 258
2016-12-16 20:30 | 244 | 243
2016-12-16 21:00 | 232 | 231
2016-12-16 21:30 | 226 | 224
2016-12-16 22:00 | 237 | 236
2016-12-16 22:30 | 221 | 221
2016-12-16 23:00 | 196 | 196
2016-12-16 23:30 | 183 | 182
2016-12-17 | 159 | 159
2016-12-17 00:30 | 154 | 154
2016-12-17 01:00 | 158 | 158
2016-12-17 01:30 | 147 | 147
2016-12-17 02:00 | 148 | 148
2016-12-17 02:30 | 150 | 150
2016-12-17 03:00 | 146 | 146
2016-12-17 03:30 | 142 | 142
2016-12-17 04:00 | 141 | 141
2016-12-17 04:30 | 145 | 145
2016-12-17 05:00 | 159 | 159
2016-12-17 05:30 | 166 | 166
2016-12-17 06:00 | 177 | 177
2016-12-17 06:30 | 190 | 190
2016-12-17 07:00 | 194 | 193
2016-12-17 07:30 | 201 | 199
2016-12-17 08:00 | 202 | 202
2016-12-17 08:30 | 216 | 216
2016-12-17 09:00 | 227 | 227
2016-12-17 09:30 | 238 | 238
2016-12-17 10:00 | 237 | 237
2016-12-17 10:30 | 239 | 239
2016-12-17 11:00 | 219 | 219
2016-12-17 11:30 | 220 | 220
2016-12-17 12:00 | 224 | 223
2016-12-17 12:30 | 227 | 227
2016-12-17 13:00 | 244 | 244
2016-12-17 13:30 | 248 | 248
2016-12-17 14:00 | 243 | 243
2016-12-17 14:30 | 265 | 265
2016-12-17 15:00 | 277 | 277
2016-12-17 15:30 | 278 | 277
2016-12-17 16:00 | 275 | 275
2016-12-17 16:30 | 281 | 280
2016-12-17 17:00 | 278 | 278
2016-12-17 17:30 | 275 | 275
2016-12-17 18:00 | 267 | 267
2016-12-17 18:30 | 269 | 269
2016-12-17 19:00 | 267 | 267
2016-12-17 19:30 | 266 | 266
2016-12-17 20:00 | 257 | 257
2016-12-17 20:30 | 245 | 245
2016-12-17 21:00 | 236 | 236
2016-12-17 21:30 | 231 | 231
2016-12-17 22:00 | 245 | 245
2016-12-17 22:30 | 228 | 228
2016-12-17 23:00 | 207 | 207
2016-12-17 23:30 | 207 | 206
2016-12-18 | 193 | 193
2016-12-18 00:30 | 186 | 186
2016-12-18 01:00 | 180 | 180
2016-12-18 01:30 | 174 | 174
2016-12-18 02:00 | 171 | 171
2016-12-18 02:30 | 170 | 170
2016-12-18 03:00 | 169 | 169
2016-12-18 03:30 | 168 | 168
2016-12-18 04:00 | 166 | 166
2016-12-18 04:30 | 164 | 164
2016-12-18 05:00 | 164 | 163
2016-12-18 05:30 | 166 | 166
2016-12-18 06:00 | 171 | 171
2016-12-18 06:30 | 180 | 180
2016-12-18 07:00 | 194 | 193
2016-12-18 07:30 | 204 | 204
2016-12-18 08:00 | 201 | 199
2016-12-18 08:30 | 197 | 197
2016-12-18 09:00 | 198 | 197
2016-12-18 09:30 | 206 | 206
2016-12-18 10:00 | 219 | 218
2016-12-18 10:30 | 231 | 231
2016-12-18 11:00 | 249 | 249
2016-12-18 11:30 | 240 | 240
2016-12-18 12:00 | 221 | 220
2016-12-18 12:30 | 212 | 212
2016-12-18 13:00 | 214 | 214
2016-12-18 13:30 | 221 | 221
2016-12-18 14:00 | 230 | 230
2016-12-18 14:30 | 227 | 227
2016-12-18 15:00 | 215 | 214
2016-12-18 15:30 | 201 | 201
2016-12-18 16:00 | 211 | 211
2016-12-18 16:30 | 228 | 227
2016-12-18 17:00 | 232 | 232
2016-12-18 17:30 | 233 | 232
2016-12-18 18:00 | 230 | 229
2016-12-18 18:30 | 225 | 224
2016-12-18 19:00 | 230 | 229
2016-12-18 19:30 | 225 | 225
2016-12-18 20:00 | 220 | 220
2016-12-18 20:30 | 212 | 212
2016-12-18 21:00 | 195 | 195
2016-12-18 21:30 | 193 | 193
2016-12-18 22:00 | 186 | 186
2016-12-18 22:30 | 192 | 192
2016-12-18 23:00 | 170 | 170
2016-12-18 23:30 | 165 | 165
2016-12-19 | 154 | 154
2016-12-19 00:30 | 156 | 156
2016-12-19 01:00 | 141 | 141
2016-12-19 01:30 | 141 | 141
2016-12-19 02:00 | 146 | 145
2016-12-19 02:30 | 142 | 141
2016-12-19 03:00 | 145 | 144
2016-12-19 03:30 | 148 | 148
2016-12-19 04:00 | 153 | 153
2016-12-19 04:30 | 159 | 159
2016-12-19 05:00 | 164 | 164
2016-12-19 05:30 | 176 | 176
2016-12-19 06:00 | 173 | 173
2016-12-19 06:30 | 179 | 178
2016-12-19 07:00 | 197 | 196
2016-12-19 07:30 | 210 | 209
2016-12-19 08:00 | 216 | 216
2016-12-19 08:30 | 222 | 222
2016-12-19 09:00 | 220 | 220
2016-12-19 09:30 | 219 | 219
2016-12-19 10:00 | 220 | 220
2016-12-19 10:30 | 219 | 219
2016-12-19 11:00 | 217 | 217
2016-12-19 11:30 | 216 | 216
2016-12-19 12:00 | 213 | 213
2016-12-19 12:30 | 209 | 209
2016-12-19 13:00 | 213 | 212
2016-12-19 13:30 | 214 | 214
2016-12-19 14:00 | 215 | 214
2016-12-19 14:30 | 222 | 221
2016-12-19 15:00 | 226 | 226
2016-12-19 15:30 | 237 | 237
2016-12-19 16:00 | 234 | 234
2016-12-19 16:30 | 237 | 237
2016-12-19 17:00 | 239 | 239
2016-12-19 17:30 | 242 | 242
2016-12-19 18:00 | 238 | 238
2016-12-19 18:30 | 247 | 247
2016-12-19 19:00 | 247 | 247
2016-12-19 19:30 | 245 | 245
2016-12-19 20:00 | 249 | 249
2016-12-19 20:30 | 244 | 243
2016-12-19 21:00 | 235 | 234
2016-12-19 21:30 | 228 | 227
2016-12-19 22:00 | 230 | 229
2016-12-19 22:30 | 219 | 219
2016-12-19 23:00 | 199 | 199
2016-12-19 23:30 | 190 | 189
2016-12-20 | 179 | 179
2016-12-20 00:30 | 170 | 169
2016-12-20 01:00 | 172 | 171
2016-12-20 01:30 | 168 | 167
2016-12-20 02:00 | 163 | 162
2016-12-20 02:30 | 160 | 159
2016-12-20 03:00 | 160 | 159
2016-12-20 03:30 | 162 | 161
2016-12-20 04:00 | 171 | 171
2016-12-20 04:30 | 177 | 176
2016-12-20 05:00 | 181 | 181
2016-12-20 05:30 | 192 | 192
2016-12-20 06:00 | 211 | 211
2016-12-20 06:30 | 218 | 218
2016-12-20 07:00 | 228 | 228
2016-12-20 07:30 | 236 | 236
2016-12-20 08:00 | 236 | 236
2016-12-20 08:30 | 238 | 238
2016-12-20 09:00 | 247 | 247
2016-12-20 09:30 | 257 | 257
2016-12-20 10:00 | 262 | 262
2016-12-20 10:30 | 260 | 260
2016-12-20 11:00 | 261 | 261
2016-12-20 11:30 | 257 | 257
2016-12-20 12:00 | 259 | 259
2016-12-20 12:30 | 256 | 256
2016-12-20 13:00 | 258 | 258
2016-12-20 13:30 | 262 | 262
2016-12-20 14:00 | 269 | 268
2016-12-20 14:30 | 271 | 270
2016-12-20 15:00 | 271 | 270
2016-12-20 15:30 | 281 | 281
2016-12-20 16:00 | 283 | 282
2016-12-20 16:30 | 291 | 290
2016-12-20 17:00 | 284 | 282
2016-12-20 17:30 | 286 | 284
2016-12-20 18:00 | 282 | 281
2016-12-20 18:30 | 282 | 282
2016-12-20 19:00 | 275 | 275
2016-12-20 19:30 | 276 | 276
2016-12-20 20:00 | 274 | 274
2016-12-20 20:30 | 264 | 263
2016-12-20 21:00 | 257 | 256
2016-12-20 21:30 | 251 | 249
2016-12-20 22:00 | 249 | 249
2016-12-20 22:30 | 240 | 240
2016-12-20 23:00 | 217 | 217
2016-12-20 23:30 | 211 | 210
2016-12-21 | 199 | 199
2016-12-21 00:30 | 189 | 189
2016-12-21 01:00 | 187 | 186
2016-12-21 01:30 | 184 | 183
2016-12-21 02:00 | 183 | 183
2016-12-21 02:30 | 183 | 183
2016-12-21 03:00 | 185 | 185
2016-12-21 03:30 | 188 | 187
2016-12-21 04:00 | 189 | 189
2016-12-21 04:30 | 190 | 190
2016-12-21 05:00 | 195 | 194
2016-12-21 05:30 | 201 | 200
2016-12-21 06:00 | 216 | 216
2016-12-21 06:30 | 227 | 227
2016-12-21 07:00 | 240 | 240
2016-12-21 07:30 | 250 | 250
2016-12-21 08:00 | 260 | 259
2016-12-21 08:30 | 270 | 270
2016-12-21 09:00 | 279 | 279
2016-12-21 09:30 | 285 | 285
2016-12-21 10:00 | 291 | 291
2016-12-21 10:30 | 294 | 294
2016-12-21 11:00 | 285 | 285
2016-12-21 11:30 | 289 | 289
2016-12-21 12:00 | 309 | 309
2016-12-21 12:30 | 311 | 311
2016-12-21 13:00 | 317 | 316
2016-12-21 13:30 | 322 | 321
2016-12-21 14:00 | 340 | 339
2016-12-21 14:30 | 353 | 352
2016-12-21 15:00 | 357 | 357
2016-12-21 15:30 | 354 | 354
2016-12-21 16:00 | 347 | 346
2016-12-21 16:30 | 341 | 340
2016-12-21 17:00 | 330 | 328
2016-12-21 17:30 | 336 | 333
2016-12-21 18:00 | 325 | 324
2016-12-21 18:30 | 327 | 327
2016-12-21 19:00 | 322 | 322
2016-12-21 19:30 | 320 | 320
2016-12-21 20:00 | 312 | 312
2016-12-21 20:30 | 295 | 295
2016-12-21 21:00 | 280 | 280
2016-12-21 21:30 | 268 | 268
2016-12-21 22:00 | 260 | 260
2016-12-21 22:30 | 248 | 248
2016-12-21 23:00 | 226 | 226
2016-12-21 23:30 | 212 | 212
2016-12-22 | 197 | 197
2016-12-22 00:30 | 193 | 193
2016-12-22 01:00 | 191 | 191
2016-12-22 01:30 | 188 | 188
2016-12-22 02:00 | 184 | 184
2016-12-22 02:30 | 184 | 184
2016-12-22 03:00 | 185 | 185
2016-12-22 03:30 | 184 | 184
2016-12-22 04:00 | 193 | 193
2016-12-22 04:30 | 192 | 191
2016-12-22 05:00 | 199 | 199
2016-12-22 05:30 | 212 | 212
2016-12-22 06:00 | 217 | 217
2016-12-22 06:30 | 226 | 225
2016-12-22 07:00 | 239 | 239
2016-12-22 07:30 | 250 | 250
2016-12-22 08:00 | 253 | 253
2016-12-22 08:30 | 263 | 263
2016-12-22 09:00 | 268 | 267
2016-12-22 09:30 | 274 | 274
2016-12-22 10:00 | 279 | 278
2016-12-22 10:30 | 267 | 266
2016-12-22 11:00 | 251 | 250
2016-12-22 11:30 | 248 | 247
2016-12-22 12:00 | 252 | 251
2016-12-22 12:30 | 256 | 256
2016-12-22 13:00 | 262 | 262
2016-12-22 13:30 | 269 | 269
2016-12-22 14:00 | 268 | 267
2016-12-22 14:30 | 275 | 274
2016-12-22 15:00 | 275 | 273
2016-12-22 15:30 | 272 | 270
2016-12-22 16:00 | 272 | 272
2016-12-22 16:30 | 261 | 260
2016-12-22 17:00 | 267 | 267
2016-12-22 17:30 | 265 | 265
2016-12-22 18:00 | 262 | 261
2016-12-22 18:30 | 260 | 259
2016-12-22 19:00 | 260 | 259
2016-12-22 19:30 | 264 | 264
2016-12-22 20:00 | 261 | 261
2016-12-22 20:30 | 257 | 257
2016-12-22 21:00 | 250 | 250
2016-12-22 21:30 | 245 | 245
2016-12-22 22:00 | 245 | 245
2016-12-22 22:30 | 235 | 235
2016-12-22 23:00 | 217 | 216
2016-12-22 23:30 | 200 | 200
2016-12-23 | 195 | 195
2016-12-23 00:30 | 188 | 188
2016-12-23 01:00 | 181 | 181
2016-12-23 01:30 | 182 | 182
2016-12-23 02:00 | 182 | 182
2016-12-23 02:30 | 181 | 181
2016-12-23 03:00 | 181 | 180
2016-12-23 03:30 | 182 | 182
2016-12-23 04:00 | 186 | 186
2016-12-23 04:30 | 189 | 189
2016-12-23 05:00 | 194 | 194
2016-12-23 05:30 | 197 | 197
2016-12-23 06:00 | 208 | 208
2016-12-23 06:30 | 214 | 214
2016-12-23 07:00 | 227 | 227
2016-12-23 07:30 | 236 | 236
2016-12-23 08:00 | 240 | 240
2016-12-23 08:30 | 244 | 244
2016-12-23 09:00 | 247 | 247
2016-12-23 09:30 | 252 | 252
2016-12-23 10:00 | 250 | 250
2016-12-23 10:30 | 249 | 249
2016-12-23 11:00 | 253 | 253
2016-12-23 11:30 | 253 | 253
2016-12-23 12:00 | 254 | 254
2016-12-23 12:30 | 258 | 258
2016-12-23 13:00 | 265 | 265
2016-12-23 13:30 | 264 | 264
2016-12-23 14:00 | 264 | 264
2016-12-23 14:30 | 268 | 268
2016-12-23 15:00 | 269 | 269
2016-12-23 15:30 | 269 | 269
2016-12-23 16:00 | 272 | 272
2016-12-23 16:30 | 272 | 272
2016-12-23 17:00 | 271 | 271
2016-12-23 17:30 | 273 | 272
2016-12-23 18:00 | 269 | 268
2016-12-23 18:30 | 272 | 271
2016-12-23 19:00 | 272 | 272
2016-12-23 19:30 | 275 | 274
2016-12-23 20:00 | 270 | 270
2016-12-23 20:30 | 260 | 260
2016-12-23 21:00 | 253 | 253
2016-12-23 21:30 | 243 | 243
2016-12-23 22:00 | 244 | 244
2016-12-23 22:30 | 246 | 246
2016-12-23 23:00 | 225 | 225
2016-12-23 23:30 | 205 | 205
2016-12-24 | 188 | 188
2016-12-24 00:30 | 175 | 175
2016-12-24 01:00 | 167 | 166
2016-12-24 01:30 | 161 | 160
2016-12-24 02:00 | 156 | 156
2016-12-24 02:30 | 154 | 154
2016-12-24 03:00 | 153 | 153
2016-12-24 03:30 | 152 | 152
2016-12-24 04:00 | 153 | 153
2016-12-24 04:30 | 152 | 152
2016-12-24 05:00 | 156 | 155
2016-12-24 05:30 | 162 | 162
2016-12-24 06:00 | 172 | 172
2016-12-24 06:30 | 180 | 180
2016-12-24 07:00 | 192 | 192
2016-12-24 07:30 | 205 | 204
2016-12-24 08:00 | 215 | 215
2016-12-24 08:30 | 222 | 222
2016-12-24 09:00 | 226 | 225
2016-12-24 09:30 | 226 | 224
2016-12-24 10:00 | 227 | 226
2016-12-24 10:30 | 229 | 228
2016-12-24 11:00 | 235 | 234
2016-12-24 11:30 | 239 | 239
2016-12-24 12:00 | 239 | 239
2016-12-24 12:30 | 241 | 241
2016-12-24 13:00 | 244 | 244
2016-12-24 13:30 | 248 | 248
2016-12-24 14:00 | 253 | 253
2016-12-24 14:30 | 257 | 257
2016-12-24 15:00 | 267 | 267
2016-12-24 15:30 | 277 | 276
2016-12-24 16:00 | 277 | 277
2016-12-24 16:30 | 286 | 286
2016-12-24 17:00 | 286 | 286
2016-12-24 17:30 | 284 | 283
2016-12-24 18:00 | 281 | 280
2016-12-24 18:30 | 285 | 284
2016-12-24 19:00 | 287 | 287
2016-12-24 19:30 | 288 | 287
2016-12-24 20:00 | 280 | 279
2016-12-24 20:30 | 269 | 269
2016-12-24 21:00 | 262 | 262
2016-12-24 21:30 | 253 | 253
2016-12-24 22:00 | 243 | 243
2016-12-24 22:30 | 232 | 231
2016-12-24 23:00 | 216 | 216
2016-12-24 23:30 | 206 | 206
2016-12-25 | 198 | 198
2016-12-25 00:30 | 197 | 196
2016-12-25 01:00 | 190 | 190
2016-12-25 01:30 | 184 | 183
2016-12-25 02:00 | 180 | 179
2016-12-25 02:30 | 180 | 179
2016-12-25 03:00 | 176 | 175
2016-12-25 03:30 | 170 | 170
2016-12-25 04:00 | 170 | 170
2016-12-25 04:30 | 167 | 167
2016-12-25 05:00 | 172 | 172
2016-12-25 05:30 | 180 | 180
2016-12-25 06:00 | 189 | 189
2016-12-25 06:30 | 198 | 198
2016-12-25 07:00 | 217 | 216
2016-12-25 07:30 | 231 | 230
2016-12-25 08:00 | 242 | 241
2016-12-25 08:30 | 247 | 247
2016-12-25 09:00 | 250 | 250
2016-12-25 09:30 | 249 | 249
2016-12-25 10:00 | 244 | 244
2016-12-25 10:30 | 244 | 244
2016-12-25 11:00 | 242 | 242
2016-12-25 11:30 | 237 | 237
2016-12-25 12:00 | 234 | 234
2016-12-25 12:30 | 227 | 227
2016-12-25 13:00 | 226 | 226
2016-12-25 13:30 | 218 | 218
2016-12-25 14:00 | 224 | 224
2016-12-25 14:30 | 224 | 224
2016-12-25 15:00 | 224 | 224
2016-12-25 15:30 | 225 | 225
2016-12-25 16:00 | 226 | 226
2016-12-25 16:30 | 227 | 227
2016-12-25 17:00 | 225 | 225
2016-12-25 17:30 | 225 | 225
2016-12-25 18:00 | 228 | 228
2016-12-25 18:30 | 233 | 233
2016-12-25 19:00 | 238 | 238
2016-12-25 19:30 | 243 | 242
2016-12-25 20:00 | 242 | 241
2016-12-25 20:30 | 239 | 239
2016-12-25 21:00 | 236 | 236
2016-12-25 21:30 | 233 | 233
2016-12-25 22:00 | 230 | 230
2016-12-25 22:30 | 227 | 227
2016-12-25 23:00 | 212 | 211
2016-12-25 23:30 | 200 | 199
2016-12-26 | 189 | 189
2016-12-26 00:30 | 183 | 183
2016-12-26 01:00 | 178 | 178
2016-12-26 01:30 | 176 | 176
2016-12-26 02:00 | 175 | 175
2016-12-26 02:30 | 174 | 174
2016-12-26 03:00 | 174 | 174
2016-12-26 03:30 | 173 | 173
2016-12-26 04:00 | 175 | 175
2016-12-26 04:30 | 173 | 172
2016-12-26 05:00 | 176 | 176
2016-12-26 05:30 | 179 | 179
2016-12-26 06:00 | 187 | 187
2016-12-26 06:30 | 195 | 195
2016-12-26 07:00 | 211 | 211
2016-12-26 07:30 | 222 | 222
2016-12-26 08:00 | 235 | 235
2016-12-26 08:30 | 241 | 241
2016-12-26 09:00 | 245 | 244
2016-12-26 09:30 | 246 | 246
2016-12-26 10:00 | 256 | 256
2016-12-26 10:30 | 251 | 251
2016-12-26 11:00 | 244 | 244
2016-12-26 11:30 | 241 | 241
2016-12-26 12:00 | 241 | 241
2016-12-26 12:30 | 242 | 242
2016-12-26 13:00 | 243 | 243
2016-12-26 13:30 | 248 | 248
2016-12-26 14:00 | 250 | 250
2016-12-26 14:30 | 250 | 250
2016-12-26 15:00 | 251 | 251
2016-12-26 15:30 | 252 | 252
2016-12-26 16:00 | 253 | 253
2016-12-26 16:30 | 252 | 251
2016-12-26 17:00 | 252 | 252
2016-12-26 17:30 | 253 | 253
2016-12-26 18:00 | 252 | 252
2016-12-26 18:30 | 254 | 254
2016-12-26 19:00 | 256 | 256
2016-12-26 19:30 | 258 | 258
2016-12-26 20:00 | 254 | 254
2016-12-26 20:30 | 250 | 249
2016-12-26 21:00 | 246 | 245
2016-12-26 21:30 | 238 | 237
2016-12-26 22:00 | 231 | 231
2016-12-26 22:30 | 230 | 230
2016-12-26 23:00 | 213 | 213
2016-12-26 23:30 | 203 | 203
2016-12-27 | 195 | 195
2016-12-27 00:30 | 190 | 190
2016-12-27 01:00 | 185 | 185
2016-12-27 01:30 | 182 | 182
2016-12-27 02:00 | 179 | 178
2016-12-27 02:30 | 179 | 179
2016-12-27 03:00 | 178 | 178
2016-12-27 03:30 | 177 | 177
2016-12-27 04:00 | 178 | 178
2016-12-27 04:30 | 177 | 176
2016-12-27 05:00 | 179 | 179
2016-12-27 05:30 | 183 | 183
2016-12-27 06:00 | 191 | 191
2016-12-27 06:30 | 199 | 199
2016-12-27 07:00 | 213 | 213
2016-12-27 07:30 | 223 | 223
2016-12-27 08:00 | 232 | 232
2016-12-27 08:30 | 237 | 236
2016-12-27 09:00 | 241 | 241
2016-12-27 09:30 | 237 | 236
2016-12-27 10:00 | 242 | 241
2016-12-27 10:30 | 235 | 234
2016-12-27 11:00 | 236 | 235
2016-12-27 11:30 | 240 | 240
2016-12-27 12:00 | 239 | 239
2016-12-27 12:30 | 237 | 237
2016-12-27 13:00 | 237 | 237
2016-12-27 13:30 | 241 | 241
2016-12-27 14:00 | 248 | 248
2016-12-27 14:30 | 252 | 251
2016-12-27 15:00 | 261 | 261
2016-12-27 15:30 | 269 | 268
2016-12-27 16:00 | 273 | 272
2016-12-27 16:30 | 268 | 268
2016-12-27 17:00 | 269 | 268
2016-12-27 17:30 | 268 | 268
2016-12-27 18:00 | 261 | 261
2016-12-27 18:30 | 264 | 264
2016-12-27 19:00 | 265 | 264
2016-12-27 19:30 | 267 | 267
2016-12-27 20:00 | 259 | 259
2016-12-27 20:30 | 256 | 255
2016-12-27 21:00 | 251 | 251
2016-12-27 21:30 | 244 | 244
2016-12-27 22:00 | 239 | 239
2016-12-27 22:30 | 233 | 233
2016-12-27 23:00 | 214 | 214
2016-12-27 23:30 | 206 | 206
2016-12-28 | 196 | 196
2016-12-28 00:30 | 189 | 189
2016-12-28 01:00 | 187 | 187
2016-12-28 01:30 | 183 | 183
2016-12-28 02:00 | 179 | 179
2016-12-28 02:30 | 180 | 180
2016-12-28 03:00 | 174 | 174
2016-12-28 03:30 | 176 | 176
2016-12-28 04:00 | 178 | 178
2016-12-28 04:30 | 180 | 180
2016-12-28 05:00 | 190 | 190
2016-12-28 05:30 | 194 | 194
2016-12-28 06:00 | 203 | 203
2016-12-28 06:30 | 209 | 209
2016-12-28 07:00 | 221 | 220
2016-12-28 07:30 | 235 | 234
2016-12-28 08:00 | 242 | 242
2016-12-28 08:30 | 245 | 244
2016-12-28 09:00 | 249 | 249
2016-12-28 09:30 | 252 | 252
2016-12-28 10:00 | 251 | 250
2016-12-28 10:30 | 248 | 248
2016-12-28 11:00 | 246 | 246
2016-12-28 11:30 | 246 | 246
2016-12-28 12:00 | 245 | 245
2016-12-28 12:30 | 248 | 248
2016-12-28 13:00 | 255 | 254
2016-12-28 13:30 | 261 | 261
2016-12-28 14:00 | 266 | 265
2016-12-28 14:30 | 268 | 267
2016-12-28 15:00 | 274 | 273
2016-12-28 15:30 | 281 | 281
2016-12-28 16:00 | 288 | 288
2016-12-28 16:30 | 286 | 285
2016-12-28 17:00 | 291 | 291
2016-12-28 17:30 | 285 | 285
2016-12-28 18:00 | 287 | 286
2016-12-28 18:30 | 284 | 283
2016-12-28 19:00 | 282 | 281
2016-12-28 19:30 | 294 | 293
2016-12-28 20:00 | 286 | 285
2016-12-28 20:30 | 276 | 276
2016-12-28 21:00 | 264 | 263
2016-12-28 21:30 | 250 | 250
2016-12-28 22:00 | 246 | 246
2016-12-28 22:30 | 227 | 227
2016-12-28 23:00 | 211 | 211
2016-12-28 23:30 | 202 | 202
2016-12-29 | 193 | 193
2016-12-29 00:30 | 188 | 188
2016-12-29 01:00 | 180 | 180
2016-12-29 01:30 | 176 | 176
2016-12-29 02:00 | 174 | 174
2016-12-29 02:30 | 174 | 174
2016-12-29 03:00 | 173 | 173
2016-12-29 03:30 | 174 | 174
2016-12-29 04:00 | 173 | 173
2016-12-29 04:30 | 172 | 172
2016-12-29 05:00 | 183 | 182
2016-12-29 05:30 | 189 | 188
2016-12-29 06:00 | 198 | 197
2016-12-29 06:30 | 207 | 206
2016-12-29 07:00 | 221 | 221
2016-12-29 07:30 | 234 | 234
2016-12-29 08:00 | 246 | 245
2016-12-29 08:30 | 252 | 252
2016-12-29 09:00 | 258 | 258
2016-12-29 09:30 | 260 | 259
2016-12-29 10:00 | 255 | 255
2016-12-29 10:30 | 258 | 258
2016-12-29 11:00 | 259 | 258
2016-12-29 11:30 | 260 | 259
2016-12-29 12:00 | 260 | 259
2016-12-29 12:30 | 260 | 259
2016-12-29 13:00 | 263 | 262
2016-12-29 13:30 | 264 | 264
2016-12-29 14:00 | 257 | 256
2016-12-29 14:30 | 264 | 263
2016-12-29 15:00 | 266 | 266
2016-12-29 15:30 | 273 | 272
2016-12-29 16:00 | 294 | 294
2016-12-29 16:30 | 298 | 297
2016-12-29 17:00 | 305 | 305
2016-12-29 17:30 | 307 | 306
2016-12-29 18:00 | 303 | 302
2016-12-29 18:30 | 308 | 307
2016-12-29 19:00 | 306 | 306
2016-12-29 19:30 | 309 | 309
2016-12-29 20:00 | 299 | 298
2016-12-29 20:30 | 281 | 281
2016-12-29 21:00 | 266 | 265
2016-12-29 21:30 | 256 | 256
2016-12-29 22:00 | 256 | 256
2016-12-29 22:30 | 245 | 245
2016-12-29 23:00 | 226 | 225
2016-12-29 23:30 | 212 | 212
2016-12-30 | 197 | 197
2016-12-30 00:30 | 192 | 192
2016-12-30 01:00 | 188 | 188
2016-12-30 01:30 | 188 | 188
2016-12-30 02:00 | 183 | 183
2016-12-30 02:30 | 182 | 182
2016-12-30 03:00 | 183 | 183
2016-12-30 03:30 | 183 | 183
2016-12-30 04:00 | 182 | 182
2016-12-30 04:30 | 182 | 182
2016-12-30 05:00 | 184 | 184
2016-12-30 05:30 | 195 | 195
2016-12-30 06:00 | 206 | 206
2016-12-30 06:30 | 217 | 217
2016-12-30 07:00 | 233 | 233
2016-12-30 07:30 | 244 | 244
2016-12-30 08:00 | 252 | 252
2016-12-30 08:30 | 260 | 260
2016-12-30 09:00 | 272 | 272
2016-12-30 09:30 | 278 | 278
2016-12-30 10:00 | 280 | 280
2016-12-30 10:30 | 278 | 278
2016-12-30 11:00 | 282 | 282
2016-12-30 11:30 | 281 | 280
2016-12-30 12:00 | 276 | 276
2016-12-30 12:30 | 273 | 273
2016-12-30 13:00 | 273 | 273
2016-12-30 13:30 | 271 | 271
2016-12-30 14:00 | 294 | 293
2016-12-30 14:30 | 306 | 306
2016-12-30 15:00 | 317 | 317
2016-12-30 15:30 | 325 | 325
2016-12-30 16:00 | 332 | 332
2016-12-30 16:30 | 344 | 344
2016-12-30 17:00 | 333 | 333
2016-12-30 17:30 | 327 | 326
2016-12-30 18:00 | 320 | 320
2016-12-30 18:30 | 318 | 318
2016-12-30 19:00 | 318 | 318
2016-12-30 19:30 | 316 | 316
2016-12-30 20:00 | 306 | 306
2016-12-30 20:30 | 299 | 299
2016-12-30 21:00 | 289 | 289
2016-12-30 21:30 | 282 | 281
2016-12-30 22:00 | 278 | 277
2016-12-30 22:30 | 252 | 251
2016-12-30 23:00 | 239 | 238
2016-12-30 23:30 | 229 | 228
2016-12-31 | 221 | 221
2016-12-31 00:30 | 210 | 209
2016-12-31 01:00 | 201 | 199
2016-12-31 01:30 | 196 | 194
2016-12-31 02:00 | 209 | 208
2016-12-31 02:30 | 209 | 208
2016-12-31 03:00 | 208 | 206
2016-12-31 03:30 | 207 | 205
2016-12-31 04:00 | 206 | 205
2016-12-31 04:30 | 208 | 206
2016-12-31 05:00 | 208 | 206
2016-12-31 05:30 | 214 | 211
2016-12-31 06:00 | 222 | 221
2016-12-31 06:30 | 230 | 229
2016-12-31 07:00 | 246 | 246
2016-12-31 07:30 | 256 | 256
2016-12-31 08:00 | 268 | 268
2016-12-31 08:30 | 285 | 284
2016-12-31 09:00 | 293 | 292
2016-12-31 09:30 | 299 | 299
2016-12-31 10:00 | 303 | 303
2016-12-31 10:30 | 299 | 299
2016-12-31 11:00 | 305 | 305
2016-12-31 11:30 | 297 | 297
2016-12-31 12:00 | 311 | 310
2016-12-31 12:30 | 315 | 315
2016-12-31 13:00 | 309 | 309
2016-12-31 13:30 | 348 | 348
2016-12-31 14:00 | 353 | 353
2016-12-31 14:30 | 350 | 349
2016-12-31 15:00 | 349 | 349
2016-12-31 15:30 | 358 | 358
2016-12-31 16:00 | 366 | 366
2016-12-31 16:30 | 371 | 370
2016-12-31 17:00 | 367 | 367
2016-12-31 17:30 | 355 | 354
2016-12-31 18:00 | 343 | 342
2016-12-31 18:30 | 337 | 336
2016-12-31 19:00 | 327 | 327
2016-12-31 19:30 | 327 | 326
2016-12-31 20:00 | 316 | 315
2016-12-31 20:30 | 305 | 305
2016-12-31 21:00 | 300 | 300
2016-12-31 21:30 | 300 | 300
2016-12-31 22:00 | 297 | 296
2016-12-31 22:30 | 292 | 291
2016-12-31 23:00 | 274 | 273
2016-12-31 23:30 | 259 | 259
2017-01-01 | 244 | 244
2017-01-01 00:30 | 236 | 235
2017-01-01 01:00 | 224 | 223
2017-01-01 01:30 | 214 | 213
2017-01-01 02:00 | 209 | 209
2017-01-01 02:30 | 211 | 210
2017-01-01 03:00 | 207 | 206
2017-01-01 03:30 | 198 | 197
2017-01-01 04:00 | 197 | 197
2017-01-01 04:30 | 195 | 195
2017-01-01 05:00 | 193 | 193
2017-01-01 05:30 | 196 | 196
2017-01-01 06:00 | 202 | 202
2017-01-01 06:30 | 213 | 213
2017-01-01 07:00 | 224 | 224
2017-01-01 07:30 | 236 | 235
2017-01-01 08:00 | 252 | 252
2017-01-01 08:30 | 263 | 263
2017-01-01 09:00 | 276 | 276
2017-01-01 09:30 | 286 | 286
2017-01-01 10:00 | 289 | 289
2017-01-01 10:30 | 294 | 294
2017-01-01 11:00 | 296 | 296
2017-01-01 11:30 | 295 | 295
2017-01-01 12:00 | 307 | 306
2017-01-01 12:30 | 315 | 315
2017-01-01 13:00 | 314 | 313
2017-01-01 13:30 | 305 | 304
2017-01-01 14:00 | 309 | 308
2017-01-01 14:30 | 316 | 315
2017-01-01 15:00 | 326 | 326
2017-01-01 15:30 | 340 | 339
2017-01-01 16:00 | 341 | 341
2017-01-01 16:30 | 345 | 345
2017-01-01 17:00 | 338 | 337
2017-01-01 17:30 | 344 | 343
2017-01-01 18:00 | 329 | 328
2017-01-01 18:30 | 328 | 327
2017-01-01 19:00 | 326 | 326
2017-01-01 19:30 | 324 | 324
2017-01-01 20:00 | 314 | 313
2017-01-01 20:30 | 307 | 306
2017-01-01 21:00 | 291 | 291
2017-01-01 21:30 | 289 | 288
2017-01-01 22:00 | 280 | 280
2017-01-01 22:30 | 261 | 261
2017-01-01 23:00 | 247 | 247
2017-01-01 23:30 | 233 | 233
2017-01-02 | 207 | 207
2017-01-02 00:30 | 204 | 204
2017-01-02 01:00 | 202 | 202
2017-01-02 01:30 | 199 | 199
2017-01-02 02:00 | 194 | 194
2017-01-02 02:30 | 193 | 193
2017-01-02 03:00 | 192 | 192
2017-01-02 03:30 | 191 | 191
2017-01-02 04:00 | 191 | 191
2017-01-02 04:30 | 191 | 191
2017-01-02 05:00 | 191 | 191
2017-01-02 05:30 | 196 | 196
2017-01-02 06:00 | 206 | 206
2017-01-02 06:30 | 219 | 219
2017-01-02 07:00 | 235 | 235
2017-01-02 07:30 | 241 | 241
2017-01-02 08:00 | 240 | 239
2017-01-02 08:30 | 254 | 254
2017-01-02 09:00 | 269 | 268
2017-01-02 09:30 | 283 | 283
2017-01-02 10:00 | 277 | 277
2017-01-02 10:30 | 272 | 272
2017-01-02 11:00 | 276 | 276
2017-01-02 11:30 | 281 | 281
2017-01-02 12:00 | 294 | 294
2017-01-02 12:30 | 287 | 287
2017-01-02 13:00 | 287 | 287
2017-01-02 13:30 | 296 | 296
2017-01-02 14:00 | 303 | 303
2017-01-02 14:30 | 321 | 320
2017-01-02 15:00 | 321 | 320
2017-01-02 15:30 | 331 | 329
2017-01-02 16:00 | 327 | 326
2017-01-02 16:30 | 326 | 325
2017-01-02 17:00 | 326 | 325
2017-01-02 17:30 | 330 | 329
2017-01-02 18:00 | 325 | 323
2017-01-02 18:30 | 321 | 320
2017-01-02 19:00 | 312 | 311
2017-01-02 19:30 | 301 | 301
2017-01-02 20:00 | 291 | 290
2017-01-02 20:30 | 276 | 276
2017-01-02 21:00 | 264 | 264
2017-01-02 21:30 | 250 | 250
2017-01-02 22:00 | 243 | 243
2017-01-02 22:30 | 240 | 240
2017-01-02 23:00 | 227 | 226
2017-01-02 23:30 | 211 | 211
2017-01-03 | 201 | 201
2017-01-03 00:30 | 195 | 195
2017-01-03 01:00 | 192 | 192
2017-01-03 01:30 | 187 | 187
2017-01-03 02:00 | 187 | 187
2017-01-03 02:30 | 187 | 187
2017-01-03 03:00 | 189 | 189
2017-01-03 03:30 | 188 | 188
2017-01-03 04:00 | 192 | 192
2017-01-03 04:30 | 191 | 191
2017-01-03 05:00 | 196 | 196
2017-01-03 05:30 | 199 | 199
2017-01-03 06:00 | 213 | 213
2017-01-03 06:30 | 229 | 228
2017-01-03 07:00 | 249 | 248
2017-01-03 07:30 | 262 | 262
2017-01-03 08:00 | 275 | 275
2017-01-03 08:30 | 279 | 279
2017-01-03 09:00 | 287 | 287
2017-01-03 09:30 | 293 | 293
2017-01-03 10:00 | 292 | 290
2017-01-03 10:30 | 288 | 285
2017-01-03 11:00 | 286 | 284
2017-01-03 11:30 | 284 | 282
2017-01-03 12:00 | 283 | 280
2017-01-03 12:30 | 281 | 278
2017-01-03 13:00 | 277 | 275
2017-01-03 13:30 | 272 | 271
2017-01-03 14:00 | 276 | 275
2017-01-03 14:30 | 276 | 275
2017-01-03 15:00 | 282 | 280
2017-01-03 15:30 | 283 | 282
2017-01-03 16:00 | 287 | 285
2017-01-03 16:30 | 292 | 291
2017-01-03 17:00 | 290 | 288
2017-01-03 17:30 | 289 | 287
2017-01-03 18:00 | 285 | 283
2017-01-03 18:30 | 296 | 295
2017-01-03 19:00 | 296 | 295
2017-01-03 19:30 | 294 | 293
2017-01-03 20:00 | 282 | 282
2017-01-03 20:30 | 265 | 265
2017-01-03 21:00 | 251 | 251
2017-01-03 21:30 | 237 | 237
2017-01-03 22:00 | 232 | 232
2017-01-03 22:30 | 227 | 227
2017-01-03 23:00 | 207 | 207
2017-01-03 23:30 | 195 | 195
2017-01-04 | 185 | 185
2017-01-04 00:30 | 180 | 180
2017-01-04 01:00 | 178 | 178
2017-01-04 01:30 | 177 | 177
2017-01-04 02:00 | 178 | 178
2017-01-04 02:30 | 176 | 176
2017-01-04 03:00 | 176 | 176
2017-01-04 03:30 | 176 | 176
2017-01-04 04:00 | 177 | 177
2017-01-04 04:30 | 178 | 177
2017-01-04 05:00 | 185 | 185
2017-01-04 05:30 | 192 | 192
2017-01-04 06:00 | 203 | 203
2017-01-04 06:30 | 217 | 217
2017-01-04 07:00 | 235 | 234
2017-01-04 07:30 | 245 | 245
2017-01-04 08:00 | 253 | 253
2017-01-04 08:30 | 257 | 257
2017-01-04 09:00 | 264 | 264
2017-01-04 09:30 | 264 | 263
2017-01-04 10:00 | 261 | 260
2017-01-04 10:30 | 257 | 256
2017-01-04 11:00 | 253 | 252
2017-01-04 11:30 | 254 | 253
2017-01-04 12:00 | 254 | 253
2017-01-04 12:30 | 254 | 253
2017-01-04 13:00 | 254 | 253
2017-01-04 13:30 | 256 | 256
2017-01-04 14:00 | 263 | 262
2017-01-04 14:30 | 269 | 269
2017-01-04 15:00 | 282 | 282
2017-01-04 15:30 | 285 | 284
2017-01-04 16:00 | 293 | 292
2017-01-04 16:30 | 299 | 298
2017-01-04 17:00 | 299 | 298
2017-01-04 17:30 | 293 | 292
2017-01-04 18:00 | 287 | 286
2017-01-04 18:30 | 296 | 296
2017-01-04 19:00 | 298 | 298
2017-01-04 19:30 | 297 | 296
2017-01-04 20:00 | 285 | 284
2017-01-04 20:30 | 271 | 271
2017-01-04 21:00 | 259 | 259
2017-01-04 21:30 | 247 | 247
2017-01-04 22:00 | 242 | 242
2017-01-04 22:30 | 235 | 235
2017-01-04 23:00 | 208 | 208
2017-01-04 23:30 | 198 | 198
2017-01-05 | 186 | 186
2017-01-05 00:30 | 183 | 183
2017-01-05 01:00 | 180 | 180
2017-01-05 01:30 | 178 | 178
2017-01-05 02:00 | 179 | 179
2017-01-05 02:30 | 178 | 178
2017-01-05 03:00 | 179 | 179
2017-01-05 03:30 | 179 | 179
2017-01-05 04:00 | 182 | 182
2017-01-05 04:30 | 183 | 183
2017-01-05 05:00 | 187 | 187
2017-01-05 05:30 | 193 | 193
2017-01-05 06:00 | 201 | 200
2017-01-05 06:30 | 213 | 213
2017-01-05 07:00 | 233 | 233
2017-01-05 07:30 | 253 | 252
2017-01-05 08:00 | 266 | 266
2017-01-05 08:30 | 270 | 270
2017-01-05 09:00 | 270 | 270
2017-01-05 09:30 | 273 | 272
2017-01-05 10:00 | 276 | 276
2017-01-05 10:30 | 269 | 269
2017-01-05 11:00 | 264 | 264
2017-01-05 11:30 | 268 | 268
2017-01-05 12:00 | 271 | 271
2017-01-05 12:30 | 276 | 276
2017-01-05 13:00 | 272 | 272
2017-01-05 13:30 | 272 | 272
2017-01-05 14:00 | 280 | 280
2017-01-05 14:30 | 286 | 286
2017-01-05 15:00 | 288 | 288
2017-01-05 15:30 | 294 | 294
2017-01-05 16:00 | 295 | 295
2017-01-05 16:30 | 301 | 301
2017-01-05 17:00 | 299 | 299
2017-01-05 17:30 | 296 | 296
2017-01-05 18:00 | 295 | 295
2017-01-05 18:30 | 300 | 300
2017-01-05 19:00 | 298 | 298
2017-01-05 19:30 | 298 | 298
2017-01-05 20:00 | 297 | 296
2017-01-05 20:30 | 287 | 286
2017-01-05 21:00 | 274 | 273
2017-01-05 21:30 | 261 | 259
2017-01-05 22:00 | 248 | 248
2017-01-05 22:30 | 241 | 240
2017-01-05 23:00 | 216 | 216
2017-01-05 23:30 | 202 | 202
2017-01-06 | 192 | 192
2017-01-06 00:30 | 187 | 187
2017-01-06 01:00 | 184 | 184
2017-01-06 01:30 | 182 | 182
2017-01-06 02:00 | 182 | 182
2017-01-06 02:30 | 178 | 178
2017-01-06 03:00 | 180 | 180
2017-01-06 03:30 | 183 | 183
2017-01-06 04:00 | 184 | 184
2017-01-06 04:30 | 184 | 184
2017-01-06 05:00 | 190 | 190
2017-01-06 05:30 | 195 | 195
2017-01-06 06:00 | 202 | 202
2017-01-06 06:30 | 216 | 216
2017-01-06 07:00 | 235 | 233
2017-01-06 07:30 | 249 | 248
2017-01-06 08:00 | 261 | 260
2017-01-06 08:30 | 270 | 270
2017-01-06 09:00 | 273 | 272
2017-01-06 09:30 | 281 | 280
2017-01-06 10:00 | 278 | 278
2017-01-06 10:30 | 274 | 274
2017-01-06 11:00 | 275 | 275
2017-01-06 11:30 | 282 | 282
2017-01-06 12:00 | 289 | 289
2017-01-06 12:30 | 289 | 289
2017-01-06 13:00 | 293 | 293
2017-01-06 13:30 | 305 | 305
2017-01-06 14:00 | 304 | 304
2017-01-06 14:30 | 313 | 313
2017-01-06 15:00 | 321 | 321
2017-01-06 15:30 | 328 | 328
2017-01-06 16:00 | 330 | 330
2017-01-06 16:30 | 339 | 338
2017-01-06 17:00 | 328 | 327
2017-01-06 17:30 | 316 | 315
2017-01-06 18:00 | 309 | 309
2017-01-06 18:30 | 316 | 316
2017-01-06 19:00 | 314 | 314
2017-01-06 19:30 | 306 | 306
2017-01-06 20:00 | 297 | 297
2017-01-06 20:30 | 284 | 284
2017-01-06 21:00 | 275 | 274
2017-01-06 21:30 | 266 | 266
2017-01-06 22:00 | 255 | 255
2017-01-06 22:30 | 249 | 249
2017-01-06 23:00 | 230 | 230
2017-01-06 23:30 | 214 | 214
2017-01-07 | 198 | 197
2017-01-07 00:30 | 192 | 191
2017-01-07 01:00 | 189 | 189
2017-01-07 01:30 | 187 | 187
2017-01-07 02:00 | 188 | 187
2017-01-07 02:30 | 189 | 189
2017-01-07 03:00 | 188 | 187
2017-01-07 03:30 | 188 | 188
2017-01-07 04:00 | 189 | 188
2017-01-07 04:30 | 188 | 187
2017-01-07 05:00 | 189 | 189
2017-01-07 05:30 | 195 | 194
2017-01-07 06:00 | 200 | 199
2017-01-07 06:30 | 204 | 203
2017-01-07 07:00 | 215 | 215
2017-01-07 07:30 | 226 | 225
2017-01-07 08:00 | 240 | 240
2017-01-07 08:30 | 251 | 251
2017-01-07 09:00 | 256 | 256
2017-01-07 09:30 | 257 | 257
2017-01-07 10:00 | 258 | 258
2017-01-07 10:30 | 254 | 254
2017-01-07 11:00 | 254 | 254
2017-01-07 11:30 | 256 | 256
2017-01-07 12:00 | 256 | 255
2017-01-07 12:30 | 249 | 247
2017-01-07 13:00 | 247 | 245
2017-01-07 13:30 | 249 | 247
2017-01-07 14:00 | 251 | 249
2017-01-07 14:30 | 255 | 253
2017-01-07 15:00 | 259 | 257
2017-01-07 15:30 | 266 | 264
2017-01-07 16:00 | 274 | 273
2017-01-07 16:30 | 281 | 280
2017-01-07 17:00 | 286 | 285
2017-01-07 17:30 | 286 | 285
2017-01-07 18:00 | 281 | 279
2017-01-07 18:30 | 283 | 281
2017-01-07 19:00 | 285 | 283
2017-01-07 19:30 | 281 | 279
2017-01-07 20:00 | 278 | 276
2017-01-07 20:30 | 267 | 267
2017-01-07 21:00 | 258 | 258
2017-01-07 21:30 | 249 | 249
2017-01-07 22:00 | 241 | 241
2017-01-07 22:30 | 235 | 235
2017-01-07 23:00 | 216 | 216
2017-01-07 23:30 | 205 | 205
2017-01-08 | 194 | 194
2017-01-08 00:30 | 187 | 187
2017-01-08 01:00 | 185 | 185
2017-01-08 01:30 | 182 | 182
2017-01-08 02:00 | 183 | 183
2017-01-08 02:30 | 184 | 184
2017-01-08 03:00 | 184 | 184
2017-01-08 03:30 | 181 | 181
2017-01-08 04:00 | 183 | 183
2017-01-08 04:30 | 183 | 182
2017-01-08 05:00 | 183 | 183
2017-01-08 05:30 | 186 | 185
2017-01-08 06:00 | 189 | 189
2017-01-08 06:30 | 195 | 195
2017-01-08 07:00 | 204 | 204
2017-01-08 07:30 | 211 | 210
2017-01-08 08:00 | 221 | 220
2017-01-08 08:30 | 226 | 226
2017-01-08 09:00 | 228 | 228
2017-01-08 09:30 | 228 | 227
2017-01-08 10:00 | 228 | 228
2017-01-08 10:30 | 230 | 230
2017-01-08 11:00 | 232 | 232
2017-01-08 11:30 | 233 | 233
2017-01-08 12:00 | 234 | 234
2017-01-08 12:30 | 235 | 235
2017-01-08 13:00 | 238 | 238
2017-01-08 13:30 | 243 | 243
2017-01-08 14:00 | 249 | 249
2017-01-08 14:30 | 254 | 254
2017-01-08 15:00 | 261 | 261
2017-01-08 15:30 | 265 | 265
2017-01-08 16:00 | 269 | 269
2017-01-08 16:30 | 270 | 270
2017-01-08 17:00 | 268 | 268
2017-01-08 17:30 | 271 | 271
2017-01-08 18:00 | 274 | 274
2017-01-08 18:30 | 273 | 273
2017-01-08 19:00 | 274 | 274
2017-01-08 19:30 | 275 | 275
2017-01-08 20:00 | 269 | 269
2017-01-08 20:30 | 263 | 263
2017-01-08 21:00 | 253 | 253
2017-01-08 21:30 | 240 | 240
2017-01-08 22:00 | 229 | 229
2017-01-08 22:30 | 225 | 225
2017-01-08 23:00 | 206 | 206
2017-01-08 23:30 | 196 | 196
2017-01-09 | 186 | 186
2017-01-09 00:30 | 182 | 182
2017-01-09 01:00 | 180 | 180
2017-01-09 01:30 | 179 | 179
2017-01-09 02:00 | 175 | 175
2017-01-09 02:30 | 182 | 182
2017-01-09 03:00 | 181 | 181
2017-01-09 03:30 | 181 | 181
2017-01-09 04:00 | 184 | 184
2017-01-09 04:30 | 185 | 185
2017-01-09 05:00 | 188 | 188
2017-01-09 05:30 | 195 | 195
2017-01-09 06:00 | 205 | 205
2017-01-09 06:30 | 217 | 216
2017-01-09 07:00 | 239 | 238
2017-01-09 07:30 | 254 | 254
2017-01-09 08:00 | 264 | 264
2017-01-09 08:30 | 272 | 272
2017-01-09 09:00 | 281 | 279
2017-01-09 09:30 | 284 | 283
2017-01-09 10:00 | 290 | 289
2017-01-09 10:30 | 291 | 291
2017-01-09 11:00 | 293 | 292
2017-01-09 11:30 | 291 | 290
2017-01-09 12:00 | 293 | 293
2017-01-09 12:30 | 296 | 296
2017-01-09 13:00 | 296 | 295
2017-01-09 13:30 | 300 | 299
2017-01-09 14:00 | 303 | 303
2017-01-09 14:30 | 305 | 304
2017-01-09 15:00 | 311 | 311
2017-01-09 15:30 | 313 | 312
2017-01-09 16:00 | 316 | 314
2017-01-09 16:30 | 319 | 316
2017-01-09 17:00 | 318 | 316
2017-01-09 17:30 | 316 | 315
2017-01-09 18:00 | 314 | 313
2017-01-09 18:30 | 315 | 314
2017-01-09 19:00 | 316 | 315
2017-01-09 19:30 | 313 | 312
2017-01-09 20:00 | 309 | 308
2017-01-09 20:30 | 296 | 296
2017-01-09 21:00 | 282 | 282
2017-01-09 21:30 | 267 | 267
2017-01-09 22:00 | 258 | 258
2017-01-09 22:30 | 253 | 253
2017-01-09 23:00 | 228 | 228
2017-01-09 23:30 | 213 | 212
2017-01-10 | 200 | 199
2017-01-10 00:30 | 192 | 192
2017-01-10 01:00 | 190 | 190
2017-01-10 01:30 | 188 | 188
2017-01-10 02:00 | 187 | 187
2017-01-10 02:30 | 190 | 190
2017-01-10 03:00 | 189 | 189
2017-01-10 03:30 | 190 | 190
2017-01-10 04:00 | 189 | 189
2017-01-10 04:30 | 189 | 189
2017-01-10 05:00 | 196 | 196
2017-01-10 05:30 | 203 | 203
2017-01-10 06:00 | 216 | 216
2017-01-10 06:30 | 234 | 234
2017-01-10 07:00 | 256 | 256
2017-01-10 07:30 | 268 | 268
2017-01-10 08:00 | 277 | 277
2017-01-10 08:30 | 288 | 288
2017-01-10 09:00 | 292 | 292
2017-01-10 09:30 | 293 | 293
2017-01-10 10:00 | 291 | 291
2017-01-10 10:30 | 300 | 300
2017-01-10 11:00 | 302 | 302
2017-01-10 11:30 | 304 | 304
2017-01-10 12:00 | 306 | 306
2017-01-10 12:30 | 305 | 305
2017-01-10 13:00 | 311 | 311
2017-01-10 13:30 | 315 | 315
2017-01-10 14:00 | 323 | 323
2017-01-10 14:30 | 334 | 334
2017-01-10 15:00 | 338 | 338
2017-01-10 15:30 | 352 | 350
2017-01-10 16:00 | 358 | 357
2017-01-10 16:30 | 360 | 358
2017-01-10 17:00 | 353 | 352
2017-01-10 17:30 | 346 | 344
2017-01-10 18:00 | 337 | 335
2017-01-10 18:30 | 337 | 335
2017-01-10 19:00 | 335 | 333
2017-01-10 19:30 | 332 | 331
2017-01-10 20:00 | 317 | 317
2017-01-10 20:30 | 305 | 303
2017-01-10 21:00 | 290 | 287
2017-01-10 21:30 | 277 | 274
2017-01-10 22:00 | 264 | 263
2017-01-10 22:30 | 243 | 243
2017-01-10 23:00 | 229 | 228
2017-01-10 23:30 | 215 | 215
2017-01-11 | 203 | 203
2017-01-11 00:30 | 194 | 194
2017-01-11 01:00 | 191 | 190
2017-01-11 01:30 | 191 | 191
2017-01-11 02:00 | 191 | 191
2017-01-11 02:30 | 191 | 191
2017-01-11 03:00 | 188 | 188
2017-01-11 03:30 | 195 | 195
2017-01-11 04:00 | 195 | 195
2017-01-11 04:30 | 198 | 198
2017-01-11 05:00 | 204 | 204
2017-01-11 05:30 | 212 | 212
2017-01-11 06:00 | 225 | 224
2017-01-11 06:30 | 242 | 242
2017-01-11 07:00 | 265 | 265
2017-01-11 07:30 | 280 | 280
2017-01-11 08:00 | 296 | 296
2017-01-11 08:30 | 308 | 307
2017-01-11 09:00 | 316 | 316
2017-01-11 09:30 | 320 | 319
2017-01-11 10:00 | 328 | 327
2017-01-11 10:30 | 327 | 326
2017-01-11 11:00 | 330 | 329
2017-01-11 11:30 | 335 | 335
2017-01-11 12:00 | 338 | 338
2017-01-11 12:30 | 344 | 344
2017-01-11 13:00 | 355 | 355
2017-01-11 13:30 | 371 | 371
2017-01-11 14:00 | 386 | 386
2017-01-11 14:30 | 393 | 393
2017-01-11 15:00 | 400 | 400
2017-01-11 15:30 | 405 | 405
2017-01-11 16:00 | 409 | 409
2017-01-11 16:30 | 411 | 411
2017-01-11 17:00 | 405 | 405
2017-01-11 17:30 | 394 | 393
2017-01-11 18:00 | 370 | 369
2017-01-11 18:30 | 366 | 364
2017-01-11 19:00 | 365 | 363
2017-01-11 19:30 | 359 | 357
2017-01-11 20:00 | 339 | 336
2017-01-11 20:30 | 318 | 314
2017-01-11 21:00 | 302 | 296
2017-01-11 21:30 | 279 | 277
2017-01-11 22:00 | 267 | 265
2017-01-11 22:30 | 273 | 271
2017-01-11 23:00 | 254 | 250
2017-01-11 23:30 | 225 | 222
2017-01-12 | 208 | 208
2017-01-12 00:30 | 204 | 204
2017-01-12 01:00 | 201 | 201
2017-01-12 01:30 | 199 | 198
2017-01-12 02:00 | 200 | 199
2017-01-12 02:30 | 202 | 202
2017-01-12 03:00 | 204 | 203
2017-01-12 03:30 | 205 | 205
2017-01-12 04:00 | 207 | 206
2017-01-12 04:30 | 209 | 209
2017-01-12 05:00 | 213 | 213
2017-01-12 05:30 | 222 | 222
2017-01-12 06:00 | 232 | 232
2017-01-12 06:30 | 247 | 245
2017-01-12 07:00 | 272 | 271
2017-01-12 07:30 | 287 | 286
2017-01-12 08:00 | 308 | 307
2017-01-12 08:30 | 310 | 310
2017-01-12 09:00 | 308 | 308
2017-01-12 09:30 | 310 | 310
2017-01-12 10:00 | 336 | 336
2017-01-12 10:30 | 332 | 331
2017-01-12 11:00 | 340 | 340
2017-01-12 11:30 | 346 | 345
2017-01-12 12:00 | 351 | 351
2017-01-12 12:30 | 363 | 363
2017-01-12 13:00 | 374 | 374
2017-01-12 13:30 | 364 | 364
2017-01-12 14:00 | 357 | 357
2017-01-12 14:30 | 356 | 356
2017-01-12 15:00 | 363 | 363
2017-01-12 15:30 | 374 | 373
2017-01-12 16:00 | 392 | 392
2017-01-12 16:30 | 402 | 402
2017-01-12 17:00 | 399 | 399
2017-01-12 17:30 | 390 | 390
2017-01-12 18:00 | 381 | 381
2017-01-12 18:30 | 387 | 387
2017-01-12 19:00 | 390 | 390
2017-01-12 19:30 | 382 | 382
2017-01-12 20:00 | 365 | 365
2017-01-12 20:30 | 336 | 336
2017-01-12 21:00 | 320 | 320
2017-01-12 21:30 | 304 | 303
2017-01-12 22:00 | 290 | 290
2017-01-12 22:30 | 277 | 277
2017-01-12 23:00 | 250 | 250
2017-01-12 23:30 | 236 | 236
2017-01-13 | 217 | 216
2017-01-13 00:30 | 206 | 206
2017-01-13 01:00 | 201 | 200
2017-01-13 01:30 | 197 | 197
2017-01-13 02:00 | 197 | 196
2017-01-13 02:30 | 199 | 198
2017-01-13 03:00 | 194 | 194
2017-01-13 03:30 | 193 | 193
2017-01-13 04:00 | 196 | 196
2017-01-13 04:30 | 196 | 196
2017-01-13 05:00 | 201 | 201
2017-01-13 05:30 | 207 | 207
2017-01-13 06:00 | 222 | 221
2017-01-13 06:30 | 250 | 250
2017-01-13 07:00 | 295 | 293
2017-01-13 07:30 | 303 | 303
2017-01-13 08:00 | 306 | 306
2017-01-13 08:30 | 313 | 312
2017-01-13 09:00 | 330 | 330
2017-01-13 09:30 | 342 | 342
2017-01-13 10:00 | 339 | 339
2017-01-13 10:30 | 342 | 342
2017-01-13 11:00 | 348 | 348
2017-01-13 11:30 | 350 | 350
2017-01-13 12:00 | 355 | 355
2017-01-13 12:30 | 357 | 357
2017-01-13 13:00 | 371 | 371
2017-01-13 13:30 | 388 | 388
2017-01-13 14:00 | 400 | 400
2017-01-13 14:30 | 418 | 418
2017-01-13 15:00 | 425 | 425
2017-01-13 15:30 | 430 | 430
2017-01-13 16:00 | 438 | 438
2017-01-13 16:30 | 442 | 442
2017-01-13 17:00 | 438 | 437
2017-01-13 17:30 | 427 | 427
2017-01-13 18:00 | 419 | 418
2017-01-13 18:30 | 415 | 414
2017-01-13 19:00 | 415 | 414
2017-01-13 19:30 | 418 | 417
2017-01-13 20:00 | 408 | 406
2017-01-13 20:30 | 391 | 390
2017-01-13 21:00 | 375 | 374
2017-01-13 21:30 | 318 | 317
2017-01-13 22:00 | 298 | 297
2017-01-13 22:30 | 303 | 303
2017-01-13 23:00 | 274 | 274
2017-01-13 23:30 | 253 | 253
2017-01-14 | 221 | 221
2017-01-14 00:30 | 206 | 206
2017-01-14 01:00 | 199 | 198
2017-01-14 01:30 | 214 | 214
2017-01-14 02:00 | 219 | 219
2017-01-14 02:30 | 213 | 213
2017-01-14 03:00 | 212 | 212
2017-01-14 03:30 | 207 | 207
2017-01-14 04:00 | 208 | 208
2017-01-14 04:30 | 206 | 206
2017-01-14 05:00 | 210 | 210
2017-01-14 05:30 | 218 | 218
2017-01-14 06:00 | 226 | 225
2017-01-14 06:30 | 245 | 244
2017-01-14 07:00 | 279 | 279
2017-01-14 07:30 | 281 | 281
2017-01-14 08:00 | 296 | 296
2017-01-14 08:30 | 294 | 294
2017-01-14 09:00 | 307 | 307
2017-01-14 09:30 | 314 | 313
2017-01-14 10:00 | 335 | 334
2017-01-14 10:30 | 342 | 342
2017-01-14 11:00 | 347 | 347
2017-01-14 11:30 | 360 | 360
2017-01-14 12:00 | 372 | 372
2017-01-14 12:30 | 374 | 374
2017-01-14 13:00 | 374 | 373
2017-01-14 13:30 | 372 | 372
2017-01-14 14:00 | 378 | 378
2017-01-14 14:30 | 388 | 388
2017-01-14 15:00 | 394 | 394
2017-01-14 15:30 | 401 | 401
2017-01-14 16:00 | 407 | 407
2017-01-14 16:30 | 414 | 414
2017-01-14 17:00 | 414 | 414
2017-01-14 17:30 | 427 | 427
2017-01-14 18:00 | 426 | 426
2017-01-14 18:30 | 426 | 425
2017-01-14 19:00 | 426 | 426
2017-01-14 19:30 | 402 | 401
2017-01-14 20:00 | 405 | 405
2017-01-14 20:30 | 390 | 389
2017-01-14 21:00 | 347 | 346
2017-01-14 21:30 | 332 | 332
2017-01-14 22:00 | 309 | 309
2017-01-14 22:30 | 303 | 303
2017-01-14 23:00 | 272 | 272
2017-01-14 23:30 | 252 | 252
2017-01-15 | 235 | 234
2017-01-15 00:30 | 215 | 214
2017-01-15 01:00 | 220 | 219
2017-01-15 01:30 | 216 | 214
2017-01-15 02:00 | 218 | 216
2017-01-15 02:30 | 218 | 216
2017-01-15 03:00 | 218 | 216
2017-01-15 03:30 | 218 | 216
2017-01-15 04:00 | 211 | 209
2017-01-15 04:30 | 208 | 205
2017-01-15 05:00 | 206 | 203
2017-01-15 05:30 | 205 | 202
2017-01-15 06:00 | 211 | 208
2017-01-15 06:30 | 214 | 211
2017-01-15 07:00 | 229 | 227
2017-01-15 07:30 | 237 | 235
2017-01-15 08:00 | 245 | 244
2017-01-15 08:30 | 252 | 251
2017-01-15 09:00 | 265 | 265
2017-01-15 09:30 | 271 | 269
2017-01-15 10:00 | 264 | 263
2017-01-15 10:30 | 267 | 266
2017-01-15 11:00 | 271 | 271
2017-01-15 11:30 | 279 | 279
2017-01-15 12:00 | 303 | 303
2017-01-15 12:30 | 302 | 302
2017-01-15 13:00 | 296 | 296
2017-01-15 13:30 | 290 | 290
2017-01-15 14:00 | 301 | 301
2017-01-15 14:30 | 307 | 307
2017-01-15 15:00 | 334 | 333
2017-01-15 15:30 | 331 | 331
2017-01-15 16:00 | 322 | 322
2017-01-15 16:30 | 324 | 324
2017-01-15 17:00 | 327 | 327
2017-01-15 17:30 | 329 | 329
2017-01-15 18:00 | 322 | 321
2017-01-15 18:30 | 321 | 321
2017-01-15 19:00 | 318 | 318
2017-01-15 19:30 | 307 | 307
2017-01-15 20:00 | 304 | 303
2017-01-15 20:30 | 292 | 292
2017-01-15 21:00 | 281 | 281
2017-01-15 21:30 | 275 | 275
2017-01-15 22:00 | 265 | 265
2017-01-15 22:30 | 255 | 254
2017-01-15 23:00 | 230 | 229
2017-01-15 23:30 | 218 | 218
2017-01-16 | 207 | 207
2017-01-16 00:30 | 200 | 200
2017-01-16 01:00 | 192 | 191
2017-01-16 01:30 | 186 | 186
2017-01-16 02:00 | 182 | 181
2017-01-16 02:30 | 179 | 178
2017-01-16 03:00 | 177 | 176
2017-01-16 03:30 | 179 | 178
2017-01-16 04:00 | 182 | 182
2017-01-16 04:30 | 184 | 184
2017-01-16 05:00 | 190 | 189
2017-01-16 05:30 | 194 | 194
2017-01-16 06:00 | 216 | 216
2017-01-16 06:30 | 231 | 231
2017-01-16 07:00 | 256 | 256
2017-01-16 07:30 | 274 | 274
2017-01-16 08:00 | 287 | 287
2017-01-16 08:30 | 292 | 292
2017-01-16 09:00 | 299 | 299
2017-01-16 09:30 | 300 | 299
2017-01-16 10:00 | 308 | 308
2017-01-16 10:30 | 312 | 312
2017-01-16 11:00 | 315 | 315
2017-01-16 11:30 | 318 | 318
2017-01-16 12:00 | 323 | 323
2017-01-16 12:30 | 328 | 327
2017-01-16 13:00 | 331 | 331
2017-01-16 13:30 | 339 | 339
2017-01-16 14:00 | 348 | 348
2017-01-16 14:30 | 356 | 356
2017-01-16 15:00 | 364 | 364
2017-01-16 15:30 | 370 | 370
2017-01-16 16:00 | 375 | 375
2017-01-16 16:30 | 380 | 380
2017-01-16 17:00 | 378 | 378
2017-01-16 17:30 | 370 | 370
2017-01-16 18:00 | 364 | 364
2017-01-16 18:30 | 363 | 363
2017-01-16 19:00 | 362 | 362
2017-01-16 19:30 | 360 | 360
2017-01-16 20:00 | 349 | 349
2017-01-16 20:30 | 332 | 332
2017-01-16 21:00 | 313 | 313
2017-01-16 21:30 | 293 | 292
2017-01-16 22:00 | 281 | 280
2017-01-16 22:30 | 268 | 268
2017-01-16 23:00 | 245 | 244
2017-01-16 23:30 | 227 | 227
2017-01-17 | 211 | 211
2017-01-17 00:30 | 197 | 196
2017-01-17 01:00 | 191 | 189
2017-01-17 01:30 | 189 | 187
2017-01-17 02:00 | 190 | 189
2017-01-17 02:30 | 190 | 189
2017-01-17 03:00 | 193 | 192
2017-01-17 03:30 | 195 | 193
2017-01-17 04:00 | 196 | 194
2017-01-17 04:30 | 190 | 188
2017-01-17 05:00 | 209 | 207
2017-01-17 05:30 | 217 | 215
2017-01-17 06:00 | 229 | 229
2017-01-17 06:30 | 244 | 244
2017-01-17 07:00 | 273 | 273
2017-01-17 07:30 | 290 | 290
2017-01-17 08:00 | 302 | 302
2017-01-17 08:30 | 308 | 308
2017-01-17 09:00 | 307 | 307
2017-01-17 09:30 | 317 | 317
2017-01-17 10:00 | 325 | 325
2017-01-17 10:30 | 328 | 328
2017-01-17 11:00 | 330 | 330
2017-01-17 11:30 | 330 | 330
2017-01-17 12:00 | 337 | 337
2017-01-17 12:30 | 347 | 347
2017-01-17 13:00 | 356 | 356
2017-01-17 13:30 | 376 | 376
2017-01-17 14:00 | 384 | 384
2017-01-17 14:30 | 379 | 379
2017-01-17 15:00 | 387 | 387
2017-01-17 15:30 | 393 | 393
2017-01-17 16:00 | 402 | 402
2017-01-17 16:30 | 409 | 409
2017-01-17 17:00 | 408 | 408
2017-01-17 17:30 | 400 | 399
2017-01-17 18:00 | 388 | 388
2017-01-17 18:30 | 385 | 384
2017-01-17 19:00 | 375 | 375
2017-01-17 19:30 | 378 | 378
2017-01-17 20:00 | 367 | 367
2017-01-17 20:30 | 350 | 349
2017-01-17 21:00 | 330 | 329
2017-01-17 21:30 | 306 | 305
2017-01-17 22:00 | 288 | 287
2017-01-17 22:30 | 272 | 270
2017-01-17 23:00 | 248 | 247
2017-01-17 23:30 | 233 | 232
2017-01-18 | 217 | 216
2017-01-18 00:30 | 205 | 204
2017-01-18 01:00 | 202 | 202
2017-01-18 01:30 | 202 | 201
2017-01-18 02:00 | 201 | 200
2017-01-18 02:30 | 202 | 202
2017-01-18 03:00 | 205 | 205
2017-01-18 03:30 | 207 | 206
2017-01-18 04:00 | 207 | 207
2017-01-18 04:30 | 210 | 209
2017-01-18 05:00 | 218 | 217
2017-01-18 05:30 | 227 | 227
2017-01-18 06:00 | 240 | 239
2017-01-18 06:30 | 252 | 251
2017-01-18 07:00 | 283 | 283
2017-01-18 07:30 | 306 | 306
2017-01-18 08:00 | 315 | 315
2017-01-18 08:30 | 325 | 325
2017-01-18 09:00 | 332 | 332
2017-01-18 09:30 | 336 | 336
2017-01-18 10:00 | 348 | 348
2017-01-18 10:30 | 352 | 352
2017-01-18 11:00 | 362 | 362
2017-01-18 11:30 | 371 | 371
2017-01-18 12:00 | 380 | 380
2017-01-18 12:30 | 391 | 391
2017-01-18 13:00 | 402 | 402
2017-01-18 13:30 | 415 | 415
2017-01-18 14:00 | 429 | 429
2017-01-18 14:30 | 447 | 447
2017-01-18 15:00 | 461 | 461
2017-01-18 15:30 | 473 | 473
2017-01-18 16:00 | 483 | 483
2017-01-18 16:30 | 493 | 493
2017-01-18 17:00 | 497 | 497
2017-01-18 17:30 | 494 | 493
2017-01-18 18:00 | 480 | 479
2017-01-18 18:30 | 474 | 473
2017-01-18 19:00 | 467 | 466
2017-01-18 19:30 | 458 | 457
2017-01-18 20:00 | 440 | 439
2017-01-18 20:30 | 408 | 406
2017-01-18 21:00 | 360 | 360
2017-01-18 21:30 | 352 | 352
2017-01-18 22:00 | 348 | 348
2017-01-18 22:30 | 332 | 332
2017-01-18 23:00 | 303 | 303
2017-01-18 23:30 | 279 | 278
2017-01-19 | 262 | 262
2017-01-19 00:30 | 253 | 253
2017-01-19 01:00 | 247 | 247
2017-01-19 01:30 | 243 | 242
2017-01-19 02:00 | 211 | 211
2017-01-19 02:30 | 208 | 208
2017-01-19 03:00 | 209 | 209
2017-01-19 03:30 | 210 | 210
2017-01-19 04:00 | 209 | 209
2017-01-19 04:30 | 212 | 211
2017-01-19 05:00 | 220 | 219
2017-01-19 05:30 | 233 | 233
2017-01-19 06:00 | 250 | 250
2017-01-19 06:30 | 266 | 266
2017-01-19 07:00 | 289 | 289
2017-01-19 07:30 | 296 | 296
2017-01-19 08:00 | 307 | 306
2017-01-19 08:30 | 310 | 309
2017-01-19 09:00 | 311 | 310
2017-01-19 09:30 | 328 | 327
2017-01-19 10:00 | 333 | 333
2017-01-19 10:30 | 328 | 328
2017-01-19 11:00 | 347 | 347
2017-01-19 11:30 | 340 | 340
2017-01-19 12:00 | 333 | 333
2017-01-19 12:30 | 322 | 321
2017-01-19 13:00 | 316 | 316
2017-01-19 13:30 | 323 | 322
2017-01-19 14:00 | 324 | 324
2017-01-19 14:30 | 326 | 326
2017-01-19 15:00 | 329 | 329
2017-01-19 15:30 | 329 | 329
2017-01-19 16:00 | 329 | 329
2017-01-19 16:30 | 327 | 326
2017-01-19 17:00 | 326 | 326
2017-01-19 17:30 | 327 | 327
2017-01-19 18:00 | 322 | 322
2017-01-19 18:30 | 316 | 316
2017-01-19 19:00 | 316 | 316
2017-01-19 19:30 | 314 | 314
2017-01-19 20:00 | 305 | 304
2017-01-19 20:30 | 291 | 291
2017-01-19 21:00 | 277 | 277
2017-01-19 21:30 | 270 | 267
2017-01-19 22:00 | 265 | 262
2017-01-19 22:30 | 252 | 249
2017-01-19 23:00 | 234 | 232
2017-01-19 23:30 | 224 | 222
2017-01-20 | 209 | 208
2017-01-20 00:30 | 196 | 195
2017-01-20 01:00 | 191 | 191
2017-01-20 01:30 | 189 | 188
2017-01-20 02:00 | 189 | 188
2017-01-20 02:30 | 191 | 190
2017-01-20 03:00 | 193 | 193
2017-01-20 03:30 | 192 | 192
2017-01-20 04:00 | 194 | 193
2017-01-20 04:30 | 197 | 197
2017-01-20 05:00 | 197 | 197
2017-01-20 05:30 | 208 | 208
2017-01-20 06:00 | 218 | 218
2017-01-20 06:30 | 242 | 242
2017-01-20 07:00 | 264 | 263
2017-01-20 07:30 | 271 | 271
2017-01-20 08:00 | 286 | 284
2017-01-20 08:30 | 283 | 281
2017-01-20 09:00 | 276 | 273
2017-01-20 09:30 | 295 | 295
2017-01-20 10:00 | 297 | 297
2017-01-20 10:30 | 298 | 298
2017-01-20 11:00 | 318 | 318
2017-01-20 11:30 | 323 | 323
2017-01-20 12:00 | 315 | 315
2017-01-20 12:30 | 315 | 315
2017-01-20 13:00 | 323 | 323
2017-01-20 13:30 | 328 | 328
2017-01-20 14:00 | 345 | 345
2017-01-20 14:30 | 359 | 359
2017-01-20 15:00 | 380 | 380
2017-01-20 15:30 | 406 | 406
2017-01-20 16:00 | 418 | 418
2017-01-20 16:30 | 427 | 426
2017-01-20 17:00 | 425 | 425
2017-01-20 17:30 | 415 | 414
2017-01-20 18:00 | 406 | 404
2017-01-20 18:30 | 408 | 406
2017-01-20 19:00 | 407 | 406
2017-01-20 19:30 | 407 | 406
2017-01-20 20:00 | 397 | 397
2017-01-20 20:30 | 377 | 376
2017-01-20 21:00 | 361 | 358
2017-01-20 21:30 | 342 | 340
2017-01-20 22:00 | 334 | 333
2017-01-20 22:30 | 327 | 325
2017-01-20 23:00 | 299 | 298
2017-01-20 23:30 | 264 | 263
2017-01-21 | 233 | 233
2017-01-21 00:30 | 220 | 219
2017-01-21 01:00 | 208 | 208
2017-01-21 01:30 | 210 | 209
2017-01-21 02:00 | 210 | 210
2017-01-21 02:30 | 209 | 208
2017-01-21 03:00 | 210 | 210
2017-01-21 03:30 | 212 | 212
2017-01-21 04:00 | 211 | 211
2017-01-21 04:30 | 212 | 212
2017-01-21 05:00 | 213 | 213
2017-01-21 05:30 | 221 | 221
2017-01-21 06:00 | 226 | 226
2017-01-21 06:30 | 237 | 236
2017-01-21 07:00 | 254 | 254
2017-01-21 07:30 | 264 | 264
2017-01-21 08:00 | 281 | 281
2017-01-21 08:30 | 301 | 300
2017-01-21 09:00 | 301 | 301
2017-01-21 09:30 | 307 | 307
2017-01-21 10:00 | 312 | 312
2017-01-21 10:30 | 311 | 311
2017-01-21 11:00 | 310 | 310
2017-01-21 11:30 | 305 | 304
2017-01-21 12:00 | 291 | 291
2017-01-21 12:30 | 282 | 281
2017-01-21 13:00 | 275 | 275
2017-01-21 13:30 | 279 | 279
2017-01-21 14:00 | 268 | 268
2017-01-21 14:30 | 273 | 273
2017-01-21 15:00 | 277 | 277
2017-01-21 15:30 | 281 | 281
2017-01-21 16:00 | 280 | 280
2017-01-21 16:30 | 283 | 283
2017-01-21 17:00 | 278 | 278
2017-01-21 17:30 | 274 | 274
2017-01-21 18:00 | 273 | 272
2017-01-21 18:30 | 275 | 274
2017-01-21 19:00 | 270 | 269
2017-01-21 19:30 | 268 | 267
2017-01-21 20:00 | 263 | 263
2017-01-21 20:30 | 248 | 248
2017-01-21 21:00 | 246 | 246
2017-01-21 21:30 | 244 | 244
2017-01-21 22:00 | 238 | 238
2017-01-21 22:30 | 236 | 236
2017-01-21 23:00 | 219 | 219
2017-01-21 23:30 | 209 | 208
2017-01-22 | 196 | 196
2017-01-22 00:30 | 187 | 187
2017-01-22 01:00 | 183 | 183
2017-01-22 01:30 | 184 | 183
2017-01-22 02:00 | 183 | 182
2017-01-22 02:30 | 183 | 183
2017-01-22 03:00 | 185 | 184
2017-01-22 03:30 | 185 | 184
2017-01-22 04:00 | 184 | 183
2017-01-22 04:30 | 183 | 183
2017-01-22 05:00 | 186 | 185
2017-01-22 05:30 | 191 | 190
2017-01-22 06:00 | 196 | 196
2017-01-22 06:30 | 200 | 199
2017-01-22 07:00 | 212 | 212
2017-01-22 07:30 | 222 | 222
2017-01-22 08:00 | 229 | 229
2017-01-22 08:30 | 226 | 226
2017-01-22 09:00 | 237 | 237
2017-01-22 09:30 | 240 | 240
2017-01-22 10:00 | 240 | 239
2017-01-22 10:30 | 236 | 236
2017-01-22 11:00 | 235 | 235
2017-01-22 11:30 | 227 | 226
2017-01-22 12:00 | 223 | 222
2017-01-22 12:30 | 224 | 223
2017-01-22 13:00 | 229 | 229
2017-01-22 13:30 | 233 | 232
2017-01-22 14:00 | 237 | 237
2017-01-22 14:30 | 243 | 243
2017-01-22 15:00 | 249 | 249
2017-01-22 15:30 | 258 | 257
2017-01-22 16:00 | 262 | 262
2017-01-22 16:30 | 270 | 270
2017-01-22 17:00 | 270 | 270
2017-01-22 17:30 | 274 | 274
2017-01-22 18:00 | 274 | 273
2017-01-22 18:30 | 270 | 270
2017-01-22 19:00 | 277 | 277
2017-01-22 19:30 | 272 | 272
2017-01-22 20:00 | 267 | 267
2017-01-22 20:30 | 263 | 263
2017-01-22 21:00 | 257 | 256
2017-01-22 21:30 | 250 | 249
2017-01-22 22:00 | 239 | 239
2017-01-22 22:30 | 234 | 233
2017-01-22 23:00 | 219 | 219
2017-01-22 23:30 | 207 | 206
2017-01-23 | 200 | 199
2017-01-23 00:30 | 193 | 191
2017-01-23 01:00 | 185 | 183
2017-01-23 01:30 | 178 | 178
2017-01-23 02:00 | 176 | 175
2017-01-23 02:30 | 177 | 176
2017-01-23 03:00 | 177 | 177
2017-01-23 03:30 | 178 | 178
2017-01-23 04:00 | 182 | 182
2017-01-23 04:30 | 188 | 187
2017-01-23 05:00 | 187 | 187
2017-01-23 05:30 | 201 | 201
2017-01-23 06:00 | 217 | 217
2017-01-23 06:30 | 231 | 231
2017-01-23 07:00 | 253 | 253
2017-01-23 07:30 | 266 | 266
2017-01-23 08:00 | 278 | 277
2017-01-23 08:30 | 283 | 282
2017-01-23 09:00 | 284 | 284
2017-01-23 09:30 | 282 | 282
2017-01-23 10:00 | 279 | 278
2017-01-23 10:30 | 273 | 272
2017-01-23 11:00 | 268 | 268
2017-01-23 11:30 | 267 | 267
2017-01-23 12:00 | 264 | 263
2017-01-23 12:30 | 264 | 264
2017-01-23 13:00 | 269 | 268
2017-01-23 13:30 | 274 | 274
2017-01-23 14:00 | 281 | 281
2017-01-23 14:30 | 286 | 286
2017-01-23 15:00 | 296 | 296
2017-01-23 15:30 | 312 | 310
2017-01-23 16:00 | 319 | 316
2017-01-23 16:30 | 327 | 324
2017-01-23 17:00 | 328 | 325
2017-01-23 17:30 | 323 | 321
2017-01-23 18:00 | 317 | 314
2017-01-23 18:30 | 318 | 316
2017-01-23 19:00 | 315 | 315
2017-01-23 19:30 | 312 | 312
2017-01-23 20:00 | 301 | 301
2017-01-23 20:30 | 284 | 283
2017-01-23 21:00 | 268 | 267
2017-01-23 21:30 | 250 | 248
2017-01-23 22:00 | 243 | 242
2017-01-23 22:30 | 239 | 238
2017-01-23 23:00 | 216 | 216
2017-01-23 23:30 | 195 | 195
2017-01-24 | 180 | 180
2017-01-24 00:30 | 171 | 170
2017-01-24 01:00 | 163 | 162
2017-01-24 01:30 | 158 | 158
2017-01-24 02:00 | 156 | 156
2017-01-24 02:30 | 154 | 153
2017-01-24 03:00 | 153 | 152
2017-01-24 03:30 | 154 | 153
2017-01-24 04:00 | 158 | 157
2017-01-24 04:30 | 163 | 162
2017-01-24 05:00 | 171 | 171
2017-01-24 05:30 | 182 | 182
2017-01-24 06:00 | 202 | 202
2017-01-24 06:30 | 222 | 222
2017-01-24 07:00 | 244 | 244
2017-01-24 07:30 | 252 | 251
2017-01-24 08:00 | 257 | 257
2017-01-24 08:30 | 260 | 260
2017-01-24 09:00 | 266 | 265
2017-01-24 09:30 | 267 | 267
2017-01-24 10:00 | 269 | 269
2017-01-24 10:30 | 272 | 271
2017-01-24 11:00 | 275 | 275
2017-01-24 11:30 | 281 | 281
2017-01-24 12:00 | 289 | 289
2017-01-24 12:30 | 297 | 297
2017-01-24 13:00 | 305 | 305
2017-01-24 13:30 | 314 | 314
2017-01-24 14:00 | 320 | 320
2017-01-24 14:30 | 326 | 326
2017-01-24 15:00 | 333 | 333
2017-01-24 15:30 | 349 | 347
2017-01-24 16:00 | 365 | 363
2017-01-24 16:30 | 378 | 376
2017-01-24 17:00 | 381 | 379
2017-01-24 17:30 | 376 | 373
2017-01-24 18:00 | 366 | 363
2017-01-24 18:30 | 366 | 363
2017-01-24 19:00 | 357 | 355
2017-01-24 19:30 | 341 | 338
2017-01-24 20:00 | 315 | 313
2017-01-24 20:30 | 295 | 294
2017-01-24 21:00 | 277 | 276
2017-01-24 21:30 | 264 | 262
2017-01-24 22:00 | 257 | 257
2017-01-24 22:30 | 250 | 249
2017-01-24 23:00 | 228 | 228
2017-01-24 23:30 | 218 | 218
2017-01-25 | 202 | 202
2017-01-25 00:30 | 194 | 193
2017-01-25 01:00 | 188 | 187
2017-01-25 01:30 | 186 | 185
2017-01-25 02:00 | 186 | 185
2017-01-25 02:30 | 186 | 185
2017-01-25 03:00 | 186 | 186
2017-01-25 03:30 | 188 | 188
2017-01-25 04:00 | 189 | 189
2017-01-25 04:30 | 192 | 192
2017-01-25 05:00 | 198 | 198
2017-01-25 05:30 | 209 | 209
2017-01-25 06:00 | 221 | 221
2017-01-25 06:30 | 246 | 246
2017-01-25 07:00 | 268 | 268
2017-01-25 07:30 | 277 | 277
2017-01-25 08:00 | 287 | 287
2017-01-25 08:30 | 293 | 293
2017-01-25 09:00 | 301 | 300
2017-01-25 09:30 | 309 | 307
2017-01-25 10:00 | 314 | 312
2017-01-25 10:30 | 318 | 316
2017-01-25 11:00 | 320 | 319
2017-01-25 11:30 | 325 | 324
2017-01-25 12:00 | 329 | 327
2017-01-25 12:30 | 331 | 330
2017-01-25 13:00 | 333 | 331
2017-01-25 13:30 | 333 | 331
2017-01-25 14:00 | 340 | 339
2017-01-25 14:30 | 352 | 351
2017-01-25 15:00 | 369 | 367
2017-01-25 15:30 | 378 | 377
2017-01-25 16:00 | 384 | 383
2017-01-25 16:30 | 389 | 388
2017-01-25 17:00 | 386 | 384
2017-01-25 17:30 | 379 | 376
2017-01-25 18:00 | 368 | 365
2017-01-25 18:30 | 368 | 365
2017-01-25 19:00 | 351 | 349
2017-01-25 19:30 | 334 | 331
2017-01-25 20:00 | 322 | 320
2017-01-25 20:30 | 304 | 303
2017-01-25 21:00 | 290 | 290
2017-01-25 21:30 | 275 | 274
2017-01-25 22:00 | 275 | 273
2017-01-25 22:30 | 263 | 261
2017-01-25 23:00 | 241 | 240
2017-01-25 23:30 | 224 | 224
2017-01-26 | 212 | 211
2017-01-26 00:30 | 199 | 197
2017-01-26 01:00 | 189 | 189
2017-01-26 01:30 | 186 | 186
2017-01-26 02:00 | 185 | 185
2017-01-26 02:30 | 183 | 183
2017-01-26 03:00 | 185 | 185
2017-01-26 03:30 | 180 | 180
2017-01-26 04:00 | 188 | 188
2017-01-26 04:30 | 192 | 192
2017-01-26 05:00 | 194 | 194
2017-01-26 05:30 | 198 | 198
2017-01-26 06:00 | 200 | 200
2017-01-26 06:30 | 203 | 203
2017-01-26 07:00 | 219 | 219
2017-01-26 07:30 | 230 | 230
2017-01-26 08:00 | 238 | 238
2017-01-26 08:30 | 235 | 235
2017-01-26 09:00 | 242 | 242
2017-01-26 09:30 | 259 | 259
2017-01-26 10:00 | 264 | 264
2017-01-26 10:30 | 267 | 266
2017-01-26 11:00 | 258 | 258
2017-01-26 11:30 | 261 | 261
2017-01-26 12:00 | 255 | 255
2017-01-26 12:30 | 262 | 261
2017-01-26 13:00 | 255 | 255
2017-01-26 13:30 | 262 | 261
2017-01-26 14:00 | 270 | 270
2017-01-26 14:30 | 278 | 278
2017-01-26 15:00 | 288 | 288
2017-01-26 15:30 | 298 | 298
2017-01-26 16:00 | 307 | 307
2017-01-26 16:30 | 323 | 322
2017-01-26 17:00 | 321 | 320
2017-01-26 17:30 | 320 | 318
2017-01-26 18:00 | 329 | 326
2017-01-26 18:30 | 331 | 330
2017-01-26 19:00 | 324 | 324
2017-01-26 19:30 | 321 | 320
2017-01-26 20:00 | 313 | 312
2017-01-26 20:30 | 299 | 298
2017-01-26 21:00 | 281 | 278
2017-01-26 21:30 | 259 | 258
2017-01-26 22:00 | 263 | 262
2017-01-26 22:30 | 251 | 249
2017-01-26 23:00 | 225 | 225
2017-01-26 23:30 | 212 | 212
2017-01-27 | 194 | 193
2017-01-27 00:30 | 190 | 189
2017-01-27 01:00 | 183 | 182
2017-01-27 01:30 | 182 | 181
2017-01-27 02:00 | 181 | 181
2017-01-27 02:30 | 181 | 181
2017-01-27 03:00 | 183 | 182
2017-01-27 03:30 | 176 | 176
2017-01-27 04:00 | 184 | 184
2017-01-27 04:30 | 188 | 188
2017-01-27 05:00 | 189 | 189
2017-01-27 05:30 | 194 | 194
2017-01-27 06:00 | 210 | 210
2017-01-27 06:30 | 234 | 234
2017-01-27 07:00 | 250 | 250
2017-01-27 07:30 | 254 | 253
2017-01-27 08:00 | 266 | 265
2017-01-27 08:30 | 281 | 281
2017-01-27 09:00 | 294 | 294
2017-01-27 09:30 | 300 | 300
2017-01-27 10:00 | 310 | 310
2017-01-27 10:30 | 336 | 335
2017-01-27 11:00 | 333 | 332
2017-01-27 11:30 | 327 | 326
2017-01-27 12:00 | 327 | 326
2017-01-27 12:30 | 326 | 325
2017-01-27 13:00 | 327 | 326
2017-01-27 13:30 | 325 | 324
2017-01-27 14:00 | 326 | 325
2017-01-27 14:30 | 320 | 318
2017-01-27 15:00 | 329 | 327
2017-01-27 15:30 | 335 | 333
2017-01-27 16:00 | 337 | 335
2017-01-27 16:30 | 340 | 337
2017-01-27 17:00 | 327 | 325
2017-01-27 17:30 | 320 | 318
2017-01-27 18:00 | 311 | 308
2017-01-27 18:30 | 310 | 307
2017-01-27 19:00 | 309 | 306
2017-01-27 19:30 | 308 | 304
2017-01-27 20:00 | 293 | 292
2017-01-27 20:30 | 280 | 280
2017-01-27 21:00 | 270 | 270
2017-01-27 21:30 | 264 | 263
2017-01-27 22:00 | 257 | 256
2017-01-27 22:30 | 252 | 251
2017-01-27 23:00 | 231 | 231
2017-01-27 23:30 | 218 | 216
2017-01-28 | 202 | 201
2017-01-28 00:30 | 189 | 189
2017-01-28 01:00 | 181 | 181
2017-01-28 01:30 | 179 | 178
2017-01-28 02:00 | 180 | 180
2017-01-28 02:30 | 180 | 180
2017-01-28 03:00 | 180 | 180
2017-01-28 03:30 | 180 | 180
2017-01-28 04:00 | 179 | 179
2017-01-28 04:30 | 180 | 180
2017-01-28 05:00 | 182 | 182
2017-01-28 05:30 | 189 | 188
2017-01-28 06:00 | 197 | 197
2017-01-28 06:30 | 200 | 200
2017-01-28 07:00 | 211 | 210
2017-01-28 07:30 | 223 | 223
2017-01-28 08:00 | 241 | 241
2017-01-28 08:30 | 254 | 254
2017-01-28 09:00 | 257 | 257
2017-01-28 09:30 | 260 | 260
2017-01-28 10:00 | 261 | 261
2017-01-28 10:30 | 268 | 268
2017-01-28 11:00 | 269 | 269
2017-01-28 11:30 | 271 | 270
2017-01-28 12:00 | 273 | 273
2017-01-28 12:30 | 278 | 277
2017-01-28 13:00 | 284 | 284
2017-01-28 13:30 | 289 | 289
2017-01-28 14:00 | 296 | 296
2017-01-28 14:30 | 301 | 301
2017-01-28 15:00 | 307 | 307
2017-01-28 15:30 | 311 | 311
2017-01-28 16:00 | 314 | 314
2017-01-28 16:30 | 324 | 324
2017-01-28 17:00 | 327 | 327
2017-01-28 17:30 | 326 | 325
2017-01-28 18:00 | 316 | 316
2017-01-28 18:30 | 317 | 316
2017-01-28 19:00 | 320 | 320
2017-01-28 19:30 | 317 | 316
2017-01-28 20:00 | 306 | 305
2017-01-28 20:30 | 293 | 291
2017-01-28 21:00 | 277 | 275
2017-01-28 21:30 | 266 | 264
2017-01-28 22:00 | 258 | 257
2017-01-28 22:30 | 249 | 249
2017-01-28 23:00 | 237 | 237
2017-01-28 23:30 | 222 | 222
2017-01-29 | 207 | 207
2017-01-29 00:30 | 195 | 195
2017-01-29 01:00 | 189 | 189
2017-01-29 01:30 | 186 | 186
2017-01-29 02:00 | 184 | 184
2017-01-29 02:30 | 187 | 186
2017-01-29 03:00 | 187 | 187
2017-01-29 03:30 | 183 | 182
2017-01-29 04:00 | 185 | 185
2017-01-29 04:30 | 184 | 184
2017-01-29 05:00 | 185 | 185
2017-01-29 05:30 | 187 | 187
2017-01-29 06:00 | 192 | 191
2017-01-29 06:30 | 195 | 195
2017-01-29 07:00 | 207 | 207
2017-01-29 07:30 | 217 | 217
2017-01-29 08:00 | 229 | 229
2017-01-29 08:30 | 237 | 237
2017-01-29 09:00 | 247 | 247
2017-01-29 09:30 | 255 | 255
2017-01-29 10:00 | 254 | 254
2017-01-29 10:30 | 249 | 249
2017-01-29 11:00 | 260 | 259
2017-01-29 11:30 | 275 | 275
2017-01-29 12:00 | 283 | 283
2017-01-29 12:30 | 290 | 290
2017-01-29 13:00 | 294 | 294
2017-01-29 13:30 | 295 | 295
2017-01-29 14:00 | 301 | 301
2017-01-29 14:30 | 305 | 305
2017-01-29 15:00 | 310 | 310
2017-01-29 15:30 | 320 | 319
2017-01-29 16:00 | 338 | 337
2017-01-29 16:30 | 337 | 337
2017-01-29 17:00 | 337 | 336
2017-01-29 17:30 | 340 | 339
2017-01-29 18:00 | 339 | 338
2017-01-29 18:30 | 341 | 340
2017-01-29 19:00 | 342 | 341
2017-01-29 19:30 | 334 | 332
2017-01-29 20:00 | 321 | 320
2017-01-29 20:30 | 301 | 301
2017-01-29 21:00 | 290 | 290
2017-01-29 21:30 | 280 | 279
2017-01-29 22:00 | 276 | 274
2017-01-29 22:30 | 267 | 265
2017-01-29 23:00 | 244 | 243
2017-01-29 23:30 | 221 | 221
2017-01-30 | 207 | 207
2017-01-30 00:30 | 198 | 198
2017-01-30 01:00 | 187 | 187
2017-01-30 01:30 | 181 | 181
2017-01-30 02:00 | 180 | 180
2017-01-30 02:30 | 178 | 178
2017-01-30 03:00 | 178 | 178
2017-01-30 03:30 | 181 | 181
2017-01-30 04:00 | 181 | 181
2017-01-30 04:30 | 185 | 185
2017-01-30 05:00 | 197 | 197
2017-01-30 05:30 | 211 | 211
2017-01-30 06:00 | 230 | 230
2017-01-30 06:30 | 246 | 246
2017-01-30 07:00 | 273 | 273
2017-01-30 07:30 | 287 | 286
2017-01-30 08:00 | 297 | 297
2017-01-30 08:30 | 305 | 304
2017-01-30 09:00 | 313 | 312
2017-01-30 09:30 | 316 | 313
2017-01-30 10:00 | 319 | 316
2017-01-30 10:30 | 321 | 319
2017-01-30 11:00 | 329 | 326
2017-01-30 11:30 | 331 | 329
2017-01-30 12:00 | 330 | 328
2017-01-30 12:30 | 334 | 332
2017-01-30 13:00 | 339 | 337
2017-01-30 13:30 | 342 | 341
2017-01-30 14:00 | 350 | 349
2017-01-30 14:30 | 358 | 356
2017-01-30 15:00 | 364 | 363
2017-01-30 15:30 | 376 | 374
2017-01-30 16:00 | 387 | 386
2017-01-30 16:30 | 396 | 395
2017-01-30 17:00 | 402 | 400
2017-01-30 17:30 | 391 | 388
2017-01-30 18:00 | 380 | 377
2017-01-30 18:30 | 374 | 372
2017-01-30 19:00 | 364 | 362
2017-01-30 19:30 | 359 | 357
2017-01-30 20:00 | 343 | 341
2017-01-30 20:30 | 327 | 325
2017-01-30 21:00 | 309 | 308
2017-01-30 21:30 | 295 | 295
2017-01-30 22:00 | 279 | 278
2017-01-30 22:30 | 266 | 266
2017-01-30 23:00 | 240 | 240
2017-01-30 23:30 | 222 | 222
2017-01-31 | 207 | 207
2017-01-31 00:30 | 195 | 195
2017-01-31 01:00 | 188 | 188
2017-01-31 01:30 | 185 | 185
2017-01-31 02:00 | 184 | 184
2017-01-31 02:30 | 184 | 184
2017-01-31 03:00 | 184 | 184
2017-01-31 03:30 | 183 | 183
2017-01-31 04:00 | 187 | 187
2017-01-31 04:30 | 191 | 191
2017-01-31 05:00 | 196 | 196
2017-01-31 05:30 | 206 | 205
2017-01-31 06:00 | 226 | 226
2017-01-31 06:30 | 245 | 245
2017-01-31 07:00 | 265 | 265
2017-01-31 07:30 | 282 | 282
2017-01-31 08:00 | 294 | 294
2017-01-31 08:30 | 299 | 299
2017-01-31 09:00 | 306 | 306
2017-01-31 09:30 | 308 | 308
2017-01-31 10:00 | 309 | 309
2017-01-31 10:30 | 316 | 316
2017-01-31 11:00 | 317 | 317
2017-01-31 11:30 | 319 | 319
2017-01-31 12:00 | 326 | 325
2017-01-31 12:30 | 327 | 327
2017-01-31 13:00 | 341 | 340
2017-01-31 13:30 | 350 | 350
2017-01-31 14:00 | 367 | 367
2017-01-31 14:30 | 376 | 376
2017-01-31 15:00 | 383 | 383
2017-01-31 15:30 | 394 | 394
2017-01-31 16:00 | 408 | 408
2017-01-31 16:30 | 415 | 414
2017-01-31 17:00 | 413 | 412
2017-01-31 17:30 | 407 | 406
2017-01-31 18:00 | 400 | 398
2017-01-31 18:30 | 398 | 396
2017-01-31 19:00 | 382 | 380
2017-01-31 19:30 | 366 | 364
2017-01-31 20:00 | 345 | 343
2017-01-31 20:30 | 318 | 317
2017-01-31 21:00 | 298 | 297
2017-01-31 21:30 | 277 | 275
2017-01-31 22:00 | 278 | 276
2017-01-31 22:30 | 262 | 262
2017-01-31 23:00 | 235 | 235
2017-01-31 23:30 | 222 | 221
2017-02-01 | 208 | 207
2017-02-01 00:30 | 214 | 212
2017-02-01 01:00 | 199 | 196
2017-02-01 01:30 | 182 | 180
2017-02-01 02:00 | 188 | 185
2017-02-01 02:30 | 189 | 186
2017-02-01 03:00 | 188 | 185
2017-02-01 03:30 | 185 | 182
2017-02-01 04:00 | 186 | 183
2017-02-01 04:30 | 186 | 183
2017-02-01 05:00 | 190 | 188
2017-02-01 05:30 | 214 | 212
2017-02-01 06:00 | 236 | 235
2017-02-01 06:30 | 251 | 251
2017-02-01 07:00 | 268 | 267
2017-02-01 07:30 | 278 | 278
2017-02-01 08:00 | 289 | 289
2017-02-01 08:30 | 299 | 298
2017-02-01 09:00 | 303 | 302
2017-02-01 09:30 | 311 | 310
2017-02-01 10:00 | 316 | 316
2017-02-01 10:30 | 320 | 320
2017-02-01 11:00 | 322 | 322
2017-02-01 11:30 | 335 | 334
2017-02-01 12:00 | 347 | 346
2017-02-01 12:30 | 349 | 349
2017-02-01 13:00 | 362 | 362
2017-02-01 13:30 | 371 | 371
2017-02-01 14:00 | 375 | 375
2017-02-01 14:30 | 380 | 380
2017-02-01 15:00 | 389 | 389
2017-02-01 15:30 | 403 | 403
2017-02-01 16:00 | 412 | 412
2017-02-01 16:30 | 420 | 420
2017-02-01 17:00 | 418 | 417
2017-02-01 17:30 | 412 | 411
2017-02-01 18:00 | 400 | 399
2017-02-01 18:30 | 400 | 400
2017-02-01 19:00 | 390 | 390
2017-02-01 19:30 | 371 | 370
2017-02-01 20:00 | 355 | 354
2017-02-01 20:30 | 338 | 337
2017-02-01 21:00 | 318 | 318
2017-02-01 21:30 | 299 | 299
2017-02-01 22:00 | 288 | 287
2017-02-01 22:30 | 277 | 277
2017-02-01 23:00 | 256 | 255
2017-02-01 23:30 | 238 | 238
2017-02-02 | 219 | 219
2017-02-02 00:30 | 207 | 207
2017-02-02 01:00 | 201 | 201
2017-02-02 01:30 | 201 | 197
2017-02-02 02:00 | 199 | 195
2017-02-02 02:30 | 201 | 200
2017-02-02 03:00 | 203 | 202
2017-02-02 03:30 | 204 | 203
2017-02-02 04:00 | 205 | 205
2017-02-02 04:30 | 207 | 206
2017-02-02 05:00 | 216 | 215
2017-02-02 05:30 | 228 | 225
2017-02-02 06:00 | 243 | 241
2017-02-02 06:30 | 261 | 259
2017-02-02 07:00 | 285 | 284
2017-02-02 07:30 | 294 | 294
2017-02-02 08:00 | 303 | 303
2017-02-02 08:30 | 307 | 307
2017-02-02 09:00 | 319 | 318
2017-02-02 09:30 | 334 | 331
2017-02-02 10:00 | 336 | 334
2017-02-02 10:30 | 342 | 340
2017-02-02 11:00 | 354 | 352
2017-02-02 11:30 | 371 | 369
2017-02-02 12:00 | 380 | 379
2017-02-02 12:30 | 384 | 383
2017-02-02 13:00 | 392 | 391
2017-02-02 13:30 | 396 | 396
2017-02-02 14:00 | 403 | 403
2017-02-02 14:30 | 407 | 407
2017-02-02 15:00 | 415 | 415
2017-02-02 15:30 | 429 | 429
2017-02-02 16:00 | 441 | 441
2017-02-02 16:30 | 448 | 448
2017-02-02 17:00 | 444 | 444
2017-02-02 17:30 | 436 | 436
2017-02-02 18:00 | 426 | 426
2017-02-02 18:30 | 424 | 424
2017-02-02 19:00 | 425 | 425
2017-02-02 19:30 | 408 | 407
2017-02-02 20:00 | 384 | 384
2017-02-02 20:30 | 348 | 348
2017-02-02 21:00 | 325 | 325
2017-02-02 21:30 | 311 | 309
2017-02-02 22:00 | 297 | 297
2017-02-02 22:30 | 277 | 277
2017-02-02 23:00 | 251 | 251
2017-02-02 23:30 | 237 | 237
2017-02-03 | 222 | 222
2017-02-03 00:30 | 213 | 212
2017-02-03 01:00 | 209 | 208
2017-02-03 01:30 | 204 | 203
2017-02-03 02:00 | 201 | 200
2017-02-03 02:30 | 198 | 198
2017-02-03 03:00 | 198 | 198
2017-02-03 03:30 | 196 | 196
2017-02-03 04:00 | 199 | 199
2017-02-03 04:30 | 206 | 206
2017-02-03 05:00 | 215 | 215
2017-02-03 05:30 | 224 | 224
2017-02-03 06:00 | 246 | 246
2017-02-03 06:30 | 270 | 270
2017-02-03 07:00 | 301 | 301
2017-02-03 07:30 | 320 | 319
2017-02-03 08:00 | 328 | 328
2017-02-03 08:30 | 332 | 332
2017-02-03 09:00 | 331 | 331
2017-02-03 09:30 | 339 | 338
2017-02-03 10:00 | 348 | 347
2017-02-03 10:30 | 350 | 349
2017-02-03 11:00 | 348 | 347
2017-02-03 11:30 | 353 | 352
2017-02-03 12:00 | 352 | 351
2017-02-03 12:30 | 357 | 356
2017-02-03 13:00 | 364 | 363
2017-02-03 13:30 | 375 | 375
2017-02-03 14:00 | 386 | 385
2017-02-03 14:30 | 389 | 388
2017-02-03 15:00 | 395 | 394
2017-02-03 15:30 | 406 | 406
2017-02-03 16:00 | 416 | 415
2017-02-03 16:30 | 420 | 419
2017-02-03 17:00 | 415 | 414
2017-02-03 17:30 | 405 | 403
2017-02-03 18:00 | 382 | 380
2017-02-03 18:30 | 375 | 373
2017-02-03 19:00 | 364 | 362
2017-02-03 19:30 | 359 | 356
2017-02-03 20:00 | 349 | 347
2017-02-03 20:30 | 334 | 333
2017-02-03 21:00 | 324 | 323
2017-02-03 21:30 | 312 | 311
2017-02-03 22:00 | 295 | 295
2017-02-03 22:30 | 280 | 279
2017-02-03 23:00 | 254 | 253
2017-02-03 23:30 | 238 | 236
2017-02-04 | 220 | 220
2017-02-04 00:30 | 215 | 215
2017-02-04 01:00 | 205 | 205
2017-02-04 01:30 | 202 | 202
2017-02-04 02:00 | 200 | 200
2017-02-04 02:30 | 198 | 198
2017-02-04 03:00 | 200 | 200
2017-02-04 03:30 | 200 | 199
2017-02-04 04:00 | 194 | 193
2017-02-04 04:30 | 196 | 196
2017-02-04 05:00 | 197 | 197
2017-02-04 05:30 | 203 | 202
2017-02-04 06:00 | 214 | 213
2017-02-04 06:30 | 220 | 220
2017-02-04 07:00 | 237 | 237
2017-02-04 07:30 | 253 | 253
2017-02-04 08:00 | 267 | 267
2017-02-04 08:30 | 276 | 276
2017-02-04 09:00 | 284 | 284
2017-02-04 09:30 | 293 | 293
2017-02-04 10:00 | 296 | 296
2017-02-04 10:30 | 300 | 300
2017-02-04 11:00 | 311 | 311
2017-02-04 11:30 | 308 | 307
2017-02-04 12:00 | 307 | 306
2017-02-04 12:30 | 307 | 306
2017-02-04 13:00 | 310 | 309
2017-02-04 13:30 | 323 | 323
2017-02-04 14:00 | 340 | 339
2017-02-04 14:30 | 344 | 343
2017-02-04 15:00 | 351 | 351
2017-02-04 15:30 | 360 | 360
2017-02-04 16:00 | 356 | 356
2017-02-04 16:30 | 377 | 377
2017-02-04 17:00 | 372 | 372
2017-02-04 17:30 | 362 | 362
2017-02-04 18:00 | 361 | 360
2017-02-04 18:30 | 363 | 362
2017-02-04 19:00 | 354 | 354
2017-02-04 19:30 | 350 | 350
2017-02-04 20:00 | 339 | 338
2017-02-04 20:30 | 325 | 324
2017-02-04 21:00 | 309 | 309
2017-02-04 21:30 | 303 | 302
2017-02-04 22:00 | 299 | 298
2017-02-04 22:30 | 281 | 280
2017-02-04 23:00 | 259 | 259
2017-02-04 23:30 | 242 | 242
2017-02-05 | 230 | 230
2017-02-05 00:30 | 219 | 219
2017-02-05 01:00 | 211 | 210
2017-02-05 01:30 | 206 | 205
2017-02-05 02:00 | 204 | 203
2017-02-05 02:30 | 204 | 203
2017-02-05 03:00 | 206 | 206
2017-02-05 03:30 | 207 | 207
2017-02-05 04:00 | 205 | 204
2017-02-05 04:30 | 205 | 204
2017-02-05 05:00 | 208 | 208
2017-02-05 05:30 | 212 | 212
2017-02-05 06:00 | 219 | 218
2017-02-05 06:30 | 227 | 226
2017-02-05 07:00 | 239 | 239
2017-02-05 07:30 | 256 | 255
2017-02-05 08:00 | 269 | 269
2017-02-05 08:30 | 279 | 279
2017-02-05 09:00 | 288 | 288
2017-02-05 09:30 | 295 | 295
2017-02-05 10:00 | 294 | 294
2017-02-05 10:30 | 297 | 297
2017-02-05 11:00 | 301 | 300
2017-02-05 11:30 | 303 | 302
2017-02-05 12:00 | 304 | 304
2017-02-05 12:30 | 316 | 316
2017-02-05 13:00 | 320 | 320
2017-02-05 13:30 | 335 | 335
2017-02-05 14:00 | 338 | 337
2017-02-05 14:30 | 339 | 339
2017-02-05 15:00 | 340 | 340
2017-02-05 15:30 | 348 | 348
2017-02-05 16:00 | 357 | 357
2017-02-05 16:30 | 365 | 365
2017-02-05 17:00 | 380 | 379
2017-02-05 17:30 | 378 | 378
2017-02-05 18:00 | 372 | 372
2017-02-05 18:30 | 369 | 369
2017-02-05 19:00 | 368 | 367
2017-02-05 19:30 | 360 | 359
2017-02-05 20:00 | 347 | 346
2017-02-05 20:30 | 329 | 329
2017-02-05 21:00 | 313 | 313
2017-02-05 21:30 | 298 | 298
2017-02-05 22:00 | 285 | 285
2017-02-05 22:30 | 268 | 268
2017-02-05 23:00 | 246 | 245
2017-02-05 23:30 | 230 | 230
2017-02-06 | 220 | 220
2017-02-06 00:30 | 220 | 219
2017-02-06 01:00 | 213 | 212
2017-02-06 01:30 | 210 | 209
2017-02-06 02:00 | 207 | 206
2017-02-06 02:30 | 204 | 203
2017-02-06 03:00 | 203 | 202
2017-02-06 03:30 | 203 | 203
2017-02-06 04:00 | 205 | 205
2017-02-06 04:30 | 209 | 208
2017-02-06 05:00 | 217 | 216
2017-02-06 05:30 | 230 | 229
2017-02-06 06:00 | 246 | 246
2017-02-06 06:30 | 260 | 260
2017-02-06 07:00 | 283 | 283
2017-02-06 07:30 | 309 | 308
2017-02-06 08:00 | 324 | 324
2017-02-06 08:30 | 335 | 334
2017-02-06 09:00 | 340 | 339
2017-02-06 09:30 | 345 | 345
2017-02-06 10:00 | 348 | 347
2017-02-06 10:30 | 349 | 348
2017-02-06 11:00 | 352 | 352
2017-02-06 11:30 | 353 | 353
2017-02-06 12:00 | 353 | 353
2017-02-06 12:30 | 358 | 358
2017-02-06 13:00 | 359 | 359
2017-02-06 13:30 | 375 | 375
2017-02-06 14:00 | 384 | 384
2017-02-06 14:30 | 391 | 391
2017-02-06 15:00 | 398 | 397
2017-02-06 15:30 | 409 | 409
2017-02-06 16:00 | 417 | 417
2017-02-06 16:30 | 425 | 425
2017-02-06 17:00 | 424 | 424
2017-02-06 17:30 | 418 | 418
2017-02-06 18:00 | 409 | 408
2017-02-06 18:30 | 410 | 409
2017-02-06 19:00 | 394 | 393
2017-02-06 19:30 | 381 | 380
2017-02-06 20:00 | 368 | 367
2017-02-06 20:30 | 354 | 352
2017-02-06 21:00 | 335 | 334
2017-02-06 21:30 | 318 | 317
2017-02-06 22:00 | 298 | 298
2017-02-06 22:30 | 279 | 279
2017-02-06 23:00 | 255 | 255
2017-02-06 23:30 | 233 | 233
2017-02-07 | 224 | 223
2017-02-07 00:30 | 214 | 214
2017-02-07 01:00 | 210 | 209
2017-02-07 01:30 | 207 | 206
2017-02-07 02:00 | 204 | 204
2017-02-07 02:30 | 204 | 204
2017-02-07 03:00 | 202 | 201
2017-02-07 03:30 | 201 | 201
2017-02-07 04:00 | 207 | 206
2017-02-07 04:30 | 215 | 214
2017-02-07 05:00 | 224 | 223
2017-02-07 05:30 | 233 | 233
2017-02-07 06:00 | 252 | 252
2017-02-07 06:30 | 265 | 265
2017-02-07 07:00 | 290 | 290
2017-02-07 07:30 | 279 | 279
2017-02-07 08:00 | 289 | 289
2017-02-07 08:30 | 293 | 293
2017-02-07 09:00 | 297 | 297
2017-02-07 09:30 | 307 | 307
2017-02-07 10:00 | 305 | 305
2017-02-07 10:30 | 304 | 304
2017-02-07 11:00 | 306 | 306
2017-02-07 11:30 | 304 | 303
2017-02-07 12:00 | 308 | 307
2017-02-07 12:30 | 315 | 314
2017-02-07 13:00 | 329 | 328
2017-02-07 13:30 | 346 | 346
2017-02-07 14:00 | 358 | 357
2017-02-07 14:30 | 363 | 362
2017-02-07 15:00 | 369 | 369
2017-02-07 15:30 | 381 | 380
2017-02-07 16:00 | 390 | 390
2017-02-07 16:30 | 396 | 396
2017-02-07 17:00 | 395 | 394
2017-02-07 17:30 | 387 | 386
2017-02-07 18:00 | 378 | 376
2017-02-07 18:30 | 379 | 377
2017-02-07 19:00 | 378 | 376
2017-02-07 19:30 | 348 | 346
2017-02-07 20:00 | 330 | 329
2017-02-07 20:30 | 313 | 311
2017-02-07 21:00 | 299 | 295
2017-02-07 21:30 | 289 | 286
2017-02-07 22:00 | 268 | 268
2017-02-07 22:30 | 254 | 254
2017-02-07 23:00 | 227 | 227
2017-02-07 23:30 | 217 | 217
2017-02-08 | 208 | 208
2017-02-08 00:30 | 196 | 196
2017-02-08 01:00 | 195 | 194
2017-02-08 01:30 | 191 | 190
2017-02-08 02:00 | 194 | 193
2017-02-08 02:30 | 191 | 190
2017-02-08 03:00 | 190 | 189
2017-02-08 03:30 | 192 | 191
2017-02-08 04:00 | 199 | 198
2017-02-08 04:30 | 204 | 203
2017-02-08 05:00 | 208 | 207
2017-02-08 05:30 | 216 | 216
2017-02-08 06:00 | 234 | 233
2017-02-08 06:30 | 242 | 242
2017-02-08 07:00 | 258 | 258
2017-02-08 07:30 | 277 | 277
2017-02-08 08:00 | 281 | 281
2017-02-08 08:30 | 284 | 284
2017-02-08 09:00 | 288 | 287
2017-02-08 09:30 | 303 | 302
2017-02-08 10:00 | 300 | 300
2017-02-08 10:30 | 298 | 298
2017-02-08 11:00 | 299 | 299
2017-02-08 11:30 | 301 | 301
2017-02-08 12:00 | 302 | 302
2017-02-08 12:30 | 305 | 305
2017-02-08 13:00 | 306 | 306
2017-02-08 13:30 | 311 | 311
2017-02-08 14:00 | 318 | 317
2017-02-08 14:30 | 322 | 322
2017-02-08 15:00 | 331 | 331
2017-02-08 15:30 | 341 | 341
2017-02-08 16:00 | 341 | 340
2017-02-08 16:30 | 338 | 337
2017-02-08 17:00 | 340 | 338
2017-02-08 17:30 | 333 | 332
2017-02-08 18:00 | 329 | 329
2017-02-08 18:30 | 330 | 329
2017-02-08 19:00 | 356 | 356
2017-02-08 19:30 | 356 | 356
2017-02-08 20:00 | 344 | 344
2017-02-08 20:30 | 328 | 328
2017-02-08 21:00 | 318 | 317
2017-02-08 21:30 | 303 | 302
2017-02-08 22:00 | 286 | 285
2017-02-08 22:30 | 277 | 277
2017-02-08 23:00 | 250 | 250
2017-02-08 23:30 | 236 | 236
2017-02-09 | 223 | 223
2017-02-09 00:30 | 216 | 216
2017-02-09 01:00 | 213 | 213
2017-02-09 01:30 | 210 | 210
2017-02-09 02:00 | 211 | 211
2017-02-09 02:30 | 212 | 212
2017-02-09 03:00 | 213 | 213
2017-02-09 03:30 | 213 | 213
2017-02-09 04:00 | 214 | 214
2017-02-09 04:30 | 216 | 216
2017-02-09 05:00 | 223 | 223
2017-02-09 05:30 | 239 | 239
2017-02-09 06:00 | 254 | 254
2017-02-09 06:30 | 260 | 260
2017-02-09 07:00 | 283 | 282
2017-02-09 07:30 | 305 | 305
2017-02-09 08:00 | 313 | 313
2017-02-09 08:30 | 322 | 322
2017-02-09 09:00 | 324 | 324
2017-02-09 09:30 | 332 | 332
2017-02-09 10:00 | 337 | 337
2017-02-09 10:30 | 337 | 337
2017-02-09 11:00 | 337 | 337
2017-02-09 11:30 | 343 | 343
2017-02-09 12:00 | 347 | 347
2017-02-09 12:30 | 347 | 347
2017-02-09 13:00 | 357 | 357
2017-02-09 13:30 | 363 | 362
2017-02-09 14:00 | 367 | 365
2017-02-09 14:30 | 373 | 372
2017-02-09 15:00 | 381 | 379
2017-02-09 15:30 | 392 | 391
2017-02-09 16:00 | 398 | 397
2017-02-09 16:30 | 403 | 402
2017-02-09 17:00 | 397 | 396
2017-02-09 17:30 | 390 | 389
2017-02-09 18:00 | 390 | 389
2017-02-09 18:30 | 388 | 388
2017-02-09 19:00 | 389 | 388
2017-02-09 19:30 | 383 | 381
2017-02-09 20:00 | 365 | 365
2017-02-09 20:30 | 349 | 349
2017-02-09 21:00 | 331 | 331
2017-02-09 21:30 | 306 | 306
2017-02-09 22:00 | 292 | 292
2017-02-09 22:30 | 281 | 281
2017-02-09 23:00 | 255 | 255
2017-02-09 23:30 | 240 | 239
2017-02-10 | 228 | 228
2017-02-10 00:30 | 219 | 219
2017-02-10 01:00 | 212 | 212
2017-02-10 01:30 | 209 | 209
2017-02-10 02:00 | 207 | 207
2017-02-10 02:30 | 205 | 205
2017-02-10 03:00 | 204 | 204
2017-02-10 03:30 | 206 | 206
2017-02-10 04:00 | 208 | 208
2017-02-10 04:30 | 210 | 210
2017-02-10 05:00 | 219 | 219
2017-02-10 05:30 | 228 | 228
2017-02-10 06:00 | 243 | 243
2017-02-10 06:30 | 261 | 261
2017-02-10 07:00 | 287 | 287
2017-02-10 07:30 | 301 | 301
2017-02-10 08:00 | 315 | 315
2017-02-10 08:30 | 327 | 327
2017-02-10 09:00 | 333 | 333
2017-02-10 09:30 | 338 | 338
2017-02-10 10:00 | 337 | 337
2017-02-10 10:30 | 340 | 340
2017-02-10 11:00 | 345 | 344
2017-02-10 11:30 | 346 | 346
2017-02-10 12:00 | 351 | 350
2017-02-10 12:30 | 355 | 355
2017-02-10 13:00 | 364 | 364
2017-02-10 13:30 | 375 | 375
2017-02-10 14:00 | 381 | 381
2017-02-10 14:30 | 384 | 384
2017-02-10 15:00 | 394 | 394
2017-02-10 15:30 | 403 | 402
2017-02-10 16:00 | 402 | 402
2017-02-10 16:30 | 421 | 420
2017-02-10 17:00 | 403 | 402
2017-02-10 17:30 | 388 | 387
2017-02-10 18:00 | 373 | 373
2017-02-10 18:30 | 377 | 377
2017-02-10 19:00 | 376 | 376
2017-02-10 19:30 | 372 | 372
2017-02-10 20:00 | 364 | 364
2017-02-10 20:30 | 351 | 351
2017-02-10 21:00 | 344 | 343
2017-02-10 21:30 | 335 | 334
2017-02-10 22:00 | 306 | 305
2017-02-10 22:30 | 291 | 291
2017-02-10 23:00 | 271 | 270
2017-02-10 23:30 | 256 | 256
2017-02-11 | 238 | 238
2017-02-11 00:30 | 227 | 226
2017-02-11 01:00 | 216 | 216
2017-02-11 01:30 | 211 | 211
2017-02-11 02:00 | 213 | 213
2017-02-11 02:30 | 211 | 211
2017-02-11 03:00 | 210 | 210
2017-02-11 03:30 | 209 | 209
2017-02-11 04:00 | 207 | 207
2017-02-11 04:30 | 211 | 211
2017-02-11 05:00 | 213 | 213
2017-02-11 05:30 | 219 | 219
2017-02-11 06:00 | 233 | 233
2017-02-11 06:30 | 241 | 240
2017-02-11 07:00 | 254 | 254
2017-02-11 07:30 | 269 | 269
2017-02-11 08:00 | 284 | 284
2017-02-11 08:30 | 298 | 298
2017-02-11 09:00 | 310 | 309
2017-02-11 09:30 | 327 | 326
2017-02-11 10:00 | 341 | 340
2017-02-11 10:30 | 347 | 346
2017-02-11 11:00 | 355 | 355
2017-02-11 11:30 | 368 | 367
2017-02-11 12:00 | 364 | 364
2017-02-11 12:30 | 374 | 373
2017-02-11 13:00 | 385 | 384
2017-02-11 13:30 | 385 | 384
2017-02-11 14:00 | 404 | 404
2017-02-11 14:30 | 413 | 412
2017-02-11 15:00 | 420 | 420
2017-02-11 15:30 | 429 | 429
2017-02-11 16:00 | 436 | 436
2017-02-11 16:30 | 443 | 443
2017-02-11 17:00 | 441 | 441
2017-02-11 17:30 | 435 | 434
2017-02-11 18:00 | 425 | 424
2017-02-11 18:30 | 421 | 420
2017-02-11 19:00 | 416 | 415
2017-02-11 19:30 | 406 | 405
2017-02-11 20:00 | 385 | 383
2017-02-11 20:30 | 369 | 366
2017-02-11 21:00 | 355 | 351
2017-02-11 21:30 | 328 | 324
2017-02-11 22:00 | 318 | 315
2017-02-11 22:30 | 301 | 300
2017-02-11 23:00 | 278 | 277
2017-02-11 23:30 | 262 | 261
2017-02-12 | 248 | 246
2017-02-12 00:30 | 239 | 237
2017-02-12 01:00 | 231 | 229
2017-02-12 01:30 | 222 | 222
2017-02-12 02:00 | 217 | 217
2017-02-12 02:30 | 222 | 222
2017-02-12 03:00 | 221 | 221
2017-02-12 03:30 | 223 | 223
2017-02-12 04:00 | 221 | 221
2017-02-12 04:30 | 218 | 218
2017-02-12 05:00 | 217 | 217
2017-02-12 05:30 | 230 | 230
2017-02-12 06:00 | 240 | 240
2017-02-12 06:30 | 248 | 248
2017-02-12 07:00 | 263 | 261
2017-02-12 07:30 | 275 | 274
2017-02-12 08:00 | 289 | 288
2017-02-12 08:30 | 297 | 297
2017-02-12 09:00 | 310 | 309
2017-02-12 09:30 | 328 | 328
2017-02-12 10:00 | 338 | 338
2017-02-12 10:30 | 355 | 355
2017-02-12 11:00 | 370 | 370
2017-02-12 11:30 | 387 | 387
2017-02-12 12:00 | 406 | 405
2017-02-12 12:30 | 411 | 411
2017-02-12 13:00 | 418 | 418
2017-02-12 13:30 | 426 | 425
2017-02-12 14:00 | 433 | 433
2017-02-12 14:30 | 442 | 442
2017-02-12 15:00 | 454 | 454
2017-02-12 15:30 | 465 | 464
2017-02-12 16:00 | 478 | 477
2017-02-12 16:30 | 487 | 487
2017-02-12 17:00 | 490 | 489
2017-02-12 17:30 | 488 | 487
2017-02-12 18:00 | 480 | 479
2017-02-12 18:30 | 481 | 480
2017-02-12 19:00 | 472 | 471
2017-02-12 19:30 | 457 | 455
2017-02-12 20:00 | 438 | 435
2017-02-12 20:30 | 401 | 399
2017-02-12 21:00 | 359 | 357
2017-02-12 21:30 | 331 | 328
2017-02-12 22:00 | 326 | 325
2017-02-12 22:30 | 298 | 297
2017-02-12 23:00 | 278 | 276
2017-02-12 23:30 | 273 | 270
2017-02-13 | 259 | 257
2017-02-13 00:30 | 248 | 246
2017-02-13 01:00 | 246 | 244
2017-02-13 01:30 | 243 | 240
2017-02-13 02:00 | 235 | 233
2017-02-13 02:30 | 235 | 231
2017-02-13 03:00 | 234 | 230
2017-02-13 03:30 | 236 | 232
2017-02-13 04:00 | 246 | 244
2017-02-13 04:30 | 245 | 243
2017-02-13 05:00 | 251 | 248
2017-02-13 05:30 | 261 | 259
2017-02-13 06:00 | 285 | 282
2017-02-13 06:30 | 291 | 290
2017-02-13 07:00 | 325 | 324
2017-02-13 07:30 | 341 | 341
2017-02-13 08:00 | 344 | 344
2017-02-13 08:30 | 352 | 351
2017-02-13 09:00 | 378 | 378
2017-02-13 09:30 | 401 | 400
2017-02-13 10:00 | 407 | 406
2017-02-13 10:30 | 408 | 408
2017-02-13 11:00 | 413 | 413
2017-02-13 11:30 | 417 | 416
2017-02-13 12:00 | 422 | 422
2017-02-13 12:30 | 425 | 424
2017-02-13 13:00 | 423 | 423
2017-02-13 13:30 | 419 | 419
2017-02-13 14:00 | 411 | 411
2017-02-13 14:30 | 410 | 409
2017-02-13 15:00 | 407 | 406
2017-02-13 15:30 | 408 | 407
2017-02-13 16:00 | 405 | 403
2017-02-13 16:30 | 400 | 398
2017-02-13 17:00 | 389 | 388
2017-02-13 17:30 | 393 | 392
2017-02-13 18:00 | 379 | 377
2017-02-13 18:30 | 368 | 368
2017-02-13 19:00 | 361 | 360
2017-02-13 19:30 | 349 | 348
2017-02-13 20:00 | 348 | 347
2017-02-13 20:30 | 341 | 339
2017-02-13 21:00 | 315 | 315
2017-02-13 21:30 | 304 | 303
2017-02-13 22:00 | 281 | 280
2017-02-13 22:30 | 279 | 278
2017-02-13 23:00 | 261 | 261
2017-02-13 23:30 | 245 | 245
2017-02-14 | 240 | 239
2017-02-14 00:30 | 237 | 236
2017-02-14 01:00 | 225 | 224
2017-02-14 01:30 | 219 | 218
2017-02-14 02:00 | 218 | 217
2017-02-14 02:30 | 217 | 216
2017-02-14 03:00 | 218 | 217
2017-02-14 03:30 | 218 | 217
2017-02-14 04:00 | 219 | 219
2017-02-14 04:30 | 226 | 226
2017-02-14 05:00 | 232 | 232
2017-02-14 05:30 | 242 | 242
2017-02-14 06:00 | 259 | 259
2017-02-14 06:30 | 270 | 269
2017-02-14 07:00 | 291 | 291
2017-02-14 07:30 | 304 | 303
2017-02-14 08:00 | 310 | 310
2017-02-14 08:30 | 310 | 310
2017-02-14 09:00 | 311 | 311
2017-02-14 09:30 | 321 | 320
2017-02-14 10:00 | 324 | 323
2017-02-14 10:30 | 319 | 317
2017-02-14 11:00 | 316 | 314
2017-02-14 11:30 | 310 | 308
2017-02-14 12:00 | 309 | 307
2017-02-14 12:30 | 305 | 304
2017-02-14 13:00 | 306 | 304
2017-02-14 13:30 | 306 | 305
2017-02-14 14:00 | 312 | 310
2017-02-14 14:30 | 313 | 312
2017-02-14 15:00 | 311 | 310
2017-02-14 15:30 | 317 | 316
2017-02-14 16:00 | 322 | 321
2017-02-14 16:30 | 331 | 329
2017-02-14 17:00 | 332 | 330
2017-02-14 17:30 | 332 | 330
2017-02-14 18:00 | 329 | 327
2017-02-14 18:30 | 332 | 331
2017-02-14 19:00 | 330 | 328
2017-02-14 19:30 | 328 | 326
2017-02-14 20:00 | 311 | 309
2017-02-14 20:30 | 297 | 296
2017-02-14 21:00 | 288 | 287
2017-02-14 21:30 | 280 | 278
2017-02-14 22:00 | 267 | 265
2017-02-14 22:30 | 255 | 252
2017-02-14 23:00 | 230 | 229
2017-02-14 23:30 | 220 | 220
2017-02-15 | 211 | 211
2017-02-15 00:30 | 202 | 201
2017-02-15 01:00 | 201 | 201
2017-02-15 01:30 | 198 | 198
2017-02-15 02:00 | 198 | 197
2017-02-15 02:30 | 198 | 198
2017-02-15 03:00 | 200 | 200
2017-02-15 03:30 | 201 | 201
2017-02-15 04:00 | 203 | 202
2017-02-15 04:30 | 207 | 206
2017-02-15 05:00 | 219 | 219
2017-02-15 05:30 | 223 | 223
2017-02-15 06:00 | 240 | 240
2017-02-15 06:30 | 251 | 251
2017-02-15 07:00 | 271 | 271
2017-02-15 07:30 | 285 | 285
2017-02-15 08:00 | 292 | 292
2017-02-15 08:30 | 292 | 292
2017-02-15 09:00 | 290 | 290
2017-02-15 09:30 | 293 | 293
2017-02-15 10:00 | 299 | 299
2017-02-15 10:30 | 303 | 303
2017-02-15 11:00 | 311 | 311
2017-02-15 11:30 | 307 | 307
2017-02-15 12:00 | 299 | 299
2017-02-15 12:30 | 296 | 296
2017-02-15 13:00 | 308 | 308
2017-02-15 13:30 | 311 | 311
2017-02-15 14:00 | 317 | 317
2017-02-15 14:30 | 317 | 317
2017-02-15 15:00 | 322 | 322
2017-02-15 15:30 | 328 | 328
2017-02-15 16:00 | 333 | 333
2017-02-15 16:30 | 334 | 334
2017-02-15 17:00 | 330 | 329
2017-02-15 17:30 | 326 | 325
2017-02-15 18:00 | 322 | 321
2017-02-15 18:30 | 333 | 332
2017-02-15 19:00 | 330 | 330
2017-02-15 19:30 | 329 | 328
2017-02-15 20:00 | 320 | 319
2017-02-15 20:30 | 314 | 313
2017-02-15 21:00 | 301 | 300
2017-02-15 21:30 | 285 | 283
2017-02-15 22:00 | 270 | 269
2017-02-15 22:30 | 255 | 255
2017-02-15 23:00 | 237 | 236
2017-02-15 23:30 | 227 | 226
2017-02-16 | 219 | 218
2017-02-16 00:30 | 209 | 208
2017-02-16 01:00 | 204 | 202
2017-02-16 01:30 | 201 | 199
2017-02-16 02:00 | 199 | 197
2017-02-16 02:30 | 201 | 199
2017-02-16 03:00 | 202 | 201
2017-02-16 03:30 | 202 | 201
2017-02-16 04:00 | 205 | 204
2017-02-16 04:30 | 215 | 214
2017-02-16 05:00 | 227 | 226
2017-02-16 05:30 | 234 | 233
2017-02-16 06:00 | 244 | 244
2017-02-16 06:30 | 252 | 252
2017-02-16 07:00 | 271 | 271
2017-02-16 07:30 | 285 | 285
2017-02-16 08:00 | 286 | 286
2017-02-16 08:30 | 289 | 289
2017-02-16 09:00 | 295 | 295
2017-02-16 09:30 | 301 | 301
2017-02-16 10:00 | 302 | 301
2017-02-16 10:30 | 304 | 304
2017-02-16 11:00 | 306 | 306
2017-02-16 11:30 | 307 | 307
2017-02-16 12:00 | 310 | 310
2017-02-16 12:30 | 316 | 316
2017-02-16 13:00 | 319 | 319
2017-02-16 13:30 | 332 | 332
2017-02-16 14:00 | 345 | 343
2017-02-16 14:30 | 351 | 350
2017-02-16 15:00 | 365 | 363
2017-02-16 15:30 | 365 | 364
2017-02-16 16:00 | 369 | 368
2017-02-16 16:30 | 373 | 371
2017-02-16 17:00 | 370 | 368
2017-02-16 17:30 | 364 | 362
2017-02-16 18:00 | 359 | 358
2017-02-16 18:30 | 362 | 362
2017-02-16 19:00 | 361 | 360
2017-02-16 19:30 | 360 | 359
2017-02-16 20:00 | 346 | 345
2017-02-16 20:30 | 333 | 331
2017-02-16 21:00 | 318 | 317
2017-02-16 21:30 | 297 | 296
2017-02-16 22:00 | 284 | 284
2017-02-16 22:30 | 275 | 275
2017-02-16 23:00 | 256 | 255
2017-02-16 23:30 | 241 | 241
2017-02-17 | 224 | 224
2017-02-17 00:30 | 213 | 212
2017-02-17 01:00 | 203 | 202
2017-02-17 01:30 | 196 | 196
2017-02-17 02:00 | 195 | 194
2017-02-17 02:30 | 193 | 192
2017-02-17 03:00 | 196 | 196
2017-02-17 03:30 | 197 | 197
2017-02-17 04:00 | 201 | 201
2017-02-17 04:30 | 203 | 203
2017-02-17 05:00 | 213 | 213
2017-02-17 05:30 | 223 | 223
2017-02-17 06:00 | 236 | 236
2017-02-17 06:30 | 245 | 245
2017-02-17 07:00 | 268 | 268
2017-02-17 07:30 | 283 | 283
2017-02-17 08:00 | 291 | 291
2017-02-17 08:30 | 303 | 303
2017-02-17 09:00 | 311 | 311
2017-02-17 09:30 | 313 | 313
2017-02-17 10:00 | 311 | 311
2017-02-17 10:30 | 310 | 310
2017-02-17 11:00 | 312 | 311
2017-02-17 11:30 | 315 | 314
2017-02-17 12:00 | 318 | 318
2017-02-17 12:30 | 327 | 327
2017-02-17 13:00 | 335 | 334
2017-02-17 13:30 | 333 | 332
2017-02-17 14:00 | 337 | 336
2017-02-17 14:30 | 338 | 337
2017-02-17 15:00 | 348 | 347
2017-02-17 15:30 | 359 | 358
2017-02-17 16:00 | 362 | 361
2017-02-17 16:30 | 362 | 361
2017-02-17 17:00 | 353 | 351
2017-02-17 17:30 | 342 | 341
2017-02-17 18:00 | 333 | 331
2017-02-17 18:30 | 337 | 336
2017-02-17 19:00 | 338 | 337
2017-02-17 19:30 | 335 | 333
2017-02-17 20:00 | 325 | 323
2017-02-17 20:30 | 307 | 307
2017-02-17 21:00 | 295 | 294
2017-02-17 21:30 | 283 | 282
2017-02-17 22:00 | 276 | 275
2017-02-17 22:30 | 265 | 264
2017-02-17 23:00 | 242 | 240
2017-02-17 23:30 | 223 | 223
2017-02-18 | 215 | 215
2017-02-18 00:30 | 210 | 209
2017-02-18 01:00 | 204 | 204
2017-02-18 01:30 | 206 | 205
2017-02-18 02:00 | 205 | 205
2017-02-18 02:30 | 204 | 204
2017-02-18 03:00 | 198 | 198
2017-02-18 03:30 | 198 | 197
2017-02-18 04:00 | 204 | 203
2017-02-18 04:30 | 205 | 205
2017-02-18 05:00 | 207 | 206
2017-02-18 05:30 | 209 | 208
2017-02-18 06:00 | 216 | 216
2017-02-18 06:30 | 228 | 228
2017-02-18 07:00 | 240 | 240
2017-02-18 07:30 | 252 | 252
2017-02-18 08:00 | 262 | 262
2017-02-18 08:30 | 268 | 268
2017-02-18 09:00 | 273 | 273
2017-02-18 09:30 | 279 | 278
2017-02-18 10:00 | 280 | 279
2017-02-18 10:30 | 283 | 282
2017-02-18 11:00 | 292 | 292
2017-02-18 11:30 | 295 | 294
2017-02-18 12:00 | 297 | 296
2017-02-18 12:30 | 302 | 301
2017-02-18 13:00 | 315 | 314
2017-02-18 13:30 | 312 | 309
2017-02-18 14:00 | 317 | 314
2017-02-18 14:30 | 323 | 321
2017-02-18 15:00 | 326 | 324
2017-02-18 15:30 | 330 | 328
2017-02-18 16:00 | 335 | 333
2017-02-18 16:30 | 342 | 340
2017-02-18 17:00 | 339 | 337
2017-02-18 17:30 | 333 | 331
2017-02-18 18:00 | 328 | 326
2017-02-18 18:30 | 335 | 334
2017-02-18 19:00 | 337 | 336
2017-02-18 19:30 | 333 | 331
2017-02-18 20:00 | 319 | 317
2017-02-18 20:30 | 303 | 303
2017-02-18 21:00 | 291 | 291
2017-02-18 21:30 | 278 | 278
2017-02-18 22:00 | 276 | 276
2017-02-18 22:30 | 268 | 268
2017-02-18 23:00 | 249 | 248
2017-02-18 23:30 | 237 | 237
2017-02-19 | 220 | 220
2017-02-19 00:30 | 210 | 210
2017-02-19 01:00 | 211 | 211
2017-02-19 01:30 | 204 | 204
2017-02-19 02:00 | 209 | 208
2017-02-19 02:30 | 210 | 209
2017-02-19 03:00 | 209 | 209
2017-02-19 03:30 | 208 | 207
2017-02-19 04:00 | 207 | 206
2017-02-19 04:30 | 206 | 206
2017-02-19 05:00 | 207 | 207
2017-02-19 05:30 | 210 | 209
2017-02-19 06:00 | 216 | 216
2017-02-19 06:30 | 221 | 220
2017-02-19 07:00 | 230 | 230
2017-02-19 07:30 | 245 | 245
2017-02-19 08:00 | 255 | 255
2017-02-19 08:30 | 255 | 255
2017-02-19 09:00 | 250 | 250
2017-02-19 09:30 | 253 | 253
2017-02-19 10:00 | 261 | 260
2017-02-19 10:30 | 262 | 262
2017-02-19 11:00 | 271 | 271
2017-02-19 11:30 | 287 | 287
2017-02-19 12:00 | 285 | 285
2017-02-19 12:30 | 300 | 299
2017-02-19 13:00 | 312 | 311
2017-02-19 13:30 | 322 | 321
2017-02-19 14:00 | 329 | 329
2017-02-19 14:30 | 335 | 335
2017-02-19 15:00 | 344 | 344
2017-02-19 15:30 | 345 | 345
2017-02-19 16:00 | 344 | 344
2017-02-19 16:30 | 350 | 349
2017-02-19 17:00 | 347 | 346
2017-02-19 17:30 | 345 | 344
2017-02-19 18:00 | 343 | 342
2017-02-19 18:30 | 343 | 342
2017-02-19 19:00 | 334 | 333
2017-02-19 19:30 | 328 | 327
2017-02-19 20:00 | 314 | 312
2017-02-19 20:30 | 295 | 295
2017-02-19 21:00 | 283 | 282
2017-02-19 21:30 | 271 | 270
2017-02-19 22:00 | 262 | 261
2017-02-19 22:30 | 252 | 250
2017-02-19 23:00 | 230 | 229
2017-02-19 23:30 | 217 | 215
2017-02-20 | 211 | 211
2017-02-20 00:30 | 207 | 207
2017-02-20 01:00 | 202 | 201
2017-02-20 01:30 | 200 | 199
2017-02-20 02:00 | 202 | 202
2017-02-20 02:30 | 203 | 202
2017-02-20 03:00 | 204 | 203
2017-02-20 03:30 | 205 | 204
2017-02-20 04:00 | 207 | 207
2017-02-20 04:30 | 210 | 209
2017-02-20 05:00 | 217 | 217
2017-02-20 05:30 | 223 | 223
2017-02-20 06:00 | 242 | 242
2017-02-20 06:30 | 253 | 253
2017-02-20 07:00 | 281 | 280
2017-02-20 07:30 | 274 | 274
2017-02-20 08:00 | 273 | 273
2017-02-20 08:30 | 272 | 272
2017-02-20 09:00 | 275 | 275
2017-02-20 09:30 | 277 | 277
2017-02-20 10:00 | 276 | 276
2017-02-20 10:30 | 277 | 277
2017-02-20 11:00 | 302 | 302
2017-02-20 11:30 | 302 | 302
2017-02-20 12:00 | 304 | 304
2017-02-20 12:30 | 307 | 306
2017-02-20 13:00 | 308 | 308
2017-02-20 13:30 | 311 | 311
2017-02-20 14:00 | 316 | 315
2017-02-20 14:30 | 317 | 317
2017-02-20 15:00 | 328 | 328
2017-02-20 15:30 | 344 | 343
2017-02-20 16:00 | 356 | 354
2017-02-20 16:30 | 360 | 358
2017-02-20 17:00 | 355 | 353
2017-02-20 17:30 | 353 | 351
2017-02-20 18:00 | 352 | 348
2017-02-20 18:30 | 356 | 351
2017-02-20 19:00 | 353 | 348
2017-02-20 19:30 | 351 | 347
2017-02-20 20:00 | 336 | 335
2017-02-20 20:30 | 316 | 314
2017-02-20 21:00 | 302 | 299
2017-02-20 21:30 | 289 | 286
2017-02-20 22:00 | 275 | 273
2017-02-20 22:30 | 263 | 259
2017-02-20 23:00 | 235 | 234
2017-02-20 23:30 | 224 | 224
2017-02-21 | 211 | 210
2017-02-21 00:30 | 205 | 204
2017-02-21 01:00 | 200 | 200
2017-02-21 01:30 | 196 | 195
2017-02-21 02:00 | 198 | 197
2017-02-21 02:30 | 200 | 199
2017-02-21 03:00 | 200 | 200
2017-02-21 03:30 | 202 | 202
2017-02-21 04:00 | 206 | 205
2017-02-21 04:30 | 206 | 206
2017-02-21 05:00 | 216 | 216
2017-02-21 05:30 | 229 | 227
2017-02-21 06:00 | 244 | 243
2017-02-21 06:30 | 257 | 257
2017-02-21 07:00 | 281 | 281
2017-02-21 07:30 | 294 | 294
2017-02-21 08:00 | 307 | 306
2017-02-21 08:30 | 311 | 310
2017-02-21 09:00 | 313 | 313
2017-02-21 09:30 | 321 | 321
2017-02-21 10:00 | 321 | 321
2017-02-21 10:30 | 324 | 322
2017-02-21 11:00 | 325 | 323
2017-02-21 11:30 | 327 | 325
2017-02-21 12:00 | 329 | 328
2017-02-21 12:30 | 324 | 323
2017-02-21 13:00 | 325 | 323
2017-02-21 13:30 | 325 | 323
2017-02-21 14:00 | 328 | 325
2017-02-21 14:30 | 332 | 330
2017-02-21 15:00 | 341 | 338
2017-02-21 15:30 | 346 | 344
2017-02-21 16:00 | 346 | 343
2017-02-21 16:30 | 346 | 342
2017-02-21 17:00 | 337 | 333
2017-02-21 17:30 | 332 | 328
2017-02-21 18:00 | 331 | 327
2017-02-21 18:30 | 330 | 328
2017-02-21 19:00 | 329 | 326
2017-02-21 19:30 | 326 | 323
2017-02-21 20:00 | 317 | 312
2017-02-21 20:30 | 297 | 296
2017-02-21 21:00 | 284 | 283
2017-02-21 21:30 | 266 | 266
2017-02-21 22:00 | 252 | 252
2017-02-21 22:30 | 243 | 243
2017-02-21 23:00 | 225 | 224
2017-02-21 23:30 | 212 | 211
2017-02-22 | 202 | 201
2017-02-22 00:30 | 195 | 194
2017-02-22 01:00 | 190 | 189
2017-02-22 01:30 | 188 | 187
2017-02-22 02:00 | 188 | 186
2017-02-22 02:30 | 189 | 188
2017-02-22 03:00 | 189 | 187
2017-02-22 03:30 | 189 | 188
2017-02-22 04:00 | 192 | 191
2017-02-22 04:30 | 199 | 198
2017-02-22 05:00 | 208 | 207
2017-02-22 05:30 | 218 | 218
2017-02-22 06:00 | 233 | 233
2017-02-22 06:30 | 246 | 246
2017-02-22 07:00 | 266 | 266
2017-02-22 07:30 | 273 | 272
2017-02-22 08:00 | 285 | 285
2017-02-22 08:30 | 279 | 279
2017-02-22 09:00 | 284 | 284
2017-02-22 09:30 | 281 | 281
2017-02-22 10:00 | 285 | 285
2017-02-22 10:30 | 291 | 291
2017-02-22 11:00 | 290 | 290
2017-02-22 11:30 | 291 | 291
2017-02-22 12:00 | 291 | 291
2017-02-22 12:30 | 292 | 292
2017-02-22 13:00 | 300 | 300
2017-02-22 13:30 | 305 | 305
2017-02-22 14:00 | 309 | 309
2017-02-22 14:30 | 316 | 316
2017-02-22 15:00 | 317 | 317
2017-02-22 15:30 | 325 | 325
2017-02-22 16:00 | 328 | 328
2017-02-22 16:30 | 331 | 331
2017-02-22 17:00 | 326 | 326
2017-02-22 17:30 | 318 | 317
2017-02-22 18:00 | 312 | 311
2017-02-22 18:30 | 320 | 319
2017-02-22 19:00 | 317 | 316
2017-02-22 19:30 | 314 | 313
2017-02-22 20:00 | 298 | 297
2017-02-22 20:30 | 286 | 285
2017-02-22 21:00 | 272 | 272
2017-02-22 21:30 | 262 | 261
2017-02-22 22:00 | 255 | 254
2017-02-22 22:30 | 247 | 245
2017-02-22 23:00 | 226 | 225
2017-02-22 23:30 | 214 | 213
2017-02-23 | 202 | 200
2017-02-23 00:30 | 200 | 198
2017-02-23 01:00 | 198 | 196
2017-02-23 01:30 | 197 | 194
2017-02-23 02:00 | 197 | 194
2017-02-23 02:30 | 196 | 193
2017-02-23 03:00 | 197 | 193
2017-02-23 03:30 | 194 | 191
2017-02-23 04:00 | 202 | 199
2017-02-23 04:30 | 210 | 207
2017-02-23 05:00 | 222 | 220
2017-02-23 05:30 | 228 | 226
2017-02-23 06:00 | 238 | 237
2017-02-23 06:30 | 256 | 254
2017-02-23 07:00 | 270 | 269
2017-02-23 07:30 | 278 | 278
2017-02-23 08:00 | 280 | 280
2017-02-23 08:30 | 281 | 281
2017-02-23 09:00 | 285 | 285
2017-02-23 09:30 | 296 | 295
2017-02-23 10:00 | 299 | 298
2017-02-23 10:30 | 303 | 303
2017-02-23 11:00 | 305 | 304
2017-02-23 11:30 | 308 | 308
2017-02-23 12:00 | 309 | 309
2017-02-23 12:30 | 313 | 313
2017-02-23 13:00 | 317 | 317
2017-02-23 13:30 | 319 | 318
2017-02-23 14:00 | 317 | 316
2017-02-23 14:30 | 326 | 324
2017-02-23 15:00 | 335 | 330
2017-02-23 15:30 | 336 | 332
2017-02-23 16:00 | 346 | 342
2017-02-23 16:30 | 354 | 349
2017-02-23 17:00 | 353 | 347
2017-02-23 17:30 | 349 | 344
2017-02-23 18:00 | 345 | 341
2017-02-23 18:30 | 351 | 348
2017-02-23 19:00 | 349 | 346
2017-02-23 19:30 | 343 | 340
2017-02-23 20:00 | 325 | 323
2017-02-23 20:30 | 303 | 301
2017-02-23 21:00 | 287 | 286
2017-02-23 21:30 | 274 | 273
2017-02-23 22:00 | 262 | 261
2017-02-23 22:30 | 250 | 248
2017-02-23 23:00 | 229 | 228
2017-02-23 23:30 | 209 | 208
2017-02-24 | 203 | 201
2017-02-24 00:30 | 204 | 201
2017-02-24 01:00 | 196 | 193
2017-02-24 01:30 | 196 | 192
2017-02-24 02:00 | 197 | 193
2017-02-24 02:30 | 196 | 193
2017-02-24 03:00 | 197 | 194
2017-02-24 03:30 | 196 | 193
2017-02-24 04:00 | 200 | 197
2017-02-24 04:30 | 205 | 202
2017-02-24 05:00 | 214 | 212
2017-02-24 05:30 | 222 | 220
2017-02-24 06:00 | 236 | 235
2017-02-24 06:30 | 249 | 248
2017-02-24 07:00 | 271 | 271
2017-02-24 07:30 | 283 | 283
2017-02-24 08:00 | 288 | 288
2017-02-24 08:30 | 293 | 292
2017-02-24 09:00 | 300 | 300
2017-02-24 09:30 | 303 | 303
2017-02-24 10:00 | 307 | 307
2017-02-24 10:30 | 315 | 315
2017-02-24 11:00 | 322 | 322
2017-02-24 11:30 | 324 | 324
2017-02-24 12:00 | 312 | 312
2017-02-24 12:30 | 314 | 314
2017-02-24 13:00 | 325 | 325
2017-02-24 13:30 | 336 | 336
2017-02-24 14:00 | 324 | 323
2017-02-24 14:30 | 322 | 321
2017-02-24 15:00 | 326 | 325
2017-02-24 15:30 | 331 | 331
2017-02-24 16:00 | 332 | 332
2017-02-24 16:30 | 337 | 337
2017-02-24 17:00 | 328 | 328
2017-02-24 17:30 | 323 | 323
2017-02-24 18:00 | 316 | 316
2017-02-24 18:30 | 323 | 323
2017-02-24 19:00 | 323 | 323
2017-02-24 19:30 | 319 | 319
2017-02-24 20:00 | 307 | 307
2017-02-24 20:30 | 296 | 296
2017-02-24 21:00 | 288 | 288
2017-02-24 21:30 | 278 | 277
2017-02-24 22:00 | 265 | 265
2017-02-24 22:30 | 251 | 251
2017-02-24 23:00 | 228 | 228
2017-02-24 23:30 | 211 | 211
2017-02-25 | 203 | 203
2017-02-25 00:30 | 198 | 198
2017-02-25 01:00 | 189 | 189
2017-02-25 01:30 | 184 | 184
2017-02-25 02:00 | 183 | 183
2017-02-25 02:30 | 184 | 184
2017-02-25 03:00 | 183 | 183
2017-02-25 03:30 | 184 | 184
2017-02-25 04:00 | 184 | 184
2017-02-25 04:30 | 184 | 184
2017-02-25 05:00 | 188 | 188
2017-02-25 05:30 | 191 | 191
2017-02-25 06:00 | 201 | 201
2017-02-25 06:30 | 208 | 208
2017-02-25 07:00 | 223 | 223
2017-02-25 07:30 | 235 | 234
2017-02-25 08:00 | 240 | 238
2017-02-25 08:30 | 244 | 243
2017-02-25 09:00 | 245 | 243
2017-02-25 09:30 | 250 | 248
2017-02-25 10:00 | 254 | 253
2017-02-25 10:30 | 258 | 258
2017-02-25 11:00 | 260 | 260
2017-02-25 11:30 | 260 | 260
2017-02-25 12:00 | 259 | 259
2017-02-25 12:30 | 262 | 262
2017-02-25 13:00 | 262 | 262
2017-02-25 13:30 | 261 | 260
2017-02-25 14:00 | 263 | 263
2017-02-25 14:30 | 265 | 265
2017-02-25 15:00 | 270 | 270
2017-02-25 15:30 | 274 | 274
2017-02-25 16:00 | 279 | 278
2017-02-25 16:30 | 282 | 282
2017-02-25 17:00 | 281 | 281
2017-02-25 17:30 | 285 | 285
2017-02-25 18:00 | 286 | 285
2017-02-25 18:30 | 289 | 289
2017-02-25 19:00 | 285 | 285
2017-02-25 19:30 | 283 | 283
2017-02-25 20:00 | 274 | 274
2017-02-25 20:30 | 266 | 266
2017-02-25 21:00 | 256 | 256
2017-02-25 21:30 | 244 | 244
2017-02-25 22:00 | 242 | 241
2017-02-25 22:30 | 234 | 234
2017-02-25 23:00 | 215 | 215
2017-02-25 23:30 | 203 | 203
2017-02-26 | 196 | 196
2017-02-26 00:30 | 194 | 194
2017-02-26 01:00 | 191 | 191
2017-02-26 01:30 | 189 | 189
2017-02-26 02:00 | 188 | 188
2017-02-26 02:30 | 185 | 185
2017-02-26 03:00 | 183 | 183
2017-02-26 03:30 | 183 | 183
2017-02-26 04:00 | 186 | 186
2017-02-26 04:30 | 186 | 186
2017-02-26 05:00 | 188 | 187
2017-02-26 05:30 | 190 | 190
2017-02-26 06:00 | 193 | 193
2017-02-26 06:30 | 196 | 196
2017-02-26 07:00 | 206 | 206
2017-02-26 07:30 | 216 | 216
2017-02-26 08:00 | 225 | 224
2017-02-26 08:30 | 230 | 228
2017-02-26 09:00 | 236 | 236
2017-02-26 09:30 | 242 | 242
2017-02-26 10:00 | 242 | 242
2017-02-26 10:30 | 240 | 240
2017-02-26 11:00 | 238 | 238
2017-02-26 11:30 | 238 | 238
2017-02-26 12:00 | 245 | 245
2017-02-26 12:30 | 252 | 252
2017-02-26 13:00 | 249 | 249
2017-02-26 13:30 | 260 | 260
2017-02-26 14:00 | 262 | 262
2017-02-26 14:30 | 271 | 271
2017-02-26 15:00 | 272 | 272
2017-02-26 15:30 | 271 | 271
2017-02-26 16:00 | 275 | 275
2017-02-26 16:30 | 282 | 282
2017-02-26 17:00 | 280 | 280
2017-02-26 17:30 | 280 | 280
2017-02-26 18:00 | 282 | 282
2017-02-26 18:30 | 290 | 290
2017-02-26 19:00 | 285 | 285
2017-02-26 19:30 | 280 | 280
2017-02-26 20:00 | 273 | 273
2017-02-26 20:30 | 261 | 260
2017-02-26 21:00 | 252 | 251
2017-02-26 21:30 | 244 | 243
2017-02-26 22:00 | 238 | 237
2017-02-26 22:30 | 230 | 230
2017-02-26 23:00 | 216 | 216
2017-02-26 23:30 | 205 | 205
2017-02-27 | 194 | 194
2017-02-27 00:30 | 192 | 192
2017-02-27 01:00 | 188 | 188
2017-02-27 01:30 | 187 | 187
2017-02-27 02:00 | 186 | 186
2017-02-27 02:30 | 184 | 184
2017-02-27 03:00 | 186 | 186
2017-02-27 03:30 | 187 | 187
2017-02-27 04:00 | 192 | 192
2017-02-27 04:30 | 203 | 203
2017-02-27 05:00 | 208 | 208
2017-02-27 05:30 | 214 | 214
2017-02-27 06:00 | 226 | 226
2017-02-27 06:30 | 241 | 241
2017-02-27 07:00 | 258 | 258
2017-02-27 07:30 | 267 | 267
2017-02-27 08:00 | 272 | 271
2017-02-27 08:30 | 281 | 279
2017-02-27 09:00 | 287 | 285
2017-02-27 09:30 | 289 | 287
2017-02-27 10:00 | 287 | 285
2017-02-27 10:30 | 284 | 282
2017-02-27 11:00 | 282 | 280
2017-02-27 11:30 | 289 | 287
2017-02-27 12:00 | 290 | 290
2017-02-27 12:30 | 283 | 283
2017-02-27 13:00 | 283 | 282
2017-02-27 13:30 | 278 | 277
2017-02-27 14:00 | 281 | 280
2017-02-27 14:30 | 277 | 276
2017-02-27 15:00 | 268 | 267
2017-02-27 15:30 | 274 | 272
2017-02-27 16:00 | 272 | 270
2017-02-27 16:30 | 277 | 275
2017-02-27 17:00 | 275 | 272
2017-02-27 17:30 | 279 | 276
2017-02-27 18:00 | 276 | 275
2017-02-27 18:30 | 283 | 282
2017-02-27 19:00 | 283 | 282
2017-02-27 19:30 | 278 | 277
2017-02-27 20:00 | 271 | 268
2017-02-27 20:30 | 256 | 255
2017-02-27 21:00 | 245 | 245
2017-02-27 21:30 | 235 | 234
2017-02-27 22:00 | 227 | 226
2017-02-27 22:30 | 221 | 220
2017-02-27 23:00 | 207 | 205
2017-02-27 23:30 | 197 | 195
2017-02-28 | 187 | 184
2017-02-28 00:30 | 186 | 182
2017-02-28 01:00 | 185 | 181
2017-02-28 01:30 | 185 | 180
2017-02-28 02:00 | 185 | 181
2017-02-28 02:30 | 182 | 178
2017-02-28 03:00 | 184 | 180
2017-02-28 03:30 | 186 | 183
2017-02-28 04:00 | 191 | 188
2017-02-28 04:30 | 192 | 189
2017-02-28 05:00 | 202 | 200
2017-02-28 05:30 | 210 | 209
2017-02-28 06:00 | 224 | 223
2017-02-28 06:30 | 245 | 244
2017-02-28 07:00 | 263 | 263
2017-02-28 07:30 | 273 | 273
2017-02-28 08:00 | 274 | 274
2017-02-28 08:30 | 276 | 275
2017-02-28 09:00 | 275 | 275
2017-02-28 09:30 | 275 | 275
2017-02-28 10:00 | 271 | 271
2017-02-28 10:30 | 270 | 270
2017-02-28 11:00 | 271 | 271
2017-02-28 11:30 | 273 | 273
2017-02-28 12:00 | 276 | 276
2017-02-28 12:30 | 274 | 274
2017-02-28 13:00 | 275 | 275
2017-02-28 13:30 | 275 | 274
2017-02-28 14:00 | 281 | 281
2017-02-28 14:30 | 285 | 284
2017-02-28 15:00 | 291 | 291
2017-02-28 15:30 | 299 | 298
2017-02-28 16:00 | 303 | 302
2017-02-28 16:30 | 310 | 309
2017-02-28 17:00 | 308 | 305
2017-02-28 17:30 | 301 | 299
2017-02-28 18:00 | 296 | 295
2017-02-28 18:30 | 300 | 300
2017-02-28 19:00 | 294 | 294
2017-02-28 19:30 | 288 | 286
2017-02-28 20:00 | 279 | 278
2017-02-28 20:30 | 263 | 263
2017-02-28 21:00 | 254 | 253
2017-02-28 21:30 | 243 | 241
2017-02-28 22:00 | 232 | 232
2017-02-28 22:30 | 224 | 224
2017-02-28 23:00 | 206 | 206
2017-02-28 23:30 | 197 | 197
2017-03-01 | 192 | 192
2017-03-01 00:30 | 191 | 190
2017-03-01 01:00 | 188 | 188
2017-03-01 01:30 | 186 | 185
2017-03-01 02:00 | 186 | 185
2017-03-01 02:30 | 183 | 182
2017-03-01 03:00 | 184 | 183
2017-03-01 03:30 | 188 | 188
2017-03-01 04:00 | 189 | 188
2017-03-01 04:30 | 191 | 191
2017-03-01 05:00 | 202 | 201
2017-03-01 05:30 | 211 | 211
2017-03-01 06:00 | 231 | 231
2017-03-01 06:30 | 246 | 245
2017-03-01 07:00 | 259 | 258
2017-03-01 07:30 | 272 | 271
2017-03-01 08:00 | 273 | 272
2017-03-01 08:30 | 279 | 278
2017-03-01 09:00 | 285 | 285
2017-03-01 09:30 | 292 | 292
2017-03-01 10:00 | 294 | 294
2017-03-01 10:30 | 297 | 297
2017-03-01 11:00 | 300 | 300
2017-03-01 11:30 | 306 | 304
2017-03-01 12:00 | 308 | 306
2017-03-01 12:30 | 307 | 306
2017-03-01 13:00 | 311 | 310
2017-03-01 13:30 | 312 | 311
2017-03-01 14:00 | 322 | 318
2017-03-01 14:30 | 329 | 323
2017-03-01 15:00 | 341 | 336
2017-03-01 15:30 | 341 | 335
2017-03-01 16:00 | 327 | 322
2017-03-01 16:30 | 330 | 324
2017-03-01 17:00 | 326 | 321
2017-03-01 17:30 | 323 | 320
2017-03-01 18:00 | 317 | 314
2017-03-01 18:30 | 321 | 319
2017-03-01 19:00 | 312 | 310
2017-03-01 19:30 | 311 | 309
2017-03-01 20:00 | 303 | 301
2017-03-01 20:30 | 291 | 288
2017-03-01 21:00 | 279 | 275
2017-03-01 21:30 | 265 | 260
2017-03-01 22:00 | 253 | 249
2017-03-01 22:30 | 246 | 241
2017-03-01 23:00 | 224 | 221
2017-03-01 23:30 | 214 | 212
2017-03-02 | 206 | 204
2017-03-02 00:30 | 199 | 196
2017-03-02 01:00 | 194 | 191
2017-03-02 01:30 | 193 | 190
2017-03-02 02:00 | 191 | 188
2017-03-02 02:30 | 191 | 188
2017-03-02 03:00 | 192 | 189
2017-03-02 03:30 | 187 | 185
2017-03-02 04:00 | 194 | 192
2017-03-02 04:30 | 200 | 198
2017-03-02 05:00 | 211 | 209
2017-03-02 05:30 | 218 | 217
2017-03-02 06:00 | 236 | 236
2017-03-02 06:30 | 253 | 253
2017-03-02 07:00 | 271 | 271
2017-03-02 07:30 | 281 | 281
2017-03-02 08:00 | 288 | 288
2017-03-02 08:30 | 290 | 290
2017-03-02 09:00 | 303 | 303
2017-03-02 09:30 | 316 | 312
2017-03-02 10:00 | 316 | 312
2017-03-02 10:30 | 318 | 315
2017-03-02 11:00 | 323 | 321
2017-03-02 11:30 | 327 | 324
2017-03-02 12:00 | 328 | 324
2017-03-02 12:30 | 325 | 321
2017-03-02 13:00 | 327 | 322
2017-03-02 13:30 | 333 | 329
2017-03-02 14:00 | 339 | 335
2017-03-02 14:30 | 344 | 340
2017-03-02 15:00 | 343 | 339
2017-03-02 15:30 | 346 | 342
2017-03-02 16:00 | 349 | 345
2017-03-02 16:30 | 348 | 343
2017-03-02 17:00 | 344 | 339
2017-03-02 17:30 | 344 | 340
2017-03-02 18:00 | 339 | 335
2017-03-02 18:30 | 343 | 340
2017-03-02 19:00 | 339 | 335
2017-03-02 19:30 | 326 | 325
2017-03-02 20:00 | 318 | 317
2017-03-02 20:30 | 308 | 306
2017-03-02 21:00 | 294 | 291
2017-03-02 21:30 | 278 | 274
2017-03-02 22:00 | 263 | 261
2017-03-02 22:30 | 251 | 250
2017-03-02 23:00 | 232 | 231
2017-03-02 23:30 | 223 | 222
2017-03-03 | 209 | 208
2017-03-03 00:30 | 203 | 201
2017-03-03 01:00 | 201 | 199
2017-03-03 01:30 | 198 | 196
2017-03-03 02:00 | 195 | 192
2017-03-03 02:30 | 192 | 189
2017-03-03 03:00 | 190 | 187
2017-03-03 03:30 | 192 | 190
2017-03-03 04:00 | 199 | 196
2017-03-03 04:30 | 203 | 201
2017-03-03 05:00 | 209 | 207
2017-03-03 05:30 | 216 | 215
2017-03-03 06:00 | 231 | 230
2017-03-03 06:30 | 251 | 251
2017-03-03 07:00 | 270 | 270
2017-03-03 07:30 | 280 | 280
2017-03-03 08:00 | 291 | 290
2017-03-03 08:30 | 295 | 294
2017-03-03 09:00 | 303 | 303
2017-03-03 09:30 | 306 | 306
2017-03-03 10:00 | 306 | 306
2017-03-03 10:30 | 311 | 311
2017-03-03 11:00 | 317 | 317
2017-03-03 11:30 | 343 | 343
2017-03-03 12:00 | 350 | 349
2017-03-03 12:30 | 362 | 361
2017-03-03 13:00 | 361 | 360
2017-03-03 13:30 | 365 | 365
2017-03-03 14:00 | 373 | 372
2017-03-03 14:30 | 344 | 343
2017-03-03 15:00 | 333 | 333
2017-03-03 15:30 | 337 | 337
2017-03-03 16:00 | 342 | 342
2017-03-03 16:30 | 345 | 345
2017-03-03 17:00 | 333 | 332
2017-03-03 17:30 | 322 | 322
2017-03-03 18:00 | 323 | 323
2017-03-03 18:30 | 330 | 330
2017-03-03 19:00 | 325 | 325
2017-03-03 19:30 | 320 | 320
2017-03-03 20:00 | 311 | 310
2017-03-03 20:30 | 299 | 299
2017-03-03 21:00 | 289 | 289
2017-03-03 21:30 | 279 | 279
2017-03-03 22:00 | 268 | 268
2017-03-03 22:30 | 259 | 259
2017-03-03 23:00 | 238 | 238
2017-03-03 23:30 | 226 | 226
2017-03-04 | 215 | 215
2017-03-04 00:30 | 209 | 209
2017-03-04 01:00 | 207 | 206
2017-03-04 01:30 | 204 | 204
2017-03-04 02:00 | 200 | 200
2017-03-04 02:30 | 193 | 193
2017-03-04 03:00 | 190 | 190
2017-03-04 03:30 | 190 | 190
2017-03-04 04:00 | 193 | 193
2017-03-04 04:30 | 198 | 198
2017-03-04 05:00 | 203 | 203
2017-03-04 05:30 | 205 | 205
2017-03-04 06:00 | 211 | 211
2017-03-04 06:30 | 222 | 222
2017-03-04 07:00 | 241 | 240
2017-03-04 07:30 | 249 | 248
2017-03-04 08:00 | 265 | 265
2017-03-04 08:30 | 274 | 273
2017-03-04 09:00 | 286 | 285
2017-03-04 09:30 | 286 | 285
2017-03-04 10:00 | 293 | 291
2017-03-04 10:30 | 299 | 298
2017-03-04 11:00 | 302 | 301
2017-03-04 11:30 | 309 | 308
2017-03-04 12:00 | 308 | 307
2017-03-04 12:30 | 288 | 287
2017-03-04 13:00 | 287 | 285
2017-03-04 13:30 | 295 | 294
2017-03-04 14:00 | 310 | 309
2017-03-04 14:30 | 317 | 315
2017-03-04 15:00 | 326 | 325
2017-03-04 15:30 | 326 | 325
2017-03-04 16:00 | 324 | 323
2017-03-04 16:30 | 324 | 323
2017-03-04 17:00 | 323 | 322
2017-03-04 17:30 | 320 | 319
2017-03-04 18:00 | 315 | 315
2017-03-04 18:30 | 316 | 315
2017-03-04 19:00 | 313 | 313
2017-03-04 19:30 | 308 | 308
2017-03-04 20:00 | 300 | 299
2017-03-04 20:30 | 290 | 289
2017-03-04 21:00 | 279 | 279
2017-03-04 21:30 | 267 | 267
2017-03-04 22:00 | 260 | 259
2017-03-04 22:30 | 245 | 245
2017-03-04 23:00 | 232 | 232
2017-03-04 23:30 | 222 | 221
2017-03-05 | 213 | 213
2017-03-05 00:30 | 209 | 209
2017-03-05 01:00 | 206 | 205
2017-03-05 01:30 | 204 | 203
2017-03-05 02:00 | 201 | 199
2017-03-05 02:30 | 198 | 197
2017-03-05 03:00 | 197 | 196
2017-03-05 03:30 | 197 | 196
2017-03-05 04:00 | 198 | 197
2017-03-05 04:30 | 198 | 197
2017-03-05 05:00 | 202 | 200
2017-03-05 05:30 | 201 | 200
2017-03-05 06:00 | 207 | 206
2017-03-05 06:30 | 212 | 211
2017-03-05 07:00 | 220 | 218
2017-03-05 07:30 | 223 | 221
2017-03-05 08:00 | 239 | 236
2017-03-05 08:30 | 248 | 248
2017-03-05 09:00 | 259 | 258
2017-03-05 09:30 | 257 | 256
2017-03-05 10:00 | 262 | 261
2017-03-05 10:30 | 270 | 270
2017-03-05 11:00 | 272 | 272
2017-03-05 11:30 | 275 | 275
2017-03-05 12:00 | 278 | 278
2017-03-05 12:30 | 276 | 276
2017-03-05 13:00 | 282 | 282
2017-03-05 13:30 | 289 | 289
2017-03-05 14:00 | 291 | 291
2017-03-05 14:30 | 293 | 293
2017-03-05 15:00 | 299 | 299
2017-03-05 15:30 | 300 | 300
2017-03-05 16:00 | 311 | 311
2017-03-05 16:30 | 319 | 319
2017-03-05 17:00 | 320 | 320
2017-03-05 17:30 | 319 | 319
2017-03-05 18:00 | 317 | 317
2017-03-05 18:30 | 327 | 327
2017-03-05 19:00 | 319 | 319
2017-03-05 19:30 | 307 | 307
2017-03-05 20:00 | 298 | 297
2017-03-05 20:30 | 290 | 289
2017-03-05 21:00 | 274 | 274
2017-03-05 21:30 | 261 | 260
2017-03-05 22:00 | 251 | 251
2017-03-05 22:30 | 246 | 246
2017-03-05 23:00 | 227 | 226
2017-03-05 23:30 | 215 | 215
2017-03-06 | 203 | 203
2017-03-06 00:30 | 197 | 197
2017-03-06 01:00 | 192 | 192
2017-03-06 01:30 | 190 | 189
2017-03-06 02:00 | 189 | 188
2017-03-06 02:30 | 186 | 185
2017-03-06 03:00 | 186 | 185
2017-03-06 03:30 | 188 | 187
2017-03-06 04:00 | 198 | 197
2017-03-06 04:30 | 201 | 200
2017-03-06 05:00 | 210 | 209
2017-03-06 05:30 | 217 | 216
2017-03-06 06:00 | 230 | 229
2017-03-06 06:30 | 249 | 248
2017-03-06 07:00 | 265 | 265
2017-03-06 07:30 | 275 | 274
2017-03-06 08:00 | 278 | 278
2017-03-06 08:30 | 283 | 283
2017-03-06 09:00 | 286 | 286
2017-03-06 09:30 | 293 | 293
2017-03-06 10:00 | 293 | 292
2017-03-06 10:30 | 299 | 299
2017-03-06 11:00 | 305 | 304
2017-03-06 11:30 | 306 | 305
2017-03-06 12:00 | 305 | 305
2017-03-06 12:30 | 306 | 306
2017-03-06 13:00 | 305 | 305
2017-03-06 13:30 | 301 | 300
2017-03-06 14:00 | 301 | 301
2017-03-06 14:30 | 304 | 303
2017-03-06 15:00 | 310 | 309
2017-03-06 15:30 | 318 | 317
2017-03-06 16:00 | 323 | 322
2017-03-06 16:30 | 328 | 328
2017-03-06 17:00 | 325 | 324
2017-03-06 17:30 | 321 | 320
2017-03-06 18:00 | 318 | 318
2017-03-06 18:30 | 319 | 319
2017-03-06 19:00 | 311 | 311
2017-03-06 19:30 | 311 | 311
2017-03-06 20:00 | 301 | 301
2017-03-06 20:30 | 283 | 283
2017-03-06 21:00 | 268 | 268
2017-03-06 21:30 | 256 | 256
2017-03-06 22:00 | 248 | 248
2017-03-06 22:30 | 239 | 239
2017-03-06 23:00 | 221 | 221
2017-03-06 23:30 | 210 | 210
2017-03-07 | 198 | 198
2017-03-07 00:30 | 194 | 193
2017-03-07 01:00 | 185 | 185
2017-03-07 01:30 | 190 | 190
2017-03-07 02:00 | 183 | 183
2017-03-07 02:30 | 182 | 182
2017-03-07 03:00 | 178 | 178
2017-03-07 03:30 | 175 | 175
2017-03-07 04:00 | 193 | 193
2017-03-07 04:30 | 196 | 196
2017-03-07 05:00 | 203 | 202
2017-03-07 05:30 | 206 | 206
2017-03-07 06:00 | 224 | 224
2017-03-07 06:30 | 243 | 242
2017-03-07 07:00 | 256 | 256
2017-03-07 07:30 | 262 | 262
2017-03-07 08:00 | 268 | 267
2017-03-07 08:30 | 270 | 270
2017-03-07 09:00 | 268 | 268
2017-03-07 09:30 | 269 | 269
2017-03-07 10:00 | 269 | 269
2017-03-07 10:30 | 270 | 270
2017-03-07 11:00 | 270 | 270
2017-03-07 11:30 | 273 | 273
2017-03-07 12:00 | 270 | 270
2017-03-07 12:30 | 272 | 272
2017-03-07 13:00 | 276 | 276
2017-03-07 13:30 | 284 | 284
2017-03-07 14:00 | 287 | 287
2017-03-07 14:30 | 284 | 284
2017-03-07 15:00 | 289 | 289
2017-03-07 15:30 | 300 | 299
2017-03-07 16:00 | 308 | 308
2017-03-07 16:30 | 311 | 311
2017-03-07 17:00 | 308 | 307
2017-03-07 17:30 | 302 | 302
2017-03-07 18:00 | 300 | 300
2017-03-07 18:30 | 307 | 307
2017-03-07 19:00 | 300 | 299
2017-03-07 19:30 | 293 | 293
2017-03-07 20:00 | 281 | 281
2017-03-07 20:30 | 264 | 264
2017-03-07 21:00 | 252 | 251
2017-03-07 21:30 | 238 | 238
2017-03-07 22:00 | 233 | 233
2017-03-07 22:30 | 228 | 228
2017-03-07 23:00 | 212 | 212
2017-03-07 23:30 | 197 | 197
2017-03-08 | 186 | 186
2017-03-08 00:30 | 180 | 180
2017-03-08 01:00 | 174 | 174
2017-03-08 01:30 | 171 | 171
2017-03-08 02:00 | 172 | 172
2017-03-08 02:30 | 174 | 174
2017-03-08 03:00 | 175 | 175
2017-03-08 03:30 | 176 | 175
2017-03-08 04:00 | 179 | 178
2017-03-08 04:30 | 184 | 183
2017-03-08 05:00 | 196 | 195
2017-03-08 05:30 | 210 | 208
2017-03-08 06:00 | 228 | 227
2017-03-08 06:30 | 245 | 245
2017-03-08 07:00 | 257 | 255
2017-03-08 07:30 | 258 | 256
2017-03-08 08:00 | 264 | 264
2017-03-08 08:30 | 269 | 269
2017-03-08 09:00 | 274 | 274
2017-03-08 09:30 | 271 | 271
2017-03-08 10:00 | 264 | 264
2017-03-08 10:30 | 269 | 269
2017-03-08 11:00 | 269 | 269
2017-03-08 11:30 | 265 | 265
2017-03-08 12:00 | 285 | 285
2017-03-08 12:30 | 291 | 291
2017-03-08 13:00 | 297 | 297
2017-03-08 13:30 | 315 | 314
2017-03-08 14:00 | 320 | 319
2017-03-08 14:30 | 318 | 317
2017-03-08 15:00 | 319 | 317
2017-03-08 15:30 | 317 | 315
2017-03-08 16:00 | 327 | 325
2017-03-08 16:30 | 332 | 330
2017-03-08 17:00 | 332 | 330
2017-03-08 17:30 | 332 | 330
2017-03-08 18:00 | 327 | 326
2017-03-08 18:30 | 327 | 326
2017-03-08 19:00 | 320 | 319
2017-03-08 19:30 | 315 | 314
2017-03-08 20:00 | 308 | 306
2017-03-08 20:30 | 295 | 292
2017-03-08 21:00 | 284 | 282
2017-03-08 21:30 | 276 | 273
2017-03-08 22:00 | 264 | 263
2017-03-08 22:30 | 257 | 256
2017-03-08 23:00 | 234 | 234
2017-03-08 23:30 | 223 | 223
2017-03-09 | 207 | 207
2017-03-09 00:30 | 200 | 200
2017-03-09 01:00 | 198 | 198
2017-03-09 01:30 | 198 | 198
2017-03-09 02:00 | 199 | 198
2017-03-09 02:30 | 200 | 200
2017-03-09 03:00 | 197 | 197
2017-03-09 03:30 | 193 | 193
2017-03-09 04:00 | 198 | 198
2017-03-09 04:30 | 210 | 210
2017-03-09 05:00 | 221 | 221
2017-03-09 05:30 | 227 | 227
2017-03-09 06:00 | 266 | 266
2017-03-09 06:30 | 298 | 297
2017-03-09 07:00 | 304 | 304
2017-03-09 07:30 | 318 | 318
2017-03-09 08:00 | 322 | 322
2017-03-09 08:30 | 319 | 319
2017-03-09 09:00 | 320 | 319
2017-03-09 09:30 | 325 | 324
2017-03-09 10:00 | 321 | 321
2017-03-09 10:30 | 323 | 323
2017-03-09 11:00 | 322 | 322
2017-03-09 11:30 | 327 | 327
2017-03-09 12:00 | 333 | 333
2017-03-09 12:30 | 339 | 338
2017-03-09 13:00 | 343 | 343
2017-03-09 13:30 | 348 | 347
2017-03-09 14:00 | 335 | 335
2017-03-09 14:30 | 312 | 311
2017-03-09 15:00 | 314 | 313
2017-03-09 15:30 | 316 | 315
2017-03-09 16:00 | 306 | 306
2017-03-09 16:30 | 312 | 311
2017-03-09 17:00 | 313 | 312
2017-03-09 17:30 | 310 | 309
2017-03-09 18:00 | 313 | 313
2017-03-09 18:30 | 324 | 323
2017-03-09 19:00 | 314 | 314
2017-03-09 19:30 | 310 | 309
2017-03-09 20:00 | 302 | 302
2017-03-09 20:30 | 288 | 288
2017-03-09 21:00 | 276 | 276
2017-03-09 21:30 | 259 | 259
2017-03-09 22:00 | 254 | 254
2017-03-09 22:30 | 246 | 246
2017-03-09 23:00 | 226 | 226
2017-03-09 23:30 | 212 | 212
2017-03-10 | 199 | 199
2017-03-10 00:30 | 193 | 193
2017-03-10 01:00 | 190 | 190
2017-03-10 01:30 | 184 | 184
2017-03-10 02:00 | 183 | 183
2017-03-10 02:30 | 185 | 184
2017-03-10 03:00 | 186 | 186
2017-03-10 03:30 | 185 | 185
2017-03-10 04:00 | 187 | 187
2017-03-10 04:30 | 191 | 191
2017-03-10 05:00 | 203 | 203
2017-03-10 05:30 | 210 | 209
2017-03-10 06:00 | 226 | 225
2017-03-10 06:30 | 243 | 242
2017-03-10 07:00 | 263 | 262
2017-03-10 07:30 | 268 | 268
2017-03-10 08:00 | 270 | 270
2017-03-10 08:30 | 269 | 269
2017-03-10 09:00 | 270 | 270
2017-03-10 09:30 | 270 | 270
2017-03-10 10:00 | 270 | 269
2017-03-10 10:30 | 270 | 269
2017-03-10 11:00 | 274 | 273
2017-03-10 11:30 | 279 | 279
2017-03-10 12:00 | 284 | 284
2017-03-10 12:30 | 285 | 285
2017-03-10 13:00 | 288 | 288
2017-03-10 13:30 | 292 | 292
2017-03-10 14:00 | 293 | 293
2017-03-10 14:30 | 297 | 297
2017-03-10 15:00 | 299 | 298
2017-03-10 15:30 | 304 | 303
2017-03-10 16:00 | 307 | 306
2017-03-10 16:30 | 312 | 311
2017-03-10 17:00 | 308 | 306
2017-03-10 17:30 | 302 | 300
2017-03-10 18:00 | 300 | 299
2017-03-10 18:30 | 303 | 303
2017-03-10 19:00 | 299 | 298
2017-03-10 19:30 | 289 | 289
2017-03-10 20:00 | 282 | 282
2017-03-10 20:30 | 277 | 277
2017-03-10 21:00 | 271 | 271
2017-03-10 21:30 | 260 | 260
2017-03-10 22:00 | 253 | 253
2017-03-10 22:30 | 241 | 241
2017-03-10 23:00 | 225 | 225
2017-03-10 23:30 | 214 | 214
2017-03-11 | 200 | 200
2017-03-11 00:30 | 192 | 192
2017-03-11 01:00 | 186 | 186
2017-03-11 01:30 | 185 | 185
2017-03-11 02:00 | 184 | 184
2017-03-11 02:30 | 185 | 185
2017-03-11 03:00 | 186 | 185
2017-03-11 03:30 | 185 | 185
2017-03-11 04:00 | 185 | 185
2017-03-11 04:30 | 187 | 186
2017-03-11 05:00 | 189 | 189
2017-03-11 05:30 | 192 | 192
2017-03-11 06:00 | 198 | 198
2017-03-11 06:30 | 206 | 206
2017-03-11 07:00 | 217 | 216
2017-03-11 07:30 | 225 | 224
2017-03-11 08:00 | 236 | 235
2017-03-11 08:30 | 239 | 239
2017-03-11 09:00 | 243 | 243
2017-03-11 09:30 | 245 | 245
2017-03-11 10:00 | 243 | 243
2017-03-11 10:30 | 244 | 244
2017-03-11 11:00 | 248 | 248
2017-03-11 11:30 | 242 | 242
2017-03-11 12:00 | 234 | 234
2017-03-11 12:30 | 236 | 236
2017-03-11 13:00 | 238 | 238
2017-03-11 13:30 | 234 | 234
2017-03-11 14:00 | 238 | 238
2017-03-11 14:30 | 241 | 241
2017-03-11 15:00 | 245 | 245
2017-03-11 15:30 | 251 | 250
2017-03-11 16:00 | 263 | 263
2017-03-11 16:30 | 268 | 268
2017-03-11 17:00 | 268 | 268
2017-03-11 17:30 | 264 | 264
2017-03-11 18:00 | 265 | 265
2017-03-11 18:30 | 270 | 270
2017-03-11 19:00 | 262 | 262
2017-03-11 19:30 | 261 | 260
2017-03-11 20:00 | 254 | 254
2017-03-11 20:30 | 245 | 244
2017-03-11 21:00 | 238 | 237
2017-03-11 21:30 | 233 | 232
2017-03-11 22:00 | 232 | 232
2017-03-11 22:30 | 229 | 229
2017-03-11 23:00 | 212 | 212
2017-03-11 23:30 | 201 | 201
2017-03-12 | 186 | 186
2017-03-12 00:30 | 180 | 180
2017-03-12 01:00 | 178 | 178
2017-03-12 01:30 | 174 | 174
2017-03-12 02:00 | 173 | 173
2017-03-12 02:30 | 173 | 173
2017-03-12 03:00 | 173 | 173
2017-03-12 03:30 | 173 | 173
2017-03-12 04:00 | 173 | 173
2017-03-12 04:30 | 175 | 175
2017-03-12 05:00 | 178 | 178
2017-03-12 05:30 | 180 | 180
2017-03-12 06:00 | 184 | 184
2017-03-12 06:30 | 189 | 189
2017-03-12 07:00 | 203 | 203
2017-03-12 07:30 | 214 | 213
2017-03-12 08:00 | 219 | 218
2017-03-12 08:30 | 223 | 221
2017-03-12 09:00 | 223 | 222
2017-03-12 09:30 | 226 | 225
2017-03-12 10:00 | 231 | 231
2017-03-12 10:30 | 237 | 237
2017-03-12 11:00 | 241 | 241
2017-03-12 11:30 | 243 | 243
2017-03-12 12:00 | 246 | 245
2017-03-12 12:30 | 247 | 246
2017-03-12 13:00 | 250 | 249
2017-03-12 13:30 | 256 | 255
2017-03-12 14:00 | 264 | 264
2017-03-12 14:30 | 274 | 274
2017-03-12 15:00 | 283 | 283
2017-03-12 15:30 | 293 | 292
2017-03-12 16:00 | 297 | 297
2017-03-12 16:30 | 301 | 301
2017-03-12 17:00 | 301 | 300
2017-03-12 17:30 | 302 | 300
2017-03-12 18:00 | 305 | 304
2017-03-12 18:30 | 312 | 312
2017-03-12 19:00 | 306 | 305
2017-03-12 19:30 | 302 | 301
2017-03-12 20:00 | 288 | 288
2017-03-12 20:30 | 274 | 274
2017-03-12 21:00 | 262 | 262
2017-03-12 21:30 | 246 | 246
2017-03-12 22:00 | 244 | 244
2017-03-12 22:30 | 240 | 239
2017-03-12 23:00 | 222 | 221
2017-03-12 23:30 | 210 | 209
2017-03-13 | 198 | 197
2017-03-13 00:30 | 189 | 189
2017-03-13 01:00 | 184 | 184
2017-03-13 01:30 | 182 | 182
2017-03-13 02:00 | 182 | 182
2017-03-13 02:30 | 182 | 182
2017-03-13 03:00 | 181 | 181
2017-03-13 03:30 | 183 | 183
2017-03-13 04:00 | 187 | 187
2017-03-13 04:30 | 190 | 190
2017-03-13 05:00 | 202 | 201
2017-03-13 05:30 | 208 | 208
2017-03-13 06:00 | 227 | 226
2017-03-13 06:30 | 244 | 244
2017-03-13 07:00 | 265 | 265
2017-03-13 07:30 | 279 | 279
2017-03-13 08:00 | 286 | 286
2017-03-13 08:30 | 299 | 299
2017-03-13 09:00 | 305 | 305
2017-03-13 09:30 | 293 | 293
2017-03-13 10:00 | 282 | 281
2017-03-13 10:30 | 290 | 290
2017-03-13 11:00 | 298 | 298
2017-03-13 11:30 | 295 | 294
2017-03-13 12:00 | 273 | 272
2017-03-13 12:30 | 267 | 266
2017-03-13 13:00 | 286 | 286
2017-03-13 13:30 | 295 | 295
2017-03-13 14:00 | 301 | 300
2017-03-13 14:30 | 300 | 300
2017-03-13 15:00 | 301 | 300
2017-03-13 15:30 | 299 | 298
2017-03-13 16:00 | 303 | 303
2017-03-13 16:30 | 305 | 304
2017-03-13 17:00 | 305 | 304
2017-03-13 17:30 | 308 | 306
2017-03-13 18:00 | 311 | 311
2017-03-13 18:30 | 313 | 313
2017-03-13 19:00 | 309 | 308
2017-03-13 19:30 | 302 | 301
2017-03-13 20:00 | 291 | 289
2017-03-13 20:30 | 273 | 272
2017-03-13 21:00 | 258 | 257
2017-03-13 21:30 | 249 | 247
2017-03-13 22:00 | 238 | 238
2017-03-13 22:30 | 235 | 234
2017-03-13 23:00 | 218 | 217
2017-03-13 23:30 | 208 | 207
2017-03-14 | 196 | 196
2017-03-14 00:30 | 190 | 190
2017-03-14 01:00 | 188 | 188
2017-03-14 01:30 | 184 | 184
2017-03-14 02:00 | 185 | 185
2017-03-14 02:30 | 185 | 185
2017-03-14 03:00 | 185 | 185
2017-03-14 03:30 | 184 | 183
2017-03-14 04:00 | 187 | 187
2017-03-14 04:30 | 192 | 192
2017-03-14 05:00 | 202 | 202
2017-03-14 05:30 | 218 | 218
2017-03-14 06:00 | 236 | 235
2017-03-14 06:30 | 252 | 252
2017-03-14 07:00 | 274 | 274
2017-03-14 07:30 | 287 | 287
2017-03-14 08:00 | 295 | 295
2017-03-14 08:30 | 301 | 300
2017-03-14 09:00 | 306 | 306
2017-03-14 09:30 | 311 | 311
2017-03-14 10:00 | 307 | 306
2017-03-14 10:30 | 298 | 297
2017-03-14 11:00 | 306 | 305
2017-03-14 11:30 | 314 | 314
2017-03-14 12:00 | 309 | 308
2017-03-14 12:30 | 276 | 275
2017-03-14 13:00 | 274 | 274
2017-03-14 13:30 | 282 | 282
2017-03-14 14:00 | 296 | 296
2017-03-14 14:30 | 287 | 287
2017-03-14 15:00 | 286 | 286
2017-03-14 15:30 | 290 | 290
2017-03-14 16:00 | 301 | 301
2017-03-14 16:30 | 307 | 307
2017-03-14 17:00 | 306 | 306
2017-03-14 17:30 | 305 | 305
2017-03-14 18:00 | 306 | 305
2017-03-14 18:30 | 315 | 315
2017-03-14 19:00 | 310 | 309
2017-03-14 19:30 | 306 | 305
2017-03-14 20:00 | 296 | 295
2017-03-14 20:30 | 278 | 277
2017-03-14 21:00 | 259 | 259
2017-03-14 21:30 | 247 | 246
2017-03-14 22:00 | 241 | 240
2017-03-14 22:30 | 234 | 234
2017-03-14 23:00 | 216 | 216
2017-03-14 23:30 | 204 | 204
2017-03-15 | 187 | 186
2017-03-15 00:30 | 180 | 179
2017-03-15 01:00 | 175 | 174
2017-03-15 01:30 | 176 | 175
2017-03-15 02:00 | 175 | 174
2017-03-15 02:30 | 175 | 174
2017-03-15 03:00 | 175 | 174
2017-03-15 03:30 | 174 | 173
2017-03-15 04:00 | 180 | 179
2017-03-15 04:30 | 183 | 182
2017-03-15 05:00 | 196 | 195
2017-03-15 05:30 | 207 | 207
2017-03-15 06:00 | 219 | 218
2017-03-15 06:30 | 248 | 247
2017-03-15 07:00 | 269 | 269
2017-03-15 07:30 | 277 | 276
2017-03-15 08:00 | 283 | 283
2017-03-15 08:30 | 292 | 292
2017-03-15 09:00 | 300 | 300
2017-03-15 09:30 | 299 | 299
2017-03-15 10:00 | 293 | 293
2017-03-15 10:30 | 312 | 312
2017-03-15 11:00 | 321 | 320
2017-03-15 11:30 | 306 | 304
2017-03-15 12:00 | 305 | 303
2017-03-15 12:30 | 304 | 303
2017-03-15 13:00 | 305 | 304
2017-03-15 13:30 | 313 | 311
2017-03-15 14:00 | 307 | 305
2017-03-15 14:30 | 308 | 306
2017-03-15 15:00 | 310 | 308
2017-03-15 15:30 | 322 | 320
2017-03-15 16:00 | 321 | 319
2017-03-15 16:30 | 320 | 319
2017-03-15 17:00 | 319 | 318
2017-03-15 17:30 | 319 | 317
2017-03-15 18:00 | 320 | 319
2017-03-15 18:30 | 329 | 328
2017-03-15 19:00 | 322 | 321
2017-03-15 19:30 | 318 | 317
2017-03-15 20:00 | 311 | 309
2017-03-15 20:30 | 286 | 285
2017-03-15 21:00 | 270 | 270
2017-03-15 21:30 | 259 | 259
2017-03-15 22:00 | 253 | 253
2017-03-15 22:30 | 247 | 247
2017-03-15 23:00 | 228 | 228
2017-03-15 23:30 | 214 | 214
2017-03-16 | 196 | 196
2017-03-16 00:30 | 188 | 188
2017-03-16 01:00 | 185 | 185
2017-03-16 01:30 | 182 | 182
2017-03-16 02:00 | 179 | 179
2017-03-16 02:30 | 178 | 178
2017-03-16 03:00 | 181 | 181
2017-03-16 03:30 | 184 | 184
2017-03-16 04:00 | 187 | 187
2017-03-16 04:30 | 191 | 191
2017-03-16 05:00 | 201 | 201
2017-03-16 05:30 | 214 | 214
2017-03-16 06:00 | 235 | 235
2017-03-16 06:30 | 256 | 256
2017-03-16 07:00 | 278 | 277
2017-03-16 07:30 | 289 | 289
2017-03-16 08:00 | 297 | 297
2017-03-16 08:30 | 298 | 298
2017-03-16 09:00 | 308 | 307
2017-03-16 09:30 | 307 | 307
2017-03-16 10:00 | 299 | 298
2017-03-16 10:30 | 300 | 299
2017-03-16 11:00 | 303 | 303
2017-03-16 11:30 | 301 | 301
2017-03-16 12:00 | 315 | 314
2017-03-16 12:30 | 321 | 321
2017-03-16 13:00 | 322 | 322
2017-03-16 13:30 | 322 | 322
2017-03-16 14:00 | 321 | 321
2017-03-16 14:30 | 330 | 330
2017-03-16 15:00 | 331 | 331
2017-03-16 15:30 | 338 | 338
2017-03-16 16:00 | 343 | 343
2017-03-16 16:30 | 346 | 346
2017-03-16 17:00 | 347 | 347
2017-03-16 17:30 | 345 | 344
2017-03-16 18:00 | 349 | 347
2017-03-16 18:30 | 339 | 338
2017-03-16 19:00 | 329 | 328
2017-03-16 19:30 | 323 | 321
2017-03-16 20:00 | 309 | 308
2017-03-16 20:30 | 288 | 287
2017-03-16 21:00 | 271 | 271
2017-03-16 21:30 | 255 | 255
2017-03-16 22:00 | 247 | 246
2017-03-16 22:30 | 241 | 240
2017-03-16 23:00 | 226 | 223
2017-03-16 23:30 | 213 | 210
2017-03-17 | 200 | 195
2017-03-17 00:30 | 187 | 186
2017-03-17 01:00 | 181 | 181
2017-03-17 01:30 | 178 | 177
2017-03-17 02:00 | 179 | 178
2017-03-17 02:30 | 180 | 180
2017-03-17 03:00 | 181 | 180
2017-03-17 03:30 | 182 | 182
2017-03-17 04:00 | 186 | 185
2017-03-17 04:30 | 189 | 188
2017-03-17 05:00 | 195 | 195
2017-03-17 05:30 | 209 | 209
2017-03-17 06:00 | 236 | 235
2017-03-17 06:30 | 248 | 248
2017-03-17 07:00 | 270 | 270
2017-03-17 07:30 | 277 | 277
2017-03-17 08:00 | 279 | 279
2017-03-17 08:30 | 280 | 280
2017-03-17 09:00 | 285 | 284
2017-03-17 09:30 | 288 | 287
2017-03-17 10:00 | 292 | 291
2017-03-17 10:30 | 295 | 294
2017-03-17 11:00 | 299 | 298
2017-03-17 11:30 | 305 | 304
2017-03-17 12:00 | 319 | 318
2017-03-17 12:30 | 322 | 321
2017-03-17 13:00 | 317 | 316
2017-03-17 13:30 | 314 | 313
2017-03-17 14:00 | 319 | 318
2017-03-17 14:30 | 330 | 329
2017-03-17 15:00 | 329 | 327
2017-03-17 15:30 | 322 | 321
2017-03-17 16:00 | 313 | 311
2017-03-17 16:30 | 309 | 306
2017-03-17 17:00 | 300 | 298
2017-03-17 17:30 | 296 | 295
2017-03-17 18:00 | 297 | 295
2017-03-17 18:30 | 298 | 297
2017-03-17 19:00 | 294 | 293
2017-03-17 19:30 | 292 | 290
2017-03-17 20:00 | 286 | 284
2017-03-17 20:30 | 273 | 272
2017-03-17 21:00 | 264 | 264
2017-03-17 21:30 | 251 | 251
2017-03-17 22:00 | 245 | 244
2017-03-17 22:30 | 244 | 243
2017-03-17 23:00 | 226 | 225
2017-03-17 23:30 | 211 | 209
2017-03-18 | 195 | 192
2017-03-18 00:30 | 190 | 187
2017-03-18 01:00 | 185 | 182
2017-03-18 01:30 | 183 | 180
2017-03-18 02:00 | 183 | 180
2017-03-18 02:30 | 185 | 181
2017-03-18 03:00 | 183 | 180
2017-03-18 03:30 | 184 | 183
2017-03-18 04:00 | 184 | 183
2017-03-18 04:30 | 182 | 181
2017-03-18 05:00 | 186 | 185
2017-03-18 05:30 | 192 | 192
2017-03-18 06:00 | 201 | 200
2017-03-18 06:30 | 210 | 210
2017-03-18 07:00 | 224 | 224
2017-03-18 07:30 | 237 | 237
2017-03-18 08:00 | 250 | 249
2017-03-18 08:30 | 254 | 254
2017-03-18 09:00 | 260 | 260
2017-03-18 09:30 | 260 | 260
2017-03-18 10:00 | 262 | 262
2017-03-18 10:30 | 262 | 262
2017-03-18 11:00 | 263 | 263
2017-03-18 11:30 | 271 | 271
2017-03-18 12:00 | 271 | 271
2017-03-18 12:30 | 273 | 273
2017-03-18 13:00 | 281 | 281
2017-03-18 13:30 | 295 | 294
2017-03-18 14:00 | 301 | 300
2017-03-18 14:30 | 316 | 315
2017-03-18 15:00 | 325 | 325
2017-03-18 15:30 | 327 | 326
2017-03-18 16:00 | 329 | 328
2017-03-18 16:30 | 333 | 332
2017-03-18 17:00 | 330 | 329
2017-03-18 17:30 | 340 | 339
2017-03-18 18:00 | 337 | 336
2017-03-18 18:30 | 338 | 337
2017-03-18 19:00 | 328 | 327
2017-03-18 19:30 | 324 | 322
2017-03-18 20:00 | 310 | 308
2017-03-18 20:30 | 297 | 294
2017-03-18 21:00 | 283 | 282
2017-03-18 21:30 | 276 | 275
2017-03-18 22:00 | 270 | 269
2017-03-18 22:30 | 262 | 260
2017-03-18 23:00 | 242 | 241
2017-03-18 23:30 | 228 | 227
2017-03-19 | 210 | 208
2017-03-19 00:30 | 204 | 201
2017-03-19 01:00 | 200 | 196
2017-03-19 01:30 | 198 | 194
2017-03-19 02:00 | 195 | 191
2017-03-19 02:30 | 196 | 191
2017-03-19 03:00 | 194 | 189
2017-03-19 03:30 | 195 | 190
2017-03-19 04:00 | 195 | 190
2017-03-19 04:30 | 196 | 191
2017-03-19 05:00 | 199 | 195
2017-03-19 05:30 | 204 | 200
2017-03-19 06:00 | 208 | 204
2017-03-19 06:30 | 216 | 212
2017-03-19 07:00 | 227 | 224
2017-03-19 07:30 | 236 | 234
2017-03-19 08:00 | 251 | 250
2017-03-19 08:30 | 259 | 258
2017-03-19 09:00 | 264 | 263
2017-03-19 09:30 | 267 | 267
2017-03-19 10:00 | 274 | 274
2017-03-19 10:30 | 278 | 276
2017-03-19 11:00 | 272 | 270
2017-03-19 11:30 | 284 | 282
2017-03-19 12:00 | 293 | 291
2017-03-19 12:30 | 300 | 298
2017-03-19 13:00 | 299 | 295
2017-03-19 13:30 | 299 | 295
2017-03-19 14:00 | 297 | 293
2017-03-19 14:30 | 296 | 292
2017-03-19 15:00 | 299 | 295
2017-03-19 15:30 | 305 | 300
2017-03-19 16:00 | 310 | 305
2017-03-19 16:30 | 313 | 308
2017-03-19 17:00 | 314 | 308
2017-03-19 17:30 | 318 | 312
2017-03-19 18:00 | 321 | 317
2017-03-19 18:30 | 323 | 319
2017-03-19 19:00 | 316 | 311
2017-03-19 19:30 | 302 | 301
2017-03-19 20:00 | 289 | 288
2017-03-19 20:30 | 277 | 277
2017-03-19 21:00 | 264 | 264
2017-03-19 21:30 | 254 | 253
2017-03-19 22:00 | 248 | 247
2017-03-19 22:30 | 244 | 243
2017-03-19 23:00 | 227 | 224
2017-03-19 23:30 | 215 | 213
2017-03-20 | 203 | 201
2017-03-20 00:30 | 198 | 196
2017-03-20 01:00 | 196 | 194
2017-03-20 01:30 | 194 | 191
2017-03-20 02:00 | 195 | 192
2017-03-20 02:30 | 196 | 194
2017-03-20 03:00 | 196 | 194
2017-03-20 03:30 | 198 | 196
2017-03-20 04:00 | 200 | 198
2017-03-20 04:30 | 203 | 202
2017-03-20 05:00 | 218 | 217
2017-03-20 05:30 | 232 | 232
2017-03-20 06:00 | 255 | 254
2017-03-20 06:30 | 275 | 274
2017-03-20 07:00 | 302 | 302
2017-03-20 07:30 | 314 | 313
2017-03-20 08:00 | 323 | 323
2017-03-20 08:30 | 328 | 328
2017-03-20 09:00 | 339 | 339
2017-03-20 09:30 | 345 | 344
2017-03-20 10:00 | 347 | 346
2017-03-20 10:30 | 347 | 346
2017-03-20 11:00 | 347 | 346
2017-03-20 11:30 | 350 | 349
2017-03-20 12:00 | 351 | 350
2017-03-20 12:30 | 346 | 345
2017-03-20 13:00 | 341 | 339
2017-03-20 13:30 | 338 | 337
2017-03-20 14:00 | 339 | 337
2017-03-20 14:30 | 342 | 340
2017-03-20 15:00 | 345 | 343
2017-03-20 15:30 | 343 | 342
2017-03-20 16:00 | 345 | 345
2017-03-20 16:30 | 345 | 345
2017-03-20 17:00 | 342 | 341
2017-03-20 17:30 | 338 | 338
2017-03-20 18:00 | 339 | 338
2017-03-20 18:30 | 338 | 338
2017-03-20 19:00 | 333 | 333
2017-03-20 19:30 | 327 | 327
2017-03-20 20:00 | 308 | 308
2017-03-20 20:30 | 290 | 289
2017-03-20 21:00 | 278 | 278
2017-03-20 21:30 | 264 | 264
2017-03-20 22:00 | 257 | 257
2017-03-20 22:30 | 250 | 250
2017-03-20 23:00 | 232 | 232
2017-03-20 23:30 | 217 | 217
2017-03-21 | 198 | 198
2017-03-21 00:30 | 193 | 193
2017-03-21 01:00 | 192 | 192
2017-03-21 01:30 | 191 | 190
2017-03-21 02:00 | 185 | 185
2017-03-21 02:30 | 186 | 186
2017-03-21 03:00 | 186 | 185
2017-03-21 03:30 | 185 | 185
2017-03-21 04:00 | 191 | 190
2017-03-21 04:30 | 207 | 207
2017-03-21 05:00 | 208 | 208
2017-03-21 05:30 | 220 | 220
2017-03-21 06:00 | 243 | 242
2017-03-21 06:30 | 264 | 263
2017-03-21 07:00 | 285 | 285
2017-03-21 07:30 | 295 | 295
2017-03-21 08:00 | 305 | 305
2017-03-21 08:30 | 306 | 306
2017-03-21 09:00 | 308 | 307
2017-03-21 09:30 | 316 | 316
2017-03-21 10:00 | 320 | 320
2017-03-21 10:30 | 310 | 309
2017-03-21 11:00 | 315 | 315
2017-03-21 11:30 | 296 | 295
2017-03-21 12:00 | 320 | 319
2017-03-21 12:30 | 322 | 320
2017-03-21 13:00 | 323 | 322
2017-03-21 13:30 | 325 | 323
2017-03-21 14:00 | 330 | 329
2017-03-21 14:30 | 332 | 330
2017-03-21 15:00 | 333 | 332
2017-03-21 15:30 | 338 | 337
2017-03-21 16:00 | 343 | 341
2017-03-21 16:30 | 347 | 345
2017-03-21 17:00 | 347 | 344
2017-03-21 17:30 | 343 | 342
2017-03-21 18:00 | 347 | 347
2017-03-21 18:30 | 349 | 348
2017-03-21 19:00 | 344 | 343
2017-03-21 19:30 | 338 | 337
2017-03-21 20:00 | 328 | 327
2017-03-21 20:30 | 314 | 312
2017-03-21 21:00 | 298 | 295
2017-03-21 21:30 | 279 | 278
2017-03-21 22:00 | 269 | 269
2017-03-21 22:30 | 265 | 265
2017-03-21 23:00 | 246 | 246
2017-03-21 23:30 | 227 | 227
2017-03-22 | 212 | 212
2017-03-22 00:30 | 205 | 205
2017-03-22 01:00 | 200 | 200
2017-03-22 01:30 | 196 | 196
2017-03-22 02:00 | 195 | 195
2017-03-22 02:30 | 194 | 194
2017-03-22 03:00 | 194 | 193
2017-03-22 03:30 | 195 | 195
2017-03-22 04:00 | 199 | 199
2017-03-22 04:30 | 205 | 205
2017-03-22 05:00 | 211 | 211
2017-03-22 05:30 | 225 | 225
2017-03-22 06:00 | 245 | 245
2017-03-22 06:30 | 267 | 266
2017-03-22 07:00 | 288 | 288
2017-03-22 07:30 | 293 | 293
2017-03-22 08:00 | 310 | 309
2017-03-22 08:30 | 318 | 317
2017-03-22 09:00 | 325 | 324
2017-03-22 09:30 | 334 | 333
2017-03-22 10:00 | 339 | 337
2017-03-22 10:30 | 337 | 336
2017-03-22 11:00 | 334 | 333
2017-03-22 11:30 | 332 | 330
2017-03-22 12:00 | 334 | 332
2017-03-22 12:30 | 339 | 337
2017-03-22 13:00 | 342 | 340
2017-03-22 13:30 | 345 | 343
2017-03-22 14:00 | 343 | 342
2017-03-22 14:30 | 341 | 340
2017-03-22 15:00 | 337 | 335
2017-03-22 15:30 | 336 | 334
2017-03-22 16:00 | 339 | 336
2017-03-22 16:30 | 343 | 340
2017-03-22 17:00 | 342 | 340
2017-03-22 17:30 | 343 | 340
2017-03-22 18:00 | 342 | 341
2017-03-22 18:30 | 341 | 340
2017-03-22 19:00 | 334 | 333
2017-03-22 19:30 | 329 | 329
2017-03-22 20:00 | 321 | 319
2017-03-22 20:30 | 310 | 308
2017-03-22 21:00 | 292 | 291
2017-03-22 21:30 | 276 | 276
2017-03-22 22:00 | 270 | 270
2017-03-22 22:30 | 258 | 258
2017-03-22 23:00 | 237 | 237
2017-03-22 23:30 | 223 | 223
2017-03-23 | 209 | 209
2017-03-23 00:30 | 202 | 202
2017-03-23 01:00 | 197 | 197
2017-03-23 01:30 | 193 | 193
2017-03-23 02:00 | 191 | 191
2017-03-23 02:30 | 190 | 190
2017-03-23 03:00 | 190 | 190
2017-03-23 03:30 | 191 | 191
2017-03-23 04:00 | 195 | 195
2017-03-23 04:30 | 200 | 200
2017-03-23 05:00 | 209 | 209
2017-03-23 05:30 | 221 | 221
2017-03-23 06:00 | 243 | 243
2017-03-23 06:30 | 266 | 266
2017-03-23 07:00 | 289 | 289
2017-03-23 07:30 | 301 | 301
2017-03-23 08:00 | 301 | 301
2017-03-23 08:30 | 303 | 303
2017-03-23 09:00 | 308 | 308
2017-03-23 09:30 | 310 | 310
2017-03-23 10:00 | 315 | 315
2017-03-23 10:30 | 309 | 309
2017-03-23 11:00 | 306 | 305
2017-03-23 11:30 | 309 | 309
2017-03-23 12:00 | 315 | 315
2017-03-23 12:30 | 321 | 321
2017-03-23 13:00 | 327 | 327
2017-03-23 13:30 | 333 | 332
2017-03-23 14:00 | 341 | 340
2017-03-23 14:30 | 345 | 344
2017-03-23 15:00 | 343 | 342
2017-03-23 15:30 | 346 | 345
2017-03-23 16:00 | 348 | 346
2017-03-23 16:30 | 351 | 349
2017-03-23 17:00 | 349 | 348
2017-03-23 17:30 | 349 | 348
2017-03-23 18:00 | 354 | 354
2017-03-23 18:30 | 352 | 351
2017-03-23 19:00 | 348 | 347
2017-03-23 19:30 | 342 | 341
2017-03-23 20:00 | 323 | 323
2017-03-23 20:30 | 310 | 309
2017-03-23 21:00 | 297 | 297
2017-03-23 21:30 | 283 | 282
2017-03-23 22:00 | 272 | 272
2017-03-23 22:30 | 259 | 259
2017-03-23 23:00 | 241 | 241
2017-03-23 23:30 | 228 | 227
2017-03-24 | 213 | 213
2017-03-24 00:30 | 205 | 205
2017-03-24 01:00 | 199 | 199
2017-03-24 01:30 | 195 | 195
2017-03-24 02:00 | 193 | 193
2017-03-24 02:30 | 192 | 191
2017-03-24 03:00 | 191 | 191
2017-03-24 03:30 | 191 | 190
2017-03-24 04:00 | 194 | 194
2017-03-24 04:30 | 199 | 199
2017-03-24 05:00 | 210 | 210
2017-03-24 05:30 | 223 | 223
2017-03-24 06:00 | 241 | 241
2017-03-24 06:30 | 265 | 265
2017-03-24 07:00 | 282 | 282
2017-03-24 07:30 | 289 | 289
2017-03-24 08:00 | 301 | 301
2017-03-24 08:30 | 308 | 308
2017-03-24 09:00 | 309 | 309
2017-03-24 09:30 | 310 | 310
2017-03-24 10:00 | 311 | 311
2017-03-24 10:30 | 311 | 311
2017-03-24 11:00 | 322 | 322
2017-03-24 11:30 | 334 | 334
2017-03-24 12:00 | 337 | 336
2017-03-24 12:30 | 331 | 330
2017-03-24 13:00 | 324 | 322
2017-03-24 13:30 | 322 | 322
2017-03-24 14:00 | 324 | 323
2017-03-24 14:30 | 320 | 319
2017-03-24 15:00 | 319 | 318
2017-03-24 15:30 | 320 | 318
2017-03-24 16:00 | 327 | 326
2017-03-24 16:30 | 330 | 328
2017-03-24 17:00 | 328 | 325
2017-03-24 17:30 | 326 | 323
2017-03-24 18:00 | 327 | 325
2017-03-24 18:30 | 331 | 329
2017-03-24 19:00 | 334 | 333
2017-03-24 19:30 | 320 | 317
2017-03-24 20:00 | 304 | 302
2017-03-24 20:30 | 291 | 290
2017-03-24 21:00 | 281 | 280
2017-03-24 21:30 | 270 | 270
2017-03-24 22:00 | 259 | 259
2017-03-24 22:30 | 254 | 254
2017-03-24 23:00 | 236 | 236
2017-03-24 23:30 | 223 | 223
2017-03-25 | 213 | 213
2017-03-25 00:30 | 206 | 206
2017-03-25 01:00 | 199 | 199
2017-03-25 01:30 | 194 | 194
2017-03-25 02:00 | 195 | 195
2017-03-25 02:30 | 200 | 200
2017-03-25 03:00 | 197 | 197
2017-03-25 03:30 | 197 | 196
2017-03-25 04:00 | 195 | 195
2017-03-25 04:30 | 198 | 198
2017-03-25 05:00 | 206 | 206
2017-03-25 05:30 | 213 | 213
2017-03-25 06:00 | 218 | 217
2017-03-25 06:30 | 227 | 227
2017-03-25 07:00 | 242 | 242
2017-03-25 07:30 | 259 | 258
2017-03-25 08:00 | 276 | 276
2017-03-25 08:30 | 274 | 273
2017-03-25 09:00 | 280 | 279
2017-03-25 09:30 | 283 | 282
2017-03-25 10:00 | 282 | 282
2017-03-25 10:30 | 283 | 283
2017-03-25 11:00 | 285 | 285
2017-03-25 11:30 | 287 | 287
2017-03-25 12:00 | 286 | 286
2017-03-25 12:30 | 284 | 284
2017-03-25 13:00 | 277 | 277
2017-03-25 13:30 | 279 | 278
2017-03-25 14:00 | 280 | 280
2017-03-25 14:30 | 280 | 280
2017-03-25 15:00 | 282 | 282
2017-03-25 15:30 | 282 | 282
2017-03-25 16:00 | 285 | 285
2017-03-25 16:30 | 289 | 289
2017-03-25 17:00 | 287 | 287
2017-03-25 17:30 | 293 | 292
2017-03-25 18:00 | 297 | 297
2017-03-25 18:30 | 294 | 294
2017-03-25 19:00 | 287 | 286
2017-03-25 19:30 | 286 | 286
2017-03-25 20:00 | 279 | 279
2017-03-25 20:30 | 271 | 271
2017-03-25 21:00 | 263 | 263
2017-03-25 21:30 | 255 | 255
2017-03-25 22:00 | 254 | 254
2017-03-25 22:30 | 247 | 247
2017-03-25 23:00 | 233 | 233
2017-03-25 23:30 | 221 | 220
2017-03-26 | 206 | 206
2017-03-26 00:30 | 198 | 198
2017-03-26 01:00 | 195 | 195
2017-03-26 01:30 | 194 | 194
2017-03-26 02:00 | 190 | 190
2017-03-26 02:30 | 191 | 191
2017-03-26 03:00 | 189 | 189
2017-03-26 03:30 | 188 | 188
2017-03-26 04:00 | 188 | 188
2017-03-26 04:30 | 189 | 189
2017-03-26 05:00 | 190 | 190
2017-03-26 05:30 | 195 | 195
2017-03-26 06:00 | 201 | 201
2017-03-26 06:30 | 208 | 208
2017-03-26 07:00 | 221 | 221
2017-03-26 07:30 | 229 | 228
2017-03-26 08:00 | 240 | 240
2017-03-26 08:30 | 249 | 249
2017-03-26 09:00 | 244 | 243
2017-03-26 09:30 | 243 | 242
2017-03-26 10:00 | 252 | 251
2017-03-26 10:30 | 250 | 249
2017-03-26 11:00 | 252 | 251
2017-03-26 11:30 | 262 | 261
2017-03-26 12:00 | 263 | 263
2017-03-26 12:30 | 263 | 263
2017-03-26 13:00 | 263 | 263
2017-03-26 13:30 | 269 | 269
2017-03-26 14:00 | 275 | 274
2017-03-26 14:30 | 284 | 284
2017-03-26 15:00 | 291 | 291
2017-03-26 15:30 | 299 | 299
2017-03-26 16:00 | 305 | 305
2017-03-26 16:30 | 310 | 310
2017-03-26 17:00 | 314 | 314
2017-03-26 17:30 | 317 | 316
2017-03-26 18:00 | 322 | 322
2017-03-26 18:30 | 323 | 322
2017-03-26 19:00 | 315 | 315
2017-03-26 19:30 | 309 | 308
2017-03-26 20:00 | 292 | 291
2017-03-26 20:30 | 285 | 284
2017-03-26 21:00 | 275 | 272
2017-03-26 21:30 | 260 | 259
2017-03-26 22:00 | 253 | 252
2017-03-26 22:30 | 245 | 244
2017-03-26 23:00 | 229 | 228
2017-03-26 23:30 | 217 | 216
2017-03-27 | 208 | 206
2017-03-27 00:30 | 203 | 201
2017-03-27 01:00 | 195 | 192
2017-03-27 01:30 | 191 | 188
2017-03-27 02:00 | 191 | 188
2017-03-27 02:30 | 191 | 188
2017-03-27 03:00 | 193 | 190
2017-03-27 03:30 | 195 | 193
2017-03-27 04:00 | 197 | 194
2017-03-27 04:30 | 200 | 197
2017-03-27 05:00 | 214 | 212
2017-03-27 05:30 | 230 | 230
2017-03-27 06:00 | 246 | 246
2017-03-27 06:30 | 262 | 261
2017-03-27 07:00 | 282 | 281
2017-03-27 07:30 | 291 | 290
2017-03-27 08:00 | 294 | 294
2017-03-27 08:30 | 297 | 297
2017-03-27 09:00 | 304 | 304
2017-03-27 09:30 | 306 | 306
2017-03-27 10:00 | 306 | 306
2017-03-27 10:30 | 320 | 320
2017-03-27 11:00 | 328 | 328
2017-03-27 11:30 | 335 | 335
2017-03-27 12:00 | 335 | 335
2017-03-27 12:30 | 336 | 335
2017-03-27 13:00 | 335 | 335
2017-03-27 13:30 | 337 | 336
2017-03-27 14:00 | 342 | 341
2017-03-27 14:30 | 347 | 346
2017-03-27 15:00 | 355 | 354
2017-03-27 15:30 | 362 | 361
2017-03-27 16:00 | 372 | 371
2017-03-27 16:30 | 374 | 372
2017-03-27 17:00 | 368 | 367
2017-03-27 17:30 | 368 | 365
2017-03-27 18:00 | 369 | 367
2017-03-27 18:30 | 371 | 369
2017-03-27 19:00 | 361 | 359
2017-03-27 19:30 | 359 | 357
2017-03-27 20:00 | 346 | 344
2017-03-27 20:30 | 333 | 331
2017-03-27 21:00 | 321 | 318
2017-03-27 21:30 | 306 | 303
2017-03-27 22:00 | 292 | 290
2017-03-27 22:30 | 282 | 281
2017-03-27 23:00 | 266 | 264
2017-03-27 23:30 | 249 | 246
2017-03-28 | 238 | 235
2017-03-28 00:30 | 229 | 225
2017-03-28 01:00 | 221 | 219
2017-03-28 01:30 | 216 | 214
2017-03-28 02:00 | 211 | 209
2017-03-28 02:30 | 211 | 209
2017-03-28 03:00 | 214 | 212
2017-03-28 03:30 | 211 | 209
2017-03-28 04:00 | 217 | 215
2017-03-28 04:30 | 225 | 223
2017-03-28 05:00 | 237 | 236
2017-03-28 05:30 | 243 | 242
2017-03-28 06:00 | 254 | 254
2017-03-28 06:30 | 274 | 274
2017-03-28 07:00 | 296 | 294
2017-03-28 07:30 | 301 | 300
2017-03-28 08:00 | 307 | 307
2017-03-28 08:30 | 312 | 312
2017-03-28 09:00 | 319 | 319
2017-03-28 09:30 | 320 | 320
2017-03-28 10:00 | 319 | 319
2017-03-28 10:30 | 320 | 320
2017-03-28 11:00 | 322 | 322
2017-03-28 11:30 | 325 | 325
2017-03-28 12:00 | 328 | 328
2017-03-28 12:30 | 330 | 330
2017-03-28 13:00 | 336 | 336
2017-03-28 13:30 | 343 | 343
2017-03-28 14:00 | 350 | 349
2017-03-28 14:30 | 354 | 354
2017-03-28 15:00 | 361 | 361
2017-03-28 15:30 | 373 | 372
2017-03-28 16:00 | 387 | 384
2017-03-28 16:30 | 386 | 383
2017-03-28 17:00 | 382 | 379
2017-03-28 17:30 | 383 | 379
2017-03-28 18:00 | 383 | 380
2017-03-28 18:30 | 383 | 380
2017-03-28 19:00 | 378 | 374
2017-03-28 19:30 | 373 | 369
2017-03-28 20:00 | 357 | 353
2017-03-28 20:30 | 336 | 332
2017-03-28 21:00 | 315 | 314
2017-03-28 21:30 | 300 | 299
2017-03-28 22:00 | 292 | 291
2017-03-28 22:30 | 285 | 284
2017-03-28 23:00 | 265 | 263
2017-03-28 23:30 | 244 | 244
2017-03-29 | 230 | 229
2017-03-29 00:30 | 222 | 221
2017-03-29 01:00 | 216 | 214
2017-03-29 01:30 | 212 | 210
2017-03-29 02:00 | 209 | 207
2017-03-29 02:30 | 207 | 205
2017-03-29 03:00 | 206 | 204
2017-03-29 03:30 | 208 | 205
2017-03-29 04:00 | 211 | 209
2017-03-29 04:30 | 215 | 213
2017-03-29 05:00 | 228 | 227
2017-03-29 05:30 | 241 | 240
2017-03-29 06:00 | 259 | 258
2017-03-29 06:30 | 275 | 275
2017-03-29 07:00 | 294 | 294
2017-03-29 07:30 | 311 | 310
2017-03-29 08:00 | 316 | 315
2017-03-29 08:30 | 305 | 305
2017-03-29 09:00 | 324 | 324
2017-03-29 09:30 | 340 | 337
2017-03-29 10:00 | 341 | 339
2017-03-29 10:30 | 347 | 345
2017-03-29 11:00 | 353 | 351
2017-03-29 11:30 | 359 | 357
2017-03-29 12:00 | 368 | 366
2017-03-29 12:30 | 371 | 369
2017-03-29 13:00 | 364 | 362
2017-03-29 13:30 | 369 | 367
2017-03-29 14:00 | 376 | 374
2017-03-29 14:30 | 378 | 376
2017-03-29 15:00 | 379 | 376
2017-03-29 15:30 | 380 | 377
2017-03-29 16:00 | 382 | 380
2017-03-29 16:30 | 386 | 383
2017-03-29 17:00 | 386 | 383
2017-03-29 17:30 | 382 | 379
2017-03-29 18:00 | 379 | 376
2017-03-29 18:30 | 375 | 373
2017-03-29 19:00 | 367 | 364
2017-03-29 19:30 | 366 | 364
2017-03-29 20:00 | 356 | 354
2017-03-29 20:30 | 347 | 345
2017-03-29 21:00 | 335 | 332
2017-03-29 21:30 | 317 | 313
2017-03-29 22:00 | 293 | 291
2017-03-29 22:30 | 279 | 279
2017-03-29 23:00 | 261 | 261
2017-03-29 23:30 | 248 | 248
2017-03-30 | 233 | 233
2017-03-30 00:30 | 224 | 224
2017-03-30 01:00 | 222 | 221
2017-03-30 01:30 | 218 | 218
2017-03-30 02:00 | 219 | 219
2017-03-30 02:30 | 219 | 219
2017-03-30 03:00 | 220 | 219
2017-03-30 03:30 | 221 | 221
2017-03-30 04:00 | 225 | 225
2017-03-30 04:30 | 230 | 230
2017-03-30 05:00 | 244 | 244
2017-03-30 05:30 | 258 | 258
2017-03-30 06:00 | 279 | 279
2017-03-30 06:30 | 304 | 304
2017-03-30 07:00 | 329 | 329
2017-03-30 07:30 | 337 | 337
2017-03-30 08:00 | 360 | 359
2017-03-30 08:30 | 368 | 367
2017-03-30 09:00 | 376 | 375
2017-03-30 09:30 | 379 | 377
2017-03-30 10:00 | 377 | 375
2017-03-30 10:30 | 373 | 372
2017-03-30 11:00 | 366 | 364
2017-03-30 11:30 | 361 | 360
2017-03-30 12:00 | 356 | 355
2017-03-30 12:30 | 347 | 345
2017-03-30 13:00 | 335 | 334
2017-03-30 13:30 | 331 | 330
2017-03-30 14:00 | 327 | 327
2017-03-30 14:30 | 320 | 320
2017-03-30 15:00 | 321 | 321
2017-03-30 15:30 | 323 | 322
2017-03-30 16:00 | 321 | 321
2017-03-30 16:30 | 328 | 328
2017-03-30 17:00 | 333 | 332
2017-03-30 17:30 | 342 | 341
2017-03-30 18:00 | 353 | 352
2017-03-30 18:30 | 378 | 376
2017-03-30 19:00 | 360 | 357
2017-03-30 19:30 | 352 | 349
2017-03-30 20:00 | 340 | 337
2017-03-30 20:30 | 318 | 318
2017-03-30 21:00 | 290 | 290
2017-03-30 21:30 | 280 | 279
2017-03-30 22:00 | 275 | 274
2017-03-30 22:30 | 268 | 267
2017-03-30 23:00 | 252 | 251
2017-03-30 23:30 | 238 | 237
2017-03-31 | 225 | 224
2017-03-31 00:30 | 221 | 220
2017-03-31 01:00 | 197 | 196
2017-03-31 01:30 | 191 | 191
2017-03-31 02:00 | 188 | 188
2017-03-31 02:30 | 184 | 183
2017-03-31 03:00 | 183 | 182
2017-03-31 03:30 | 181 | 181
2017-03-31 04:00 | 183 | 182
2017-03-31 04:30 | 184 | 183
2017-03-31 05:00 | 192 | 191
2017-03-31 05:30 | 201 | 201
2017-03-31 06:00 | 214 | 214
2017-03-31 06:30 | 231 | 231
2017-03-31 07:00 | 254 | 254
2017-03-31 07:30 | 269 | 269
2017-03-31 08:00 | 276 | 276
2017-03-31 08:30 | 275 | 275
2017-03-31 09:00 | 272 | 271
2017-03-31 09:30 | 268 | 268
2017-03-31 10:00 | 270 | 269
2017-03-31 10:30 | 270 | 270
2017-03-31 11:00 | 272 | 271
2017-03-31 11:30 | 278 | 277
2017-03-31 12:00 | 281 | 280
2017-03-31 12:30 | 288 | 287
2017-03-31 13:00 | 293 | 293
2017-03-31 13:30 | 296 | 296
2017-03-31 14:00 | 292 | 291
2017-03-31 14:30 | 293 | 293
2017-03-31 15:00 | 300 | 299
2017-03-31 15:30 | 300 | 299
2017-03-31 16:00 | 304 | 303
2017-03-31 16:30 | 311 | 311
2017-03-31 17:00 | 307 | 307
2017-03-31 17:30 | 304 | 304
2017-03-31 18:00 | 308 | 308
2017-03-31 18:30 | 306 | 306
2017-03-31 19:00 | 299 | 299
2017-03-31 19:30 | 296 | 296
2017-03-31 20:00 | 290 | 289
2017-03-31 20:30 | 282 | 281
2017-03-31 21:00 | 269 | 269
2017-03-31 21:30 | 261 | 260
2017-03-31 22:00 | 255 | 255
2017-03-31 22:30 | 251 | 251
2017-03-31 23:00 | 234 | 234
2017-03-31 23:30 | 213 | 213
2017-04-01 | 198 | 198
2017-04-01 00:30 | 188 | 188
2017-04-01 01:00 | 180 | 179
2017-04-01 01:30 | 174 | 174
2017-04-01 02:00 | 171 | 171
2017-04-01 02:30 | 170 | 169
2017-04-01 03:00 | 169 | 168
2017-04-01 03:30 | 168 | 167
2017-04-01 04:00 | 171 | 169
2017-04-01 04:30 | 173 | 171
2017-04-01 05:00 | 179 | 177
2017-04-01 05:30 | 186 | 183
2017-04-01 06:00 | 194 | 192
2017-04-01 06:30 | 203 | 201
2017-04-01 07:00 | 218 | 216
2017-04-01 07:30 | 228 | 225
2017-04-01 08:00 | 238 | 235
2017-04-01 08:30 | 247 | 245
2017-04-01 09:00 | 253 | 251
2017-04-01 09:30 | 249 | 248
2017-04-01 10:00 | 246 | 245
2017-04-01 10:30 | 241 | 240
2017-04-01 11:00 | 233 | 232
2017-04-01 11:30 | 231 | 231
2017-04-01 12:00 | 233 | 233
2017-04-01 12:30 | 235 | 235
2017-04-01 13:00 | 240 | 239
2017-04-01 13:30 | 249 | 248
2017-04-01 14:00 | 255 | 255
2017-04-01 14:30 | 256 | 256
2017-04-01 15:00 | 262 | 262
2017-04-01 15:30 | 269 | 268
2017-04-01 16:00 | 276 | 276
2017-04-01 16:30 | 286 | 286
2017-04-01 17:00 | 292 | 291
2017-04-01 17:30 | 295 | 295
2017-04-01 18:00 | 302 | 301
2017-04-01 18:30 | 302 | 302
2017-04-01 19:00 | 292 | 291
2017-04-01 19:30 | 286 | 285
2017-04-01 20:00 | 279 | 279
2017-04-01 20:30 | 264 | 264
2017-04-01 21:00 | 256 | 256
2017-04-01 21:30 | 246 | 244
2017-04-01 22:00 | 249 | 246
2017-04-01 22:30 | 251 | 249
2017-04-01 23:00 | 234 | 233
2017-04-01 23:30 | 215 | 214
2017-04-02 | 199 | 198
2017-04-02 00:30 | 189 | 188
2017-04-02 01:00 | 180 | 180
2017-04-02 01:30 | 174 | 174
2017-04-02 02:00 | 171 | 171
2017-04-02 02:30 | 169 | 169
2017-04-02 03:00 | 168 | 167
2017-04-02 03:30 | 166 | 166
2017-04-02 04:00 | 167 | 167
2017-04-02 04:30 | 168 | 168
2017-04-02 05:00 | 172 | 171
2017-04-02 05:30 | 176 | 175
2017-04-02 06:00 | 182 | 181
2017-04-02 06:30 | 190 | 190
2017-04-02 07:00 | 203 | 202
2017-04-02 07:30 | 215 | 214
2017-04-02 08:00 | 225 | 224
2017-04-02 08:30 | 232 | 230
2017-04-02 09:00 | 242 | 241
2017-04-02 09:30 | 247 | 246
2017-04-02 10:00 | 245 | 244
2017-04-02 10:30 | 240 | 240
2017-04-02 11:00 | 231 | 230
2017-04-02 11:30 | 225 | 225
2017-04-02 12:00 | 215 | 215
2017-04-02 12:30 | 216 | 216
2017-04-02 13:00 | 217 | 216
2017-04-02 13:30 | 220 | 219
2017-04-02 14:00 | 229 | 228
2017-04-02 14:30 | 242 | 241
2017-04-02 15:00 | 259 | 258
2017-04-02 15:30 | 260 | 260
2017-04-02 16:00 | 266 | 265
2017-04-02 16:30 | 277 | 276
2017-04-02 17:00 | 283 | 283
2017-04-02 17:30 | 294 | 294
2017-04-02 18:00 | 308 | 308
2017-04-02 18:30 | 307 | 306
2017-04-02 19:00 | 292 | 291
2017-04-02 19:30 | 284 | 284
2017-04-02 20:00 | 277 | 277
2017-04-02 20:30 | 261 | 261
2017-04-02 21:00 | 249 | 249
2017-04-02 21:30 | 238 | 238
2017-04-02 22:00 | 237 | 237
2017-04-02 22:30 | 236 | 236
2017-04-02 23:00 | 222 | 221
2017-04-02 23:30 | 202 | 201
2017-04-03 | 187 | 186
2017-04-03 00:30 | 178 | 177
2017-04-03 01:00 | 173 | 172
2017-04-03 01:30 | 167 | 166
2017-04-03 02:00 | 164 | 164
2017-04-03 02:30 | 162 | 162
2017-04-03 03:00 | 162 | 162
2017-04-03 03:30 | 164 | 164
2017-04-03 04:00 | 168 | 168
2017-04-03 04:30 | 174 | 174
2017-04-03 05:00 | 184 | 184
2017-04-03 05:30 | 197 | 197
2017-04-03 06:00 | 218 | 217
2017-04-03 06:30 | 235 | 234
2017-04-03 07:00 | 249 | 248
2017-04-03 07:30 | 254 | 254
2017-04-03 08:00 | 259 | 259
2017-04-03 08:30 | 261 | 261
2017-04-03 09:00 | 264 | 264
2017-04-03 09:30 | 257 | 256
2017-04-03 10:00 | 251 | 251
2017-04-03 10:30 | 248 | 247
2017-04-03 11:00 | 250 | 249
2017-04-03 11:30 | 250 | 250
2017-04-03 12:00 | 247 | 246
2017-04-03 12:30 | 253 | 253
2017-04-03 13:00 | 262 | 262
2017-04-03 13:30 | 258 | 258
2017-04-03 14:00 | 259 | 259
2017-04-03 14:30 | 265 | 264
2017-04-03 15:00 | 273 | 273
2017-04-03 15:30 | 283 | 283
2017-04-03 16:00 | 293 | 293
2017-04-03 16:30 | 302 | 302
2017-04-03 17:00 | 307 | 306
2017-04-03 17:30 | 312 | 312
2017-04-03 18:00 | 318 | 318
2017-04-03 18:30 | 318 | 318
2017-04-03 19:00 | 305 | 305
2017-04-03 19:30 | 298 | 298
2017-04-03 20:00 | 289 | 289
2017-04-03 20:30 | 273 | 272
2017-04-03 21:00 | 261 | 261
2017-04-03 21:30 | 247 | 247
2017-04-03 22:00 | 244 | 244
2017-04-03 22:30 | 243 | 243
2017-04-03 23:00 | 227 | 226
2017-04-03 23:30 | 208 | 207
2017-04-04 | 192 | 192
2017-04-04 00:30 | 184 | 183
2017-04-04 01:00 | 178 | 177
2017-04-04 01:30 | 170 | 170
2017-04-04 02:00 | 166 | 166
2017-04-04 02:30 | 164 | 163
2017-04-04 03:00 | 162 | 162
2017-04-04 03:30 | 163 | 163
2017-04-04 04:00 | 168 | 167
2017-04-04 04:30 | 173 | 173
2017-04-04 05:00 | 185 | 185
2017-04-04 05:30 | 200 | 200
2017-04-04 06:00 | 219 | 219
2017-04-04 06:30 | 232 | 231
2017-04-04 07:00 | 249 | 248
2017-04-04 07:30 | 251 | 251
2017-04-04 08:00 | 250 | 250
2017-04-04 08:30 | 252 | 251
2017-04-04 09:00 | 260 | 260
2017-04-04 09:30 | 256 | 256
2017-04-04 10:00 | 252 | 252
2017-04-04 10:30 | 258 | 258
2017-04-04 11:00 | 272 | 272
2017-04-04 11:30 | 267 | 267
2017-04-04 12:00 | 267 | 267
2017-04-04 12:30 | 275 | 275
2017-04-04 13:00 | 284 | 284
2017-04-04 13:30 | 276 | 276
2017-04-04 14:00 | 281 | 281
2017-04-04 14:30 | 283 | 283
2017-04-04 15:00 | 296 | 296
2017-04-04 15:30 | 299 | 299
2017-04-04 16:00 | 303 | 303
2017-04-04 16:30 | 310 | 310
2017-04-04 17:00 | 311 | 311
2017-04-04 17:30 | 316 | 316
2017-04-04 18:00 | 321 | 321
2017-04-04 18:30 | 321 | 321
2017-04-04 19:00 | 314 | 314
2017-04-04 19:30 | 313 | 313
2017-04-04 20:00 | 306 | 306
2017-04-04 20:30 | 293 | 292
2017-04-04 21:00 | 279 | 279
2017-04-04 21:30 | 266 | 266
2017-04-04 22:00 | 261 | 261
2017-04-04 22:30 | 257 | 257
2017-04-04 23:00 | 244 | 244
2017-04-04 23:30 | 227 | 227
2017-04-05 | 212 | 211
2017-04-05 00:30 | 203 | 202
2017-04-05 01:00 | 198 | 196
2017-04-05 01:30 | 192 | 190
2017-04-05 02:00 | 187 | 186
2017-04-05 02:30 | 184 | 183
2017-04-05 03:00 | 184 | 183
2017-04-05 03:30 | 185 | 184
2017-04-05 04:00 | 189 | 188
2017-04-05 04:30 | 195 | 194
2017-04-05 05:00 | 208 | 208
2017-04-05 05:30 | 222 | 222
2017-04-05 06:00 | 242 | 241
2017-04-05 06:30 | 257 | 256
2017-04-05 07:00 | 271 | 270
2017-04-05 07:30 | 276 | 275
2017-04-05 08:00 | 279 | 279
2017-04-05 08:30 | 276 | 276
2017-04-05 09:00 | 273 | 273
2017-04-05 09:30 | 269 | 269
2017-04-05 10:00 | 271 | 270
2017-04-05 10:30 | 273 | 273
2017-04-05 11:00 | 274 | 274
2017-04-05 11:30 | 269 | 269
2017-04-05 12:00 | 268 | 268
2017-04-05 12:30 | 268 | 268
2017-04-05 13:00 | 275 | 275
2017-04-05 13:30 | 285 | 285
2017-04-05 14:00 | 299 | 298
2017-04-05 14:30 | 298 | 296
2017-04-05 15:00 | 295 | 294
2017-04-05 15:30 | 290 | 289
2017-04-05 16:00 | 302 | 301
2017-04-05 16:30 | 306 | 305
2017-04-05 17:00 | 308 | 307
2017-04-05 17:30 | 314 | 313
2017-04-05 18:00 | 319 | 319
2017-04-05 18:30 | 321 | 320
2017-04-05 19:00 | 314 | 314
2017-04-05 19:30 | 313 | 313
2017-04-05 20:00 | 310 | 309
2017-04-05 20:30 | 294 | 293
2017-04-05 21:00 | 284 | 282
2017-04-05 21:30 | 268 | 268
2017-04-05 22:00 | 265 | 264
2017-04-05 22:30 | 263 | 263
2017-04-05 23:00 | 248 | 248
2017-04-05 23:30 | 229 | 229
2017-04-06 | 214 | 213
2017-04-06 00:30 | 204 | 203
2017-04-06 01:00 | 199 | 198
2017-04-06 01:30 | 192 | 192
2017-04-06 02:00 | 187 | 187
2017-04-06 02:30 | 184 | 184
2017-04-06 03:00 | 184 | 184
2017-04-06 03:30 | 185 | 184
2017-04-06 04:00 | 189 | 189
2017-04-06 04:30 | 195 | 194
2017-04-06 05:00 | 208 | 208
2017-04-06 05:30 | 224 | 224
2017-04-06 06:00 | 243 | 243
2017-04-06 06:30 | 258 | 258
2017-04-06 07:00 | 275 | 275
2017-04-06 07:30 | 281 | 281
2017-04-06 08:00 | 285 | 284
2017-04-06 08:30 | 281 | 280
2017-04-06 09:00 | 278 | 277
2017-04-06 09:30 | 281 | 279
2017-04-06 10:00 | 289 | 288
2017-04-06 10:30 | 288 | 286
2017-04-06 11:00 | 281 | 279
2017-04-06 11:30 | 278 | 276
2017-04-06 12:00 | 276 | 274
2017-04-06 12:30 | 283 | 281
2017-04-06 13:00 | 289 | 287
2017-04-06 13:30 | 290 | 290
2017-04-06 14:00 | 295 | 295
2017-04-06 14:30 | 295 | 295
2017-04-06 15:00 | 298 | 298
2017-04-06 15:30 | 301 | 301
2017-04-06 16:00 | 305 | 305
2017-04-06 16:30 | 315 | 315
2017-04-06 17:00 | 318 | 318
2017-04-06 17:30 | 328 | 328
2017-04-06 18:00 | 333 | 332
2017-04-06 18:30 | 332 | 331
2017-04-06 19:00 | 326 | 325
2017-04-06 19:30 | 325 | 325
2017-04-06 20:00 | 320 | 319
2017-04-06 20:30 | 306 | 305
2017-04-06 21:00 | 292 | 291
2017-04-06 21:30 | 277 | 276
2017-04-06 22:00 | 270 | 270
2017-04-06 22:30 | 268 | 268
2017-04-06 23:00 | 252 | 252
2017-04-06 23:30 | 233 | 232
2017-04-07 | 217 | 216
2017-04-07 00:30 | 204 | 204
2017-04-07 01:00 | 197 | 197
2017-04-07 01:30 | 191 | 191
2017-04-07 02:00 | 188 | 187
2017-04-07 02:30 | 186 | 186
2017-04-07 03:00 | 187 | 187
2017-04-07 03:30 | 189 | 189
2017-04-07 04:00 | 193 | 193
2017-04-07 04:30 | 200 | 200
2017-04-07 05:00 | 211 | 211
2017-04-07 05:30 | 222 | 222
2017-04-07 06:00 | 238 | 238
2017-04-07 06:30 | 255 | 253
2017-04-07 07:00 | 271 | 271
2017-04-07 07:30 | 277 | 277
2017-04-07 08:00 | 278 | 278
2017-04-07 08:30 | 276 | 276
2017-04-07 09:00 | 277 | 277
2017-04-07 09:30 | 272 | 272
2017-04-07 10:00 | 268 | 268
2017-04-07 10:30 | 266 | 266
2017-04-07 11:00 | 265 | 265
2017-04-07 11:30 | 267 | 267
2017-04-07 12:00 | 269 | 269
2017-04-07 12:30 | 270 | 270
2017-04-07 13:00 | 269 | 269
2017-04-07 13:30 | 272 | 272
2017-04-07 14:00 | 280 | 280
2017-04-07 14:30 | 282 | 282
2017-04-07 15:00 | 285 | 285
2017-04-07 15:30 | 292 | 292
2017-04-07 16:00 | 301 | 301
2017-04-07 16:30 | 311 | 311
2017-04-07 17:00 | 311 | 311
2017-04-07 17:30 | 315 | 314
2017-04-07 18:00 | 317 | 317
2017-04-07 18:30 | 317 | 316
2017-04-07 19:00 | 307 | 307
2017-04-07 19:30 | 304 | 303
2017-04-07 20:00 | 294 | 293
2017-04-07 20:30 | 281 | 281
2017-04-07 21:00 | 271 | 270
2017-04-07 21:30 | 261 | 261
2017-04-07 22:00 | 260 | 260
2017-04-07 22:30 | 259 | 259
2017-04-07 23:00 | 243 | 243
2017-04-07 23:30 | 224 | 224
2017-04-08 | 209 | 209
2017-04-08 00:30 | 200 | 199
2017-04-08 01:00 | 193 | 192
2017-04-08 01:30 | 185 | 184
2017-04-08 02:00 | 179 | 179
2017-04-08 02:30 | 177 | 177
2017-04-08 03:00 | 175 | 175
2017-04-08 03:30 | 175 | 175
2017-04-08 04:00 | 177 | 177
2017-04-08 04:30 | 180 | 180
2017-04-08 05:00 | 187 | 187
2017-04-08 05:30 | 193 | 193
2017-04-08 06:00 | 203 | 203
2017-04-08 06:30 | 212 | 212
2017-04-08 07:00 | 225 | 225
2017-04-08 07:30 | 233 | 232
2017-04-08 08:00 | 241 | 241
2017-04-08 08:30 | 255 | 255
2017-04-08 09:00 | 264 | 262
2017-04-08 09:30 | 253 | 249
2017-04-08 10:00 | 240 | 238
2017-04-08 10:30 | 240 | 240
2017-04-08 11:00 | 243 | 242
2017-04-08 11:30 | 232 | 231
2017-04-08 12:00 | 226 | 225
2017-04-08 12:30 | 225 | 224
2017-04-08 13:00 | 230 | 230
2017-04-08 13:30 | 244 | 244
2017-04-08 14:00 | 243 | 243
2017-04-08 14:30 | 245 | 245
2017-04-08 15:00 | 253 | 253
2017-04-08 15:30 | 270 | 269
2017-04-08 16:00 | 278 | 277
2017-04-08 16:30 | 288 | 287
2017-04-08 17:00 | 291 | 290
2017-04-08 17:30 | 297 | 296
2017-04-08 18:00 | 300 | 300
2017-04-08 18:30 | 298 | 297
2017-04-08 19:00 | 292 | 291
2017-04-08 19:30 | 290 | 289
2017-04-08 20:00 | 284 | 283
2017-04-08 20:30 | 271 | 271
2017-04-08 21:00 | 260 | 260
2017-04-08 21:30 | 253 | 253
2017-04-08 22:00 | 251 | 251
2017-04-08 22:30 | 247 | 247
2017-04-08 23:00 | 230 | 230
2017-04-08 23:30 | 219 | 218
2017-04-09 | 206 | 206
2017-04-09 00:30 | 197 | 197
2017-04-09 01:00 | 191 | 190
2017-04-09 01:30 | 182 | 181
2017-04-09 02:00 | 177 | 177
2017-04-09 02:30 | 175 | 175
2017-04-09 03:00 | 174 | 174
2017-04-09 03:30 | 172 | 172
2017-04-09 04:00 | 173 | 173
2017-04-09 04:30 | 175 | 175
2017-04-09 05:00 | 180 | 179
2017-04-09 05:30 | 185 | 185
2017-04-09 06:00 | 191 | 191
2017-04-09 06:30 | 200 | 200
2017-04-09 07:00 | 210 | 210
2017-04-09 07:30 | 220 | 220
2017-04-09 08:00 | 229 | 229
2017-04-09 08:30 | 236 | 236
2017-04-09 09:00 | 239 | 239
2017-04-09 09:30 | 242 | 242
2017-04-09 10:00 | 240 | 239
2017-04-09 10:30 | 232 | 232
2017-04-09 11:00 | 228 | 228
2017-04-09 11:30 | 231 | 231
2017-04-09 12:00 | 237 | 237
2017-04-09 12:30 | 238 | 238
2017-04-09 13:00 | 239 | 239
2017-04-09 13:30 | 243 | 243
2017-04-09 14:00 | 249 | 249
2017-04-09 14:30 | 250 | 250
2017-04-09 15:00 | 235 | 235
2017-04-09 15:30 | 245 | 245
2017-04-09 16:00 | 260 | 260
2017-04-09 16:30 | 283 | 282
2017-04-09 17:00 | 281 | 280
2017-04-09 17:30 | 283 | 283
2017-04-09 18:00 | 292 | 291
2017-04-09 18:30 | 288 | 287
2017-04-09 19:00 | 279 | 279
2017-04-09 19:30 | 275 | 275
2017-04-09 20:00 | 270 | 269
2017-04-09 20:30 | 260 | 260
2017-04-09 21:00 | 254 | 253
2017-04-09 21:30 | 248 | 248
2017-04-09 22:00 | 242 | 241
2017-04-09 22:30 | 236 | 236
2017-04-09 23:00 | 223 | 222
2017-04-09 23:30 | 209 | 209
2017-04-10 | 193 | 193
2017-04-10 00:30 | 182 | 182
2017-04-10 01:00 | 178 | 178
2017-04-10 01:30 | 174 | 173
2017-04-10 02:00 | 173 | 173
2017-04-10 02:30 | 166 | 166
2017-04-10 03:00 | 165 | 165
2017-04-10 03:30 | 165 | 164
2017-04-10 04:00 | 169 | 168
2017-04-10 04:30 | 175 | 174
2017-04-10 05:00 | 186 | 186
2017-04-10 05:30 | 202 | 202
2017-04-10 06:00 | 222 | 222
2017-04-10 06:30 | 235 | 235
2017-04-10 07:00 | 251 | 251
2017-04-10 07:30 | 262 | 262
2017-04-10 08:00 | 274 | 274
2017-04-10 08:30 | 278 | 277
2017-04-10 09:00 | 277 | 277
2017-04-10 09:30 | 274 | 273
2017-04-10 10:00 | 274 | 273
2017-04-10 10:30 | 269 | 269
2017-04-10 11:00 | 268 | 267
2017-04-10 11:30 | 270 | 269
2017-04-10 12:00 | 275 | 275
2017-04-10 12:30 | 283 | 283
2017-04-10 13:00 | 287 | 287
2017-04-10 13:30 | 292 | 292
2017-04-10 14:00 | 298 | 298
2017-04-10 14:30 | 303 | 303
2017-04-10 15:00 | 302 | 301
2017-04-10 15:30 | 300 | 300
2017-04-10 16:00 | 304 | 304
2017-04-10 16:30 | 312 | 311
2017-04-10 17:00 | 311 | 310
2017-04-10 17:30 | 315 | 314
2017-04-10 18:00 | 321 | 318
2017-04-10 18:30 | 315 | 314
2017-04-10 19:00 | 308 | 307
2017-04-10 19:30 | 306 | 304
2017-04-10 20:00 | 303 | 301
2017-04-10 20:30 | 289 | 288
2017-04-10 21:00 | 277 | 276
2017-04-10 21:30 | 260 | 260
2017-04-10 22:00 | 256 | 256
2017-04-10 22:30 | 249 | 249
2017-04-10 23:00 | 234 | 234
2017-04-10 23:30 | 218 | 218
2017-04-11 | 203 | 203
2017-04-11 00:30 | 195 | 195
2017-04-11 01:00 | 189 | 188
2017-04-11 01:30 | 182 | 181
2017-04-11 02:00 | 178 | 176
2017-04-11 02:30 | 176 | 174
2017-04-11 03:00 | 175 | 174
2017-04-11 03:30 | 176 | 175
2017-04-11 04:00 | 180 | 179
2017-04-11 04:30 | 186 | 185
2017-04-11 05:00 | 198 | 198
2017-04-11 05:30 | 211 | 211
2017-04-11 06:00 | 229 | 229
2017-04-11 06:30 | 245 | 245
2017-04-11 07:00 | 259 | 259
2017-04-11 07:30 | 262 | 262
2017-04-11 08:00 | 262 | 262
2017-04-11 08:30 | 259 | 259
2017-04-11 09:00 | 255 | 254
2017-04-11 09:30 | 251 | 250
2017-04-11 10:00 | 249 | 248
2017-04-11 10:30 | 247 | 246
2017-04-11 11:00 | 244 | 243
2017-04-11 11:30 | 246 | 244
2017-04-11 12:00 | 246 | 245
2017-04-11 12:30 | 248 | 247
2017-04-11 13:00 | 252 | 251
2017-04-11 13:30 | 257 | 256
2017-04-11 14:00 | 263 | 263
2017-04-11 14:30 | 270 | 269
2017-04-11 15:00 | 272 | 272
2017-04-11 15:30 | 277 | 277
2017-04-11 16:00 | 284 | 284
2017-04-11 16:30 | 289 | 289
2017-04-11 17:00 | 292 | 292
2017-04-11 17:30 | 297 | 297
2017-04-11 18:00 | 308 | 308
2017-04-11 18:30 | 307 | 307
2017-04-11 19:00 | 299 | 299
2017-04-11 19:30 | 296 | 296
2017-04-11 20:00 | 292 | 292
2017-04-11 20:30 | 283 | 283
2017-04-11 21:00 | 273 | 272
2017-04-11 21:30 | 260 | 260
2017-04-11 22:00 | 246 | 246
2017-04-11 22:30 | 240 | 240
2017-04-11 23:00 | 231 | 231
2017-04-11 23:30 | 218 | 218
2017-04-12 | 205 | 204
2017-04-12 00:30 | 195 | 195
2017-04-12 01:00 | 192 | 191
2017-04-12 01:30 | 185 | 184
2017-04-12 02:00 | 181 | 180
2017-04-12 02:30 | 177 | 176
2017-04-12 03:00 | 177 | 176
2017-04-12 03:30 | 178 | 177
2017-04-12 04:00 | 183 | 182
2017-04-12 04:30 | 188 | 187
2017-04-12 05:00 | 200 | 200
2017-04-12 05:30 | 214 | 213
2017-04-12 06:00 | 223 | 223
2017-04-12 06:30 | 240 | 240
2017-04-12 07:00 | 257 | 257
2017-04-12 07:30 | 263 | 262
2017-04-12 08:00 | 268 | 268
2017-04-12 08:30 | 272 | 271
2017-04-12 09:00 | 273 | 273
2017-04-12 09:30 | 271 | 271
2017-04-12 10:00 | 274 | 274
2017-04-12 10:30 | 273 | 273
2017-04-12 11:00 | 274 | 274
2017-04-12 11:30 | 270 | 270
2017-04-12 12:00 | 275 | 275
2017-04-12 12:30 | 286 | 286
2017-04-12 13:00 | 287 | 287
2017-04-12 13:30 | 281 | 281
2017-04-12 14:00 | 285 | 285
2017-04-12 14:30 | 286 | 286
2017-04-12 15:00 | 296 | 296
2017-04-12 15:30 | 302 | 302
2017-04-12 16:00 | 304 | 304
2017-04-12 16:30 | 309 | 309
2017-04-12 17:00 | 311 | 310
2017-04-12 17:30 | 314 | 314
2017-04-12 18:00 | 318 | 318
2017-04-12 18:30 | 316 | 316
2017-04-12 19:00 | 310 | 310
2017-04-12 19:30 | 309 | 309
2017-04-12 20:00 | 301 | 301
2017-04-12 20:30 | 296 | 296
2017-04-12 21:00 | 282 | 282
2017-04-12 21:30 | 265 | 265
2017-04-12 22:00 | 249 | 249
2017-04-12 22:30 | 243 | 243
2017-04-12 23:00 | 232 | 231
2017-04-12 23:30 | 222 | 221
2017-04-13 | 209 | 208
2017-04-13 00:30 | 200 | 199
2017-04-13 01:00 | 194 | 193
2017-04-13 01:30 | 191 | 190
2017-04-13 02:00 | 191 | 190
2017-04-13 02:30 | 190 | 189
2017-04-13 03:00 | 190 | 189
2017-04-13 03:30 | 188 | 187
2017-04-13 04:00 | 190 | 189
2017-04-13 04:30 | 194 | 193
2017-04-13 05:00 | 203 | 202
2017-04-13 05:30 | 211 | 210
2017-04-13 06:00 | 224 | 224
2017-04-13 06:30 | 237 | 237
2017-04-13 07:00 | 256 | 256
2017-04-13 07:30 | 274 | 273
2017-04-13 08:00 | 281 | 279
2017-04-13 08:30 | 278 | 277
2017-04-13 09:00 | 277 | 276
2017-04-13 09:30 | 274 | 273
2017-04-13 10:00 | 272 | 271
2017-04-13 10:30 | 272 | 272
2017-04-13 11:00 | 275 | 275
2017-04-13 11:30 | 282 | 282
2017-04-13 12:00 | 281 | 281
2017-04-13 12:30 | 284 | 284
2017-04-13 13:00 | 291 | 291
2017-04-13 13:30 | 289 | 289
2017-04-13 14:00 | 289 | 288
2017-04-13 14:30 | 288 | 287
2017-04-13 15:00 | 290 | 289
2017-04-13 15:30 | 291 | 291
2017-04-13 16:00 | 295 | 295
2017-04-13 16:30 | 302 | 301
2017-04-13 17:00 | 307 | 306
2017-04-13 17:30 | 312 | 311
2017-04-13 18:00 | 314 | 313
2017-04-13 18:30 | 315 | 314
2017-04-13 19:00 | 306 | 305
2017-04-13 19:30 | 303 | 302
2017-04-13 20:00 | 297 | 296
2017-04-13 20:30 | 286 | 286
2017-04-13 21:00 | 276 | 276
2017-04-13 21:30 | 271 | 271
2017-04-13 22:00 | 259 | 259
2017-04-13 22:30 | 255 | 255
2017-04-13 23:00 | 242 | 242
2017-04-13 23:30 | 228 | 227
2017-04-14 | 211 | 210
2017-04-14 00:30 | 196 | 195
2017-04-14 01:00 | 193 | 192
2017-04-14 01:30 | 188 | 187
2017-04-14 02:00 | 189 | 189
2017-04-14 02:30 | 190 | 190
2017-04-14 03:00 | 188 | 188
2017-04-14 03:30 | 185 | 185
2017-04-14 04:00 | 183 | 183
2017-04-14 04:30 | 185 | 184
2017-04-14 05:00 | 188 | 187
2017-04-14 05:30 | 196 | 196
2017-04-14 06:00 | 205 | 204
2017-04-14 06:30 | 212 | 212
2017-04-14 07:00 | 225 | 225
2017-04-14 07:30 | 242 | 242
2017-04-14 08:00 | 249 | 249
2017-04-14 08:30 | 253 | 253
2017-04-14 09:00 | 261 | 261
2017-04-14 09:30 | 259 | 258
2017-04-14 10:00 | 253 | 253
2017-04-14 10:30 | 245 | 245
2017-04-14 11:00 | 240 | 240
2017-04-14 11:30 | 233 | 233
2017-04-14 12:00 | 230 | 230
2017-04-14 12:30 | 240 | 240
2017-04-14 13:00 | 234 | 234
2017-04-14 13:30 | 233 | 233
2017-04-14 14:00 | 239 | 239
2017-04-14 14:30 | 245 | 245
2017-04-14 15:00 | 252 | 251
2017-04-14 15:30 | 258 | 255
2017-04-14 16:00 | 265 | 263
2017-04-14 16:30 | 273 | 271
2017-04-14 17:00 | 282 | 280
2017-04-14 17:30 | 291 | 290
2017-04-14 18:00 | 290 | 290
2017-04-14 18:30 | 290 | 289
2017-04-14 19:00 | 286 | 285
2017-04-14 19:30 | 286 | 285
2017-04-14 20:00 | 282 | 280
2017-04-14 20:30 | 271 | 269
2017-04-14 21:00 | 267 | 264
2017-04-14 21:30 | 264 | 261
2017-04-14 22:00 | 254 | 254
2017-04-14 22:30 | 250 | 250
2017-04-14 23:00 | 237 | 236
2017-04-14 23:30 | 221 | 220
2017-04-15 | 210 | 209
2017-04-15 00:30 | 204 | 203
2017-04-15 01:00 | 198 | 197
2017-04-15 01:30 | 194 | 193
2017-04-15 02:00 | 194 | 193
2017-04-15 02:30 | 197 | 196
2017-04-15 03:00 | 195 | 194
2017-04-15 03:30 | 195 | 194
2017-04-15 04:00 | 195 | 194
2017-04-15 04:30 | 194 | 193
2017-04-15 05:00 | 194 | 193
2017-04-15 05:30 | 196 | 195
2017-04-15 06:00 | 203 | 201
2017-04-15 06:30 | 205 | 205
2017-04-15 07:00 | 214 | 214
2017-04-15 07:30 | 228 | 227
2017-04-15 08:00 | 238 | 238
2017-04-15 08:30 | 240 | 240
2017-04-15 09:00 | 241 | 241
2017-04-15 09:30 | 243 | 242
2017-04-15 10:00 | 243 | 243
2017-04-15 10:30 | 244 | 244
2017-04-15 11:00 | 241 | 241
2017-04-15 11:30 | 245 | 245
2017-04-15 12:00 | 244 | 244
2017-04-15 12:30 | 245 | 245
2017-04-15 13:00 | 246 | 246
2017-04-15 13:30 | 251 | 251
2017-04-15 14:00 | 252 | 252
2017-04-15 14:30 | 246 | 246
2017-04-15 15:00 | 250 | 249
2017-04-15 15:30 | 252 | 252
2017-04-15 16:00 | 259 | 258
2017-04-15 16:30 | 267 | 267
2017-04-15 17:00 | 274 | 274
2017-04-15 17:30 | 282 | 281
2017-04-15 18:00 | 283 | 282
2017-04-15 18:30 | 283 | 281
2017-04-15 19:00 | 283 | 281
2017-04-15 19:30 | 275 | 275
2017-04-15 20:00 | 272 | 272
2017-04-15 20:30 | 262 | 262
2017-04-15 21:00 | 257 | 257
2017-04-15 21:30 | 256 | 256
2017-04-15 22:00 | 251 | 251
2017-04-15 22:30 | 249 | 249
2017-04-15 23:00 | 238 | 237
2017-04-15 23:30 | 225 | 224
2017-04-16 | 213 | 213
2017-04-16 00:30 | 207 | 207
2017-04-16 01:00 | 202 | 201
2017-04-16 01:30 | 197 | 196
2017-04-16 02:00 | 197 | 196
2017-04-16 02:30 | 197 | 196
2017-04-16 03:00 | 192 | 191
2017-04-16 03:30 | 190 | 190
2017-04-16 04:00 | 194 | 194
2017-04-16 04:30 | 192 | 192
2017-04-16 05:00 | 194 | 194
2017-04-16 05:30 | 196 | 196
2017-04-16 06:00 | 200 | 199
2017-04-16 06:30 | 205 | 205
2017-04-16 07:00 | 219 | 219
2017-04-16 07:30 | 230 | 230
2017-04-16 08:00 | 239 | 239
2017-04-16 08:30 | 247 | 246
2017-04-16 09:00 | 248 | 248
2017-04-16 09:30 | 249 | 248
2017-04-16 10:00 | 257 | 257
2017-04-16 10:30 | 239 | 239
2017-04-16 11:00 | 230 | 230
2017-04-16 11:30 | 228 | 228
2017-04-16 12:00 | 227 | 227
2017-04-16 12:30 | 234 | 234
2017-04-16 13:00 | 241 | 241
2017-04-16 13:30 | 241 | 241
2017-04-16 14:00 | 238 | 238
2017-04-16 14:30 | 236 | 236
2017-04-16 15:00 | 242 | 242
2017-04-16 15:30 | 252 | 252
2017-04-16 16:00 | 258 | 258
2017-04-16 16:30 | 262 | 262
2017-04-16 17:00 | 267 | 267
2017-04-16 17:30 | 275 | 275
2017-04-16 18:00 | 275 | 275
2017-04-16 18:30 | 274 | 274
2017-04-16 19:00 | 266 | 266
2017-04-16 19:30 | 267 | 267
2017-04-16 20:00 | 264 | 264
2017-04-16 20:30 | 257 | 257
2017-04-16 21:00 | 253 | 253
2017-04-16 21:30 | 248 | 248
2017-04-16 22:00 | 247 | 247
2017-04-16 22:30 | 246 | 246
2017-04-16 23:00 | 236 | 236
2017-04-16 23:30 | 223 | 222
2017-04-17 | 210 | 209
2017-04-17 00:30 | 205 | 204
2017-04-17 01:00 | 201 | 200
2017-04-17 01:30 | 195 | 194
2017-04-17 02:00 | 192 | 192
2017-04-17 02:30 | 189 | 189
2017-04-17 03:00 | 189 | 189
2017-04-17 03:30 | 188 | 188
2017-04-17 04:00 | 188 | 188
2017-04-17 04:30 | 190 | 190
2017-04-17 05:00 | 194 | 194
2017-04-17 05:30 | 196 | 196
2017-04-17 06:00 | 201 | 201
2017-04-17 06:30 | 211 | 210
2017-04-17 07:00 | 223 | 222
2017-04-17 07:30 | 228 | 228
2017-04-17 08:00 | 239 | 239
2017-04-17 08:30 | 245 | 245
2017-04-17 09:00 | 246 | 246
2017-04-17 09:30 | 249 | 249
2017-04-17 10:00 | 250 | 250
2017-04-17 10:30 | 248 | 248
2017-04-17 11:00 | 247 | 247
2017-04-17 11:30 | 244 | 244
2017-04-17 12:00 | 241 | 241
2017-04-17 12:30 | 243 | 242
2017-04-17 13:00 | 246 | 246
2017-04-17 13:30 | 247 | 246
2017-04-17 14:00 | 252 | 252
2017-04-17 14:30 | 257 | 257
2017-04-17 15:00 | 262 | 261
2017-04-17 15:30 | 273 | 272
2017-04-17 16:00 | 283 | 283
2017-04-17 16:30 | 292 | 290
2017-04-17 17:00 | 296 | 294
2017-04-17 17:30 | 305 | 304
2017-04-17 18:00 | 306 | 305
2017-04-17 18:30 | 302 | 301
2017-04-17 19:00 | 292 | 292
2017-04-17 19:30 | 289 | 289
2017-04-17 20:00 | 283 | 283
2017-04-17 20:30 | 271 | 271
2017-04-17 21:00 | 260 | 260
2017-04-17 21:30 | 252 | 252
2017-04-17 22:00 | 247 | 247
2017-04-17 22:30 | 246 | 246
2017-04-17 23:00 | 233 | 233
2017-04-17 23:30 | 221 | 220
2017-04-18 | 208 | 207
2017-04-18 00:30 | 203 | 202
2017-04-18 01:00 | 196 | 195
2017-04-18 01:30 | 191 | 191
2017-04-18 02:00 | 190 | 189
2017-04-18 02:30 | 188 | 188
2017-04-18 03:00 | 188 | 188
2017-04-18 03:30 | 190 | 189
2017-04-18 04:00 | 192 | 192
2017-04-18 04:30 | 197 | 197
2017-04-18 05:00 | 209 | 209
2017-04-18 05:30 | 225 | 225
2017-04-18 06:00 | 243 | 243
2017-04-18 06:30 | 256 | 255
2017-04-18 07:00 | 272 | 271
2017-04-18 07:30 | 280 | 278
2017-04-18 08:00 | 280 | 279
2017-04-18 08:30 | 278 | 278
2017-04-18 09:00 | 282 | 282
2017-04-18 09:30 | 284 | 284
2017-04-18 10:00 | 282 | 282
2017-04-18 10:30 | 278 | 278
2017-04-18 11:00 | 274 | 274
2017-04-18 11:30 | 276 | 276
2017-04-18 12:00 | 278 | 278
2017-04-18 12:30 | 281 | 281
2017-04-18 13:00 | 283 | 283
2017-04-18 13:30 | 288 | 288
2017-04-18 14:00 | 294 | 294
2017-04-18 14:30 | 291 | 291
2017-04-18 15:00 | 294 | 294
2017-04-18 15:30 | 301 | 301
2017-04-18 16:00 | 308 | 308
2017-04-18 16:30 | 314 | 314
2017-04-18 17:00 | 318 | 318
2017-04-18 17:30 | 327 | 327
2017-04-18 18:00 | 323 | 323
2017-04-18 18:30 | 320 | 320
2017-04-18 19:00 | 314 | 314
2017-04-18 19:30 | 314 | 313
2017-04-18 20:00 | 306 | 305
2017-04-18 20:30 | 294 | 293
2017-04-18 21:00 | 279 | 278
2017-04-18 21:30 | 268 | 267
2017-04-18 22:00 | 258 | 256
2017-04-18 22:30 | 251 | 248
2017-04-18 23:00 | 240 | 236
2017-04-18 23:30 | 227 | 222
2017-04-19 | 216 | 210
2017-04-19 00:30 | 211 | 205
2017-04-19 01:00 | 206 | 199
2017-04-19 01:30 | 205 | 198
2017-04-19 02:00 | 203 | 196
2017-04-19 02:30 | 197 | 191
2017-04-19 03:00 | 196 | 191
2017-04-19 03:30 | 197 | 192
2017-04-19 04:00 | 201 | 196
2017-04-19 04:30 | 207 | 203
2017-04-19 05:00 | 215 | 212
2017-04-19 05:30 | 225 | 223
2017-04-19 06:00 | 240 | 239
2017-04-19 06:30 | 252 | 251
2017-04-19 07:00 | 278 | 277
2017-04-19 07:30 | 289 | 286
2017-04-19 08:00 | 291 | 288
2017-04-19 08:30 | 294 | 289
2017-04-19 09:00 | 294 | 289
2017-04-19 09:30 | 296 | 292
2017-04-19 10:00 | 305 | 303
2017-04-19 10:30 | 300 | 298
2017-04-19 11:00 | 287 | 286
2017-04-19 11:30 | 295 | 294
2017-04-19 12:00 | 287 | 285
2017-04-19 12:30 | 282 | 281
2017-04-19 13:00 | 284 | 283
2017-04-19 13:30 | 288 | 287
2017-04-19 14:00 | 293 | 292
2017-04-19 14:30 | 292 | 291
2017-04-19 15:00 | 292 | 291
2017-04-19 15:30 | 297 | 296
2017-04-19 16:00 | 303 | 302
2017-04-19 16:30 | 311 | 310
2017-04-19 17:00 | 319 | 318
2017-04-19 17:30 | 328 | 327
2017-04-19 18:00 | 326 | 326
2017-04-19 18:30 | 325 | 324
2017-04-19 19:00 | 314 | 313
2017-04-19 19:30 | 307 | 307
2017-04-19 20:00 | 299 | 299
2017-04-19 20:30 | 290 | 290
2017-04-19 21:00 | 275 | 275
2017-04-19 21:30 | 261 | 261
2017-04-19 22:00 | 250 | 250
2017-04-19 22:30 | 247 | 246
2017-04-19 23:00 | 235 | 235
2017-04-19 23:30 | 224 | 223
2017-04-20 | 206 | 206
2017-04-20 00:30 | 202 | 201
2017-04-20 01:00 | 198 | 197
2017-04-20 01:30 | 194 | 193
2017-04-20 02:00 | 191 | 190
2017-04-20 02:30 | 189 | 189
2017-04-20 03:00 | 189 | 189
2017-04-20 03:30 | 190 | 190
2017-04-20 04:00 | 192 | 192
2017-04-20 04:30 | 198 | 198
2017-04-20 05:00 | 208 | 208
2017-04-20 05:30 | 219 | 219
2017-04-20 06:00 | 238 | 238
2017-04-20 06:30 | 253 | 252
2017-04-20 07:00 | 275 | 275
2017-04-20 07:30 | 287 | 287
2017-04-20 08:00 | 289 | 289
2017-04-20 08:30 | 290 | 290
2017-04-20 09:00 | 284 | 284
2017-04-20 09:30 | 280 | 279
2017-04-20 10:00 | 284 | 284
2017-04-20 10:30 | 276 | 276
2017-04-20 11:00 | 272 | 271
2017-04-20 11:30 | 279 | 278
2017-04-20 12:00 | 274 | 273
2017-04-20 12:30 | 277 | 276
2017-04-20 13:00 | 281 | 280
2017-04-20 13:30 | 283 | 283
2017-04-20 14:00 | 289 | 288
2017-04-20 14:30 | 292 | 291
2017-04-20 15:00 | 289 | 288
2017-04-20 15:30 | 300 | 299
2017-04-20 16:00 | 308 | 308
2017-04-20 16:30 | 313 | 313
2017-04-20 17:00 | 319 | 319
2017-04-20 17:30 | 326 | 326
2017-04-20 18:00 | 326 | 326
2017-04-20 18:30 | 323 | 323
2017-04-20 19:00 | 317 | 317
2017-04-20 19:30 | 317 | 316
2017-04-20 20:00 | 307 | 307
2017-04-20 20:30 | 297 | 297
2017-04-20 21:00 | 285 | 285
2017-04-20 21:30 | 270 | 270
2017-04-20 22:00 | 259 | 259
2017-04-20 22:30 | 252 | 252
2017-04-20 23:00 | 239 | 239
2017-04-20 23:30 | 227 | 227
2017-04-21 | 214 | 213
2017-04-21 00:30 | 207 | 206
2017-04-21 01:00 | 202 | 201
2017-04-21 01:30 | 200 | 199
2017-04-21 02:00 | 200 | 199
2017-04-21 02:30 | 200 | 199
2017-04-21 03:00 | 201 | 200
2017-04-21 03:30 | 200 | 199
2017-04-21 04:00 | 206 | 205
2017-04-21 04:30 | 206 | 205
2017-04-21 05:00 | 205 | 204
2017-04-21 05:30 | 215 | 215
2017-04-21 06:00 | 229 | 229
2017-04-21 06:30 | 242 | 242
2017-04-21 07:00 | 260 | 260
2017-04-21 07:30 | 268 | 268
2017-04-21 08:00 | 273 | 273
2017-04-21 08:30 | 270 | 270
2017-04-21 09:00 | 276 | 276
2017-04-21 09:30 | 286 | 286
2017-04-21 10:00 | 284 | 284
2017-04-21 10:30 | 278 | 277
2017-04-21 11:00 | 276 | 275
2017-04-21 11:30 | 277 | 276
2017-04-21 12:00 | 276 | 275
2017-04-21 12:30 | 277 | 276
2017-04-21 13:00 | 280 | 279
2017-04-21 13:30 | 277 | 276
2017-04-21 14:00 | 281 | 280
2017-04-21 14:30 | 285 | 283
2017-04-21 15:00 | 292 | 290
2017-04-21 15:30 | 294 | 292
2017-04-21 16:00 | 293 | 292
2017-04-21 16:30 | 302 | 300
2017-04-21 17:00 | 307 | 305
2017-04-21 17:30 | 316 | 315
2017-04-21 18:00 | 309 | 309
2017-04-21 18:30 | 308 | 307
2017-04-21 19:00 | 302 | 302
2017-04-21 19:30 | 298 | 298
2017-04-21 20:00 | 293 | 293
2017-04-21 20:30 | 280 | 280
2017-04-21 21:00 | 271 | 270
2017-04-21 21:30 | 260 | 260
2017-04-21 22:00 | 246 | 246
2017-04-21 22:30 | 246 | 245
2017-04-21 23:00 | 234 | 234
2017-04-21 23:30 | 225 | 224
2017-04-22 | 212 | 211
2017-04-22 00:30 | 204 | 204
2017-04-22 01:00 | 197 | 197
2017-04-22 01:30 | 194 | 194
2017-04-22 02:00 | 191 | 191
2017-04-22 02:30 | 190 | 189
2017-04-22 03:00 | 190 | 190
2017-04-22 03:30 | 189 | 189
2017-04-22 04:00 | 191 | 191
2017-04-22 04:30 | 194 | 194
2017-04-22 05:00 | 203 | 203
2017-04-22 05:30 | 209 | 209
2017-04-22 06:00 | 218 | 218
2017-04-22 06:30 | 227 | 227
2017-04-22 07:00 | 240 | 239
2017-04-22 07:30 | 245 | 245
2017-04-22 08:00 | 251 | 251
2017-04-22 08:30 | 254 | 254
2017-04-22 09:00 | 255 | 255
2017-04-22 09:30 | 255 | 254
2017-04-22 10:00 | 254 | 254
2017-04-22 10:30 | 248 | 248
2017-04-22 11:00 | 245 | 245
2017-04-22 11:30 | 237 | 237
2017-04-22 12:00 | 233 | 233
2017-04-22 12:30 | 228 | 228
2017-04-22 13:00 | 230 | 230
2017-04-22 13:30 | 232 | 231
2017-04-22 14:00 | 236 | 236
2017-04-22 14:30 | 243 | 243
2017-04-22 15:00 | 249 | 249
2017-04-22 15:30 | 259 | 259
2017-04-22 16:00 | 272 | 271
2017-04-22 16:30 | 283 | 283
2017-04-22 17:00 | 292 | 290
2017-04-22 17:30 | 303 | 302
2017-04-22 18:00 | 300 | 299
2017-04-22 18:30 | 295 | 294
2017-04-22 19:00 | 289 | 288
2017-04-22 19:30 | 285 | 284
2017-04-22 20:00 | 276 | 276
2017-04-22 20:30 | 263 | 263
2017-04-22 21:00 | 256 | 256
2017-04-22 21:30 | 248 | 248
2017-04-22 22:00 | 250 | 250
2017-04-22 22:30 | 251 | 251
2017-04-22 23:00 | 237 | 237
2017-04-22 23:30 | 217 | 217
2017-04-23 | 200 | 200
2017-04-23 00:30 | 191 | 190
2017-04-23 01:00 | 183 | 182
2017-04-23 01:30 | 175 | 175
2017-04-23 02:00 | 171 | 170
2017-04-23 02:30 | 168 | 168
2017-04-23 03:00 | 168 | 167
2017-04-23 03:30 | 167 | 167
2017-04-23 04:00 | 168 | 168
2017-04-23 04:30 | 171 | 171
2017-04-23 05:00 | 174 | 174
2017-04-23 05:30 | 180 | 179
2017-04-23 06:00 | 185 | 185
2017-04-23 06:30 | 194 | 194
2017-04-23 07:00 | 203 | 203
2017-04-23 07:30 | 210 | 210
2017-04-23 08:00 | 220 | 220
2017-04-23 08:30 | 225 | 224
2017-04-23 09:00 | 226 | 226
2017-04-23 09:30 | 227 | 227
2017-04-23 10:00 | 229 | 228
2017-04-23 10:30 | 229 | 229
2017-04-23 11:00 | 229 | 228
2017-04-23 11:30 | 221 | 220
2017-04-23 12:00 | 221 | 220
2017-04-23 12:30 | 223 | 223
2017-04-23 13:00 | 230 | 230
2017-04-23 13:30 | 234 | 233
2017-04-23 14:00 | 230 | 230
2017-04-23 14:30 | 236 | 236
2017-04-23 15:00 | 245 | 245
2017-04-23 15:30 | 257 | 257
2017-04-23 16:00 | 272 | 271
2017-04-23 16:30 | 284 | 284
2017-04-23 17:00 | 291 | 291
2017-04-23 17:30 | 299 | 299
2017-04-23 18:00 | 296 | 296
2017-04-23 18:30 | 289 | 289
2017-04-23 19:00 | 281 | 280
2017-04-23 19:30 | 278 | 277
2017-04-23 20:00 | 275 | 274
2017-04-23 20:30 | 269 | 267
2017-04-23 21:00 | 257 | 257
2017-04-23 21:30 | 247 | 247
2017-04-23 22:00 | 246 | 246
2017-04-23 22:30 | 246 | 246
2017-04-23 23:00 | 232 | 231
2017-04-23 23:30 | 212 | 212
2017-04-24 | 196 | 196
2017-04-24 00:30 | 187 | 186
2017-04-24 01:00 | 180 | 179
2017-04-24 01:30 | 173 | 173
2017-04-24 02:00 | 170 | 169
2017-04-24 02:30 | 168 | 168
2017-04-24 03:00 | 168 | 168
2017-04-24 03:30 | 169 | 169
2017-04-24 04:00 | 173 | 173
2017-04-24 04:30 | 179 | 179
2017-04-24 05:00 | 194 | 194
2017-04-24 05:30 | 210 | 210
2017-04-24 06:00 | 229 | 229
2017-04-24 06:30 | 246 | 246
2017-04-24 07:00 | 267 | 267
2017-04-24 07:30 | 273 | 272
2017-04-24 08:00 | 271 | 271
2017-04-24 08:30 | 266 | 266
2017-04-24 09:00 | 266 | 266
2017-04-24 09:30 | 264 | 264
2017-04-24 10:00 | 269 | 269
2017-04-24 10:30 | 268 | 268
2017-04-24 11:00 | 266 | 266
2017-04-24 11:30 | 263 | 263
2017-04-24 12:00 | 263 | 263
2017-04-24 12:30 | 262 | 262
2017-04-24 13:00 | 263 | 263
2017-04-24 13:30 | 265 | 265
2017-04-24 14:00 | 274 | 274
2017-04-24 14:30 | 280 | 280
2017-04-24 15:00 | 289 | 289
2017-04-24 15:30 | 296 | 296
2017-04-24 16:00 | 302 | 302
2017-04-24 16:30 | 308 | 307
2017-04-24 17:00 | 311 | 310
2017-04-24 17:30 | 322 | 322
2017-04-24 18:00 | 320 | 320
2017-04-24 18:30 | 315 | 314
2017-04-24 19:00 | 307 | 307
2017-04-24 19:30 | 304 | 304
2017-04-24 20:00 | 293 | 293
2017-04-24 20:30 | 282 | 282
2017-04-24 21:00 | 272 | 272
2017-04-24 21:30 | 267 | 267
2017-04-24 22:00 | 253 | 253
2017-04-24 22:30 | 251 | 251
2017-04-24 23:00 | 238 | 238
2017-04-24 23:30 | 223 | 223
2017-04-25 | 209 | 209
2017-04-25 00:30 | 204 | 203
2017-04-25 01:00 | 203 | 203
2017-04-25 01:30 | 194 | 193
2017-04-25 02:00 | 190 | 188
2017-04-25 02:30 | 193 | 191
2017-04-25 03:00 | 192 | 191
2017-04-25 03:30 | 191 | 190
2017-04-25 04:00 | 189 | 187
2017-04-25 04:30 | 192 | 191
2017-04-25 05:00 | 193 | 192
2017-04-25 05:30 | 197 | 196
2017-04-25 06:00 | 202 | 200
2017-04-25 06:30 | 208 | 206
2017-04-25 07:00 | 214 | 213
2017-04-25 07:30 | 226 | 225
2017-04-25 08:00 | 232 | 232
2017-04-25 08:30 | 231 | 231
2017-04-25 09:00 | 239 | 239
2017-04-25 09:30 | 250 | 250
2017-04-25 10:00 | 253 | 253
2017-04-25 10:30 | 249 | 249
2017-04-25 11:00 | 243 | 243
2017-04-25 11:30 | 235 | 235
2017-04-25 12:00 | 234 | 234
2017-04-25 12:30 | 235 | 234
2017-04-25 13:00 | 234 | 234
2017-04-25 13:30 | 233 | 233
2017-04-25 14:00 | 236 | 236
2017-04-25 14:30 | 240 | 240
2017-04-25 15:00 | 244 | 244
2017-04-25 15:30 | 251 | 251
2017-04-25 16:00 | 259 | 259
2017-04-25 16:30 | 271 | 271
2017-04-25 17:00 | 278 | 278
2017-04-25 17:30 | 287 | 286
2017-04-25 18:00 | 288 | 288
2017-04-25 18:30 | 286 | 286
2017-04-25 19:00 | 278 | 278
2017-04-25 19:30 | 272 | 272
2017-04-25 20:00 | 270 | 270
2017-04-25 20:30 | 260 | 260
2017-04-25 21:00 | 250 | 250
2017-04-25 21:30 | 243 | 243
2017-04-25 22:00 | 238 | 238
2017-04-25 22:30 | 233 | 233
2017-04-25 23:00 | 221 | 221
2017-04-25 23:30 | 208 | 207
2017-04-26 | 197 | 196
2017-04-26 00:30 | 194 | 193
2017-04-26 01:00 | 187 | 186
2017-04-26 01:30 | 179 | 179
2017-04-26 02:00 | 181 | 180
2017-04-26 02:30 | 183 | 183
2017-04-26 03:00 | 181 | 181
2017-04-26 03:30 | 184 | 184
2017-04-26 04:00 | 187 | 187
2017-04-26 04:30 | 192 | 192
2017-04-26 05:00 | 199 | 199
2017-04-26 05:30 | 211 | 211
2017-04-26 06:00 | 228 | 228
2017-04-26 06:30 | 248 | 248
2017-04-26 07:00 | 269 | 269
2017-04-26 07:30 | 285 | 285
2017-04-26 08:00 | 294 | 293
2017-04-26 08:30 | 298 | 298
2017-04-26 09:00 | 302 | 302
2017-04-26 09:30 | 298 | 298
2017-04-26 10:00 | 291 | 291
2017-04-26 10:30 | 295 | 295
2017-04-26 11:00 | 305 | 305
2017-04-26 11:30 | 299 | 299
2017-04-26 12:00 | 298 | 298
2017-04-26 12:30 | 292 | 292
2017-04-26 13:00 | 284 | 284
2017-04-26 13:30 | 289 | 289
2017-04-26 14:00 | 292 | 292
2017-04-26 14:30 | 288 | 288
2017-04-26 15:00 | 281 | 281
2017-04-26 15:30 | 277 | 277
2017-04-26 16:00 | 291 | 291
2017-04-26 16:30 | 303 | 303
2017-04-26 17:00 | 318 | 318
2017-04-26 17:30 | 325 | 325
2017-04-26 18:00 | 319 | 319
2017-04-26 18:30 | 316 | 316
2017-04-26 19:00 | 307 | 307
2017-04-26 19:30 | 306 | 306
2017-04-26 20:00 | 300 | 300
2017-04-26 20:30 | 288 | 288
2017-04-26 21:00 | 273 | 273
2017-04-26 21:30 | 263 | 263
2017-04-26 22:00 | 250 | 249
2017-04-26 22:30 | 244 | 243
2017-04-26 23:00 | 233 | 232
2017-04-26 23:30 | 220 | 219
2017-04-27 | 210 | 209
2017-04-27 00:30 | 203 | 202
2017-04-27 01:00 | 197 | 195
2017-04-27 01:30 | 192 | 190
2017-04-27 02:00 | 195 | 193
2017-04-27 02:30 | 196 | 195
2017-04-27 03:00 | 194 | 192
2017-04-27 03:30 | 194 | 193
2017-04-27 04:00 | 199 | 198
2017-04-27 04:30 | 205 | 204
2017-04-27 05:00 | 215 | 214
2017-04-27 05:30 | 225 | 224
2017-04-27 06:00 | 239 | 239
2017-04-27 06:30 | 252 | 252
2017-04-27 07:00 | 271 | 271
2017-04-27 07:30 | 271 | 271
2017-04-27 08:00 | 269 | 269
2017-04-27 08:30 | 263 | 263
2017-04-27 09:00 | 257 | 257
2017-04-27 09:30 | 255 | 255
2017-04-27 10:00 | 252 | 252
2017-04-27 10:30 | 253 | 252
2017-04-27 11:00 | 247 | 247
2017-04-27 11:30 | 247 | 246
2017-04-27 12:00 | 244 | 244
2017-04-27 12:30 | 244 | 244
2017-04-27 13:00 | 249 | 248
2017-04-27 13:30 | 254 | 253
2017-04-27 14:00 | 263 | 262
2017-04-27 14:30 | 266 | 266
2017-04-27 15:00 | 272 | 271
2017-04-27 15:30 | 277 | 277
2017-04-27 16:00 | 287 | 287
2017-04-27 16:30 | 297 | 297
2017-04-27 17:00 | 307 | 306
2017-04-27 17:30 | 320 | 320
2017-04-27 18:00 | 325 | 325
2017-04-27 18:30 | 320 | 319
2017-04-27 19:00 | 312 | 312
2017-04-27 19:30 | 310 | 310
2017-04-27 20:00 | 301 | 301
2017-04-27 20:30 | 289 | 289
2017-04-27 21:00 | 275 | 275
2017-04-27 21:30 | 263 | 263
2017-04-27 22:00 | 251 | 251
2017-04-27 22:30 | 247 | 247
2017-04-27 23:00 | 237 | 236
2017-04-27 23:30 | 223 | 223
2017-04-28 | 202 | 202
2017-04-28 00:30 | 191 | 191
2017-04-28 01:00 | 189 | 189
2017-04-28 01:30 | 188 | 188
2017-04-28 02:00 | 191 | 191
2017-04-28 02:30 | 193 | 193
2017-04-28 03:00 | 194 | 193
2017-04-28 03:30 | 196 | 196
2017-04-28 04:00 | 200 | 200
2017-04-28 04:30 | 205 | 205
2017-04-28 05:00 | 210 | 210
2017-04-28 05:30 | 217 | 217
2017-04-28 06:00 | 229 | 229
2017-04-28 06:30 | 242 | 242
2017-04-28 07:00 | 265 | 264
2017-04-28 07:30 | 274 | 274
2017-04-28 08:00 | 273 | 273
2017-04-28 08:30 | 265 | 264
2017-04-28 09:00 | 260 | 259
2017-04-28 09:30 | 258 | 257
2017-04-28 10:00 | 255 | 254
2017-04-28 10:30 | 252 | 251
2017-04-28 11:00 | 248 | 247
2017-04-28 11:30 | 251 | 250
2017-04-28 12:00 | 257 | 256
2017-04-28 12:30 | 259 | 259
2017-04-28 13:00 | 262 | 261
2017-04-28 13:30 | 273 | 272
2017-04-28 14:00 | 273 | 272
2017-04-28 14:30 | 265 | 264
2017-04-28 15:00 | 271 | 271
2017-04-28 15:30 | 275 | 274
2017-04-28 16:00 | 285 | 285
2017-04-28 16:30 | 292 | 291
2017-04-28 17:00 | 299 | 299
2017-04-28 17:30 | 308 | 307
2017-04-28 18:00 | 305 | 304
2017-04-28 18:30 | 301 | 301
2017-04-28 19:00 | 292 | 291
2017-04-28 19:30 | 286 | 286
2017-04-28 20:00 | 283 | 283
2017-04-28 20:30 | 279 | 279
2017-04-28 21:00 | 266 | 266
2017-04-28 21:30 | 262 | 262
2017-04-28 22:00 | 256 | 256
2017-04-28 22:30 | 250 | 250
2017-04-28 23:00 | 237 | 237
2017-04-28 23:30 | 225 | 224
2017-04-29 | 210 | 210
2017-04-29 00:30 | 205 | 205
2017-04-29 01:00 | 200 | 200
2017-04-29 01:30 | 195 | 195
2017-04-29 02:00 | 194 | 194
2017-04-29 02:30 | 190 | 190
2017-04-29 03:00 | 187 | 187
2017-04-29 03:30 | 189 | 189
2017-04-29 04:00 | 190 | 190
2017-04-29 04:30 | 190 | 189
2017-04-29 05:00 | 193 | 193
2017-04-29 05:30 | 201 | 201
2017-04-29 06:00 | 211 | 211
2017-04-29 06:30 | 220 | 220
2017-04-29 07:00 | 230 | 230
2017-04-29 07:30 | 237 | 237
2017-04-29 08:00 | 245 | 244
2017-04-29 08:30 | 245 | 244
2017-04-29 09:00 | 243 | 243
2017-04-29 09:30 | 241 | 240
2017-04-29 10:00 | 239 | 238
2017-04-29 10:30 | 236 | 234
2017-04-29 11:00 | 231 | 230
2017-04-29 11:30 | 230 | 229
2017-04-29 12:00 | 229 | 228
2017-04-29 12:30 | 228 | 227
2017-04-29 13:00 | 227 | 226
2017-04-29 13:30 | 231 | 230
2017-04-29 14:00 | 239 | 238
2017-04-29 14:30 | 242 | 241
2017-04-29 15:00 | 247 | 246
2017-04-29 15:30 | 253 | 252
2017-04-29 16:00 | 259 | 258
2017-04-29 16:30 | 266 | 266
2017-04-29 17:00 | 274 | 274
2017-04-29 17:30 | 285 | 285
2017-04-29 18:00 | 286 | 285
2017-04-29 18:30 | 283 | 282
2017-04-29 19:00 | 277 | 276
2017-04-29 19:30 | 275 | 275
2017-04-29 20:00 | 269 | 269
2017-04-29 20:30 | 260 | 260
2017-04-29 21:00 | 250 | 250
2017-04-29 21:30 | 242 | 242
2017-04-29 22:00 | 240 | 240
2017-04-29 22:30 | 239 | 239
2017-04-29 23:00 | 230 | 229
2017-04-29 23:30 | 218 | 218
2017-04-30 | 202 | 202
2017-04-30 00:30 | 196 | 196
2017-04-30 01:00 | 192 | 191
2017-04-30 01:30 | 187 | 187
2017-04-30 02:00 | 182 | 182
2017-04-30 02:30 | 179 | 179
2017-04-30 03:00 | 178 | 178
2017-04-30 03:30 | 177 | 177
2017-04-30 04:00 | 178 | 178
2017-04-30 04:30 | 179 | 179
2017-04-30 05:00 | 182 | 182
2017-04-30 05:30 | 187 | 187
2017-04-30 06:00 | 193 | 193
2017-04-30 06:30 | 197 | 197
2017-04-30 07:00 | 206 | 206
2017-04-30 07:30 | 214 | 214
2017-04-30 08:00 | 223 | 222
2017-04-30 08:30 | 228 | 227
2017-04-30 09:00 | 235 | 233
2017-04-30 09:30 | 238 | 237
2017-04-30 10:00 | 239 | 238
2017-04-30 10:30 | 234 | 233
2017-04-30 11:00 | 227 | 226
2017-04-30 11:30 | 223 | 223
2017-04-30 12:00 | 220 | 220
2017-04-30 12:30 | 219 | 218
2017-04-30 13:00 | 219 | 219
2017-04-30 13:30 | 221 | 221
2017-04-30 14:00 | 226 | 226
2017-04-30 14:30 | 230 | 230
2017-04-30 15:00 | 236 | 236
2017-04-30 15:30 | 245 | 245
2017-04-30 16:00 | 256 | 256
2017-04-30 16:30 | 267 | 267
2017-04-30 17:00 | 275 | 275
2017-04-30 17:30 | 281 | 281
2017-04-30 18:00 | 278 | 278
2017-04-30 18:30 | 273 | 273
2017-04-30 19:00 | 268 | 267
2017-04-30 19:30 | 268 | 268
2017-04-30 20:00 | 262 | 262
2017-04-30 20:30 | 250 | 250
2017-04-30 21:00 | 246 | 246
2017-04-30 21:30 | 238 | 238
2017-04-30 22:00 | 238 | 238
2017-04-30 22:30 | 237 | 237
2017-04-30 23:00 | 223 | 223
2017-04-30 23:30 | 212 | 212
2017-05-01 | 197 | 197
2017-05-01 00:30 | 187 | 187
2017-05-01 01:00 | 180 | 180
2017-05-01 01:30 | 177 | 177
2017-05-01 02:00 | 174 | 174
2017-05-01 02:30 | 173 | 173
2017-05-01 03:00 | 171 | 171
2017-05-01 03:30 | 170 | 170
2017-05-01 04:00 | 165 | 165
2017-05-01 04:30 | 170 | 170
2017-05-01 05:00 | 174 | 174
2017-05-01 05:30 | 179 | 179
2017-05-01 06:00 | 189 | 189
2017-05-01 06:30 | 196 | 196
2017-05-01 07:00 | 205 | 205
2017-05-01 07:30 | 212 | 212
2017-05-01 08:00 | 220 | 219
2017-05-01 08:30 | 224 | 223
2017-05-01 09:00 | 228 | 227
2017-05-01 09:30 | 227 | 226
2017-05-01 10:00 | 222 | 222
2017-05-01 10:30 | 220 | 220
2017-05-01 11:00 | 218 | 217
2017-05-01 11:30 | 216 | 215
2017-05-01 12:00 | 216 | 216
2017-05-01 12:30 | 215 | 215
2017-05-01 13:00 | 216 | 215
2017-05-01 13:30 | 224 | 223
2017-05-01 14:00 | 226 | 225
2017-05-01 14:30 | 231 | 230
2017-05-01 15:00 | 243 | 242
2017-05-01 15:30 | 254 | 254
2017-05-01 16:00 | 261 | 261
2017-05-01 16:30 | 272 | 272
2017-05-01 17:00 | 282 | 282
2017-05-01 17:30 | 288 | 288
2017-05-01 18:00 | 285 | 285
2017-05-01 18:30 | 284 | 284
2017-05-01 19:00 | 276 | 276
2017-05-01 19:30 | 272 | 272
2017-05-01 20:00 | 264 | 264
2017-05-01 20:30 | 246 | 245
2017-05-01 21:00 | 237 | 236
2017-05-01 21:30 | 231 | 231
2017-05-01 22:00 | 228 | 228
2017-05-01 22:30 | 227 | 226
2017-05-01 23:00 | 219 | 218
2017-05-01 23:30 | 209 | 209
2017-05-02 | 194 | 194
2017-05-02 00:30 | 186 | 186
2017-05-02 01:00 | 180 | 180
2017-05-02 01:30 | 176 | 176
2017-05-02 02:00 | 173 | 173
2017-05-02 02:30 | 172 | 172
2017-05-02 03:00 | 173 | 173
2017-05-02 03:30 | 173 | 173
2017-05-02 04:00 | 180 | 180
2017-05-02 04:30 | 184 | 184
2017-05-02 05:00 | 195 | 195
2017-05-02 05:30 | 207 | 207
2017-05-02 06:00 | 229 | 229
2017-05-02 06:30 | 250 | 249
2017-05-02 07:00 | 264 | 264
2017-05-02 07:30 | 269 | 269
2017-05-02 08:00 | 260 | 260
2017-05-02 08:30 | 256 | 256
2017-05-02 09:00 | 252 | 251
2017-05-02 09:30 | 247 | 246
2017-05-02 10:00 | 244 | 244
2017-05-02 10:30 | 245 | 245
2017-05-02 11:00 | 242 | 241
2017-05-02 11:30 | 241 | 241
2017-05-02 12:00 | 246 | 246
2017-05-02 12:30 | 250 | 250
2017-05-02 13:00 | 261 | 261
2017-05-02 13:30 | 261 | 261
2017-05-02 14:00 | 263 | 263
2017-05-02 14:30 | 267 | 267
2017-05-02 15:00 | 275 | 275
2017-05-02 15:30 | 286 | 286
2017-05-02 16:00 | 294 | 294
2017-05-02 16:30 | 299 | 299
2017-05-02 17:00 | 308 | 308
2017-05-02 17:30 | 318 | 317
2017-05-02 18:00 | 312 | 311
2017-05-02 18:30 | 307 | 307
2017-05-02 19:00 | 295 | 295
2017-05-02 19:30 | 294 | 294
2017-05-02 20:00 | 289 | 289
2017-05-02 20:30 | 276 | 275
2017-05-02 21:00 | 262 | 262
2017-05-02 21:30 | 260 | 260
2017-05-02 22:00 | 252 | 251
2017-05-02 22:30 | 249 | 249
2017-05-02 23:00 | 238 | 238
2017-05-02 23:30 | 220 | 220
2017-05-03 | 205 | 205
2017-05-03 00:30 | 198 | 197
2017-05-03 01:00 | 192 | 192
2017-05-03 01:30 | 188 | 187
2017-05-03 02:00 | 185 | 184
2017-05-03 02:30 | 186 | 185
2017-05-03 03:00 | 186 | 186
2017-05-03 03:30 | 187 | 186
2017-05-03 04:00 | 188 | 187
2017-05-03 04:30 | 190 | 190
2017-05-03 05:00 | 198 | 198
2017-05-03 05:30 | 211 | 211
2017-05-03 06:00 | 229 | 229
2017-05-03 06:30 | 251 | 251
2017-05-03 07:00 | 267 | 267
2017-05-03 07:30 | 269 | 269
2017-05-03 08:00 | 267 | 267
2017-05-03 08:30 | 261 | 261
2017-05-03 09:00 | 257 | 257
2017-05-03 09:30 | 255 | 255
2017-05-03 10:00 | 254 | 254
2017-05-03 10:30 | 275 | 275
2017-05-03 11:00 | 275 | 275
2017-05-03 11:30 | 278 | 278
2017-05-03 12:00 | 277 | 277
2017-05-03 12:30 | 269 | 269
2017-05-03 13:00 | 265 | 264
2017-05-03 13:30 | 274 | 274
2017-05-03 14:00 | 282 | 282
2017-05-03 14:30 | 281 | 280
2017-05-03 15:00 | 278 | 277
2017-05-03 15:30 | 281 | 281
2017-05-03 16:00 | 290 | 289
2017-05-03 16:30 | 299 | 298
2017-05-03 17:00 | 305 | 304
2017-05-03 17:30 | 325 | 325
2017-05-03 18:00 | 325 | 324
2017-05-03 18:30 | 322 | 321
2017-05-03 19:00 | 309 | 309
2017-05-03 19:30 | 302 | 302
2017-05-03 20:00 | 294 | 294
2017-05-03 20:30 | 283 | 283
2017-05-03 21:00 | 267 | 267
2017-05-03 21:30 | 255 | 255
2017-05-03 22:00 | 250 | 250
2017-05-03 22:30 | 250 | 250
2017-05-03 23:00 | 235 | 235
2017-05-03 23:30 | 222 | 222
2017-05-04 | 209 | 209
2017-05-04 00:30 | 203 | 203
2017-05-04 01:00 | 197 | 196
2017-05-04 01:30 | 198 | 197
2017-05-04 02:00 | 195 | 195
2017-05-04 02:30 | 191 | 191
2017-05-04 03:00 | 191 | 191
2017-05-04 03:30 | 193 | 192
2017-05-04 04:00 | 192 | 191
2017-05-04 04:30 | 197 | 197
2017-05-04 05:00 | 206 | 205
2017-05-04 05:30 | 213 | 213
2017-05-04 06:00 | 236 | 236
2017-05-04 06:30 | 254 | 254
2017-05-04 07:00 | 273 | 273
2017-05-04 07:30 | 282 | 281
2017-05-04 08:00 | 278 | 277
2017-05-04 08:30 | 273 | 272
2017-05-04 09:00 | 272 | 271
2017-05-04 09:30 | 269 | 269
2017-05-04 10:00 | 262 | 262
2017-05-04 10:30 | 254 | 254
2017-05-04 11:00 | 257 | 257
2017-05-04 11:30 | 263 | 262
2017-05-04 12:00 | 263 | 262
2017-05-04 12:30 | 262 | 262
2017-05-04 13:00 | 263 | 263
2017-05-04 13:30 | 255 | 254
2017-05-04 14:00 | 264 | 264
2017-05-04 14:30 | 266 | 265
2017-05-04 15:00 | 264 | 264
2017-05-04 15:30 | 274 | 273
2017-05-04 16:00 | 283 | 283
2017-05-04 16:30 | 294 | 294
2017-05-04 17:00 | 306 | 306
2017-05-04 17:30 | 321 | 320
2017-05-04 18:00 | 326 | 324
2017-05-04 18:30 | 323 | 320
2017-05-04 19:00 | 312 | 309
2017-05-04 19:30 | 305 | 304
2017-05-04 20:00 | 301 | 301
2017-05-04 20:30 | 290 | 290
2017-05-04 21:00 | 273 | 273
2017-05-04 21:30 | 262 | 262
2017-05-04 22:00 | 258 | 258
2017-05-04 22:30 | 251 | 251
2017-05-04 23:00 | 237 | 237
2017-05-04 23:30 | 224 | 224
2017-05-05 | 206 | 205
2017-05-05 00:30 | 193 | 192
2017-05-05 01:00 | 184 | 183
2017-05-05 01:30 | 181 | 181
2017-05-05 02:00 | 179 | 178
2017-05-05 02:30 | 181 | 181
2017-05-05 03:00 | 179 | 179
2017-05-05 03:30 | 180 | 179
2017-05-05 04:00 | 184 | 184
2017-05-05 04:30 | 186 | 185
2017-05-05 05:00 | 195 | 195
2017-05-05 05:30 | 206 | 206
2017-05-05 06:00 | 228 | 228
2017-05-05 06:30 | 247 | 245
2017-05-05 07:00 | 264 | 263
2017-05-05 07:30 | 266 | 266
2017-05-05 08:00 | 261 | 261
2017-05-05 08:30 | 255 | 255
2017-05-05 09:00 | 251 | 251
2017-05-05 09:30 | 247 | 247
2017-05-05 10:00 | 242 | 242
2017-05-05 10:30 | 240 | 240
2017-05-05 11:00 | 241 | 241
2017-05-05 11:30 | 245 | 245
2017-05-05 12:00 | 245 | 245
2017-05-05 12:30 | 247 | 247
2017-05-05 13:00 | 241 | 241
2017-05-05 13:30 | 246 | 246
2017-05-05 14:00 | 258 | 258
2017-05-05 14:30 | 260 | 260
2017-05-05 15:00 | 260 | 260
2017-05-05 15:30 | 266 | 266
2017-05-05 16:00 | 275 | 275
2017-05-05 16:30 | 286 | 286
2017-05-05 17:00 | 295 | 295
2017-05-05 17:30 | 306 | 306
2017-05-05 18:00 | 302 | 302
2017-05-05 18:30 | 297 | 297
2017-05-05 19:00 | 288 | 288
2017-05-05 19:30 | 287 | 287
2017-05-05 20:00 | 282 | 281
2017-05-05 20:30 | 272 | 271
2017-05-05 21:00 | 264 | 263
2017-05-05 21:30 | 258 | 256
2017-05-05 22:00 | 244 | 244
2017-05-05 22:30 | 239 | 239
2017-05-05 23:00 | 229 | 228
2017-05-05 23:30 | 212 | 212
2017-05-06 | 198 | 197
2017-05-06 00:30 | 194 | 193
2017-05-06 01:00 | 188 | 186
2017-05-06 01:30 | 181 | 180
2017-05-06 02:00 | 175 | 175
2017-05-06 02:30 | 172 | 172
2017-05-06 03:00 | 171 | 171
2017-05-06 03:30 | 171 | 170
2017-05-06 04:00 | 172 | 171
2017-05-06 04:30 | 174 | 174
2017-05-06 05:00 | 182 | 182
2017-05-06 05:30 | 188 | 188
2017-05-06 06:00 | 198 | 198
2017-05-06 06:30 | 190 | 190
2017-05-06 07:00 | 202 | 202
2017-05-06 07:30 | 221 | 221
2017-05-06 08:00 | 236 | 236
2017-05-06 08:30 | 243 | 242
2017-05-06 09:00 | 244 | 243
2017-05-06 09:30 | 235 | 235
2017-05-06 10:00 | 227 | 227
2017-05-06 10:30 | 222 | 222
2017-05-06 11:00 | 219 | 218
2017-05-06 11:30 | 214 | 214
2017-05-06 12:00 | 209 | 208
2017-05-06 12:30 | 206 | 206
2017-05-06 13:00 | 207 | 207
2017-05-06 13:30 | 211 | 211
2017-05-06 14:00 | 218 | 218
2017-05-06 14:30 | 223 | 223
2017-05-06 15:00 | 232 | 232
2017-05-06 15:30 | 239 | 239
2017-05-06 16:00 | 254 | 254
2017-05-06 16:30 | 268 | 267
2017-05-06 17:00 | 282 | 281
2017-05-06 17:30 | 297 | 297
2017-05-06 18:00 | 284 | 283
2017-05-06 18:30 | 271 | 270
2017-05-06 19:00 | 265 | 264
2017-05-06 19:30 | 264 | 263
2017-05-06 20:00 | 259 | 258
2017-05-06 20:30 | 249 | 248
2017-05-06 21:00 | 245 | 245
2017-05-06 21:30 | 234 | 234
2017-05-06 22:00 | 235 | 235
2017-05-06 22:30 | 233 | 232
2017-05-06 23:00 | 222 | 222
2017-05-06 23:30 | 208 | 207
2017-05-07 | 194 | 193
2017-05-07 00:30 | 189 | 189
2017-05-07 01:00 | 183 | 182
2017-05-07 01:30 | 175 | 175
2017-05-07 02:00 | 174 | 173
2017-05-07 02:30 | 171 | 170
2017-05-07 03:00 | 170 | 169
2017-05-07 03:30 | 169 | 169
2017-05-07 04:00 | 170 | 170
2017-05-07 04:30 | 171 | 170
2017-05-07 05:00 | 175 | 175
2017-05-07 05:30 | 181 | 181
2017-05-07 06:00 | 188 | 188
2017-05-07 06:30 | 197 | 197
2017-05-07 07:00 | 208 | 208
2017-05-07 07:30 | 211 | 211
2017-05-07 08:00 | 218 | 218
2017-05-07 08:30 | 224 | 224
2017-05-07 09:00 | 224 | 224
2017-05-07 09:30 | 221 | 221
2017-05-07 10:00 | 218 | 218
2017-05-07 10:30 | 212 | 212
2017-05-07 11:00 | 208 | 208
2017-05-07 11:30 | 206 | 206
2017-05-07 12:00 | 204 | 204
2017-05-07 12:30 | 204 | 204
2017-05-07 13:00 | 206 | 206
2017-05-07 13:30 | 211 | 211
2017-05-07 14:00 | 216 | 215
2017-05-07 14:30 | 218 | 217
2017-05-07 15:00 | 224 | 224
2017-05-07 15:30 | 235 | 235
2017-05-07 16:00 | 251 | 251
2017-05-07 16:30 | 265 | 264
2017-05-07 17:00 | 267 | 266
2017-05-07 17:30 | 281 | 281
2017-05-07 18:00 | 282 | 281
2017-05-07 18:30 | 277 | 277
2017-05-07 19:00 | 270 | 269
2017-05-07 19:30 | 262 | 262
2017-05-07 20:00 | 262 | 262
2017-05-07 20:30 | 249 | 249
2017-05-07 21:00 | 241 | 241
2017-05-07 21:30 | 237 | 237
2017-05-07 22:00 | 230 | 230
2017-05-07 22:30 | 225 | 225
2017-05-07 23:00 | 215 | 215
2017-05-07 23:30 | 203 | 202
2017-05-08 | 188 | 188
2017-05-08 00:30 | 185 | 184
2017-05-08 01:00 | 182 | 181
2017-05-08 01:30 | 176 | 175
2017-05-08 02:00 | 173 | 173
2017-05-08 02:30 | 171 | 171
2017-05-08 03:00 | 171 | 170
2017-05-08 03:30 | 172 | 172
2017-05-08 04:00 | 176 | 176
2017-05-08 04:30 | 183 | 183
2017-05-08 05:00 | 192 | 192
2017-05-08 05:30 | 206 | 206
2017-05-08 06:00 | 228 | 228
2017-05-08 06:30 | 253 | 253
2017-05-08 07:00 | 277 | 276
2017-05-08 07:30 | 276 | 276
2017-05-08 08:00 | 276 | 276
2017-05-08 08:30 | 278 | 278
2017-05-08 09:00 | 282 | 281
2017-05-08 09:30 | 277 | 277
2017-05-08 10:00 | 271 | 271
2017-05-08 10:30 | 265 | 264
2017-05-08 11:00 | 272 | 272
2017-05-08 11:30 | 270 | 270
2017-05-08 12:00 | 276 | 275
2017-05-08 12:30 | 278 | 278
2017-05-08 13:00 | 269 | 269
2017-05-08 13:30 | 270 | 269
2017-05-08 14:00 | 280 | 280
2017-05-08 14:30 | 281 | 281
2017-05-08 15:00 | 277 | 276
2017-05-08 15:30 | 279 | 278
2017-05-08 16:00 | 286 | 285
2017-05-08 16:30 | 297 | 297
2017-05-08 17:00 | 316 | 315
2017-05-08 17:30 | 321 | 319
2017-05-08 18:00 | 314 | 313
2017-05-08 18:30 | 309 | 308
2017-05-08 19:00 | 298 | 297
2017-05-08 19:30 | 296 | 295
2017-05-08 20:00 | 291 | 291
2017-05-08 20:30 | 278 | 278
2017-05-08 21:00 | 270 | 270
2017-05-08 21:30 | 253 | 253
2017-05-08 22:00 | 241 | 241
2017-05-08 22:30 | 237 | 237
2017-05-08 23:00 | 224 | 224
2017-05-08 23:30 | 213 | 213
2017-05-09 | 199 | 198
2017-05-09 00:30 | 192 | 191
2017-05-09 01:00 | 186 | 185
2017-05-09 01:30 | 178 | 177
2017-05-09 02:00 | 178 | 177
2017-05-09 02:30 | 177 | 176
2017-05-09 03:00 | 178 | 178
2017-05-09 03:30 | 180 | 180
2017-05-09 04:00 | 181 | 181
2017-05-09 04:30 | 185 | 185
2017-05-09 05:00 | 195 | 195
2017-05-09 05:30 | 208 | 208
2017-05-09 06:00 | 229 | 229
2017-05-09 06:30 | 254 | 253
2017-05-09 07:00 | 274 | 273
2017-05-09 07:30 | 288 | 288
2017-05-09 08:00 | 289 | 289
2017-05-09 08:30 | 286 | 286
2017-05-09 09:00 | 271 | 271
2017-05-09 09:30 | 268 | 268
2017-05-09 10:00 | 269 | 269
2017-05-09 10:30 | 266 | 266
2017-05-09 11:00 | 258 | 258
2017-05-09 11:30 | 258 | 258
2017-05-09 12:00 | 257 | 257
2017-05-09 12:30 | 258 | 257
2017-05-09 13:00 | 253 | 253
2017-05-09 13:30 | 254 | 254
2017-05-09 14:00 | 262 | 262
2017-05-09 14:30 | 263 | 263
2017-05-09 15:00 | 261 | 261
2017-05-09 15:30 | 264 | 263
2017-05-09 16:00 | 271 | 270
2017-05-09 16:30 | 282 | 282
2017-05-09 17:00 | 299 | 299
2017-05-09 17:30 | 311 | 311
2017-05-09 18:00 | 303 | 303
2017-05-09 18:30 | 300 | 299
2017-05-09 19:00 | 291 | 291
2017-05-09 19:30 | 288 | 288
2017-05-09 20:00 | 282 | 281
2017-05-09 20:30 | 271 | 270
2017-05-09 21:00 | 256 | 255
2017-05-09 21:30 | 246 | 246
2017-05-09 22:00 | 240 | 240
2017-05-09 22:30 | 236 | 236
2017-05-09 23:00 | 220 | 220
2017-05-09 23:30 | 206 | 206
2017-05-10 | 192 | 191
2017-05-10 00:30 | 189 | 189
2017-05-10 01:00 | 185 | 185
2017-05-10 01:30 | 180 | 180
2017-05-10 02:00 | 178 | 178
2017-05-10 02:30 | 176 | 176
2017-05-10 03:00 | 174 | 174
2017-05-10 03:30 | 176 | 175
2017-05-10 04:00 | 180 | 180
2017-05-10 04:30 | 187 | 187
2017-05-10 05:00 | 196 | 196
2017-05-10 05:30 | 209 | 209
2017-05-10 06:00 | 232 | 232
2017-05-10 06:30 | 251 | 251
2017-05-10 07:00 | 271 | 271
2017-05-10 07:30 | 285 | 284
2017-05-10 08:00 | 287 | 286
2017-05-10 08:30 | 274 | 274
2017-05-10 09:00 | 279 | 279
2017-05-10 09:30 | 280 | 280
2017-05-10 10:00 | 282 | 282
2017-05-10 10:30 | 283 | 282
2017-05-10 11:00 | 283 | 282
2017-05-10 11:30 | 279 | 279
2017-05-10 12:00 | 273 | 272
2017-05-10 12:30 | 273 | 273
2017-05-10 13:00 | 269 | 268
2017-05-10 13:30 | 269 | 268
2017-05-10 14:00 | 277 | 276
2017-05-10 14:30 | 274 | 273
2017-05-10 15:00 | 278 | 277
2017-05-10 15:30 | 284 | 283
2017-05-10 16:00 | 290 | 289
2017-05-10 16:30 | 299 | 298
2017-05-10 17:00 | 318 | 315
2017-05-10 17:30 | 326 | 323
2017-05-10 18:00 | 321 | 318
2017-05-10 18:30 | 317 | 313
2017-05-10 19:00 | 309 | 305
2017-05-10 19:30 | 299 | 299
2017-05-10 20:00 | 293 | 293
2017-05-10 20:30 | 282 | 282
2017-05-10 21:00 | 271 | 270
2017-05-10 21:30 | 260 | 258
2017-05-10 22:00 | 252 | 250
2017-05-10 22:30 | 244 | 242
2017-05-10 23:00 | 233 | 230
2017-05-10 23:30 | 219 | 215
2017-05-11 | 206 | 201
2017-05-11 00:30 | 197 | 195
2017-05-11 01:00 | 192 | 190
2017-05-11 01:30 | 186 | 185
2017-05-11 02:00 | 181 | 179
2017-05-11 02:30 | 178 | 176
2017-05-11 03:00 | 177 | 175
2017-05-11 03:30 | 177 | 176
2017-05-11 04:00 | 182 | 181
2017-05-11 04:30 | 188 | 187
2017-05-11 05:00 | 198 | 198
2017-05-11 05:30 | 213 | 213
2017-05-11 06:00 | 232 | 231
2017-05-11 06:30 | 253 | 251
2017-05-11 07:00 | 268 | 267
2017-05-11 07:30 | 276 | 275
2017-05-11 08:00 | 270 | 270
2017-05-11 08:30 | 259 | 258
2017-05-11 09:00 | 259 | 259
2017-05-11 09:30 | 261 | 261
2017-05-11 10:00 | 266 | 266
2017-05-11 10:30 | 257 | 257
2017-05-11 11:00 | 247 | 247
2017-05-11 11:30 | 243 | 243
2017-05-11 12:00 | 242 | 242
2017-05-11 12:30 | 243 | 242
2017-05-11 13:00 | 244 | 243
2017-05-11 13:30 | 252 | 252
2017-05-11 14:00 | 257 | 257
2017-05-11 14:30 | 260 | 260
2017-05-11 15:00 | 267 | 267
2017-05-11 15:30 | 275 | 275
2017-05-11 16:00 | 286 | 286
2017-05-11 16:30 | 288 | 287
2017-05-11 17:00 | 303 | 303
2017-05-11 17:30 | 320 | 318
2017-05-11 18:00 | 317 | 315
2017-05-11 18:30 | 317 | 315
2017-05-11 19:00 | 312 | 308
2017-05-11 19:30 | 303 | 302
2017-05-11 20:00 | 300 | 299
2017-05-11 20:30 | 290 | 289
2017-05-11 21:00 | 282 | 282
2017-05-11 21:30 | 269 | 268
2017-05-11 22:00 | 258 | 257
2017-05-11 22:30 | 250 | 249
2017-05-11 23:00 | 238 | 236
2017-05-11 23:30 | 218 | 216
2017-05-12 | 204 | 201
2017-05-12 00:30 | 197 | 195
2017-05-12 01:00 | 193 | 190
2017-05-12 01:30 | 188 | 185
2017-05-12 02:00 | 183 | 179
2017-05-12 02:30 | 179 | 176
2017-05-12 03:00 | 179 | 175
2017-05-12 03:30 | 179 | 176
2017-05-12 04:00 | 183 | 180
2017-05-12 04:30 | 190 | 187
2017-05-12 05:00 | 202 | 201
2017-05-12 05:30 | 211 | 210
2017-05-12 06:00 | 229 | 227
2017-05-12 06:30 | 245 | 244
2017-05-12 07:00 | 264 | 263
2017-05-12 07:30 | 269 | 268
2017-05-12 08:00 | 268 | 267
2017-05-12 08:30 | 268 | 267
2017-05-12 09:00 | 270 | 270
2017-05-12 09:30 | 267 | 267
2017-05-12 10:00 | 257 | 257
2017-05-12 10:30 | 253 | 253
2017-05-12 11:00 | 260 | 260
2017-05-12 11:30 | 261 | 260
2017-05-12 12:00 | 252 | 252
2017-05-12 12:30 | 251 | 251
2017-05-12 13:00 | 254 | 254
2017-05-12 13:30 | 261 | 261
2017-05-12 14:00 | 261 | 261
2017-05-12 14:30 | 263 | 263
2017-05-12 15:00 | 266 | 266
2017-05-12 15:30 | 270 | 270
2017-05-12 16:00 | 277 | 277
2017-05-12 16:30 | 282 | 282
2017-05-12 17:00 | 301 | 301
2017-05-12 17:30 | 308 | 307
2017-05-12 18:00 | 298 | 298
2017-05-12 18:30 | 295 | 295
2017-05-12 19:00 | 288 | 287
2017-05-12 19:30 | 284 | 283
2017-05-12 20:00 | 279 | 278
2017-05-12 20:30 | 267 | 265
2017-05-12 21:00 | 260 | 259
2017-05-12 21:30 | 252 | 251
2017-05-12 22:00 | 248 | 247
2017-05-12 22:30 | 244 | 243
2017-05-12 23:00 | 230 | 229
2017-05-12 23:30 | 213 | 212
2017-05-13 | 199 | 197
2017-05-13 00:30 | 188 | 186
2017-05-13 01:00 | 183 | 182
2017-05-13 01:30 | 182 | 180
2017-05-13 02:00 | 181 | 180
2017-05-13 02:30 | 178 | 176
2017-05-13 03:00 | 176 | 174
2017-05-13 03:30 | 175 | 173
2017-05-13 04:00 | 176 | 175
2017-05-13 04:30 | 178 | 177
2017-05-13 05:00 | 185 | 184
2017-05-13 05:30 | 191 | 190
2017-05-13 06:00 | 200 | 199
2017-05-13 06:30 | 210 | 210
2017-05-13 07:00 | 223 | 222
2017-05-13 07:30 | 236 | 235
2017-05-13 08:00 | 238 | 237
2017-05-13 08:30 | 241 | 241
2017-05-13 09:00 | 247 | 247
2017-05-13 09:30 | 245 | 245
2017-05-13 10:00 | 240 | 240
2017-05-13 10:30 | 242 | 242
2017-05-13 11:00 | 247 | 247
2017-05-13 11:30 | 238 | 238
2017-05-13 12:00 | 239 | 239
2017-05-13 12:30 | 235 | 235
2017-05-13 13:00 | 246 | 246
2017-05-13 13:30 | 249 | 248
2017-05-13 14:00 | 255 | 255
2017-05-13 14:30 | 260 | 260
2017-05-13 15:00 | 260 | 260
2017-05-13 15:30 | 261 | 261
2017-05-13 16:00 | 266 | 266
2017-05-13 16:30 | 278 | 278
2017-05-13 17:00 | 286 | 286
2017-05-13 17:30 | 291 | 291
2017-05-13 18:00 | 285 | 285
2017-05-13 18:30 | 281 | 281
2017-05-13 19:00 | 275 | 274
2017-05-13 19:30 | 268 | 268
2017-05-13 20:00 | 260 | 260
2017-05-13 20:30 | 254 | 254
2017-05-13 21:00 | 247 | 247
2017-05-13 21:30 | 242 | 242
2017-05-13 22:00 | 238 | 238
2017-05-13 22:30 | 241 | 241
2017-05-13 23:00 | 232 | 232
2017-05-13 23:30 | 216 | 216
2017-05-14 | 203 | 203
2017-05-14 00:30 | 194 | 194
2017-05-14 01:00 | 186 | 186
2017-05-14 01:30 | 179 | 179
2017-05-14 02:00 | 174 | 174
2017-05-14 02:30 | 171 | 171
2017-05-14 03:00 | 170 | 170
2017-05-14 03:30 | 169 | 169
2017-05-14 04:00 | 169 | 169
2017-05-14 04:30 | 170 | 170
2017-05-14 05:00 | 175 | 175
2017-05-14 05:30 | 180 | 180
2017-05-14 06:00 | 190 | 190
2017-05-14 06:30 | 201 | 201
2017-05-14 07:00 | 219 | 219
2017-05-14 07:30 | 234 | 234
2017-05-14 08:00 | 248 | 247
2017-05-14 08:30 | 256 | 256
2017-05-14 09:00 | 261 | 260
2017-05-14 09:30 | 266 | 266
2017-05-14 10:00 | 257 | 256
2017-05-14 10:30 | 247 | 247
2017-05-14 11:00 | 254 | 253
2017-05-14 11:30 | 253 | 253
2017-05-14 12:00 | 250 | 249
2017-05-14 12:30 | 243 | 242
2017-05-14 13:00 | 247 | 247
2017-05-14 13:30 | 249 | 249
2017-05-14 14:00 | 254 | 254
2017-05-14 14:30 | 253 | 252
2017-05-14 15:00 | 251 | 251
2017-05-14 15:30 | 255 | 254
2017-05-14 16:00 | 262 | 261
2017-05-14 16:30 | 271 | 271
2017-05-14 17:00 | 282 | 282
2017-05-14 17:30 | 286 | 286
2017-05-14 18:00 | 281 | 281
2017-05-14 18:30 | 277 | 277
2017-05-14 19:00 | 271 | 271
2017-05-14 19:30 | 266 | 265
2017-05-14 20:00 | 260 | 259
2017-05-14 20:30 | 253 | 253
2017-05-14 21:00 | 242 | 242
2017-05-14 21:30 | 236 | 236
2017-05-14 22:00 | 231 | 231
2017-05-14 22:30 | 232 | 232
2017-05-14 23:00 | 220 | 220
2017-05-14 23:30 | 206 | 206
2017-05-15 | 195 | 195
2017-05-15 00:30 | 189 | 189
2017-05-15 01:00 | 183 | 183
2017-05-15 01:30 | 177 | 177
2017-05-15 02:00 | 173 | 173
2017-05-15 02:30 | 172 | 171
2017-05-15 03:00 | 172 | 171
2017-05-15 03:30 | 173 | 173
2017-05-15 04:00 | 178 | 178
2017-05-15 04:30 | 185 | 185
2017-05-15 05:00 | 198 | 198
2017-05-15 05:30 | 209 | 209
2017-05-15 06:00 | 230 | 230
2017-05-15 06:30 | 250 | 250
2017-05-15 07:00 | 261 | 261
2017-05-15 07:30 | 268 | 268
2017-05-15 08:00 | 263 | 263
2017-05-15 08:30 | 255 | 255
2017-05-15 09:00 | 251 | 250
2017-05-15 09:30 | 249 | 248
2017-05-15 10:00 | 247 | 245
2017-05-15 10:30 | 245 | 244
2017-05-15 11:00 | 245 | 244
2017-05-15 11:30 | 243 | 243
2017-05-15 12:00 | 242 | 241
2017-05-15 12:30 | 241 | 241
2017-05-15 13:00 | 243 | 243
2017-05-15 13:30 | 248 | 247
2017-05-15 14:00 | 253 | 253
2017-05-15 14:30 | 259 | 258
2017-05-15 15:00 | 262 | 262
2017-05-15 15:30 | 271 | 271
2017-05-15 16:00 | 282 | 281
2017-05-15 16:30 | 297 | 296
2017-05-15 17:00 | 308 | 307
2017-05-15 17:30 | 320 | 320
2017-05-15 18:00 | 313 | 312
2017-05-15 18:30 | 307 | 307
2017-05-15 19:00 | 294 | 294
2017-05-15 19:30 | 290 | 289
2017-05-15 20:00 | 290 | 289
2017-05-15 20:30 | 276 | 274
2017-05-15 21:00 | 259 | 259
2017-05-15 21:30 | 246 | 245
2017-05-15 22:00 | 243 | 243
2017-05-15 22:30 | 236 | 236
2017-05-15 23:00 | 221 | 221
2017-05-15 23:30 | 205 | 204
2017-05-16 | 192 | 192
2017-05-16 00:30 | 188 | 188
2017-05-16 01:00 | 185 | 185
2017-05-16 01:30 | 181 | 181
2017-05-16 02:00 | 178 | 178
2017-05-16 02:30 | 175 | 175
2017-05-16 03:00 | 176 | 176
2017-05-16 03:30 | 177 | 177
2017-05-16 04:00 | 183 | 182
2017-05-16 04:30 | 189 | 189
2017-05-16 05:00 | 200 | 200
2017-05-16 05:30 | 206 | 206
2017-05-16 06:00 | 229 | 229
2017-05-16 06:30 | 247 | 247
2017-05-16 07:00 | 246 | 245
2017-05-16 07:30 | 254 | 253
2017-05-16 08:00 | 245 | 244
2017-05-16 08:30 | 240 | 238
2017-05-16 09:00 | 245 | 244
2017-05-16 09:30 | 240 | 239
2017-05-16 10:00 | 232 | 232
2017-05-16 10:30 | 234 | 233
2017-05-16 11:00 | 228 | 227
2017-05-16 11:30 | 225 | 224
2017-05-16 12:00 | 228 | 228
2017-05-16 12:30 | 228 | 227
2017-05-16 13:00 | 227 | 226
2017-05-16 13:30 | 229 | 229
2017-05-16 14:00 | 236 | 235
2017-05-16 14:30 | 234 | 234
2017-05-16 15:00 | 239 | 238
2017-05-16 15:30 | 246 | 246
2017-05-16 16:00 | 261 | 261
2017-05-16 16:30 | 287 | 287
2017-05-16 17:00 | 305 | 305
2017-05-16 17:30 | 316 | 316
2017-05-16 18:00 | 310 | 310
2017-05-16 18:30 | 309 | 308
2017-05-16 19:00 | 301 | 301
2017-05-16 19:30 | 297 | 296
2017-05-16 20:00 | 291 | 291
2017-05-16 20:30 | 274 | 273
2017-05-16 21:00 | 257 | 257
2017-05-16 21:30 | 242 | 242
2017-05-16 22:00 | 239 | 239
2017-05-16 22:30 | 235 | 234
2017-05-16 23:00 | 220 | 220
2017-05-16 23:30 | 203 | 202
2017-05-17 | 190 | 189
2017-05-17 00:30 | 184 | 184
2017-05-17 01:00 | 181 | 181
2017-05-17 01:30 | 176 | 176
2017-05-17 02:00 | 176 | 175
2017-05-17 02:30 | 175 | 175
2017-05-17 03:00 | 175 | 175
2017-05-17 03:30 | 177 | 176
2017-05-17 04:00 | 181 | 181
2017-05-17 04:30 | 188 | 187
2017-05-17 05:00 | 201 | 201
2017-05-17 05:30 | 216 | 216
2017-05-17 06:00 | 237 | 236
2017-05-17 06:30 | 250 | 249
2017-05-17 07:00 | 264 | 264
2017-05-17 07:30 | 267 | 267
2017-05-17 08:00 | 262 | 262
2017-05-17 08:30 | 256 | 256
2017-05-17 09:00 | 252 | 251
2017-05-17 09:30 | 253 | 253
2017-05-17 10:00 | 250 | 250
2017-05-17 10:30 | 242 | 242
2017-05-17 11:00 | 246 | 246
2017-05-17 11:30 | 246 | 246
2017-05-17 12:00 | 245 | 245
2017-05-17 12:30 | 243 | 243
2017-05-17 13:00 | 238 | 238
2017-05-17 13:30 | 247 | 247
2017-05-17 14:00 | 252 | 252
2017-05-17 14:30 | 256 | 256
2017-05-17 15:00 | 257 | 257
2017-05-17 15:30 | 267 | 267
2017-05-17 16:00 | 273 | 273
2017-05-17 16:30 | 288 | 287
2017-05-17 17:00 | 303 | 301
2017-05-17 17:30 | 316 | 315
2017-05-17 18:00 | 311 | 309
2017-05-17 18:30 | 308 | 307
2017-05-17 19:00 | 301 | 299
2017-05-17 19:30 | 298 | 297
2017-05-17 20:00 | 293 | 292
2017-05-17 20:30 | 275 | 274
2017-05-17 21:00 | 259 | 258
2017-05-17 21:30 | 252 | 250
2017-05-17 22:00 | 246 | 244
2017-05-17 22:30 | 238 | 236
2017-05-17 23:00 | 224 | 221
2017-05-17 23:30 | 208 | 204
2017-05-18 | 194 | 190
2017-05-18 00:30 | 190 | 186
2017-05-18 01:00 | 187 | 183
2017-05-18 01:30 | 186 | 182
2017-05-18 02:00 | 182 | 178
2017-05-18 02:30 | 179 | 174
2017-05-18 03:00 | 179 | 174
2017-05-18 03:30 | 180 | 176
2017-05-18 04:00 | 185 | 181
2017-05-18 04:30 | 191 | 188
2017-05-18 05:00 | 202 | 199
2017-05-18 05:30 | 216 | 214
2017-05-18 06:00 | 235 | 234
2017-05-18 06:30 | 261 | 260
2017-05-18 07:00 | 293 | 289
2017-05-18 07:30 | 291 | 287
2017-05-18 08:00 | 284 | 281
2017-05-18 08:30 | 280 | 276
2017-05-18 09:00 | 275 | 272
2017-05-18 09:30 | 274 | 271
2017-05-18 10:00 | 276 | 273
2017-05-18 10:30 | 276 | 273
2017-05-18 11:00 | 273 | 270
2017-05-18 11:30 | 269 | 266
2017-05-18 12:00 | 260 | 259
2017-05-18 12:30 | 253 | 252
2017-05-18 13:00 | 262 | 261
2017-05-18 13:30 | 269 | 268
2017-05-18 14:00 | 271 | 271
2017-05-18 14:30 | 272 | 272
2017-05-18 15:00 | 279 | 279
2017-05-18 15:30 | 286 | 285
2017-05-18 16:00 | 294 | 294
2017-05-18 16:30 | 308 | 308
2017-05-18 17:00 | 319 | 319
2017-05-18 17:30 | 316 | 315
2017-05-18 18:00 | 313 | 313
2017-05-18 18:30 | 309 | 309
2017-05-18 19:00 | 302 | 301
2017-05-18 19:30 | 302 | 302
2017-05-18 20:00 | 295 | 294
2017-05-18 20:30 | 280 | 278
2017-05-18 21:00 | 263 | 261
2017-05-18 21:30 | 251 | 249
2017-05-18 22:00 | 240 | 240
2017-05-18 22:30 | 238 | 238
2017-05-18 23:00 | 228 | 227
2017-05-18 23:30 | 211 | 210
2017-05-19 | 195 | 194
2017-05-19 00:30 | 190 | 189
2017-05-19 01:00 | 186 | 185
2017-05-19 01:30 | 182 | 181
2017-05-19 02:00 | 180 | 178
2017-05-19 02:30 | 180 | 178
2017-05-19 03:00 | 180 | 178
2017-05-19 03:30 | 180 | 178
2017-05-19 04:00 | 185 | 183
2017-05-19 04:30 | 190 | 189
2017-05-19 05:00 | 198 | 197
2017-05-19 05:30 | 209 | 209
2017-05-19 06:00 | 232 | 232
2017-05-19 06:30 | 261 | 261
2017-05-19 07:00 | 288 | 288
2017-05-19 07:30 | 296 | 296
2017-05-19 08:00 | 301 | 300
2017-05-19 08:30 | 300 | 300
2017-05-19 09:00 | 299 | 299
2017-05-19 09:30 | 298 | 298
2017-05-19 10:00 | 300 | 300
2017-05-19 10:30 | 296 | 296
2017-05-19 11:00 | 295 | 295
2017-05-19 11:30 | 295 | 295
2017-05-19 12:00 | 296 | 296
2017-05-19 12:30 | 295 | 295
2017-05-19 13:00 | 293 | 293
2017-05-19 13:30 | 295 | 295
2017-05-19 14:00 | 297 | 297
2017-05-19 14:30 | 296 | 296
2017-05-19 15:00 | 297 | 297
2017-05-19 15:30 | 304 | 304
2017-05-19 16:00 | 313 | 313
2017-05-19 16:30 | 326 | 326
2017-05-19 17:00 | 318 | 318
2017-05-19 17:30 | 315 | 315
2017-05-19 18:00 | 310 | 310
2017-05-19 18:30 | 303 | 303
2017-05-19 19:00 | 294 | 294
2017-05-19 19:30 | 289 | 289
2017-05-19 20:00 | 281 | 281
2017-05-19 20:30 | 270 | 270
2017-05-19 21:00 | 258 | 258
2017-05-19 21:30 | 250 | 250
2017-05-19 22:00 | 243 | 243
2017-05-19 22:30 | 238 | 238
2017-05-19 23:00 | 229 | 229
2017-05-19 23:30 | 219 | 218
2017-05-20 | 201 | 200
2017-05-20 00:30 | 189 | 188
2017-05-20 01:00 | 183 | 181
2017-05-20 01:30 | 177 | 175
2017-05-20 02:00 | 172 | 170
2017-05-20 02:30 | 170 | 167
2017-05-20 03:00 | 165 | 162
2017-05-20 03:30 | 169 | 166
2017-05-20 04:00 | 176 | 174
2017-05-20 04:30 | 179 | 177
2017-05-20 05:00 | 183 | 181
2017-05-20 05:30 | 187 | 185
2017-05-20 06:00 | 198 | 197
2017-05-20 06:30 | 208 | 207
2017-05-20 07:00 | 226 | 225
2017-05-20 07:30 | 233 | 233
2017-05-20 08:00 | 238 | 238
2017-05-20 08:30 | 242 | 242
2017-05-20 09:00 | 246 | 246
2017-05-20 09:30 | 242 | 242
2017-05-20 10:00 | 243 | 243
2017-05-20 10:30 | 247 | 247
2017-05-20 11:00 | 241 | 241
2017-05-20 11:30 | 242 | 242
2017-05-20 12:00 | 243 | 243
2017-05-20 12:30 | 245 | 245
2017-05-20 13:00 | 243 | 243
2017-05-20 13:30 | 240 | 240
2017-05-20 14:00 | 243 | 242
2017-05-20 14:30 | 247 | 247
2017-05-20 15:00 | 252 | 252
2017-05-20 15:30 | 252 | 252
2017-05-20 16:00 | 257 | 257
2017-05-20 16:30 | 269 | 269
2017-05-20 17:00 | 282 | 282
2017-05-20 17:30 | 286 | 286
2017-05-20 18:00 | 279 | 279
2017-05-20 18:30 | 276 | 275
2017-05-20 19:00 | 267 | 266
2017-05-20 19:30 | 263 | 262
2017-05-20 20:00 | 259 | 259
2017-05-20 20:30 | 252 | 252
2017-05-20 21:00 | 244 | 244
2017-05-20 21:30 | 236 | 236
2017-05-20 22:00 | 233 | 233
2017-05-20 22:30 | 232 | 232
2017-05-20 23:00 | 224 | 224
2017-05-20 23:30 | 209 | 209
2017-05-21 | 193 | 191
2017-05-21 00:30 | 185 | 183
2017-05-21 01:00 | 178 | 176
2017-05-21 01:30 | 179 | 177
2017-05-21 02:00 | 179 | 176
2017-05-21 02:30 | 176 | 174
2017-05-21 03:00 | 175 | 173
2017-05-21 03:30 | 175 | 173
2017-05-21 04:00 | 182 | 180
2017-05-21 04:30 | 187 | 185
2017-05-21 05:00 | 192 | 191
2017-05-21 05:30 | 199 | 198
2017-05-21 06:00 | 201 | 200
2017-05-21 06:30 | 207 | 205
2017-05-21 07:00 | 217 | 216
2017-05-21 07:30 | 230 | 230
2017-05-21 08:00 | 240 | 239
2017-05-21 08:30 | 244 | 244
2017-05-21 09:00 | 246 | 246
2017-05-21 09:30 | 247 | 247
2017-05-21 10:00 | 244 | 244
2017-05-21 10:30 | 237 | 237
2017-05-21 11:00 | 230 | 230
2017-05-21 11:30 | 223 | 223
2017-05-21 12:00 | 219 | 219
2017-05-21 12:30 | 219 | 219
2017-05-21 13:00 | 225 | 225
2017-05-21 13:30 | 229 | 229
2017-05-21 14:00 | 237 | 237
2017-05-21 14:30 | 242 | 242
2017-05-21 15:00 | 245 | 245
2017-05-21 15:30 | 250 | 250
2017-05-21 16:00 | 261 | 261
2017-05-21 16:30 | 276 | 275
2017-05-21 17:00 | 289 | 289
2017-05-21 17:30 | 296 | 296
2017-05-21 18:00 | 293 | 292
2017-05-21 18:30 | 289 | 288
2017-05-21 19:00 | 277 | 276
2017-05-21 19:30 | 272 | 272
2017-05-21 20:00 | 268 | 268
2017-05-21 20:30 | 261 | 261
2017-05-21 21:00 | 252 | 252
2017-05-21 21:30 | 244 | 244
2017-05-21 22:00 | 237 | 237
2017-05-21 22:30 | 239 | 238
2017-05-21 23:00 | 228 | 227
2017-05-21 23:30 | 212 | 211
2017-05-22 | 197 | 196
2017-05-22 00:30 | 190 | 189
2017-05-22 01:00 | 188 | 186
2017-05-22 01:30 | 188 | 185
2017-05-22 02:00 | 186 | 184
2017-05-22 02:30 | 185 | 183
2017-05-22 03:00 | 186 | 184
2017-05-22 03:30 | 185 | 183
2017-05-22 04:00 | 185 | 183
2017-05-22 04:30 | 189 | 187
2017-05-22 05:00 | 198 | 197
2017-05-22 05:30 | 210 | 210
2017-05-22 06:00 | 231 | 230
2017-05-22 06:30 | 254 | 253
2017-05-22 07:00 | 274 | 273
2017-05-22 07:30 | 281 | 280
2017-05-22 08:00 | 274 | 273
2017-05-22 08:30 | 269 | 268
2017-05-22 09:00 | 266 | 266
2017-05-22 09:30 | 261 | 260
2017-05-22 10:00 | 257 | 256
2017-05-22 10:30 | 257 | 257
2017-05-22 11:00 | 257 | 256
2017-05-22 11:30 | 257 | 256
2017-05-22 12:00 | 257 | 257
2017-05-22 12:30 | 255 | 255
2017-05-22 13:00 | 257 | 257
2017-05-22 13:30 | 262 | 262
2017-05-22 14:00 | 262 | 262
2017-05-22 14:30 | 268 | 268
2017-05-22 15:00 | 273 | 272
2017-05-22 15:30 | 277 | 277
2017-05-22 16:00 | 283 | 283
2017-05-22 16:30 | 294 | 293
2017-05-22 17:00 | 309 | 309
2017-05-22 17:30 | 315 | 315
2017-05-22 18:00 | 307 | 307
2017-05-22 18:30 | 306 | 306
2017-05-22 19:00 | 297 | 296
2017-05-22 19:30 | 295 | 295
2017-05-22 20:00 | 286 | 286
2017-05-22 20:30 | 278 | 278
2017-05-22 21:00 | 266 | 265
2017-05-22 21:30 | 256 | 255
2017-05-22 22:00 | 246 | 245
2017-05-22 22:30 | 241 | 241
2017-05-22 23:00 | 228 | 227
2017-05-22 23:30 | 216 | 215
2017-05-23 | 205 | 203
2017-05-23 00:30 | 195 | 194
2017-05-23 01:00 | 189 | 188
2017-05-23 01:30 | 186 | 185
2017-05-23 02:00 | 181 | 181
2017-05-23 02:30 | 182 | 182
2017-05-23 03:00 | 183 | 183
2017-05-23 03:30 | 186 | 186
2017-05-23 04:00 | 189 | 189
2017-05-23 04:30 | 193 | 193
2017-05-23 05:00 | 202 | 202
2017-05-23 05:30 | 214 | 214
2017-05-23 06:00 | 242 | 242
2017-05-23 06:30 | 264 | 263
2017-05-23 07:00 | 277 | 277
2017-05-23 07:30 | 283 | 283
2017-05-23 08:00 | 276 | 276
2017-05-23 08:30 | 266 | 266
2017-05-23 09:00 | 264 | 264
2017-05-23 09:30 | 265 | 265
2017-05-23 10:00 | 261 | 261
2017-05-23 10:30 | 259 | 258
2017-05-23 11:00 | 259 | 259
2017-05-23 11:30 | 260 | 260
2017-05-23 12:00 | 277 | 277
2017-05-23 12:30 | 273 | 273
2017-05-23 13:00 | 281 | 281
2017-05-23 13:30 | 288 | 286
2017-05-23 14:00 | 297 | 296
2017-05-23 14:30 | 285 | 283
2017-05-23 15:00 | 262 | 261
2017-05-23 15:30 | 259 | 259
2017-05-23 16:00 | 266 | 266
2017-05-23 16:30 | 279 | 279
2017-05-23 17:00 | 295 | 295
2017-05-23 17:30 | 305 | 302
2017-05-23 18:00 | 296 | 294
2017-05-23 18:30 | 294 | 293
2017-05-23 19:00 | 284 | 284
2017-05-23 19:30 | 278 | 278
2017-05-23 20:00 | 271 | 271
2017-05-23 20:30 | 259 | 259
2017-05-23 21:00 | 249 | 249
2017-05-23 21:30 | 242 | 242
2017-05-23 22:00 | 230 | 230
2017-05-23 22:30 | 226 | 226
2017-05-23 23:00 | 213 | 213
2017-05-23 23:30 | 201 | 201
2017-05-24 | 185 | 184
2017-05-24 00:30 | 178 | 178
2017-05-24 01:00 | 176 | 175
2017-05-24 01:30 | 173 | 173
2017-05-24 02:00 | 172 | 171
2017-05-24 02:30 | 171 | 171
2017-05-24 03:00 | 173 | 172
2017-05-24 03:30 | 175 | 174
2017-05-24 04:00 | 179 | 178
2017-05-24 04:30 | 182 | 181
2017-05-24 05:00 | 186 | 186
2017-05-24 05:30 | 196 | 196
2017-05-24 06:00 | 210 | 210
2017-05-24 06:30 | 225 | 225
2017-05-24 07:00 | 244 | 244
2017-05-24 07:30 | 255 | 254
2017-05-24 08:00 | 250 | 249
2017-05-24 08:30 | 243 | 243
2017-05-24 09:00 | 240 | 240
2017-05-24 09:30 | 238 | 238
2017-05-24 10:00 | 240 | 240
2017-05-24 10:30 | 235 | 235
2017-05-24 11:00 | 236 | 236
2017-05-24 11:30 | 234 | 234
2017-05-24 12:00 | 235 | 235
2017-05-24 12:30 | 239 | 239
2017-05-24 13:00 | 241 | 241
2017-05-24 13:30 | 250 | 250
2017-05-24 14:00 | 254 | 254
2017-05-24 14:30 | 252 | 252
2017-05-24 15:00 | 251 | 251
2017-05-24 15:30 | 253 | 253
2017-05-24 16:00 | 257 | 257
2017-05-24 16:30 | 261 | 261
2017-05-24 17:00 | 275 | 275
2017-05-24 17:30 | 286 | 286
2017-05-24 18:00 | 279 | 279
2017-05-24 18:30 | 279 | 279
2017-05-24 19:00 | 273 | 273
2017-05-24 19:30 | 271 | 271
2017-05-24 20:00 | 268 | 267
2017-05-24 20:30 | 255 | 255
2017-05-24 21:00 | 245 | 245
2017-05-24 21:30 | 237 | 237
2017-05-24 22:00 | 233 | 232
2017-05-24 22:30 | 234 | 233
2017-05-24 23:00 | 217 | 216
2017-05-24 23:30 | 194 | 193
2017-05-25 | 178 | 178
2017-05-25 00:30 | 173 | 173
2017-05-25 01:00 | 172 | 172
2017-05-25 01:30 | 170 | 169
2017-05-25 02:00 | 166 | 165
2017-05-25 02:30 | 166 | 165
2017-05-25 03:00 | 170 | 170
2017-05-25 03:30 | 172 | 171
2017-05-25 04:00 | 171 | 170
2017-05-25 04:30 | 176 | 176
2017-05-25 05:00 | 182 | 182
2017-05-25 05:30 | 192 | 192
2017-05-25 06:00 | 213 | 213
2017-05-25 06:30 | 233 | 233
2017-05-25 07:00 | 245 | 245
2017-05-25 07:30 | 255 | 255
2017-05-25 08:00 | 251 | 251
2017-05-25 08:30 | 244 | 244
2017-05-25 09:00 | 240 | 239
2017-05-25 09:30 | 236 | 235
2017-05-25 10:00 | 230 | 229
2017-05-25 10:30 | 229 | 228
2017-05-25 11:00 | 227 | 226
2017-05-25 11:30 | 226 | 225
2017-05-25 12:00 | 228 | 227
2017-05-25 12:30 | 228 | 227
2017-05-25 13:00 | 231 | 230
2017-05-25 13:30 | 237 | 236
2017-05-25 14:00 | 244 | 243
2017-05-25 14:30 | 243 | 242
2017-05-25 15:00 | 245 | 244
2017-05-25 15:30 | 248 | 248
2017-05-25 16:00 | 253 | 252
2017-05-25 16:30 | 261 | 261
2017-05-25 17:00 | 277 | 276
2017-05-25 17:30 | 287 | 287
2017-05-25 18:00 | 285 | 285
2017-05-25 18:30 | 285 | 285
2017-05-25 19:00 | 280 | 280
2017-05-25 19:30 | 278 | 278
2017-05-25 20:00 | 268 | 268
2017-05-25 20:30 | 257 | 257
2017-05-25 21:00 | 244 | 244
2017-05-25 21:30 | 234 | 234
2017-05-25 22:00 | 226 | 225
2017-05-25 22:30 | 219 | 219
2017-05-25 23:00 | 207 | 207
2017-05-25 23:30 | 196 | 196
2017-05-26 | 183 | 183
2017-05-26 00:30 | 176 | 176
2017-05-26 01:00 | 171 | 170
2017-05-26 01:30 | 166 | 165
2017-05-26 02:00 | 162 | 162
2017-05-26 02:30 | 161 | 161
2017-05-26 03:00 | 162 | 162
2017-05-26 03:30 | 163 | 163
2017-05-26 04:00 | 167 | 167
2017-05-26 04:30 | 171 | 171
2017-05-26 05:00 | 180 | 180
2017-05-26 05:30 | 191 | 191
2017-05-26 06:00 | 209 | 209
2017-05-26 06:30 | 228 | 228
2017-05-26 07:00 | 247 | 246
2017-05-26 07:30 | 252 | 252
2017-05-26 08:00 | 247 | 247
2017-05-26 08:30 | 238 | 238
2017-05-26 09:00 | 236 | 236
2017-05-26 09:30 | 233 | 232
2017-05-26 10:00 | 229 | 228
2017-05-26 10:30 | 224 | 224
2017-05-26 11:00 | 225 | 224
2017-05-26 11:30 | 222 | 222
2017-05-26 12:00 | 221 | 221
2017-05-26 12:30 | 220 | 220
2017-05-26 13:00 | 221 | 221
2017-05-26 13:30 | 227 | 226
2017-05-26 14:00 | 230 | 229
2017-05-26 14:30 | 232 | 232
2017-05-26 15:00 | 234 | 234
2017-05-26 15:30 | 238 | 238
2017-05-26 16:00 | 245 | 244
2017-05-26 16:30 | 254 | 254
2017-05-26 17:00 | 268 | 267
2017-05-26 17:30 | 277 | 276
2017-05-26 18:00 | 272 | 271
2017-05-26 18:30 | 268 | 267
2017-05-26 19:00 | 262 | 261
2017-05-26 19:30 | 257 | 257
2017-05-26 20:00 | 253 | 253
2017-05-26 20:30 | 243 | 243
2017-05-26 21:00 | 234 | 234
2017-05-26 21:30 | 228 | 228
2017-05-26 22:00 | 220 | 220
2017-05-26 22:30 | 215 | 215
2017-05-26 23:00 | 204 | 203
2017-05-26 23:30 | 190 | 190
2017-05-27 | 180 | 180
2017-05-27 00:30 | 175 | 175
2017-05-27 01:00 | 169 | 168
2017-05-27 01:30 | 164 | 163
2017-05-27 02:00 | 163 | 162
2017-05-27 02:30 | 160 | 160
2017-05-27 03:00 | 159 | 159
2017-05-27 03:30 | 158 | 158
2017-05-27 04:00 | 166 | 166
2017-05-27 04:30 | 168 | 168
2017-05-27 05:00 | 171 | 171
2017-05-27 05:30 | 174 | 174
2017-05-27 06:00 | 181 | 181
2017-05-27 06:30 | 193 | 193
2017-05-27 07:00 | 206 | 205
2017-05-27 07:30 | 216 | 215
2017-05-27 08:00 | 221 | 221
2017-05-27 08:30 | 225 | 225
2017-05-27 09:00 | 227 | 226
2017-05-27 09:30 | 220 | 220
2017-05-27 10:00 | 215 | 214
2017-05-27 10:30 | 215 | 214
2017-05-27 11:00 | 209 | 208
2017-05-27 11:30 | 206 | 205
2017-05-27 12:00 | 204 | 203
2017-05-27 12:30 | 203 | 202
2017-05-27 13:00 | 202 | 201
2017-05-27 13:30 | 206 | 205
2017-05-27 14:00 | 210 | 209
2017-05-27 14:30 | 214 | 213
2017-05-27 15:00 | 220 | 219
2017-05-27 15:30 | 224 | 223
2017-05-27 16:00 | 231 | 230
2017-05-27 16:30 | 238 | 237
2017-05-27 17:00 | 249 | 249
2017-05-27 17:30 | 251 | 251
2017-05-27 18:00 | 249 | 248
2017-05-27 18:30 | 246 | 246
2017-05-27 19:00 | 244 | 244
2017-05-27 19:30 | 240 | 240
2017-05-27 20:00 | 237 | 237
2017-05-27 20:30 | 229 | 229
2017-05-27 21:00 | 222 | 222
2017-05-27 21:30 | 217 | 216
2017-05-27 22:00 | 219 | 219
2017-05-27 22:30 | 220 | 220
2017-05-27 23:00 | 209 | 209
2017-05-27 23:30 | 199 | 199
2017-05-28 | 184 | 184
2017-05-28 00:30 | 176 | 176
2017-05-28 01:00 | 173 | 173
2017-05-28 01:30 | 171 | 170
2017-05-28 02:00 | 168 | 168
2017-05-28 02:30 | 167 | 166
2017-05-28 03:00 | 168 | 168
2017-05-28 03:30 | 167 | 167
2017-05-28 04:00 | 169 | 169
2017-05-28 04:30 | 170 | 170
2017-05-28 05:00 | 174 | 174
2017-05-28 05:30 | 177 | 177
2017-05-28 06:00 | 179 | 179
2017-05-28 06:30 | 184 | 184
2017-05-28 07:00 | 196 | 196
2017-05-28 07:30 | 205 | 205
2017-05-28 08:00 | 215 | 214
2017-05-28 08:30 | 221 | 221
2017-05-28 09:00 | 218 | 218
2017-05-28 09:30 | 215 | 215
2017-05-28 10:00 | 209 | 209
2017-05-28 10:30 | 207 | 207
2017-05-28 11:00 | 202 | 202
2017-05-28 11:30 | 206 | 206
2017-05-28 12:00 | 203 | 202
2017-05-28 12:30 | 205 | 204
2017-05-28 13:00 | 201 | 200
2017-05-28 13:30 | 208 | 207
2017-05-28 14:00 | 219 | 219
2017-05-28 14:30 | 227 | 226
2017-05-28 15:00 | 226 | 226
2017-05-28 15:30 | 230 | 229
2017-05-28 16:00 | 236 | 236
2017-05-28 16:30 | 245 | 245
2017-05-28 17:00 | 256 | 256
2017-05-28 17:30 | 265 | 265
2017-05-28 18:00 | 260 | 259
2017-05-28 18:30 | 255 | 255
2017-05-28 19:00 | 250 | 250
2017-05-28 19:30 | 250 | 250
2017-05-28 20:00 | 246 | 245
2017-05-28 20:30 | 235 | 235
2017-05-28 21:00 | 229 | 229
2017-05-28 21:30 | 218 | 218
2017-05-28 22:00 | 216 | 216
2017-05-28 22:30 | 216 | 216
2017-05-28 23:00 | 209 | 209
2017-05-28 23:30 | 195 | 195
2017-05-29 | 182 | 182
2017-05-29 00:30 | 178 | 177
2017-05-29 01:00 | 175 | 174
2017-05-29 01:30 | 170 | 170
2017-05-29 02:00 | 168 | 168
2017-05-29 02:30 | 169 | 169
2017-05-29 03:00 | 170 | 170
2017-05-29 03:30 | 175 | 175
2017-05-29 04:00 | 177 | 176
2017-05-29 04:30 | 182 | 182
2017-05-29 05:00 | 186 | 186
2017-05-29 05:30 | 193 | 193
2017-05-29 06:00 | 214 | 214
2017-05-29 06:30 | 229 | 229
2017-05-29 07:00 | 247 | 246
2017-05-29 07:30 | 254 | 253
2017-05-29 08:00 | 251 | 251
2017-05-29 08:30 | 247 | 247
2017-05-29 09:00 | 245 | 244
2017-05-29 09:30 | 239 | 239
2017-05-29 10:00 | 236 | 236
2017-05-29 10:30 | 233 | 233
2017-05-29 11:00 | 230 | 230
2017-05-29 11:30 | 228 | 228
2017-05-29 12:00 | 229 | 229
2017-05-29 12:30 | 231 | 231
2017-05-29 13:00 | 233 | 233
2017-05-29 13:30 | 234 | 234
2017-05-29 14:00 | 239 | 239
2017-05-29 14:30 | 241 | 241
2017-05-29 15:00 | 245 | 245
2017-05-29 15:30 | 255 | 254
2017-05-29 16:00 | 264 | 264
2017-05-29 16:30 | 275 | 275
2017-05-29 17:00 | 288 | 288
2017-05-29 17:30 | 295 | 295
2017-05-29 18:00 | 291 | 291
2017-05-29 18:30 | 287 | 287
2017-05-29 19:00 | 278 | 278
2017-05-29 19:30 | 274 | 274
2017-05-29 20:00 | 264 | 264
2017-05-29 20:30 | 253 | 252
2017-05-29 21:00 | 242 | 242
2017-05-29 21:30 | 235 | 235
2017-05-29 22:00 | 225 | 225
2017-05-29 22:30 | 224 | 224
2017-05-29 23:00 | 212 | 212
2017-05-29 23:30 | 199 | 199
2017-05-30 | 189 | 189
2017-05-30 00:30 | 182 | 181
2017-05-30 01:00 | 177 | 177
2017-05-30 01:30 | 172 | 171
2017-05-30 02:00 | 169 | 169
2017-05-30 02:30 | 168 | 168
2017-05-30 03:00 | 168 | 168
2017-05-30 03:30 | 173 | 173
2017-05-30 04:00 | 175 | 175
2017-05-30 04:30 | 182 | 182
2017-05-30 05:00 | 192 | 192
2017-05-30 05:30 | 206 | 206
2017-05-30 06:00 | 223 | 223
2017-05-30 06:30 | 238 | 238
2017-05-30 07:00 | 259 | 258
2017-05-30 07:30 | 224 | 222
2017-05-30 08:00 | 224 | 223
2017-05-30 08:30 | 224 | 223
2017-05-30 09:00 | 227 | 226
2017-05-30 09:30 | 224 | 224
2017-05-30 10:00 | 219 | 219
2017-05-30 10:30 | 213 | 213
2017-05-30 11:00 | 211 | 211
2017-05-30 11:30 | 211 | 211
2017-05-30 12:00 | 214 | 214
2017-05-30 12:30 | 214 | 214
2017-05-30 13:00 | 237 | 237
2017-05-30 13:30 | 241 | 241
2017-05-30 14:00 | 241 | 241
2017-05-30 14:30 | 244 | 244
2017-05-30 15:00 | 246 | 246
2017-05-30 15:30 | 252 | 251
2017-05-30 16:00 | 259 | 259
2017-05-30 16:30 | 279 | 278
2017-05-30 17:00 | 300 | 299
2017-05-30 17:30 | 308 | 306
2017-05-30 18:00 | 302 | 300
2017-05-30 18:30 | 299 | 297
2017-05-30 19:00 | 293 | 290
2017-05-30 19:30 | 285 | 285
2017-05-30 20:00 | 281 | 280
2017-05-30 20:30 | 266 | 265
2017-05-30 21:00 | 250 | 249
2017-05-30 21:30 | 239 | 237
2017-05-30 22:00 | 238 | 235
2017-05-30 22:30 | 231 | 229
2017-05-30 23:00 | 220 | 217
2017-05-30 23:30 | 205 | 202
2017-05-31 | 191 | 186
2017-05-31 00:30 | 186 | 181
2017-05-31 01:00 | 183 | 178
2017-05-31 01:30 | 180 | 175
2017-05-31 02:00 | 180 | 174
2017-05-31 02:30 | 181 | 175
2017-05-31 03:00 | 182 | 176
2017-05-31 03:30 | 183 | 177
2017-05-31 04:00 | 188 | 183
2017-05-31 04:30 | 193 | 188
2017-05-31 05:00 | 202 | 199
2017-05-31 05:30 | 211 | 208
2017-05-31 06:00 | 229 | 227
2017-05-31 06:30 | 245 | 244
2017-05-31 07:00 | 264 | 263
2017-05-31 07:30 | 270 | 269
2017-05-31 08:00 | 262 | 261
2017-05-31 08:30 | 251 | 251
2017-05-31 09:00 | 245 | 245
2017-05-31 09:30 | 238 | 237
2017-05-31 10:00 | 233 | 233
2017-05-31 10:30 | 234 | 234
2017-05-31 11:00 | 231 | 231
2017-05-31 11:30 | 228 | 228
2017-05-31 12:00 | 224 | 224
2017-05-31 12:30 | 220 | 219
2017-05-31 13:00 | 221 | 221
2017-05-31 13:30 | 227 | 227
2017-05-31 14:00 | 236 | 236
2017-05-31 14:30 | 244 | 244
2017-05-31 15:00 | 246 | 246
2017-05-31 15:30 | 254 | 254
2017-05-31 16:00 | 266 | 266
2017-05-31 16:30 | 282 | 282
2017-05-31 17:00 | 299 | 299
2017-05-31 17:30 | 307 | 306
2017-05-31 18:00 | 301 | 300
2017-05-31 18:30 | 300 | 299
2017-05-31 19:00 | 293 | 292
2017-05-31 19:30 | 288 | 288
2017-05-31 20:00 | 285 | 285
2017-05-31 20:30 | 276 | 275
2017-05-31 21:00 | 268 | 268
2017-05-31 21:30 | 254 | 253
2017-05-31 22:00 | 249 | 248
2017-05-31 22:30 | 242 | 241
2017-05-31 23:00 | 230 | 227
2017-05-31 23:30 | 218 | 215
2017-06-01 | 202 | 200
2017-06-01 00:30 | 193 | 191
2017-06-01 01:00 | 189 | 186
2017-06-01 01:30 | 184 | 181
2017-06-01 02:00 | 182 | 179
2017-06-01 02:30 | 181 | 178
2017-06-01 03:00 | 181 | 178
2017-06-01 03:30 | 182 | 179
2017-06-01 04:00 | 186 | 183
2017-06-01 04:30 | 191 | 189
2017-06-01 05:00 | 199 | 198
2017-06-01 05:30 | 211 | 210
2017-06-01 06:00 | 235 | 234
2017-06-01 06:30 | 262 | 260
2017-06-01 07:00 | 280 | 279
2017-06-01 07:30 | 289 | 288
2017-06-01 08:00 | 281 | 280
2017-06-01 08:30 | 266 | 265
2017-06-01 09:00 | 263 | 262
2017-06-01 09:30 | 254 | 253
2017-06-01 10:00 | 250 | 249
2017-06-01 10:30 | 245 | 245
2017-06-01 11:00 | 237 | 236
2017-06-01 11:30 | 234 | 233
2017-06-01 12:00 | 233 | 232
2017-06-01 12:30 | 234 | 234
2017-06-01 13:00 | 235 | 234
2017-06-01 13:30 | 239 | 238
2017-06-01 14:00 | 244 | 244
2017-06-01 14:30 | 248 | 248
2017-06-01 15:00 | 253 | 253
2017-06-01 15:30 | 263 | 262
2017-06-01 16:00 | 276 | 276
2017-06-01 16:30 | 291 | 291
2017-06-01 17:00 | 304 | 304
2017-06-01 17:30 | 318 | 316
2017-06-01 18:00 | 318 | 315
2017-06-01 18:30 | 318 | 315
2017-06-01 19:00 | 314 | 310
2017-06-01 19:30 | 307 | 306
2017-06-01 20:00 | 304 | 303
2017-06-01 20:30 | 300 | 298
2017-06-01 21:00 | 282 | 282
2017-06-01 21:30 | 269 | 269
2017-06-01 22:00 | 261 | 260
2017-06-01 22:30 | 255 | 255
2017-06-01 23:00 | 240 | 240
2017-06-01 23:30 | 225 | 225
2017-06-02 | 209 | 209
2017-06-02 00:30 | 197 | 197
2017-06-02 01:00 | 189 | 189
2017-06-02 01:30 | 185 | 185
2017-06-02 02:00 | 183 | 183
2017-06-02 02:30 | 183 | 182
2017-06-02 03:00 | 186 | 186
2017-06-02 03:30 | 189 | 189
2017-06-02 04:00 | 192 | 191
2017-06-02 04:30 | 196 | 196
2017-06-02 05:00 | 207 | 207
2017-06-02 05:30 | 218 | 218
2017-06-02 06:00 | 235 | 235
2017-06-02 06:30 | 258 | 257
2017-06-02 07:00 | 275 | 274
2017-06-02 07:30 | 284 | 283
2017-06-02 08:00 | 278 | 277
2017-06-02 08:30 | 270 | 269
2017-06-02 09:00 | 264 | 263
2017-06-02 09:30 | 256 | 255
2017-06-02 10:00 | 251 | 250
2017-06-02 10:30 | 246 | 246
2017-06-02 11:00 | 240 | 239
2017-06-02 11:30 | 231 | 231
2017-06-02 12:00 | 230 | 230
2017-06-02 12:30 | 228 | 227
2017-06-02 13:00 | 230 | 230
2017-06-02 13:30 | 234 | 234
2017-06-02 14:00 | 238 | 238
2017-06-02 14:30 | 239 | 239
2017-06-02 15:00 | 244 | 244
2017-06-02 15:30 | 256 | 256
2017-06-02 16:00 | 270 | 270
2017-06-02 16:30 | 286 | 286
2017-06-02 17:00 | 298 | 298
2017-06-02 17:30 | 300 | 300
2017-06-02 18:00 | 295 | 295
2017-06-02 18:30 | 296 | 296
2017-06-02 19:00 | 292 | 292
2017-06-02 19:30 | 293 | 293
2017-06-02 20:00 | 293 | 292
2017-06-02 20:30 | 285 | 284
2017-06-02 21:00 | 274 | 272
2017-06-02 21:30 | 265 | 264
2017-06-02 22:00 | 260 | 260
2017-06-02 22:30 | 255 | 255
2017-06-02 23:00 | 244 | 243
2017-06-02 23:30 | 229 | 228
2017-06-03 | 212 | 211
2017-06-03 00:30 | 200 | 200
2017-06-03 01:00 | 192 | 192
2017-06-03 01:30 | 190 | 190
2017-06-03 02:00 | 186 | 186
2017-06-03 02:30 | 191 | 191
2017-06-03 03:00 | 194 | 194
2017-06-03 03:30 | 194 | 194
2017-06-03 04:00 | 195 | 195
2017-06-03 04:30 | 199 | 199
2017-06-03 05:00 | 206 | 206
2017-06-03 05:30 | 207 | 207
2017-06-03 06:00 | 216 | 216
2017-06-03 06:30 | 224 | 224
2017-06-03 07:00 | 233 | 233
2017-06-03 07:30 | 241 | 241
2017-06-03 08:00 | 251 | 250
2017-06-03 08:30 | 249 | 248
2017-06-03 09:00 | 256 | 256
2017-06-03 09:30 | 256 | 256
2017-06-03 10:00 | 250 | 249
2017-06-03 10:30 | 242 | 242
2017-06-03 11:00 | 235 | 235
2017-06-03 11:30 | 231 | 230
2017-06-03 12:00 | 226 | 226
2017-06-03 12:30 | 227 | 227
2017-06-03 13:00 | 229 | 229
2017-06-03 13:30 | 234 | 234
2017-06-03 14:00 | 239 | 239
2017-06-03 14:30 | 246 | 246
2017-06-03 15:00 | 253 | 253
2017-06-03 15:30 | 248 | 248
2017-06-03 16:00 | 256 | 256
2017-06-03 16:30 | 271 | 271
2017-06-03 17:00 | 290 | 290
2017-06-03 17:30 | 297 | 296
2017-06-03 18:00 | 296 | 296
2017-06-03 18:30 | 289 | 288
2017-06-03 19:00 | 283 | 282
2017-06-03 19:30 | 279 | 278
2017-06-03 20:00 | 295 | 294
2017-06-03 20:30 | 288 | 287
2017-06-03 21:00 | 262 | 262
2017-06-03 21:30 | 259 | 259
2017-06-03 22:00 | 263 | 263
2017-06-03 22:30 | 252 | 252
2017-06-03 23:00 | 242 | 242
2017-06-03 23:30 | 231 | 231
2017-06-04 | 210 | 209
2017-06-04 00:30 | 199 | 199
2017-06-04 01:00 | 205 | 205
2017-06-04 01:30 | 198 | 198
2017-06-04 02:00 | 194 | 193
2017-06-04 02:30 | 191 | 191
2017-06-04 03:00 | 189 | 189
2017-06-04 03:30 | 189 | 189
2017-06-04 04:00 | 190 | 190
2017-06-04 04:30 | 191 | 191
2017-06-04 05:00 | 197 | 197
2017-06-04 05:30 | 203 | 203
2017-06-04 06:00 | 210 | 210
2017-06-04 06:30 | 217 | 217
2017-06-04 07:00 | 217 | 217
2017-06-04 07:30 | 226 | 226
2017-06-04 08:00 | 238 | 238
2017-06-04 08:30 | 247 | 247
2017-06-04 09:00 | 249 | 249
2017-06-04 09:30 | 244 | 244
2017-06-04 10:00 | 233 | 233
2017-06-04 10:30 | 235 | 235
2017-06-04 11:00 | 229 | 229
2017-06-04 11:30 | 222 | 222
2017-06-04 12:00 | 216 | 216
2017-06-04 12:30 | 217 | 217
2017-06-04 13:00 | 217 | 217
2017-06-04 13:30 | 221 | 221
2017-06-04 14:00 | 230 | 230
2017-06-04 14:30 | 230 | 230
2017-06-04 15:00 | 235 | 235
2017-06-04 15:30 | 242 | 242
2017-06-04 16:00 | 248 | 248
2017-06-04 16:30 | 265 | 265
2017-06-04 17:00 | 282 | 281
2017-06-04 17:30 | 292 | 290
2017-06-04 18:00 | 285 | 285
2017-06-04 18:30 | 283 | 282
2017-06-04 19:00 | 279 | 277
2017-06-04 19:30 | 277 | 275
2017-06-04 20:00 | 274 | 274
2017-06-04 20:30 | 267 | 266
2017-06-04 21:00 | 258 | 257
2017-06-04 21:30 | 247 | 247
2017-06-04 22:00 | 245 | 244
2017-06-04 22:30 | 238 | 238
2017-06-04 23:00 | 225 | 225
2017-06-04 23:30 | 212 | 212
2017-06-05 | 197 | 196
2017-06-05 00:30 | 190 | 190
2017-06-05 01:00 | 186 | 186
2017-06-05 01:30 | 187 | 187
2017-06-05 02:00 | 183 | 182
2017-06-05 02:30 | 189 | 189
2017-06-05 03:00 | 190 | 189
2017-06-05 03:30 | 192 | 192
2017-06-05 04:00 | 193 | 193
2017-06-05 04:30 | 201 | 201
2017-06-05 05:00 | 206 | 206
2017-06-05 05:30 | 217 | 216
2017-06-05 06:00 | 239 | 239
2017-06-05 06:30 | 264 | 264
2017-06-05 07:00 | 281 | 280
2017-06-05 07:30 | 285 | 285
2017-06-05 08:00 | 278 | 278
2017-06-05 08:30 | 269 | 269
2017-06-05 09:00 | 264 | 264
2017-06-05 09:30 | 258 | 258
2017-06-05 10:00 | 249 | 248
2017-06-05 10:30 | 251 | 251
2017-06-05 11:00 | 249 | 249
2017-06-05 11:30 | 244 | 244
2017-06-05 12:00 | 249 | 248
2017-06-05 12:30 | 244 | 244
2017-06-05 13:00 | 246 | 245
2017-06-05 13:30 | 253 | 253
2017-06-05 14:00 | 254 | 254
2017-06-05 14:30 | 251 | 251
2017-06-05 15:00 | 251 | 250
2017-06-05 15:30 | 257 | 256
2017-06-05 16:00 | 267 | 266
2017-06-05 16:30 | 282 | 281
2017-06-05 17:00 | 304 | 304
2017-06-05 17:30 | 312 | 312
2017-06-05 18:00 | 305 | 305
2017-06-05 18:30 | 303 | 303
2017-06-05 19:00 | 296 | 296
2017-06-05 19:30 | 292 | 292
2017-06-05 20:00 | 290 | 289
2017-06-05 20:30 | 271 | 271
2017-06-05 21:00 | 254 | 254
2017-06-05 21:30 | 244 | 244
2017-06-05 22:00 | 238 | 238
2017-06-05 22:30 | 232 | 232
2017-06-05 23:00 | 220 | 220
2017-06-05 23:30 | 211 | 211
2017-06-06 | 199 | 198
2017-06-06 00:30 | 189 | 188
2017-06-06 01:00 | 183 | 182
2017-06-06 01:30 | 179 | 179
2017-06-06 02:00 | 178 | 177
2017-06-06 02:30 | 176 | 176
2017-06-06 03:00 | 177 | 176
2017-06-06 03:30 | 180 | 180
2017-06-06 04:00 | 185 | 185
2017-06-06 04:30 | 192 | 192
2017-06-06 05:00 | 199 | 199
2017-06-06 05:30 | 213 | 213
2017-06-06 06:00 | 232 | 231
2017-06-06 06:30 | 256 | 256
2017-06-06 07:00 | 270 | 270
2017-06-06 07:30 | 272 | 272
2017-06-06 08:00 | 266 | 266
2017-06-06 08:30 | 255 | 255
2017-06-06 09:00 | 250 | 250
2017-06-06 09:30 | 245 | 245
2017-06-06 10:00 | 236 | 236
2017-06-06 10:30 | 232 | 232
2017-06-06 11:00 | 232 | 231
2017-06-06 11:30 | 229 | 229
2017-06-06 12:00 | 225 | 225
2017-06-06 12:30 | 225 | 225
2017-06-06 13:00 | 227 | 227
2017-06-06 13:30 | 233 | 233
2017-06-06 14:00 | 237 | 237
2017-06-06 14:30 | 242 | 241
2017-06-06 15:00 | 249 | 248
2017-06-06 15:30 | 259 | 259
2017-06-06 16:00 | 271 | 270
2017-06-06 16:30 | 288 | 288
2017-06-06 17:00 | 305 | 305
2017-06-06 17:30 | 315 | 314
2017-06-06 18:00 | 313 | 312
2017-06-06 18:30 | 313 | 312
2017-06-06 19:00 | 308 | 307
2017-06-06 19:30 | 304 | 304
2017-06-06 20:00 | 300 | 300
2017-06-06 20:30 | 286 | 286
2017-06-06 21:00 | 271 | 270
2017-06-06 21:30 | 254 | 253
2017-06-06 22:00 | 241 | 241
2017-06-06 22:30 | 238 | 238
2017-06-06 23:00 | 227 | 227
2017-06-06 23:30 | 212 | 211
2017-06-07 | 195 | 194
2017-06-07 00:30 | 183 | 183
2017-06-07 01:00 | 175 | 175
2017-06-07 01:30 | 170 | 169
2017-06-07 02:00 | 167 | 167
2017-06-07 02:30 | 166 | 165
2017-06-07 03:00 | 166 | 166
2017-06-07 03:30 | 168 | 168
2017-06-07 04:00 | 174 | 174
2017-06-07 04:30 | 182 | 182
2017-06-07 05:00 | 198 | 198
2017-06-07 05:30 | 210 | 210
2017-06-07 06:00 | 240 | 240
2017-06-07 06:30 | 267 | 266
2017-06-07 07:00 | 286 | 285
2017-06-07 07:30 | 291 | 289
2017-06-07 08:00 | 282 | 281
2017-06-07 08:30 | 269 | 268
2017-06-07 09:00 | 258 | 256
2017-06-07 09:30 | 245 | 245
2017-06-07 10:00 | 234 | 234
2017-06-07 10:30 | 228 | 228
2017-06-07 11:00 | 224 | 223
2017-06-07 11:30 | 221 | 221
2017-06-07 12:00 | 225 | 225
2017-06-07 12:30 | 241 | 240
2017-06-07 13:00 | 243 | 243
2017-06-07 13:30 | 240 | 240
2017-06-07 14:00 | 244 | 244
2017-06-07 14:30 | 248 | 248
2017-06-07 15:00 | 251 | 251
2017-06-07 15:30 | 261 | 260
2017-06-07 16:00 | 272 | 272
2017-06-07 16:30 | 288 | 288
2017-06-07 17:00 | 307 | 307
2017-06-07 17:30 | 318 | 318
2017-06-07 18:00 | 313 | 313
2017-06-07 18:30 | 310 | 310
2017-06-07 19:00 | 301 | 301
2017-06-07 19:30 | 299 | 299
2017-06-07 20:00 | 299 | 299
2017-06-07 20:30 | 288 | 288
2017-06-07 21:00 | 271 | 271
2017-06-07 21:30 | 254 | 253
2017-06-07 22:00 | 247 | 246
2017-06-07 22:30 | 242 | 242
2017-06-07 23:00 | 232 | 232
2017-06-07 23:30 | 219 | 219
2017-06-08 | 201 | 201
2017-06-08 00:30 | 193 | 193
2017-06-08 01:00 | 190 | 190
2017-06-08 01:30 | 186 | 186
2017-06-08 02:00 | 183 | 183
2017-06-08 02:30 | 183 | 183
2017-06-08 03:00 | 186 | 186
2017-06-08 03:30 | 190 | 190
2017-06-08 04:00 | 192 | 192
2017-06-08 04:30 | 198 | 198
2017-06-08 05:00 | 207 | 207
2017-06-08 05:30 | 221 | 221
2017-06-08 06:00 | 240 | 240
2017-06-08 06:30 | 260 | 260
2017-06-08 07:00 | 281 | 280
2017-06-08 07:30 | 284 | 284
2017-06-08 08:00 | 279 | 278
2017-06-08 08:30 | 274 | 273
2017-06-08 09:00 | 265 | 264
2017-06-08 09:30 | 256 | 256
2017-06-08 10:00 | 248 | 247
2017-06-08 10:30 | 240 | 240
2017-06-08 11:00 | 235 | 234
2017-06-08 11:30 | 235 | 235
2017-06-08 12:00 | 235 | 235
2017-06-08 12:30 | 233 | 232
2017-06-08 13:00 | 234 | 233
2017-06-08 13:30 | 233 | 232
2017-06-08 14:00 | 238 | 236
2017-06-08 14:30 | 241 | 240
2017-06-08 15:00 | 245 | 243
2017-06-08 15:30 | 251 | 250
2017-06-08 16:00 | 267 | 265
2017-06-08 16:30 | 283 | 282
2017-06-08 17:00 | 298 | 298
2017-06-08 17:30 | 306 | 305
2017-06-08 18:00 | 304 | 303
2017-06-08 18:30 | 302 | 302
2017-06-08 19:00 | 297 | 296
2017-06-08 19:30 | 297 | 297
2017-06-08 20:00 | 295 | 295
2017-06-08 20:30 | 289 | 289
2017-06-08 21:00 | 276 | 275
2017-06-08 21:30 | 262 | 262
2017-06-08 22:00 | 253 | 253
2017-06-08 22:30 | 245 | 245
2017-06-08 23:00 | 232 | 232
2017-06-08 23:30 | 218 | 217
2017-06-09 | 203 | 203
2017-06-09 00:30 | 195 | 195
2017-06-09 01:00 | 191 | 190
2017-06-09 01:30 | 187 | 186
2017-06-09 02:00 | 185 | 185
2017-06-09 02:30 | 185 | 184
2017-06-09 03:00 | 185 | 184
2017-06-09 03:30 | 209 | 209
2017-06-09 04:00 | 197 | 197
2017-06-09 04:30 | 197 | 197
2017-06-09 05:00 | 205 | 205
2017-06-09 05:30 | 213 | 213
2017-06-09 06:00 | 232 | 232
2017-06-09 06:30 | 252 | 252
2017-06-09 07:00 | 271 | 270
2017-06-09 07:30 | 267 | 267
2017-06-09 08:00 | 262 | 261
2017-06-09 08:30 | 222 | 221
2017-06-09 09:00 | 197 | 196
2017-06-09 09:30 | 239 | 238
2017-06-09 10:00 | 242 | 242
2017-06-09 10:30 | 240 | 240
2017-06-09 11:00 | 240 | 240
2017-06-09 11:30 | 242 | 242
2017-06-09 12:00 | 246 | 246
2017-06-09 12:30 | 248 | 248
2017-06-09 13:00 | 260 | 260
2017-06-09 13:30 | 260 | 260
2017-06-09 14:00 | 260 | 260
2017-06-09 14:30 | 261 | 261
2017-06-09 15:00 | 264 | 264
2017-06-09 15:30 | 270 | 270
2017-06-09 16:00 | 278 | 278
2017-06-09 16:30 | 289 | 289
2017-06-09 17:00 | 300 | 300
2017-06-09 17:30 | 304 | 304
2017-06-09 18:00 | 298 | 298
2017-06-09 18:30 | 296 | 295
2017-06-09 19:00 | 287 | 287
2017-06-09 19:30 | 285 | 285
2017-06-09 20:00 | 282 | 282
2017-06-09 20:30 | 274 | 274
2017-06-09 21:00 | 267 | 267
2017-06-09 21:30 | 260 | 260
2017-06-09 22:00 | 255 | 255
2017-06-09 22:30 | 253 | 252
2017-06-09 23:00 | 240 | 240
2017-06-09 23:30 | 223 | 223
2017-06-10 | 210 | 209
2017-06-10 00:30 | 197 | 196
2017-06-10 01:00 | 190 | 190
2017-06-10 01:30 | 188 | 187
2017-06-10 02:00 | 184 | 183
2017-06-10 02:30 | 182 | 182
2017-06-10 03:00 | 187 | 186
2017-06-10 03:30 | 189 | 188
2017-06-10 04:00 | 204 | 204
2017-06-10 04:30 | 202 | 201
2017-06-10 05:00 | 195 | 195
2017-06-10 05:30 | 196 | 196
2017-06-10 06:00 | 208 | 208
2017-06-10 06:30 | 217 | 217
2017-06-10 07:00 | 227 | 227
2017-06-10 07:30 | 237 | 237
2017-06-10 08:00 | 245 | 245
2017-06-10 08:30 | 248 | 248
2017-06-10 09:00 | 250 | 250
2017-06-10 09:30 | 249 | 249
2017-06-10 10:00 | 244 | 244
2017-06-10 10:30 | 239 | 239
2017-06-10 11:00 | 234 | 234
2017-06-10 11:30 | 236 | 236
2017-06-10 12:00 | 239 | 239
2017-06-10 12:30 | 238 | 238
2017-06-10 13:00 | 240 | 240
2017-06-10 13:30 | 244 | 244
2017-06-10 14:00 | 246 | 246
2017-06-10 14:30 | 251 | 251
2017-06-10 15:00 | 256 | 256
2017-06-10 15:30 | 258 | 258
2017-06-10 16:00 | 267 | 267
2017-06-10 16:30 | 282 | 282
2017-06-10 17:00 | 289 | 288
2017-06-10 17:30 | 290 | 290
2017-06-10 18:00 | 288 | 287
2017-06-10 18:30 | 284 | 283
2017-06-10 19:00 | 282 | 281
2017-06-10 19:30 | 279 | 278
2017-06-10 20:00 | 277 | 275
2017-06-10 20:30 | 270 | 268
2017-06-10 21:00 | 258 | 258
2017-06-10 21:30 | 247 | 247
2017-06-10 22:00 | 242 | 242
2017-06-10 22:30 | 246 | 245
2017-06-10 23:00 | 232 | 232
2017-06-10 23:30 | 220 | 219
2017-06-11 | 210 | 209
2017-06-11 00:30 | 201 | 199
2017-06-11 01:00 | 193 | 192
2017-06-11 01:30 | 186 | 185
2017-06-11 02:00 | 180 | 180
2017-06-11 02:30 | 180 | 179
2017-06-11 03:00 | 180 | 179
2017-06-11 03:30 | 180 | 179
2017-06-11 04:00 | 179 | 179
2017-06-11 04:30 | 179 | 179
2017-06-11 05:00 | 181 | 181
2017-06-11 05:30 | 184 | 184
2017-06-11 06:00 | 191 | 191
2017-06-11 06:30 | 197 | 197
2017-06-11 07:00 | 209 | 209
2017-06-11 07:30 | 223 | 223
2017-06-11 08:00 | 235 | 235
2017-06-11 08:30 | 250 | 250
2017-06-11 09:00 | 259 | 259
2017-06-11 09:30 | 267 | 267
2017-06-11 10:00 | 270 | 270
2017-06-11 10:30 | 264 | 264
2017-06-11 11:00 | 261 | 261
2017-06-11 11:30 | 251 | 251
2017-06-11 12:00 | 250 | 250
2017-06-11 12:30 | 246 | 246
2017-06-11 13:00 | 251 | 251
2017-06-11 13:30 | 255 | 255
2017-06-11 14:00 | 256 | 256
2017-06-11 14:30 | 257 | 257
2017-06-11 15:00 | 255 | 255
2017-06-11 15:30 | 258 | 258
2017-06-11 16:00 | 267 | 267
2017-06-11 16:30 | 276 | 276
2017-06-11 17:00 | 287 | 284
2017-06-11 17:30 | 292 | 289
2017-06-11 18:00 | 288 | 285
2017-06-11 18:30 | 286 | 282
2017-06-11 19:00 | 278 | 275
2017-06-11 19:30 | 271 | 269
2017-06-11 20:00 | 267 | 266
2017-06-11 20:30 | 257 | 256
2017-06-11 21:00 | 246 | 244
2017-06-11 21:30 | 238 | 235
2017-06-11 22:00 | 232 | 230
2017-06-11 22:30 | 233 | 231
2017-06-11 23:00 | 222 | 219
2017-06-11 23:30 | 210 | 205
2017-06-12 | 200 | 195
2017-06-12 00:30 | 195 | 188
2017-06-12 01:00 | 194 | 187
2017-06-12 01:30 | 192 | 185
2017-06-12 02:00 | 191 | 184
2017-06-12 02:30 | 202 | 197
2017-06-12 03:00 | 211 | 206
2017-06-12 03:30 | 208 | 203
2017-06-12 04:00 | 197 | 191
2017-06-12 04:30 | 200 | 194
2017-06-12 05:00 | 205 | 200
2017-06-12 05:30 | 212 | 208
2017-06-12 06:00 | 229 | 227
2017-06-12 06:30 | 245 | 243
2017-06-12 07:00 | 267 | 266
2017-06-12 07:30 | 276 | 276
2017-06-12 08:00 | 281 | 280
2017-06-12 08:30 | 299 | 298
2017-06-12 09:00 | 312 | 311
2017-06-12 09:30 | 304 | 303
2017-06-12 10:00 | 301 | 300
2017-06-12 10:30 | 291 | 290
2017-06-12 11:00 | 278 | 277
2017-06-12 11:30 | 268 | 267
2017-06-12 12:00 | 264 | 262
2017-06-12 12:30 | 268 | 267
2017-06-12 13:00 | 282 | 281
2017-06-12 13:30 | 286 | 285
2017-06-12 14:00 | 293 | 292
2017-06-12 14:30 | 295 | 294
2017-06-12 15:00 | 295 | 294
2017-06-12 15:30 | 300 | 299
2017-06-12 16:00 | 310 | 309
2017-06-12 16:30 | 328 | 327
2017-06-12 17:00 | 346 | 345
2017-06-12 17:30 | 350 | 348
2017-06-12 18:00 | 341 | 340
2017-06-12 18:30 | 339 | 338
2017-06-12 19:00 | 328 | 327
2017-06-12 19:30 | 325 | 324
2017-06-12 20:00 | 319 | 318
2017-06-12 20:30 | 300 | 300
2017-06-12 21:00 | 291 | 291
2017-06-12 21:30 | 283 | 283
2017-06-12 22:00 | 277 | 277
2017-06-12 22:30 | 276 | 276
2017-06-12 23:00 | 262 | 261
2017-06-12 23:30 | 241 | 241
2017-06-13 | 221 | 220
2017-06-13 00:30 | 215 | 214
2017-06-13 01:00 | 210 | 209
2017-06-13 01:30 | 205 | 205
2017-06-13 02:00 | 203 | 202
2017-06-13 02:30 | 201 | 200
2017-06-13 03:00 | 204 | 204
2017-06-13 03:30 | 223 | 223
2017-06-13 04:00 | 221 | 221
2017-06-13 04:30 | 235 | 235
2017-06-13 05:00 | 227 | 226
2017-06-13 05:30 | 236 | 236
2017-06-13 06:00 | 262 | 262
2017-06-13 06:30 | 283 | 283
2017-06-13 07:00 | 310 | 310
2017-06-13 07:30 | 328 | 328
2017-06-13 08:00 | 333 | 333
2017-06-13 08:30 | 331 | 331
2017-06-13 09:00 | 333 | 333
2017-06-13 09:30 | 331 | 331
2017-06-13 10:00 | 328 | 327
2017-06-13 10:30 | 326 | 325
2017-06-13 11:00 | 324 | 323
2017-06-13 11:30 | 326 | 326
2017-06-13 12:00 | 324 | 324
2017-06-13 12:30 | 325 | 325
2017-06-13 13:00 | 327 | 327
2017-06-13 13:30 | 323 | 323
2017-06-13 14:00 | 327 | 327
2017-06-13 14:30 | 324 | 324
2017-06-13 15:00 | 325 | 325
2017-06-13 15:30 | 334 | 334
2017-06-13 16:00 | 336 | 336
2017-06-13 16:30 | 341 | 341
2017-06-13 17:00 | 365 | 365
2017-06-13 17:30 | 381 | 380
2017-06-13 18:00 | 376 | 375
2017-06-13 18:30 | 371 | 370
2017-06-13 19:00 | 357 | 357
2017-06-13 19:30 | 351 | 350
2017-06-13 20:00 | 351 | 350
2017-06-13 20:30 | 334 | 333
2017-06-13 21:00 | 317 | 316
2017-06-13 21:30 | 307 | 305
2017-06-13 22:00 | 297 | 294
2017-06-13 22:30 | 291 | 290
2017-06-13 23:00 | 271 | 271
2017-06-13 23:30 | 249 | 249
2017-06-14 | 237 | 237
2017-06-14 00:30 | 225 | 225
2017-06-14 01:00 | 234 | 234
2017-06-14 01:30 | 238 | 238
2017-06-14 02:00 | 239 | 239
2017-06-14 02:30 | 238 | 238
2017-06-14 03:00 | 238 | 238
2017-06-14 03:30 | 231 | 231
2017-06-14 04:00 | 213 | 213
2017-06-14 04:30 | 248 | 248
2017-06-14 05:00 | 233 | 233
2017-06-14 05:30 | 245 | 245
2017-06-14 06:00 | 274 | 274
2017-06-14 06:30 | 293 | 293
2017-06-14 07:00 | 315 | 315
2017-06-14 07:30 | 326 | 324
2017-06-14 08:00 | 323 | 322
2017-06-14 08:30 | 320 | 319
2017-06-14 09:00 | 314 | 313
2017-06-14 09:30 | 318 | 317
2017-06-14 10:00 | 318 | 317
2017-06-14 10:30 | 317 | 316
2017-06-14 11:00 | 316 | 315
2017-06-14 11:30 | 319 | 319
2017-06-14 12:00 | 304 | 303
2017-06-14 12:30 | 305 | 304
2017-06-14 13:00 | 306 | 305
2017-06-14 13:30 | 310 | 308
2017-06-14 14:00 | 320 | 319
2017-06-14 14:30 | 314 | 313
2017-06-14 15:00 | 316 | 314
2017-06-14 15:30 | 325 | 324
2017-06-14 16:00 | 334 | 333
2017-06-14 16:30 | 341 | 340
2017-06-14 17:00 | 360 | 360
2017-06-14 17:30 | 370 | 370
2017-06-14 18:00 | 365 | 364
2017-06-14 18:30 | 358 | 357
2017-06-14 19:00 | 344 | 343
2017-06-14 19:30 | 336 | 336
2017-06-14 20:00 | 336 | 336
2017-06-14 20:30 | 324 | 324
2017-06-14 21:00 | 308 | 308
2017-06-14 21:30 | 294 | 293
2017-06-14 22:00 | 285 | 283
2017-06-14 22:30 | 280 | 279
2017-06-14 23:00 | 271 | 269
2017-06-14 23:30 | 251 | 250
2017-06-15 | 231 | 231
2017-06-15 00:30 | 219 | 218
2017-06-15 01:00 | 212 | 211
2017-06-15 01:30 | 208 | 207
2017-06-15 02:00 | 208 | 207
2017-06-15 02:30 | 207 | 206
2017-06-15 03:00 | 208 | 208
2017-06-15 03:30 | 219 | 219
2017-06-15 04:00 | 224 | 224
2017-06-15 04:30 | 220 | 220
2017-06-15 05:00 | 224 | 224
2017-06-15 05:30 | 236 | 236
2017-06-15 06:00 | 259 | 259
2017-06-15 06:30 | 276 | 276
2017-06-15 07:00 | 301 | 301
2017-06-15 07:30 | 317 | 317
2017-06-15 08:00 | 311 | 310
2017-06-15 08:30 | 304 | 304
2017-06-15 09:00 | 296 | 295
2017-06-15 09:30 | 288 | 287
2017-06-15 10:00 | 284 | 283
2017-06-15 10:30 | 292 | 292
2017-06-15 11:00 | 296 | 295
2017-06-15 11:30 | 282 | 281
2017-06-15 12:00 | 282 | 282
2017-06-15 12:30 | 268 | 267
2017-06-15 13:00 | 276 | 275
2017-06-15 13:30 | 283 | 282
2017-06-15 14:00 | 288 | 287
2017-06-15 14:30 | 290 | 289
2017-06-15 15:00 | 293 | 292
2017-06-15 15:30 | 304 | 303
2017-06-15 16:00 | 301 | 301
2017-06-15 16:30 | 309 | 309
2017-06-15 17:00 | 322 | 322
2017-06-15 17:30 | 336 | 335
2017-06-15 18:00 | 336 | 333
2017-06-15 18:30 | 336 | 333
2017-06-15 19:00 | 329 | 326
2017-06-15 19:30 | 325 | 323
2017-06-15 20:00 | 325 | 323
2017-06-15 20:30 | 316 | 313
2017-06-15 21:00 | 297 | 296
2017-06-15 21:30 | 281 | 279
2017-06-15 22:00 | 274 | 272
2017-06-15 22:30 | 271 | 270
2017-06-15 23:00 | 259 | 258
2017-06-15 23:30 | 241 | 241
2017-06-16 | 222 | 221
2017-06-16 00:30 | 215 | 215
2017-06-16 01:00 | 210 | 210
2017-06-16 01:30 | 210 | 210
2017-06-16 02:00 | 207 | 207
2017-06-16 02:30 | 208 | 207
2017-06-16 03:00 | 209 | 209
2017-06-16 03:30 | 209 | 209
2017-06-16 04:00 | 203 | 202
2017-06-16 04:30 | 206 | 206
2017-06-16 05:00 | 212 | 212
2017-06-16 05:30 | 225 | 225
2017-06-16 06:00 | 250 | 250
2017-06-16 06:30 | 273 | 273
2017-06-16 07:00 | 302 | 301
2017-06-16 07:30 | 318 | 317
2017-06-16 08:00 | 319 | 318
2017-06-16 08:30 | 317 | 317
2017-06-16 09:00 | 320 | 319
2017-06-16 09:30 | 321 | 321
2017-06-16 10:00 | 317 | 316
2017-06-16 10:30 | 314 | 314
2017-06-16 11:00 | 303 | 302
2017-06-16 11:30 | 296 | 296
2017-06-16 12:00 | 295 | 295
2017-06-16 12:30 | 287 | 287
2017-06-16 13:00 | 300 | 299
2017-06-16 13:30 | 299 | 298
2017-06-16 14:00 | 307 | 307
2017-06-16 14:30 | 299 | 299
2017-06-16 15:00 | 294 | 293
2017-06-16 15:30 | 306 | 306
2017-06-16 16:00 | 305 | 304
2017-06-16 16:30 | 294 | 294
2017-06-16 17:00 | 310 | 309
2017-06-16 17:30 | 316 | 313
2017-06-16 18:00 | 314 | 312
2017-06-16 18:30 | 311 | 307
2017-06-16 19:00 | 305 | 300
2017-06-16 19:30 | 302 | 297
2017-06-16 20:00 | 294 | 293
2017-06-16 20:30 | 284 | 283
2017-06-16 21:00 | 278 | 277
2017-06-16 21:30 | 267 | 266
2017-06-16 22:00 | 259 | 259
2017-06-16 22:30 | 257 | 257
2017-06-16 23:00 | 247 | 247
2017-06-16 23:30 | 225 | 225
2017-06-17 | 206 | 206
2017-06-17 00:30 | 198 | 198
2017-06-17 01:00 | 192 | 192
2017-06-17 01:30 | 186 | 186
2017-06-17 02:00 | 183 | 182
2017-06-17 02:30 | 181 | 180
2017-06-17 03:00 | 187 | 186
2017-06-17 03:30 | 191 | 191
2017-06-17 04:00 | 187 | 187
2017-06-17 04:30 | 188 | 188
2017-06-17 05:00 | 194 | 194
2017-06-17 05:30 | 199 | 199
2017-06-17 06:00 | 206 | 206
2017-06-17 06:30 | 213 | 213
2017-06-17 07:00 | 227 | 227
2017-06-17 07:30 | 241 | 241
2017-06-17 08:00 | 252 | 252
2017-06-17 08:30 | 259 | 258
2017-06-17 09:00 | 258 | 257
2017-06-17 09:30 | 262 | 262
2017-06-17 10:00 | 268 | 268
2017-06-17 10:30 | 263 | 263
2017-06-17 11:00 | 268 | 268
2017-06-17 11:30 | 267 | 267
2017-06-17 12:00 | 261 | 261
2017-06-17 12:30 | 260 | 260
2017-06-17 13:00 | 252 | 252
2017-06-17 13:30 | 257 | 257
2017-06-17 14:00 | 265 | 265
2017-06-17 14:30 | 263 | 263
2017-06-17 15:00 | 264 | 264
2017-06-17 15:30 | 266 | 266
2017-06-17 16:00 | 274 | 274
2017-06-17 16:30 | 294 | 293
2017-06-17 17:00 | 315 | 314
2017-06-17 17:30 | 323 | 322
2017-06-17 18:00 | 318 | 316
2017-06-17 18:30 | 308 | 306
2017-06-17 19:00 | 290 | 290
2017-06-17 19:30 | 283 | 283
2017-06-17 20:00 | 279 | 278
2017-06-17 20:30 | 264 | 264
2017-06-17 21:00 | 257 | 257
2017-06-17 21:30 | 251 | 251
2017-06-17 22:00 | 253 | 253
2017-06-17 22:30 | 252 | 252
2017-06-17 23:00 | 242 | 242
2017-06-17 23:30 | 226 | 225
2017-06-18 | 210 | 209
2017-06-18 00:30 | 204 | 204
2017-06-18 01:00 | 198 | 198
2017-06-18 01:30 | 197 | 197
2017-06-18 02:00 | 194 | 194
2017-06-18 02:30 | 194 | 193
2017-06-18 03:00 | 190 | 190
2017-06-18 03:30 | 189 | 188
2017-06-18 04:00 | 195 | 194
2017-06-18 04:30 | 198 | 197
2017-06-18 05:00 | 199 | 198
2017-06-18 05:30 | 204 | 203
2017-06-18 06:00 | 207 | 207
2017-06-18 06:30 | 213 | 212
2017-06-18 07:00 | 227 | 227
2017-06-18 07:30 | 236 | 236
2017-06-18 08:00 | 244 | 244
2017-06-18 08:30 | 246 | 245
2017-06-18 09:00 | 247 | 247
2017-06-18 09:30 | 245 | 245
2017-06-18 10:00 | 240 | 240
2017-06-18 10:30 | 236 | 236
2017-06-18 11:00 | 232 | 232
2017-06-18 11:30 | 229 | 229
2017-06-18 12:00 | 229 | 228
2017-06-18 12:30 | 229 | 229
2017-06-18 13:00 | 232 | 232
2017-06-18 13:30 | 235 | 235
2017-06-18 14:00 | 240 | 240
2017-06-18 14:30 | 244 | 244
2017-06-18 15:00 | 249 | 249
2017-06-18 15:30 | 254 | 254
2017-06-18 16:00 | 261 | 261
2017-06-18 16:30 | 280 | 280
2017-06-18 17:00 | 302 | 301
2017-06-18 17:30 | 310 | 309
2017-06-18 18:00 | 311 | 309
2017-06-18 18:30 | 303 | 302
2017-06-18 19:00 | 296 | 295
2017-06-18 19:30 | 288 | 288
2017-06-18 20:00 | 286 | 285
2017-06-18 20:30 | 273 | 272
2017-06-18 21:00 | 259 | 259
2017-06-18 21:30 | 251 | 251
2017-06-18 22:00 | 249 | 249
2017-06-18 22:30 | 251 | 251
2017-06-18 23:00 | 239 | 239
2017-06-18 23:30 | 223 | 223
2017-06-19 | 210 | 210
2017-06-19 00:30 | 204 | 203
2017-06-19 01:00 | 199 | 199
2017-06-19 01:30 | 196 | 196
2017-06-19 02:00 | 196 | 195
2017-06-19 02:30 | 194 | 194
2017-06-19 03:00 | 199 | 199
2017-06-19 03:30 | 204 | 204
2017-06-19 04:00 | 209 | 209
2017-06-19 04:30 | 214 | 214
2017-06-19 05:00 | 217 | 216
2017-06-19 05:30 | 226 | 226
2017-06-19 06:00 | 247 | 247
2017-06-19 06:30 | 265 | 265
2017-06-19 07:00 | 281 | 281
2017-06-19 07:30 | 291 | 291
2017-06-19 08:00 | 290 | 290
2017-06-19 08:30 | 279 | 279
2017-06-19 09:00 | 275 | 275
2017-06-19 09:30 | 267 | 267
2017-06-19 10:00 | 260 | 260
2017-06-19 10:30 | 262 | 262
2017-06-19 11:00 | 275 | 275
2017-06-19 11:30 | 281 | 281
2017-06-19 12:00 | 267 | 266
2017-06-19 12:30 | 265 | 265
2017-06-19 13:00 | 267 | 267
2017-06-19 13:30 | 267 | 267
2017-06-19 14:00 | 269 | 269
2017-06-19 14:30 | 271 | 271
2017-06-19 15:00 | 277 | 277
2017-06-19 15:30 | 285 | 284
2017-06-19 16:00 | 293 | 293
2017-06-19 16:30 | 309 | 308
2017-06-19 17:00 | 327 | 327
2017-06-19 17:30 | 335 | 335
2017-06-19 18:00 | 334 | 334
2017-06-19 18:30 | 327 | 327
2017-06-19 19:00 | 319 | 318
2017-06-19 19:30 | 312 | 312
2017-06-19 20:00 | 308 | 308
2017-06-19 20:30 | 296 | 296
2017-06-19 21:00 | 283 | 282
2017-06-19 21:30 | 264 | 264
2017-06-19 22:00 | 261 | 261
2017-06-19 22:30 | 259 | 259
2017-06-19 23:00 | 245 | 245
2017-06-19 23:30 | 231 | 231
2017-06-20 | 216 | 216
2017-06-20 00:30 | 209 | 209
2017-06-20 01:00 | 206 | 206
2017-06-20 01:30 | 204 | 204
2017-06-20 02:00 | 203 | 202
2017-06-20 02:30 | 199 | 198
2017-06-20 03:00 | 199 | 198
2017-06-20 03:30 | 204 | 204
2017-06-20 04:00 | 205 | 204
2017-06-20 04:30 | 207 | 207
2017-06-20 05:00 | 214 | 214
2017-06-20 05:30 | 225 | 225
2017-06-20 06:00 | 242 | 242
2017-06-20 06:30 | 258 | 258
2017-06-20 07:00 | 281 | 281
2017-06-20 07:30 | 289 | 289
2017-06-20 08:00 | 295 | 294
2017-06-20 08:30 | 294 | 294
2017-06-20 09:00 | 286 | 286
2017-06-20 09:30 | 281 | 281
2017-06-20 10:00 | 271 | 271
2017-06-20 10:30 | 271 | 271
2017-06-20 11:00 | 261 | 261
2017-06-20 11:30 | 255 | 255
2017-06-20 12:00 | 250 | 250
2017-06-20 12:30 | 252 | 252
2017-06-20 13:00 | 256 | 256
2017-06-20 13:30 | 268 | 268
2017-06-20 14:00 | 269 | 269
2017-06-20 14:30 | 275 | 275
2017-06-20 15:00 | 275 | 275
2017-06-20 15:30 | 284 | 284
2017-06-20 16:00 | 297 | 297
2017-06-20 16:30 | 308 | 308
2017-06-20 17:00 | 328 | 328
2017-06-20 17:30 | 338 | 338
2017-06-20 18:00 | 337 | 336
2017-06-20 18:30 | 333 | 332
2017-06-20 19:00 | 326 | 325
2017-06-20 19:30 | 323 | 323
2017-06-20 20:00 | 317 | 317
2017-06-20 20:30 | 300 | 299
2017-06-20 21:00 | 281 | 280
2017-06-20 21:30 | 272 | 270
2017-06-20 22:00 | 264 | 264
2017-06-20 22:30 | 260 | 260
2017-06-20 23:00 | 245 | 245
2017-06-20 23:30 | 234 | 234
2017-06-21 | 220 | 219
2017-06-21 00:30 | 215 | 215
2017-06-21 01:00 | 210 | 209
2017-06-21 01:30 | 214 | 214
2017-06-21 02:00 | 227 | 227
2017-06-21 02:30 | 224 | 223
2017-06-21 03:00 | 230 | 230
2017-06-21 03:30 | 232 | 232
2017-06-21 04:00 | 236 | 236
2017-06-21 04:30 | 225 | 225
2017-06-21 05:00 | 218 | 218
2017-06-21 05:30 | 228 | 228
2017-06-21 06:00 | 252 | 252
2017-06-21 06:30 | 275 | 275
2017-06-21 07:00 | 277 | 277
2017-06-21 07:30 | 280 | 280
2017-06-21 08:00 | 278 | 278
2017-06-21 08:30 | 273 | 273
2017-06-21 09:00 | 267 | 267
2017-06-21 09:30 | 265 | 265
2017-06-21 10:00 | 266 | 266
2017-06-21 10:30 | 270 | 270
2017-06-21 11:00 | 264 | 264
2017-06-21 11:30 | 260 | 260
2017-06-21 12:00 | 261 | 261
2017-06-21 12:30 | 250 | 250
2017-06-21 13:00 | 257 | 257
2017-06-21 13:30 | 255 | 255
2017-06-21 14:00 | 260 | 260
2017-06-21 14:30 | 262 | 262
2017-06-21 15:00 | 269 | 269
2017-06-21 15:30 | 269 | 269
2017-06-21 16:00 | 288 | 288
2017-06-21 16:30 | 299 | 299
2017-06-21 17:00 | 318 | 317
2017-06-21 17:30 | 326 | 325
2017-06-21 18:00 | 322 | 321
2017-06-21 18:30 | 321 | 320
2017-06-21 19:00 | 315 | 314
2017-06-21 19:30 | 312 | 311
2017-06-21 20:00 | 309 | 307
2017-06-21 20:30 | 294 | 292
2017-06-21 21:00 | 282 | 281
2017-06-21 21:30 | 268 | 267
2017-06-21 22:00 | 266 | 264
2017-06-21 22:30 | 264 | 262
2017-06-21 23:00 | 244 | 244
2017-06-21 23:30 | 233 | 233
2017-06-22 | 220 | 220
2017-06-22 00:30 | 222 | 222
2017-06-22 01:00 | 226 | 226
2017-06-22 01:30 | 218 | 218
2017-06-22 02:00 | 212 | 212
2017-06-22 02:30 | 209 | 208
2017-06-22 03:00 | 207 | 207
2017-06-22 03:30 | 208 | 208
2017-06-22 04:00 | 204 | 204
2017-06-22 04:30 | 207 | 206
2017-06-22 05:00 | 212 | 212
2017-06-22 05:30 | 218 | 218
2017-06-22 06:00 | 241 | 241
2017-06-22 06:30 | 260 | 260
2017-06-22 07:00 | 269 | 269
2017-06-22 07:30 | 278 | 276
2017-06-22 08:00 | 279 | 278
2017-06-22 08:30 | 270 | 269
2017-06-22 09:00 | 262 | 261
2017-06-22 09:30 | 251 | 251
2017-06-22 10:00 | 247 | 246
2017-06-22 10:30 | 248 | 247
2017-06-22 11:00 | 244 | 243
2017-06-22 11:30 | 241 | 241
2017-06-22 12:00 | 236 | 236
2017-06-22 12:30 | 237 | 237
2017-06-22 13:00 | 239 | 239
2017-06-22 13:30 | 242 | 242
2017-06-22 14:00 | 245 | 245
2017-06-22 14:30 | 249 | 248
2017-06-22 15:00 | 255 | 255
2017-06-22 15:30 | 255 | 255
2017-06-22 16:00 | 266 | 266
2017-06-22 16:30 | 290 | 290
2017-06-22 17:00 | 310 | 309
2017-06-22 17:30 | 326 | 326
2017-06-22 18:00 | 328 | 328
2017-06-22 18:30 | 329 | 328
2017-06-22 19:00 | 323 | 323
2017-06-22 19:30 | 322 | 321
2017-06-22 20:00 | 318 | 317
2017-06-22 20:30 | 313 | 311
2017-06-22 21:00 | 299 | 297
2017-06-22 21:30 | 284 | 281
2017-06-22 22:00 | 277 | 275
2017-06-22 22:30 | 265 | 265
2017-06-22 23:00 | 250 | 250
2017-06-22 23:30 | 233 | 232
2017-06-23 | 222 | 222
2017-06-23 00:30 | 214 | 214
2017-06-23 01:00 | 208 | 207
2017-06-23 01:30 | 202 | 201
2017-06-23 02:00 | 200 | 199
2017-06-23 02:30 | 198 | 197
2017-06-23 03:00 | 200 | 199
2017-06-23 03:30 | 198 | 197
2017-06-23 04:00 | 206 | 206
2017-06-23 04:30 | 210 | 210
2017-06-23 05:00 | 216 | 216
2017-06-23 05:30 | 230 | 230
2017-06-23 06:00 | 253 | 252
2017-06-23 06:30 | 271 | 270
2017-06-23 07:00 | 291 | 291
2017-06-23 07:30 | 299 | 299
2017-06-23 08:00 | 209 | 209
2017-06-23 08:30 | 199 | 199
2017-06-23 09:00 | 197 | 197
2017-06-23 09:30 | 190 | 190
2017-06-23 10:00 | 185 | 185
2017-06-23 10:30 | 182 | 182
2017-06-23 11:00 | 179 | 179
2017-06-23 11:30 | 177 | 177
2017-06-23 12:00 | 176 | 176
2017-06-23 12:30 | 173 | 173
2017-06-23 13:00 | 175 | 174
2017-06-23 13:30 | 177 | 176
2017-06-23 14:00 | 181 | 180
2017-06-23 14:30 | 256 | 256
2017-06-23 15:00 | 266 | 266
2017-06-23 15:30 | 271 | 270
2017-06-23 16:00 | 277 | 276
2017-06-23 16:30 | 289 | 288
2017-06-23 17:00 | 300 | 300
2017-06-23 17:30 | 309 | 308
2017-06-23 18:00 | 306 | 304
2017-06-23 18:30 | 307 | 305
2017-06-23 19:00 | 299 | 299
2017-06-23 19:30 | 300 | 300
2017-06-23 20:00 | 297 | 297
2017-06-23 20:30 | 286 | 285
2017-06-23 21:00 | 277 | 276
2017-06-23 21:30 | 267 | 266
2017-06-23 22:00 | 265 | 263
2017-06-23 22:30 | 263 | 262
2017-06-23 23:00 | 251 | 249
2017-06-23 23:30 | 238 | 235
2017-06-24 | 221 | 218
2017-06-24 00:30 | 215 | 213
2017-06-24 01:00 | 206 | 204
2017-06-24 01:30 | 200 | 198
2017-06-24 02:00 | 197 | 194
2017-06-24 02:30 | 197 | 194
2017-06-24 03:00 | 198 | 195
2017-06-24 03:30 | 196 | 193
2017-06-24 04:00 | 202 | 200
2017-06-24 04:30 | 205 | 202
2017-06-24 05:00 | 208 | 205
2017-06-24 05:30 | 213 | 211
2017-06-24 06:00 | 222 | 221
2017-06-24 06:30 | 232 | 230
2017-06-24 07:00 | 248 | 247
2017-06-24 07:30 | 262 | 262
2017-06-24 08:00 | 268 | 268
2017-06-24 08:30 | 272 | 272
2017-06-24 09:00 | 269 | 269
2017-06-24 09:30 | 263 | 263
2017-06-24 10:00 | 255 | 255
2017-06-24 10:30 | 243 | 243
2017-06-24 11:00 | 237 | 237
2017-06-24 11:30 | 232 | 232
2017-06-24 12:00 | 230 | 230
2017-06-24 12:30 | 230 | 230
2017-06-24 13:00 | 230 | 230
2017-06-24 13:30 | 233 | 233
2017-06-24 14:00 | 238 | 238
2017-06-24 14:30 | 242 | 242
2017-06-24 15:00 | 245 | 245
2017-06-24 15:30 | 249 | 249
2017-06-24 16:00 | 258 | 258
2017-06-24 16:30 | 273 | 273
2017-06-24 17:00 | 289 | 289
2017-06-24 17:30 | 297 | 296
2017-06-24 18:00 | 294 | 293
2017-06-24 18:30 | 293 | 291
2017-06-24 19:00 | 286 | 284
2017-06-24 19:30 | 283 | 280
2017-06-24 20:00 | 275 | 274
2017-06-24 20:30 | 266 | 265
2017-06-24 21:00 | 259 | 259
2017-06-24 21:30 | 258 | 258
2017-06-24 22:00 | 258 | 258
2017-06-24 22:30 | 259 | 258
2017-06-24 23:00 | 250 | 249
2017-06-24 23:30 | 235 | 234
2017-06-25 | 220 | 218
2017-06-25 00:30 | 208 | 206
2017-06-25 01:00 | 200 | 197
2017-06-25 01:30 | 192 | 188
2017-06-25 02:00 | 186 | 183
2017-06-25 02:30 | 180 | 178
2017-06-25 03:00 | 179 | 177
2017-06-25 03:30 | 178 | 177
2017-06-25 04:00 | 179 | 177
2017-06-25 04:30 | 181 | 179
2017-06-25 05:00 | 186 | 184
2017-06-25 05:30 | 192 | 191
2017-06-25 06:00 | 202 | 202
2017-06-25 06:30 | 213 | 212
2017-06-25 07:00 | 230 | 229
2017-06-25 07:30 | 240 | 239
2017-06-25 08:00 | 248 | 248
2017-06-25 08:30 | 251 | 251
2017-06-25 09:00 | 249 | 249
2017-06-25 09:30 | 245 | 245
2017-06-25 10:00 | 242 | 241
2017-06-25 10:30 | 229 | 229
2017-06-25 11:00 | 222 | 222
2017-06-25 11:30 | 218 | 218
2017-06-25 12:00 | 216 | 215
2017-06-25 12:30 | 214 | 214
2017-06-25 13:00 | 215 | 215
2017-06-25 13:30 | 219 | 218
2017-06-25 14:00 | 224 | 224
2017-06-25 14:30 | 232 | 232
2017-06-25 15:00 | 242 | 242
2017-06-25 15:30 | 252 | 252
2017-06-25 16:00 | 264 | 264
2017-06-25 16:30 | 281 | 279
2017-06-25 17:00 | 302 | 301
2017-06-25 17:30 | 318 | 317
2017-06-25 18:00 | 315 | 315
2017-06-25 18:30 | 312 | 312
2017-06-25 19:00 | 302 | 301
2017-06-25 19:30 | 296 | 295
2017-06-25 20:00 | 291 | 290
2017-06-25 20:30 | 279 | 277
2017-06-25 21:00 | 269 | 267
2017-06-25 21:30 | 259 | 256
2017-06-25 22:00 | 256 | 254
2017-06-25 22:30 | 252 | 251
2017-06-25 23:00 | 239 | 238
2017-06-25 23:30 | 221 | 219
2017-06-26 | 205 | 202
2017-06-26 00:30 | 194 | 191
2017-06-26 01:00 | 186 | 183
2017-06-26 01:30 | 179 | 175
2017-06-26 02:00 | 171 | 170
2017-06-26 02:30 | 169 | 167
2017-06-26 03:00 | 169 | 168
2017-06-26 03:30 | 171 | 169
2017-06-26 04:00 | 176 | 175
2017-06-26 04:30 | 184 | 183
2017-06-26 05:00 | 197 | 196
2017-06-26 05:30 | 216 | 215
2017-06-26 06:00 | 242 | 242
2017-06-26 06:30 | 261 | 261
2017-06-26 07:00 | 286 | 286
2017-06-26 07:30 | 295 | 293
2017-06-26 08:00 | 292 | 290
2017-06-26 08:30 | 286 | 284
2017-06-26 09:00 | 279 | 277
2017-06-26 09:30 | 270 | 269
2017-06-26 10:00 | 263 | 262
2017-06-26 10:30 | 256 | 254
2017-06-26 11:00 | 252 | 251
2017-06-26 11:30 | 249 | 248
2017-06-26 12:00 | 247 | 245
2017-06-26 12:30 | 247 | 245
2017-06-26 13:00 | 249 | 247
2017-06-26 13:30 | 253 | 251
2017-06-26 14:00 | 259 | 257
2017-06-26 14:30 | 266 | 264
2017-06-26 15:00 | 274 | 272
2017-06-26 15:30 | 276 | 273
2017-06-26 16:00 | 279 | 276
2017-06-26 16:30 | 294 | 292
2017-06-26 17:00 | 311 | 307
2017-06-26 17:30 | 326 | 321
2017-06-26 18:00 | 323 | 318
2017-06-26 18:30 | 318 | 313
2017-06-26 19:00 | 306 | 305
2017-06-26 19:30 | 302 | 301
2017-06-26 20:00 | 301 | 300
2017-06-26 20:30 | 291 | 290
2017-06-26 21:00 | 275 | 275
2017-06-26 21:30 | 262 | 262
2017-06-26 22:00 | 259 | 259
2017-06-26 22:30 | 259 | 258
2017-06-26 23:00 | 247 | 246
2017-06-26 23:30 | 233 | 232
2017-06-27 | 219 | 218
2017-06-27 00:30 | 214 | 212
2017-06-27 01:00 | 208 | 206
2017-06-27 01:30 | 203 | 200
2017-06-27 02:00 | 200 | 197
2017-06-27 02:30 | 196 | 194
2017-06-27 03:00 | 197 | 195
2017-06-27 03:30 | 201 | 199
2017-06-27 04:00 | 203 | 201
2017-06-27 04:30 | 208 | 205
2017-06-27 05:00 | 215 | 213
2017-06-27 05:30 | 226 | 226
2017-06-27 06:00 | 252 | 251
2017-06-27 06:30 | 272 | 270
2017-06-27 07:00 | 272 | 270
2017-06-27 07:30 | 268 | 268
2017-06-27 08:00 | 278 | 278
2017-06-27 08:30 | 280 | 280
2017-06-27 09:00 | 276 | 276
2017-06-27 09:30 | 267 | 267
2017-06-27 10:00 | 266 | 266
2017-06-27 10:30 | 263 | 263
2017-06-27 11:00 | 256 | 256
2017-06-27 11:30 | 250 | 250
2017-06-27 12:00 | 253 | 253
2017-06-27 12:30 | 257 | 257
2017-06-27 13:00 | 246 | 246
2017-06-27 13:30 | 255 | 255
2017-06-27 14:00 | 255 | 255
2017-06-27 14:30 | 253 | 253
2017-06-27 15:00 | 258 | 258
2017-06-27 15:30 | 267 | 267
2017-06-27 16:00 | 276 | 276
2017-06-27 16:30 | 298 | 298
2017-06-27 17:00 | 322 | 322
2017-06-27 17:30 | 334 | 333
2017-06-27 18:00 | 329 | 328
2017-06-27 18:30 | 326 | 325
2017-06-27 19:00 | 317 | 316
2017-06-27 19:30 | 311 | 311
2017-06-27 20:00 | 303 | 303
2017-06-27 20:30 | 289 | 289
2017-06-27 21:00 | 278 | 278
2017-06-27 21:30 | 267 | 267
2017-06-27 22:00 | 261 | 261
2017-06-27 22:30 | 262 | 262
2017-06-27 23:00 | 246 | 246
2017-06-27 23:30 | 228 | 228
2017-06-28 | 216 | 216
2017-06-28 00:30 | 210 | 209
2017-06-28 01:00 | 207 | 207
2017-06-28 01:30 | 201 | 200
2017-06-28 02:00 | 199 | 198
2017-06-28 02:30 | 196 | 195
2017-06-28 03:00 | 198 | 197
2017-06-28 03:30 | 201 | 200
2017-06-28 04:00 | 202 | 201
2017-06-28 04:30 | 206 | 206
2017-06-28 05:00 | 213 | 213
2017-06-28 05:30 | 225 | 225
2017-06-28 06:00 | 249 | 249
2017-06-28 06:30 | 272 | 272
2017-06-28 07:00 | 287 | 287
2017-06-28 07:30 | 293 | 293
2017-06-28 08:00 | 293 | 293
2017-06-28 08:30 | 285 | 285
2017-06-28 09:00 | 277 | 277
2017-06-28 09:30 | 274 | 273
2017-06-28 10:00 | 268 | 268
2017-06-28 10:30 | 266 | 265
2017-06-28 11:00 | 265 | 265
2017-06-28 11:30 | 261 | 261
2017-06-28 12:00 | 263 | 263
2017-06-28 12:30 | 265 | 265
2017-06-28 13:00 | 268 | 268
2017-06-28 13:30 | 272 | 272
2017-06-28 14:00 | 277 | 277
2017-06-28 14:30 | 274 | 274
2017-06-28 15:00 | 279 | 279
2017-06-28 15:30 | 284 | 284
2017-06-28 16:00 | 295 | 294
2017-06-28 16:30 | 310 | 309
2017-06-28 17:00 | 333 | 332
2017-06-28 17:30 | 347 | 345
2017-06-28 18:00 | 330 | 328
2017-06-28 18:30 | 318 | 317
2017-06-28 19:00 | 313 | 311
2017-06-28 19:30 | 311 | 309
2017-06-28 20:00 | 299 | 298
2017-06-28 20:30 | 291 | 290
2017-06-28 21:00 | 277 | 276
2017-06-28 21:30 | 264 | 262
2017-06-28 22:00 | 259 | 259
2017-06-28 22:30 | 259 | 259
2017-06-28 23:00 | 249 | 249
2017-06-28 23:30 | 233 | 233
2017-06-29 | 219 | 219
2017-06-29 00:30 | 209 | 208
2017-06-29 01:00 | 202 | 202
2017-06-29 01:30 | 196 | 195
2017-06-29 02:00 | 196 | 195
2017-06-29 02:30 | 191 | 190
2017-06-29 03:00 | 192 | 191
2017-06-29 03:30 | 193 | 192
2017-06-29 04:00 | 200 | 199
2017-06-29 04:30 | 204 | 204
2017-06-29 05:00 | 216 | 216
2017-06-29 05:30 | 230 | 229
2017-06-29 06:00 | 248 | 248
2017-06-29 06:30 | 259 | 259
2017-06-29 07:00 | 272 | 272
2017-06-29 07:30 | 287 | 287
2017-06-29 08:00 | 292 | 292
2017-06-29 08:30 | 288 | 287
2017-06-29 09:00 | 280 | 280
2017-06-29 09:30 | 272 | 272
2017-06-29 10:00 | 271 | 270
2017-06-29 10:30 | 261 | 261
2017-06-29 11:00 | 255 | 255
2017-06-29 11:30 | 256 | 255
2017-06-29 12:00 | 253 | 252
2017-06-29 12:30 | 250 | 250
2017-06-29 13:00 | 252 | 252
2017-06-29 13:30 | 257 | 256
2017-06-29 14:00 | 260 | 260
2017-06-29 14:30 | 262 | 262
2017-06-29 15:00 | 265 | 265
2017-06-29 15:30 | 270 | 269
2017-06-29 16:00 | 275 | 275
2017-06-29 16:30 | 287 | 287
2017-06-29 17:00 | 307 | 306
2017-06-29 17:30 | 318 | 317
2017-06-29 18:00 | 317 | 315
2017-06-29 18:30 | 311 | 309
2017-06-29 19:00 | 301 | 301
2017-06-29 19:30 | 297 | 297
2017-06-29 20:00 | 290 | 290
2017-06-29 20:30 | 282 | 282
2017-06-29 21:00 | 272 | 271
2017-06-29 21:30 | 264 | 263
2017-06-29 22:00 | 261 | 259
2017-06-29 22:30 | 257 | 256
2017-06-29 23:00 | 245 | 243
2017-06-29 23:30 | 230 | 227
2017-06-30 | 215 | 214
2017-06-30 00:30 | 207 | 206
2017-06-30 01:00 | 203 | 201
2017-06-30 01:30 | 198 | 196
2017-06-30 02:00 | 195 | 193
2017-06-30 02:30 | 193 | 190
2017-06-30 03:00 | 191 | 189
2017-06-30 03:30 | 192 | 192
2017-06-30 04:00 | 196 | 195
2017-06-30 04:30 | 201 | 200
2017-06-30 05:00 | 208 | 208
2017-06-30 05:30 | 222 | 222
2017-06-30 06:00 | 244 | 244
2017-06-30 06:30 | 259 | 259
2017-06-30 07:00 | 278 | 277
2017-06-30 07:30 | 288 | 287
2017-06-30 08:00 | 297 | 296
2017-06-30 08:30 | 288 | 288
2017-06-30 09:00 | 283 | 282
2017-06-30 09:30 | 269 | 268
2017-06-30 10:00 | 264 | 264
2017-06-30 10:30 | 258 | 257
2017-06-30 11:00 | 254 | 254
2017-06-30 11:30 | 254 | 254
2017-06-30 12:00 | 254 | 253
2017-06-30 12:30 | 256 | 256
2017-06-30 13:00 | 257 | 257
2017-06-30 13:30 | 262 | 262
2017-06-30 14:00 | 265 | 265
2017-06-30 14:30 | 268 | 268
2017-06-30 15:00 | 273 | 273
2017-06-30 15:30 | 280 | 280
2017-06-30 16:00 | 285 | 285
2017-06-30 16:30 | 302 | 302
2017-06-30 17:00 | 316 | 315
2017-06-30 17:30 | 333 | 333
2017-06-30 18:00 | 334 | 334
2017-06-30 18:30 | 328 | 328
2017-06-30 19:00 | 321 | 321
2017-06-30 19:30 | 315 | 315
2017-06-30 20:00 | 318 | 317
2017-06-30 20:30 | 304 | 303
2017-06-30 21:00 | 292 | 292
2017-06-30 21:30 | 280 | 280
2017-06-30 22:00 | 278 | 278
2017-06-30 22:30 | 276 | 276
2017-06-30 23:00 | 262 | 262
2017-06-30 23:30 | 250 | 250
2017-07-01 | 227 | 227
2017-07-01 00:30 | 216 | 216
2017-07-01 01:00 | 211 | 211
2017-07-01 01:30 | 206 | 206
2017-07-01 02:00 | 199 | 199
2017-07-01 02:30 | 200 | 200
2017-07-01 03:00 | 201 | 201
2017-07-01 03:30 | 207 | 207
2017-07-01 04:00 | 202 | 202
2017-07-01 04:30 | 204 | 204
2017-07-01 05:00 | 206 | 206
2017-07-01 05:30 | 214 | 214
2017-07-01 06:00 | 230 | 230
2017-07-01 06:30 | 244 | 244
2017-07-01 07:00 | 261 | 261
2017-07-01 07:30 | 273 | 272
2017-07-01 08:00 | 282 | 282
2017-07-01 08:30 | 288 | 286
2017-07-01 09:00 | 282 | 281
2017-07-01 09:30 | 273 | 271
2017-07-01 10:00 | 262 | 261
2017-07-01 10:30 | 255 | 254
2017-07-01 11:00 | 245 | 245
2017-07-01 11:30 | 253 | 253
2017-07-01 12:00 | 258 | 257
2017-07-01 12:30 | 261 | 261
2017-07-01 13:00 | 261 | 260
2017-07-01 13:30 | 268 | 267
2017-07-01 14:00 | 275 | 275
2017-07-01 14:30 | 267 | 267
2017-07-01 15:00 | 258 | 258
2017-07-01 15:30 | 266 | 266
2017-07-01 16:00 | 278 | 278
2017-07-01 16:30 | 306 | 305
2017-07-01 17:00 | 330 | 329
2017-07-01 17:30 | 342 | 341
2017-07-01 18:00 | 341 | 340
2017-07-01 18:30 | 338 | 337
2017-07-01 19:00 | 328 | 327
2017-07-01 19:30 | 328 | 327
2017-07-01 20:00 | 331 | 331
2017-07-01 20:30 | 321 | 320
2017-07-01 21:00 | 309 | 309
2017-07-01 21:30 | 295 | 294
2017-07-01 22:00 | 286 | 285
2017-07-01 22:30 | 280 | 278
2017-07-01 23:00 | 267 | 264
2017-07-01 23:30 | 248 | 246
2017-07-02 | 229 | 228
2017-07-02 00:30 | 217 | 217
2017-07-02 01:00 | 206 | 206
2017-07-02 01:30 | 200 | 200
2017-07-02 02:00 | 200 | 200
2017-07-02 02:30 | 197 | 197
2017-07-02 03:00 | 201 | 201
2017-07-02 03:30 | 205 | 205
2017-07-02 04:00 | 206 | 206
2017-07-02 04:30 | 213 | 213
2017-07-02 05:00 | 213 | 213
2017-07-02 05:30 | 213 | 213
2017-07-02 06:00 | 228 | 228
2017-07-02 06:30 | 240 | 240
2017-07-02 07:00 | 256 | 256
2017-07-02 07:30 | 267 | 267
2017-07-02 08:00 | 301 | 301
2017-07-02 08:30 | 289 | 289
2017-07-02 09:00 | 276 | 276
2017-07-02 09:30 | 272 | 272
2017-07-02 10:00 | 260 | 260
2017-07-02 10:30 | 255 | 255
2017-07-02 11:00 | 242 | 242
2017-07-02 11:30 | 232 | 232
2017-07-02 12:00 | 225 | 225
2017-07-02 12:30 | 227 | 227
2017-07-02 13:00 | 233 | 233
2017-07-02 13:30 | 248 | 248
2017-07-02 14:00 | 262 | 262
2017-07-02 14:30 | 252 | 252
2017-07-02 15:00 | 254 | 254
2017-07-02 15:30 | 265 | 265
2017-07-02 16:00 | 277 | 277
2017-07-02 16:30 | 291 | 291
2017-07-02 17:00 | 311 | 311
2017-07-02 17:30 | 324 | 324
2017-07-02 18:00 | 324 | 324
2017-07-02 18:30 | 324 | 324
2017-07-02 19:00 | 315 | 314
2017-07-02 19:30 | 310 | 309
2017-07-02 20:00 | 314 | 313
2017-07-02 20:30 | 310 | 309
2017-07-02 21:00 | 296 | 294
2017-07-02 21:30 | 282 | 281
2017-07-02 22:00 | 269 | 269
2017-07-02 22:30 | 262 | 262
2017-07-02 23:00 | 249 | 249
2017-07-02 23:30 | 234 | 234
2017-07-03 | 221 | 220
2017-07-03 00:30 | 214 | 214
2017-07-03 01:00 | 209 | 209
2017-07-03 01:30 | 206 | 205
2017-07-03 02:00 | 224 | 223
2017-07-03 02:30 | 235 | 235
2017-07-03 03:00 | 235 | 235
2017-07-03 03:30 | 236 | 236
2017-07-03 04:00 | 241 | 241
2017-07-03 04:30 | 249 | 249
2017-07-03 05:00 | 238 | 238
2017-07-03 05:30 | 240 | 240
2017-07-03 06:00 | 265 | 265
2017-07-03 06:30 | 289 | 289
2017-07-03 07:00 | 316 | 316
2017-07-03 07:30 | 330 | 330
2017-07-03 08:00 | 334 | 334
2017-07-03 08:30 | 343 | 343
2017-07-03 09:00 | 334 | 334
2017-07-03 09:30 | 330 | 330
2017-07-03 10:00 | 321 | 321
2017-07-03 10:30 | 303 | 303
2017-07-03 11:00 | 299 | 299
2017-07-03 11:30 | 300 | 300
2017-07-03 12:00 | 300 | 300
2017-07-03 12:30 | 302 | 302
2017-07-03 13:00 | 316 | 316
2017-07-03 13:30 | 327 | 327
2017-07-03 14:00 | 321 | 320
2017-07-03 14:30 | 300 | 300
2017-07-03 15:00 | 295 | 295
2017-07-03 15:30 | 299 | 299
2017-07-03 16:00 | 311 | 311
2017-07-03 16:30 | 335 | 334
2017-07-03 17:00 | 349 | 347
2017-07-03 17:30 | 361 | 359
2017-07-03 18:00 | 358 | 356
2017-07-03 18:30 | 355 | 353
2017-07-03 19:00 | 348 | 345
2017-07-03 19:30 | 349 | 346
2017-07-03 20:00 | 350 | 347
2017-07-03 20:30 | 335 | 332
2017-07-03 21:00 | 316 | 312
2017-07-03 21:30 | 295 | 294
2017-07-03 22:00 | 283 | 282
2017-07-03 22:30 | 270 | 269
2017-07-03 23:00 | 246 | 245
2017-07-03 23:30 | 232 | 232
2017-07-04 | 217 | 217
2017-07-04 00:30 | 205 | 204
2017-07-04 01:00 | 195 | 194
2017-07-04 01:30 | 190 | 189
2017-07-04 02:00 | 183 | 183
2017-07-04 02:30 | 187 | 186
2017-07-04 03:00 | 191 | 191
2017-07-04 03:30 | 187 | 187
2017-07-04 04:00 | 198 | 197
2017-07-04 04:30 | 207 | 207
2017-07-04 05:00 | 213 | 213
2017-07-04 05:30 | 226 | 226
2017-07-04 06:00 | 247 | 246
2017-07-04 06:30 | 265 | 264
2017-07-04 07:00 | 283 | 283
2017-07-04 07:30 | 290 | 290
2017-07-04 08:00 | 292 | 292
2017-07-04 08:30 | 284 | 284
2017-07-04 09:00 | 279 | 279
2017-07-04 09:30 | 271 | 271
2017-07-04 10:00 | 260 | 260
2017-07-04 10:30 | 255 | 255
2017-07-04 11:00 | 253 | 253
2017-07-04 11:30 | 250 | 250
2017-07-04 12:00 | 249 | 249
2017-07-04 12:30 | 248 | 248
2017-07-04 13:00 | 252 | 252
2017-07-04 13:30 | 256 | 256
2017-07-04 14:00 | 263 | 263
2017-07-04 14:30 | 268 | 268
2017-07-04 15:00 | 275 | 275
2017-07-04 15:30 | 278 | 278
2017-07-04 16:00 | 288 | 288
2017-07-04 16:30 | 301 | 301
2017-07-04 17:00 | 325 | 325
2017-07-04 17:30 | 342 | 342
2017-07-04 18:00 | 341 | 340
2017-07-04 18:30 | 335 | 334
2017-07-04 19:00 | 327 | 326
2017-07-04 19:30 | 321 | 320
2017-07-04 20:00 | 305 | 304
2017-07-04 20:30 | 295 | 294
2017-07-04 21:00 | 285 | 283
2017-07-04 21:30 | 271 | 270
2017-07-04 22:00 | 268 | 268
2017-07-04 22:30 | 264 | 263
2017-07-04 23:00 | 249 | 248
2017-07-04 23:30 | 233 | 232
2017-07-05 | 221 | 220
2017-07-05 00:30 | 214 | 213
2017-07-05 01:00 | 207 | 205
2017-07-05 01:30 | 201 | 199
2017-07-05 02:00 | 199 | 196
2017-07-05 02:30 | 217 | 215
2017-07-05 03:00 | 202 | 200
2017-07-05 03:30 | 203 | 201
2017-07-05 04:00 | 207 | 205
2017-07-05 04:30 | 212 | 210
2017-07-05 05:00 | 217 | 216
2017-07-05 05:30 | 228 | 228
2017-07-05 06:00 | 252 | 251
2017-07-05 06:30 | 272 | 270
2017-07-05 07:00 | 290 | 288
2017-07-05 07:30 | 298 | 296
2017-07-05 08:00 | 296 | 295
2017-07-05 08:30 | 286 | 286
2017-07-05 09:00 | 283 | 283
2017-07-05 09:30 | 277 | 277
2017-07-05 10:00 | 271 | 271
2017-07-05 10:30 | 266 | 265
2017-07-05 11:00 | 260 | 259
2017-07-05 11:30 | 259 | 259
2017-07-05 12:00 | 258 | 258
2017-07-05 12:30 | 259 | 258
2017-07-05 13:00 | 262 | 262
2017-07-05 13:30 | 266 | 265
2017-07-05 14:00 | 271 | 270
2017-07-05 14:30 | 276 | 275
2017-07-05 15:00 | 281 | 280
2017-07-05 15:30 | 287 | 286
2017-07-05 16:00 | 300 | 299
2017-07-05 16:30 | 312 | 312
2017-07-05 17:00 | 341 | 341
2017-07-05 17:30 | 348 | 344
2017-07-05 18:00 | 340 | 337
2017-07-05 18:30 | 339 | 336
2017-07-05 19:00 | 331 | 328
2017-07-05 19:30 | 321 | 320
2017-07-05 20:00 | 314 | 313
2017-07-05 20:30 | 301 | 299
2017-07-05 21:00 | 286 | 284
2017-07-05 21:30 | 275 | 272
2017-07-05 22:00 | 266 | 265
2017-07-05 22:30 | 265 | 265
2017-07-05 23:00 | 256 | 256
2017-07-05 23:30 | 244 | 244
2017-07-06 | 230 | 229
2017-07-06 00:30 | 218 | 217
2017-07-06 01:00 | 215 | 213
2017-07-06 01:30 | 218 | 217
2017-07-06 02:00 | 230 | 229
2017-07-06 02:30 | 229 | 228
2017-07-06 03:00 | 230 | 229
2017-07-06 03:30 | 230 | 229
2017-07-06 04:00 | 236 | 235
2017-07-06 04:30 | 220 | 218
2017-07-06 05:00 | 223 | 222
2017-07-06 05:30 | 238 | 237
2017-07-06 06:00 | 251 | 250
2017-07-06 06:30 | 266 | 265
2017-07-06 07:00 | 286 | 285
2017-07-06 07:30 | 292 | 291
2017-07-06 08:00 | 293 | 293
2017-07-06 08:30 | 289 | 289
2017-07-06 09:00 | 281 | 281
2017-07-06 09:30 | 273 | 273
2017-07-06 10:00 | 264 | 264
2017-07-06 10:30 | 261 | 261
2017-07-06 11:00 | 260 | 260
2017-07-06 11:30 | 256 | 256
2017-07-06 12:00 | 255 | 255
2017-07-06 12:30 | 253 | 253
2017-07-06 13:00 | 256 | 256
2017-07-06 13:30 | 262 | 262
2017-07-06 14:00 | 269 | 269
2017-07-06 14:30 | 273 | 273
2017-07-06 15:00 | 279 | 279
2017-07-06 15:30 | 284 | 283
2017-07-06 16:00 | 292 | 291
2017-07-06 16:30 | 302 | 302
2017-07-06 17:00 | 321 | 320
2017-07-06 17:30 | 333 | 332
2017-07-06 18:00 | 332 | 332
2017-07-06 18:30 | 335 | 335
2017-07-06 19:00 | 327 | 326
2017-07-06 19:30 | 324 | 323
2017-07-06 20:00 | 322 | 321
2017-07-06 20:30 | 315 | 314
2017-07-06 21:00 | 305 | 303
2017-07-06 21:30 | 289 | 287
2017-07-06 22:00 | 279 | 277
2017-07-06 22:30 | 269 | 269
2017-07-06 23:00 | 257 | 256
2017-07-06 23:30 | 239 | 238
2017-07-07 | 224 | 222
2017-07-07 00:30 | 216 | 215
2017-07-07 01:00 | 214 | 212
2017-07-07 01:30 | 219 | 217
2017-07-07 02:00 | 209 | 207
2017-07-07 02:30 | 230 | 229
2017-07-07 03:00 | 232 | 231
2017-07-07 03:30 | 234 | 233
2017-07-07 04:00 | 235 | 234
2017-07-07 04:30 | 234 | 233
2017-07-07 05:00 | 227 | 226
2017-07-07 05:30 | 235 | 234
2017-07-07 06:00 | 250 | 249
2017-07-07 06:30 | 275 | 275
2017-07-07 07:00 | 299 | 298
2017-07-07 07:30 | 322 | 321
2017-07-07 08:00 | 321 | 320
2017-07-07 08:30 | 319 | 318
2017-07-07 09:00 | 325 | 324
2017-07-07 09:30 | 326 | 326
2017-07-07 10:00 | 316 | 315
2017-07-07 10:30 | 307 | 306
2017-07-07 11:00 | 305 | 304
2017-07-07 11:30 | 310 | 309
2017-07-07 12:00 | 307 | 306
2017-07-07 12:30 | 300 | 299
2017-07-07 13:00 | 297 | 296
2017-07-07 13:30 | 298 | 296
2017-07-07 14:00 | 300 | 297
2017-07-07 14:30 | 301 | 298
2017-07-07 15:00 | 301 | 297
2017-07-07 15:30 | 305 | 302
2017-07-07 16:00 | 307 | 303
2017-07-07 16:30 | 319 | 316
2017-07-07 17:00 | 338 | 336
2017-07-07 17:30 | 349 | 347
2017-07-07 18:00 | 344 | 343
2017-07-07 18:30 | 342 | 340
2017-07-07 19:00 | 340 | 337
2017-07-07 19:30 | 337 | 335
2017-07-07 20:00 | 338 | 335
2017-07-07 20:30 | 332 | 328
2017-07-07 21:00 | 318 | 314
2017-07-07 21:30 | 303 | 297
2017-07-07 22:00 | 285 | 284
2017-07-07 22:30 | 278 | 278
2017-07-07 23:00 | 267 | 267
2017-07-07 23:30 | 252 | 251
2017-07-08 | 235 | 234
2017-07-08 00:30 | 220 | 218
2017-07-08 01:00 | 208 | 206
2017-07-08 01:30 | 203 | 201
2017-07-08 02:00 | 199 | 197
2017-07-08 02:30 | 198 | 196
2017-07-08 03:00 | 197 | 194
2017-07-08 03:30 | 195 | 192
2017-07-08 04:00 | 193 | 190
2017-07-08 04:30 | 199 | 196
2017-07-08 05:00 | 203 | 201
2017-07-08 05:30 | 207 | 205
2017-07-08 06:00 | 219 | 217
2017-07-08 06:30 | 233 | 232
2017-07-08 07:00 | 256 | 256
2017-07-08 07:30 | 269 | 269
2017-07-08 08:00 | 280 | 280
2017-07-08 08:30 | 285 | 285
2017-07-08 09:00 | 282 | 282
2017-07-08 09:30 | 268 | 268
2017-07-08 10:00 | 274 | 274
2017-07-08 10:30 | 257 | 257
2017-07-08 11:00 | 240 | 240
2017-07-08 11:30 | 233 | 232
2017-07-08 12:00 | 232 | 231
2017-07-08 12:30 | 227 | 226
2017-07-08 13:00 | 230 | 229
2017-07-08 13:30 | 235 | 234
2017-07-08 14:00 | 241 | 240
2017-07-08 14:30 | 245 | 244
2017-07-08 15:00 | 251 | 250
2017-07-08 15:30 | 256 | 256
2017-07-08 16:00 | 271 | 270
2017-07-08 16:30 | 289 | 289
2017-07-08 17:00 | 315 | 313
2017-07-08 17:30 | 327 | 323
2017-07-08 18:00 | 325 | 321
2017-07-08 18:30 | 323 | 320
2017-07-08 19:00 | 317 | 314
2017-07-08 19:30 | 315 | 311
2017-07-08 20:00 | 304 | 304
2017-07-08 20:30 | 298 | 297
2017-07-08 21:00 | 288 | 287
2017-07-08 21:30 | 277 | 277
2017-07-08 22:00 | 273 | 273
2017-07-08 22:30 | 270 | 270
2017-07-08 23:00 | 258 | 258
2017-07-08 23:30 | 247 | 246
2017-07-09 | 230 | 228
2017-07-09 00:30 | 221 | 220
2017-07-09 01:00 | 215 | 213
2017-07-09 01:30 | 209 | 207
2017-07-09 02:00 | 207 | 205
2017-07-09 02:30 | 204 | 202
2017-07-09 03:00 | 202 | 200
2017-07-09 03:30 | 201 | 198
2017-07-09 04:00 | 203 | 200
2017-07-09 04:30 | 206 | 204
2017-07-09 05:00 | 211 | 209
2017-07-09 05:30 | 217 | 215
2017-07-09 06:00 | 227 | 226
2017-07-09 06:30 | 238 | 237
2017-07-09 07:00 | 253 | 252
2017-07-09 07:30 | 260 | 260
2017-07-09 08:00 | 267 | 266
2017-07-09 08:30 | 268 | 268
2017-07-09 09:00 | 267 | 267
2017-07-09 09:30 | 267 | 267
2017-07-09 10:00 | 262 | 261
2017-07-09 10:30 | 249 | 249
2017-07-09 11:00 | 238 | 238
2017-07-09 11:30 | 236 | 236
2017-07-09 12:00 | 234 | 234
2017-07-09 12:30 | 229 | 228
2017-07-09 13:00 | 228 | 227
2017-07-09 13:30 | 232 | 232
2017-07-09 14:00 | 239 | 238
2017-07-09 14:30 | 244 | 243
2017-07-09 15:00 | 253 | 252
2017-07-09 15:30 | 263 | 262
2017-07-09 16:00 | 270 | 270
2017-07-09 16:30 | 294 | 292
2017-07-09 17:00 | 314 | 311
2017-07-09 17:30 | 331 | 327
2017-07-09 18:00 | 337 | 333
2017-07-09 18:30 | 337 | 332
2017-07-09 19:00 | 328 | 325
2017-07-09 19:30 | 324 | 321
2017-07-09 20:00 | 325 | 321
2017-07-09 20:30 | 310 | 307
2017-07-09 21:00 | 296 | 295
2017-07-09 21:30 | 288 | 286
2017-07-09 22:00 | 277 | 277
2017-07-09 22:30 | 275 | 275
2017-07-09 23:00 | 265 | 264
2017-07-09 23:30 | 252 | 251
2017-07-10 | 238 | 236
2017-07-10 00:30 | 236 | 234
2017-07-10 01:00 | 247 | 246
2017-07-10 01:30 | 228 | 226
2017-07-10 02:00 | 210 | 207
2017-07-10 02:30 | 212 | 209
2017-07-10 03:00 | 208 | 205
2017-07-10 03:30 | 207 | 204
2017-07-10 04:00 | 224 | 222
2017-07-10 04:30 | 231 | 230
2017-07-10 05:00 | 229 | 227
2017-07-10 05:30 | 240 | 239
2017-07-10 06:00 | 267 | 267
2017-07-10 06:30 | 293 | 291
2017-07-10 07:00 | 321 | 318
2017-07-10 07:30 | 336 | 333
2017-07-10 08:00 | 335 | 332
2017-07-10 08:30 | 329 | 326
2017-07-10 09:00 | 324 | 322
2017-07-10 09:30 | 310 | 307
2017-07-10 10:00 | 303 | 300
2017-07-10 10:30 | 299 | 299
2017-07-10 11:00 | 287 | 286
2017-07-10 11:30 | 294 | 293
2017-07-10 12:00 | 285 | 285
2017-07-10 12:30 | 296 | 296
2017-07-10 13:00 | 286 | 286
2017-07-10 13:30 | 300 | 299
2017-07-10 14:00 | 298 | 297
2017-07-10 14:30 | 303 | 303
2017-07-10 15:00 | 305 | 304
2017-07-10 15:30 | 313 | 312
2017-07-10 16:00 | 324 | 323
2017-07-10 16:30 | 346 | 343
2017-07-10 17:00 | 366 | 364
2017-07-10 17:30 | 376 | 374
2017-07-10 18:00 | 373 | 372
2017-07-10 18:30 | 368 | 367
2017-07-10 19:00 | 360 | 358
2017-07-10 19:30 | 356 | 354
2017-07-10 20:00 | 350 | 347
2017-07-10 20:30 | 330 | 329
2017-07-10 21:00 | 315 | 314
2017-07-10 21:30 | 304 | 303
2017-07-10 22:00 | 290 | 288
2017-07-10 22:30 | 273 | 273
2017-07-10 23:00 | 260 | 260
2017-07-10 23:30 | 249 | 249
2017-07-11 | 237 | 236
2017-07-11 00:30 | 253 | 253
2017-07-11 01:00 | 250 | 250
2017-07-11 01:30 | 243 | 243
2017-07-11 02:00 | 236 | 235
2017-07-11 02:30 | 231 | 230
2017-07-11 03:00 | 229 | 228
2017-07-11 03:30 | 230 | 229
2017-07-11 04:00 | 228 | 227
2017-07-11 04:30 | 235 | 234
2017-07-11 05:00 | 230 | 229
2017-07-11 05:30 | 246 | 245
2017-07-11 06:00 | 267 | 267
2017-07-11 06:30 | 288 | 288
2017-07-11 07:00 | 310 | 310
2017-07-11 07:30 | 322 | 322
2017-07-11 08:00 | 317 | 317
2017-07-11 08:30 | 306 | 306
2017-07-11 09:00 | 304 | 304
2017-07-11 09:30 | 290 | 290
2017-07-11 10:00 | 293 | 293
2017-07-11 10:30 | 311 | 311
2017-07-11 11:00 | 303 | 303
2017-07-11 11:30 | 299 | 299
2017-07-11 12:00 | 296 | 296
2017-07-11 12:30 | 296 | 296
2017-07-11 13:00 | 297 | 296
2017-07-11 13:30 | 304 | 303
2017-07-11 14:00 | 297 | 297
2017-07-11 14:30 | 313 | 313
2017-07-11 15:00 | 294 | 294
2017-07-11 15:30 | 294 | 293
2017-07-11 16:00 | 305 | 303
2017-07-11 16:30 | 323 | 322
2017-07-11 17:00 | 351 | 349
2017-07-11 17:30 | 369 | 367
2017-07-11 18:00 | 370 | 368
2017-07-11 18:30 | 365 | 363
2017-07-11 19:00 | 351 | 349
2017-07-11 19:30 | 348 | 346
2017-07-11 20:00 | 343 | 341
2017-07-11 20:30 | 331 | 330
2017-07-11 21:00 | 319 | 318
2017-07-11 21:30 | 306 | 304
2017-07-11 22:00 | 291 | 288
2017-07-11 22:30 | 276 | 276
2017-07-11 23:00 | 266 | 266
2017-07-11 23:30 | 252 | 252
2017-07-12 | 244 | 243
2017-07-12 00:30 | 251 | 250
2017-07-12 01:00 | 242 | 242
2017-07-12 01:30 | 241 | 240
2017-07-12 02:00 | 236 | 235
2017-07-12 02:30 | 233 | 233
2017-07-12 03:00 | 232 | 231
2017-07-12 03:30 | 230 | 229
2017-07-12 04:00 | 239 | 238
2017-07-12 04:30 | 247 | 247
2017-07-12 05:00 | 240 | 239
2017-07-12 05:30 | 247 | 247
2017-07-12 06:00 | 277 | 275
2017-07-12 06:30 | 305 | 304
2017-07-12 07:00 | 332 | 331
2017-07-12 07:30 | 339 | 339
2017-07-12 08:00 | 333 | 332
2017-07-12 08:30 | 330 | 329
2017-07-12 09:00 | 337 | 336
2017-07-12 09:30 | 324 | 323
2017-07-12 10:00 | 321 | 320
2017-07-12 10:30 | 313 | 311
2017-07-12 11:00 | 303 | 302
2017-07-12 11:30 | 299 | 298
2017-07-12 12:00 | 298 | 297
2017-07-12 12:30 | 296 | 294
2017-07-12 13:00 | 298 | 296
2017-07-12 13:30 | 304 | 302
2017-07-12 14:00 | 306 | 304
2017-07-12 14:30 | 312 | 309
2017-07-12 15:00 | 323 | 320
2017-07-12 15:30 | 333 | 329
2017-07-12 16:00 | 336 | 332
2017-07-12 16:30 | 337 | 334
2017-07-12 17:00 | 357 | 355
2017-07-12 17:30 | 369 | 368
2017-07-12 18:00 | 371 | 370
2017-07-12 18:30 | 371 | 370
2017-07-12 19:00 | 367 | 365
2017-07-12 19:30 | 361 | 359
2017-07-12 20:00 | 357 | 356
2017-07-12 20:30 | 342 | 339
2017-07-12 21:00 | 325 | 325
2017-07-12 21:30 | 311 | 311
2017-07-12 22:00 | 302 | 301
2017-07-12 22:30 | 296 | 295
2017-07-12 23:00 | 278 | 277
2017-07-12 23:30 | 264 | 263
2017-07-13 | 259 | 258
2017-07-13 00:30 | 244 | 242
2017-07-13 01:00 | 249 | 248
2017-07-13 01:30 | 245 | 244
2017-07-13 02:00 | 240 | 238
2017-07-13 02:30 | 234 | 232
2017-07-13 03:00 | 229 | 226
2017-07-13 03:30 | 237 | 235
2017-07-13 04:00 | 236 | 234
2017-07-13 04:30 | 239 | 237
2017-07-13 05:00 | 248 | 244
2017-07-13 05:30 | 253 | 249
2017-07-13 06:00 | 277 | 274
2017-07-13 06:30 | 290 | 290
2017-07-13 07:00 | 313 | 313
2017-07-13 07:30 | 320 | 320
2017-07-13 08:00 | 313 | 313
2017-07-13 08:30 | 303 | 303
2017-07-13 09:00 | 294 | 294
2017-07-13 09:30 | 279 | 278
2017-07-13 10:00 | 270 | 269
2017-07-13 10:30 | 262 | 261
2017-07-13 11:00 | 258 | 257
2017-07-13 11:30 | 255 | 254
2017-07-13 12:00 | 261 | 260
2017-07-13 12:30 | 282 | 281
2017-07-13 13:00 | 295 | 295
2017-07-13 13:30 | 296 | 296
2017-07-13 14:00 | 298 | 298
2017-07-13 14:30 | 284 | 283
2017-07-13 15:00 | 310 | 310
2017-07-13 15:30 | 303 | 302
2017-07-13 16:00 | 320 | 320
2017-07-13 16:30 | 325 | 322
2017-07-13 17:00 | 341 | 338
2017-07-13 17:30 | 358 | 356
2017-07-13 18:00 | 358 | 355
2017-07-13 18:30 | 359 | 357
2017-07-13 19:00 | 356 | 354
2017-07-13 19:30 | 355 | 352
2017-07-13 20:00 | 351 | 348
2017-07-13 20:30 | 341 | 339
2017-07-13 21:00 | 325 | 323
2017-07-13 21:30 | 308 | 306
2017-07-13 22:00 | 295 | 294
2017-07-13 22:30 | 290 | 290
2017-07-13 23:00 | 275 | 274
2017-07-13 23:30 | 257 | 255
2017-07-14 | 234 | 232
2017-07-14 00:30 | 223 | 220
2017-07-14 01:00 | 217 | 213
2017-07-14 01:30 | 220 | 216
2017-07-14 02:00 | 211 | 207
2017-07-14 02:30 | 209 | 205
2017-07-14 03:00 | 208 | 204
2017-07-14 03:30 | 211 | 207
2017-07-14 04:00 | 218 | 214
2017-07-14 04:30 | 220 | 217
2017-07-14 05:00 | 234 | 232
2017-07-14 05:30 | 246 | 244
2017-07-14 06:00 | 266 | 265
2017-07-14 06:30 | 290 | 289
2017-07-14 07:00 | 318 | 316
2017-07-14 07:30 | 320 | 319
2017-07-14 08:00 | 316 | 314
2017-07-14 08:30 | 310 | 308
2017-07-14 09:00 | 304 | 302
2017-07-14 09:30 | 298 | 296
2017-07-14 10:00 | 295 | 294
2017-07-14 10:30 | 300 | 299
2017-07-14 11:00 | 293 | 292
2017-07-14 11:30 | 285 | 283
2017-07-14 12:00 | 280 | 277
2017-07-14 12:30 | 299 | 297
2017-07-14 13:00 | 302 | 300
2017-07-14 13:30 | 291 | 289
2017-07-14 14:00 | 282 | 279
2017-07-14 14:30 | 286 | 283
2017-07-14 15:00 | 291 | 287
2017-07-14 15:30 | 294 | 291
2017-07-14 16:00 | 302 | 299
2017-07-14 16:30 | 314 | 310
2017-07-14 17:00 | 324 | 321
2017-07-14 17:30 | 334 | 331
2017-07-14 18:00 | 331 | 328
2017-07-14 18:30 | 332 | 329
2017-07-14 19:00 | 329 | 326
2017-07-14 19:30 | 324 | 323
2017-07-14 20:00 | 315 | 314
2017-07-14 20:30 | 307 | 306
2017-07-14 21:00 | 299 | 297
2017-07-14 21:30 | 291 | 289
2017-07-14 22:00 | 274 | 273
2017-07-14 22:30 | 268 | 268
2017-07-14 23:00 | 260 | 260
2017-07-14 23:30 | 246 | 245
2017-07-15 | 226 | 225
2017-07-15 00:30 | 217 | 215
2017-07-15 01:00 | 215 | 213
2017-07-15 01:30 | 210 | 208
2017-07-15 02:00 | 206 | 204
2017-07-15 02:30 | 202 | 200
2017-07-15 03:00 | 202 | 199
2017-07-15 03:30 | 203 | 201
2017-07-15 04:00 | 206 | 204
2017-07-15 04:30 | 210 | 208
2017-07-15 05:00 | 214 | 212
2017-07-15 05:30 | 220 | 219
2017-07-15 06:00 | 232 | 231
2017-07-15 06:30 | 242 | 241
2017-07-15 07:00 | 256 | 256
2017-07-15 07:30 | 267 | 267
2017-07-15 08:00 | 272 | 272
2017-07-15 08:30 | 274 | 273
2017-07-15 09:00 | 269 | 269
2017-07-15 09:30 | 266 | 265
2017-07-15 10:00 | 263 | 262
2017-07-15 10:30 | 249 | 248
2017-07-15 11:00 | 242 | 242
2017-07-15 11:30 | 238 | 238
2017-07-15 12:00 | 236 | 236
2017-07-15 12:30 | 236 | 235
2017-07-15 13:00 | 234 | 234
2017-07-15 13:30 | 239 | 239
2017-07-15 14:00 | 248 | 247
2017-07-15 14:30 | 249 | 249
2017-07-15 15:00 | 255 | 255
2017-07-15 15:30 | 262 | 262
2017-07-15 16:00 | 273 | 273
2017-07-15 16:30 | 290 | 290
2017-07-15 17:00 | 307 | 307
2017-07-15 17:30 | 309 | 309
2017-07-15 18:00 | 304 | 304
2017-07-15 18:30 | 302 | 302
2017-07-15 19:00 | 299 | 299
2017-07-15 19:30 | 298 | 298
2017-07-15 20:00 | 298 | 298
2017-07-15 20:30 | 288 | 288
2017-07-15 21:00 | 278 | 278
2017-07-15 21:30 | 271 | 270
2017-07-15 22:00 | 265 | 265
2017-07-15 22:30 | 263 | 263
2017-07-15 23:00 | 251 | 251
2017-07-15 23:30 | 239 | 239
2017-07-16 | 227 | 227
2017-07-16 00:30 | 218 | 218
2017-07-16 01:00 | 209 | 209
2017-07-16 01:30 | 203 | 203
2017-07-16 02:00 | 203 | 203
2017-07-16 02:30 | 197 | 197
2017-07-16 03:00 | 194 | 194
2017-07-16 03:30 | 194 | 194
2017-07-16 04:00 | 205 | 205
2017-07-16 04:30 | 197 | 197
2017-07-16 05:00 | 199 | 199
2017-07-16 05:30 | 203 | 203
2017-07-16 06:00 | 209 | 209
2017-07-16 06:30 | 215 | 215
2017-07-16 07:00 | 230 | 230
2017-07-16 07:30 | 246 | 246
2017-07-16 08:00 | 262 | 261
2017-07-16 08:30 | 273 | 273
2017-07-16 09:00 | 271 | 270
2017-07-16 09:30 | 267 | 267
2017-07-16 10:00 | 260 | 260
2017-07-16 10:30 | 255 | 255
2017-07-16 11:00 | 253 | 253
2017-07-16 11:30 | 255 | 254
2017-07-16 12:00 | 250 | 250
2017-07-16 12:30 | 244 | 244
2017-07-16 13:00 | 239 | 239
2017-07-16 13:30 | 240 | 240
2017-07-16 14:00 | 245 | 245
2017-07-16 14:30 | 245 | 245
2017-07-16 15:00 | 250 | 250
2017-07-16 15:30 | 263 | 263
2017-07-16 16:00 | 277 | 277
2017-07-16 16:30 | 293 | 293
2017-07-16 17:00 | 312 | 312
2017-07-16 17:30 | 323 | 322
2017-07-16 18:00 | 315 | 313
2017-07-16 18:30 | 310 | 310
2017-07-16 19:00 | 307 | 304
2017-07-16 19:30 | 307 | 303
2017-07-16 20:00 | 306 | 301
2017-07-16 20:30 | 298 | 292
2017-07-16 21:00 | 284 | 280
2017-07-16 21:30 | 274 | 270
2017-07-16 22:00 | 266 | 262
2017-07-16 22:30 | 259 | 258
2017-07-16 23:00 | 249 | 247
2017-07-16 23:30 | 234 | 232
2017-07-17 | 218 | 215
2017-07-17 00:30 | 206 | 204
2017-07-17 01:00 | 200 | 197
2017-07-17 01:30 | 197 | 194
2017-07-17 02:00 | 194 | 191
2017-07-17 02:30 | 192 | 190
2017-07-17 03:00 | 192 | 189
2017-07-17 03:30 | 180 | 178
2017-07-17 04:00 | 148 | 147
2017-07-17 04:30 | 160 | 160
2017-07-17 05:00 | 195 | 194
2017-07-17 05:30 | 231 | 231
2017-07-17 06:00 | 252 | 251
2017-07-17 06:30 | 273 | 273
2017-07-17 07:00 | 289 | 289
2017-07-17 07:30 | 295 | 295
2017-07-17 08:00 | 292 | 292
2017-07-17 08:30 | 286 | 286
2017-07-17 09:00 | 281 | 281
2017-07-17 09:30 | 277 | 277
2017-07-17 10:00 | 273 | 273
2017-07-17 10:30 | 267 | 267
2017-07-17 11:00 | 265 | 265
2017-07-17 11:30 | 268 | 268
2017-07-17 12:00 | 274 | 273
2017-07-17 12:30 | 270 | 270
2017-07-17 13:00 | 271 | 271
2017-07-17 13:30 | 272 | 272
2017-07-17 14:00 | 274 | 274
2017-07-17 14:30 | 273 | 273
2017-07-17 15:00 | 279 | 279
2017-07-17 15:30 | 288 | 288
2017-07-17 16:00 | 298 | 298
2017-07-17 16:30 | 314 | 314
2017-07-17 17:00 | 332 | 331
2017-07-17 17:30 | 344 | 344
2017-07-17 18:00 | 343 | 343
2017-07-17 18:30 | 339 | 339
2017-07-17 19:00 | 335 | 335
2017-07-17 19:30 | 331 | 330
2017-07-17 20:00 | 325 | 325
2017-07-17 20:30 | 313 | 312
2017-07-17 21:00 | 296 | 296
2017-07-17 21:30 | 284 | 284
2017-07-17 22:00 | 280 | 279
2017-07-17 22:30 | 271 | 270
2017-07-17 23:00 | 258 | 257
2017-07-17 23:30 | 238 | 237
2017-07-18 | 224 | 223
2017-07-18 00:30 | 232 | 231
2017-07-18 01:00 | 233 | 232
2017-07-18 01:30 | 208 | 207
2017-07-18 02:00 | 196 | 195
2017-07-18 02:30 | 205 | 205
2017-07-18 03:00 | 197 | 197
2017-07-18 03:30 | 198 | 198
2017-07-18 04:00 | 207 | 207
2017-07-18 04:30 | 228 | 228
2017-07-18 05:00 | 230 | 229
2017-07-18 05:30 | 238 | 237
2017-07-18 06:00 | 259 | 258
2017-07-18 06:30 | 279 | 278
2017-07-18 07:00 | 296 | 296
2017-07-18 07:30 | 299 | 299
2017-07-18 08:00 | 293 | 293
2017-07-18 08:30 | 285 | 285
2017-07-18 09:00 | 282 | 282
2017-07-18 09:30 | 271 | 271
2017-07-18 10:00 | 266 | 266
2017-07-18 10:30 | 262 | 262
2017-07-18 11:00 | 258 | 258
2017-07-18 11:30 | 258 | 258
2017-07-18 12:00 | 255 | 255
2017-07-18 12:30 | 254 | 254
2017-07-18 13:00 | 255 | 255
2017-07-18 13:30 | 257 | 257
2017-07-18 14:00 | 261 | 261
2017-07-18 14:30 | 261 | 261
2017-07-18 15:00 | 267 | 267
2017-07-18 15:30 | 276 | 276
2017-07-18 16:00 | 282 | 282
2017-07-18 16:30 | 294 | 294
2017-07-18 17:00 | 307 | 307
2017-07-18 17:30 | 317 | 317
2017-07-18 18:00 | 315 | 314
2017-07-18 18:30 | 313 | 312
2017-07-18 19:00 | 307 | 307
2017-07-18 19:30 | 305 | 305
2017-07-18 20:00 | 301 | 301
2017-07-18 20:30 | 288 | 287
2017-07-18 21:00 | 281 | 281
2017-07-18 21:30 | 270 | 270
2017-07-18 22:00 | 266 | 265
2017-07-18 22:30 | 262 | 262
2017-07-18 23:00 | 255 | 254
2017-07-18 23:30 | 243 | 241
2017-07-19 | 247 | 243
2017-07-19 00:30 | 243 | 237
2017-07-19 01:00 | 237 | 233
2017-07-19 01:30 | 224 | 220
2017-07-19 02:00 | 217 | 215
2017-07-19 02:30 | 202 | 200
2017-07-19 03:00 | 195 | 193
2017-07-19 03:30 | 195 | 193
2017-07-19 04:00 | 196 | 194
2017-07-19 04:30 | 200 | 199
2017-07-19 05:00 | 221 | 219
2017-07-19 05:30 | 237 | 235
2017-07-19 06:00 | 258 | 255
2017-07-19 06:30 | 275 | 274
2017-07-19 07:00 | 289 | 288
2017-07-19 07:30 | 297 | 296
2017-07-19 08:00 | 293 | 293
2017-07-19 08:30 | 284 | 284
2017-07-19 09:00 | 278 | 278
2017-07-19 09:30 | 270 | 269
2017-07-19 10:00 | 282 | 281
2017-07-19 10:30 | 273 | 272
2017-07-19 11:00 | 282 | 281
2017-07-19 11:30 | 271 | 270
2017-07-19 12:00 | 271 | 270
2017-07-19 12:30 | 275 | 274
2017-07-19 13:00 | 276 | 275
2017-07-19 13:30 | 262 | 261
2017-07-19 14:00 | 262 | 261
2017-07-19 14:30 | 266 | 265
2017-07-19 15:00 | 270 | 269
2017-07-19 15:30 | 284 | 283
2017-07-19 16:00 | 296 | 295
2017-07-19 16:30 | 314 | 314
2017-07-19 17:00 | 336 | 335
2017-07-19 17:30 | 355 | 353
2017-07-19 18:00 | 359 | 356
2017-07-19 18:30 | 361 | 359
2017-07-19 19:00 | 358 | 355
2017-07-19 19:30 | 357 | 353
2017-07-19 20:00 | 346 | 342
2017-07-19 20:30 | 326 | 324
2017-07-19 21:00 | 306 | 305
2017-07-19 21:30 | 290 | 289
2017-07-19 22:00 | 280 | 278
2017-07-19 22:30 | 272 | 270
2017-07-19 23:00 | 261 | 258
2017-07-19 23:30 | 247 | 243
2017-07-20 | 237 | 232
2017-07-20 00:30 | 230 | 225
2017-07-20 01:00 | 216 | 211
2017-07-20 01:30 | 211 | 207
2017-07-20 02:00 | 208 | 204
2017-07-20 02:30 | 212 | 208
2017-07-20 03:00 | 224 | 220
2017-07-20 03:30 | 222 | 218
2017-07-20 04:00 | 213 | 209
2017-07-20 04:30 | 218 | 214
2017-07-20 05:00 | 228 | 226
2017-07-20 05:30 | 242 | 240
2017-07-20 06:00 | 269 | 266
2017-07-20 06:30 | 291 | 290
2017-07-20 07:00 | 309 | 308
2017-07-20 07:30 | 314 | 314
2017-07-20 08:00 | 310 | 310
2017-07-20 08:30 | 301 | 301
2017-07-20 09:00 | 292 | 292
2017-07-20 09:30 | 281 | 280
2017-07-20 10:00 | 282 | 281
2017-07-20 10:30 | 281 | 280
2017-07-20 11:00 | 276 | 276
2017-07-20 11:30 | 274 | 274
2017-07-20 12:00 | 274 | 274
2017-07-20 12:30 | 262 | 262
2017-07-20 13:00 | 253 | 253
2017-07-20 13:30 | 255 | 254
2017-07-20 14:00 | 258 | 258
2017-07-20 14:30 | 263 | 263
2017-07-20 15:00 | 271 | 271
2017-07-20 15:30 | 284 | 284
2017-07-20 16:00 | 289 | 288
2017-07-20 16:30 | 305 | 304
2017-07-20 17:00 | 323 | 323
2017-07-20 17:30 | 344 | 344
2017-07-20 18:00 | 348 | 347
2017-07-20 18:30 | 349 | 349
2017-07-20 19:00 | 346 | 345
2017-07-20 19:30 | 348 | 347
2017-07-20 20:00 | 341 | 340
2017-07-20 20:30 | 330 | 328
2017-07-20 21:00 | 309 | 307
2017-07-20 21:30 | 289 | 289
2017-07-20 22:00 | 281 | 280
2017-07-20 22:30 | 275 | 274
2017-07-20 23:00 | 262 | 261
2017-07-20 23:30 | 254 | 252
2017-07-21 | 240 | 237
2017-07-21 00:30 | 248 | 246
2017-07-21 01:00 | 221 | 217
2017-07-21 01:30 | 212 | 207
2017-07-21 02:00 | 210 | 205
2017-07-21 02:30 | 208 | 203
2017-07-21 03:00 | 218 | 214
2017-07-21 03:30 | 227 | 223
2017-07-21 04:00 | 214 | 209
2017-07-21 04:30 | 217 | 213
2017-07-21 05:00 | 225 | 222
2017-07-21 05:30 | 244 | 243
2017-07-21 06:00 | 278 | 277
2017-07-21 06:30 | 309 | 308
2017-07-21 07:00 | 330 | 329
2017-07-21 07:30 | 334 | 333
2017-07-21 08:00 | 334 | 333
2017-07-21 08:30 | 337 | 336
2017-07-21 09:00 | 320 | 319
2017-07-21 09:30 | 304 | 303
2017-07-21 10:00 | 290 | 289
2017-07-21 10:30 | 262 | 261
2017-07-21 11:00 | 252 | 251
2017-07-21 11:30 | 247 | 246
2017-07-21 12:00 | 226 | 223
2017-07-21 12:30 | 225 | 222
2017-07-21 13:00 | 228 | 225
2017-07-21 13:30 | 237 | 234
2017-07-21 14:00 | 242 | 239
2017-07-21 14:30 | 242 | 239
2017-07-21 15:00 | 244 | 241
2017-07-21 15:30 | 253 | 250
2017-07-21 16:00 | 261 | 259
2017-07-21 16:30 | 277 | 274
2017-07-21 17:00 | 300 | 299
2017-07-21 17:30 | 316 | 316
2017-07-21 18:00 | 321 | 320
2017-07-21 18:30 | 322 | 322
2017-07-21 19:00 | 318 | 317
2017-07-21 19:30 | 317 | 317
2017-07-21 20:00 | 314 | 313
2017-07-21 20:30 | 305 | 305
2017-07-21 21:00 | 295 | 295
2017-07-21 21:30 | 285 | 285
2017-07-21 22:00 | 276 | 275
2017-07-21 22:30 | 271 | 271
2017-07-21 23:00 | 255 | 255
2017-07-21 23:30 | 242 | 242
2017-07-22 | 223 | 223
2017-07-22 00:30 | 211 | 211
2017-07-22 01:00 | 201 | 201
2017-07-22 01:30 | 195 | 195
2017-07-22 02:00 | 192 | 192
2017-07-22 02:30 | 192 | 192
2017-07-22 03:00 | 185 | 185
2017-07-22 03:30 | 184 | 184
2017-07-22 04:00 | 171 | 171
2017-07-22 04:30 | 170 | 170
2017-07-22 05:00 | 176 | 176
2017-07-22 05:30 | 204 | 204
2017-07-22 06:00 | 220 | 220
2017-07-22 06:30 | 237 | 237
2017-07-22 07:00 | 257 | 257
2017-07-22 07:30 | 270 | 270
2017-07-22 08:00 | 272 | 272
2017-07-22 08:30 | 269 | 269
2017-07-22 09:00 | 263 | 263
2017-07-22 09:30 | 255 | 255
2017-07-22 10:00 | 247 | 247
2017-07-22 10:30 | 243 | 243
2017-07-22 11:00 | 232 | 232
2017-07-22 11:30 | 222 | 222
2017-07-22 12:00 | 217 | 216
2017-07-22 12:30 | 214 | 213
2017-07-22 13:00 | 215 | 214
2017-07-22 13:30 | 214 | 213
2017-07-22 14:00 | 207 | 206
2017-07-22 14:30 | 216 | 216
2017-07-22 15:00 | 231 | 231
2017-07-22 15:30 | 241 | 240
2017-07-22 16:00 | 246 | 245
2017-07-22 16:30 | 264 | 264
2017-07-22 17:00 | 276 | 276
2017-07-22 17:30 | 292 | 292
2017-07-22 18:00 | 295 | 295
2017-07-22 18:30 | 298 | 298
2017-07-22 19:00 | 294 | 293
2017-07-22 19:30 | 287 | 287
2017-07-22 20:00 | 286 | 286
2017-07-22 20:30 | 278 | 278
2017-07-22 21:00 | 269 | 269
2017-07-22 21:30 | 260 | 260
2017-07-22 22:00 | 259 | 259
2017-07-22 22:30 | 260 | 259
2017-07-22 23:00 | 246 | 245
2017-07-22 23:30 | 234 | 234
2017-07-23 | 219 | 219
2017-07-23 00:30 | 215 | 215
2017-07-23 01:00 | 206 | 206
2017-07-23 01:30 | 201 | 201
2017-07-23 02:00 | 196 | 196
2017-07-23 02:30 | 189 | 189
2017-07-23 03:00 | 187 | 187
2017-07-23 03:30 | 188 | 188
2017-07-23 04:00 | 186 | 186
2017-07-23 04:30 | 188 | 188
2017-07-23 05:00 | 195 | 195
2017-07-23 05:30 | 198 | 198
2017-07-23 06:00 | 211 | 211
2017-07-23 06:30 | 223 | 223
2017-07-23 07:00 | 232 | 232
2017-07-23 07:30 | 240 | 240
2017-07-23 08:00 | 247 | 247
2017-07-23 08:30 | 250 | 249
2017-07-23 09:00 | 247 | 247
2017-07-23 09:30 | 243 | 242
2017-07-23 10:00 | 239 | 238
2017-07-23 10:30 | 228 | 227
2017-07-23 11:00 | 220 | 219
2017-07-23 11:30 | 213 | 213
2017-07-23 12:00 | 210 | 209
2017-07-23 12:30 | 208 | 207
2017-07-23 13:00 | 207 | 207
2017-07-23 13:30 | 208 | 208
2017-07-23 14:00 | 214 | 214
2017-07-23 14:30 | 223 | 222
2017-07-23 15:00 | 226 | 226
2017-07-23 15:30 | 233 | 232
2017-07-23 16:00 | 241 | 240
2017-07-23 16:30 | 250 | 250
2017-07-23 17:00 | 267 | 267
2017-07-23 17:30 | 276 | 276
2017-07-23 18:00 | 279 | 279
2017-07-23 18:30 | 283 | 283
2017-07-23 19:00 | 280 | 280
2017-07-23 19:30 | 278 | 278
2017-07-23 20:00 | 277 | 277
2017-07-23 20:30 | 269 | 269
2017-07-23 21:00 | 260 | 260
2017-07-23 21:30 | 252 | 251
2017-07-23 22:00 | 245 | 244
2017-07-23 22:30 | 241 | 241
2017-07-23 23:00 | 232 | 231
2017-07-23 23:30 | 221 | 220
2017-07-24 | 206 | 205
2017-07-24 00:30 | 195 | 194
2017-07-24 01:00 | 189 | 189
2017-07-24 01:30 | 189 | 189
2017-07-24 02:00 | 187 | 186
2017-07-24 02:30 | 183 | 183
2017-07-24 03:00 | 187 | 187
2017-07-24 03:30 | 188 | 188
2017-07-24 04:00 | 190 | 190
2017-07-24 04:30 | 197 | 197
2017-07-24 05:00 | 208 | 208
2017-07-24 05:30 | 222 | 220
2017-07-24 06:00 | 248 | 246
2017-07-24 06:30 | 273 | 273
2017-07-24 07:00 | 288 | 287
2017-07-24 07:30 | 298 | 298
2017-07-24 08:00 | 296 | 296
2017-07-24 08:30 | 285 | 285
2017-07-24 09:00 | 274 | 274
2017-07-24 09:30 | 261 | 261
2017-07-24 10:00 | 250 | 250
2017-07-24 10:30 | 244 | 244
2017-07-24 11:00 | 239 | 239
2017-07-24 11:30 | 239 | 239
2017-07-24 12:00 | 237 | 237
2017-07-24 12:30 | 238 | 238
2017-07-24 13:00 | 236 | 236
2017-07-24 13:30 | 240 | 240
2017-07-24 14:00 | 241 | 241
2017-07-24 14:30 | 242 | 242
2017-07-24 15:00 | 248 | 248
2017-07-24 15:30 | 253 | 253
2017-07-24 16:00 | 261 | 261
2017-07-24 16:30 | 272 | 272
2017-07-24 17:00 | 286 | 286
2017-07-24 17:30 | 309 | 309
2017-07-24 18:00 | 308 | 308
2017-07-24 18:30 | 312 | 312
2017-07-24 19:00 | 310 | 309
2017-07-24 19:30 | 307 | 307
2017-07-24 20:00 | 301 | 301
2017-07-24 20:30 | 292 | 291
2017-07-24 21:00 | 278 | 275
2017-07-24 21:30 | 265 | 262
2017-07-24 22:00 | 253 | 251
2017-07-24 22:30 | 250 | 247
2017-07-24 23:00 | 240 | 236
2017-07-24 23:30 | 225 | 224
2017-07-25 | 212 | 211
2017-07-25 00:30 | 206 | 205
2017-07-25 01:00 | 194 | 192
2017-07-25 01:30 | 184 | 183
2017-07-25 02:00 | 178 | 176
2017-07-25 02:30 | 175 | 175
2017-07-25 03:00 | 172 | 171
2017-07-25 03:30 | 162 | 162
2017-07-25 04:00 | 165 | 164
2017-07-25 04:30 | 159 | 159
2017-07-25 05:00 | 198 | 198
2017-07-25 05:30 | 219 | 219
2017-07-25 06:00 | 249 | 249
2017-07-25 06:30 | 276 | 276
2017-07-25 07:00 | 295 | 295
2017-07-25 07:30 | 301 | 301
2017-07-25 08:00 | 293 | 293
2017-07-25 08:30 | 281 | 281
2017-07-25 09:00 | 270 | 269
2017-07-25 09:30 | 259 | 258
2017-07-25 10:00 | 247 | 247
2017-07-25 10:30 | 237 | 237
2017-07-25 11:00 | 228 | 228
2017-07-25 11:30 | 225 | 225
2017-07-25 12:00 | 224 | 224
2017-07-25 12:30 | 238 | 238
2017-07-25 13:00 | 246 | 246
2017-07-25 13:30 | 249 | 249
2017-07-25 14:00 | 253 | 253
2017-07-25 14:30 | 253 | 253
2017-07-25 15:00 | 258 | 258
2017-07-25 15:30 | 265 | 265
2017-07-25 16:00 | 278 | 278
2017-07-25 16:30 | 306 | 303
2017-07-25 17:00 | 330 | 328
2017-07-25 17:30 | 352 | 349
2017-07-25 18:00 | 360 | 356
2017-07-25 18:30 | 360 | 356
2017-07-25 19:00 | 360 | 355
2017-07-25 19:30 | 363 | 358
2017-07-25 20:00 | 357 | 351
2017-07-25 20:30 | 340 | 335
2017-07-25 21:00 | 319 | 315
2017-07-25 21:30 | 299 | 296
2017-07-25 22:00 | 287 | 283
2017-07-25 22:30 | 275 | 274
2017-07-25 23:00 | 265 | 264
2017-07-25 23:30 | 254 | 252
2017-07-26 | 244 | 242
2017-07-26 00:30 | 234 | 232
2017-07-26 01:00 | 223 | 219
2017-07-26 01:30 | 216 | 212
2017-07-26 02:00 | 212 | 209
2017-07-26 02:30 | 210 | 207
2017-07-26 03:00 | 204 | 201
2017-07-26 03:30 | 206 | 203
2017-07-26 04:00 | 208 | 205
2017-07-26 04:30 | 215 | 213
2017-07-26 05:00 | 230 | 228
2017-07-26 05:30 | 257 | 256
2017-07-26 06:00 | 291 | 287
2017-07-26 06:30 | 319 | 316
2017-07-26 07:00 | 332 | 330
2017-07-26 07:30 | 336 | 335
2017-07-26 08:00 | 328 | 326
2017-07-26 08:30 | 316 | 314
2017-07-26 09:00 | 301 | 299
2017-07-26 09:30 | 283 | 283
2017-07-26 10:00 | 274 | 274
2017-07-26 10:30 | 265 | 265
2017-07-26 11:00 | 262 | 262
2017-07-26 11:30 | 256 | 256
2017-07-26 12:00 | 254 | 254
2017-07-26 12:30 | 253 | 253
2017-07-26 13:00 | 253 | 253
2017-07-26 13:30 | 257 | 257
2017-07-26 14:00 | 262 | 262
2017-07-26 14:30 | 265 | 265
2017-07-26 15:00 | 268 | 268
2017-07-26 15:30 | 275 | 274
2017-07-26 16:00 | 285 | 285
2017-07-26 16:30 | 309 | 307
2017-07-26 17:00 | 342 | 341
2017-07-26 17:30 | 368 | 366
2017-07-26 18:00 | 357 | 356
2017-07-26 18:30 | 362 | 361
2017-07-26 19:00 | 369 | 368
2017-07-26 19:30 | 362 | 361
2017-07-26 20:00 | 365 | 364
2017-07-26 20:30 | 328 | 328
2017-07-26 21:00 | 306 | 306
2017-07-26 21:30 | 292 | 292
2017-07-26 22:00 | 283 | 283
2017-07-26 22:30 | 277 | 277
2017-07-26 23:00 | 260 | 260
2017-07-26 23:30 | 242 | 242
2017-07-27 | 224 | 224
2017-07-27 00:30 | 212 | 212
2017-07-27 01:00 | 204 | 204
2017-07-27 01:30 | 196 | 196
2017-07-27 02:00 | 190 | 190
2017-07-27 02:30 | 187 | 187
2017-07-27 03:00 | 185 | 185
2017-07-27 03:30 | 187 | 187
2017-07-27 04:00 | 192 | 192
2017-07-27 04:30 | 201 | 201
2017-07-27 05:00 | 219 | 219
2017-07-27 05:30 | 245 | 245
2017-07-27 06:00 | 280 | 279
2017-07-27 06:30 | 313 | 310
2017-07-27 07:00 | 339 | 337
2017-07-27 07:30 | 335 | 333
2017-07-27 08:00 | 316 | 314
2017-07-27 08:30 | 296 | 294
2017-07-27 09:00 | 282 | 279
2017-07-27 09:30 | 262 | 262
2017-07-27 10:00 | 252 | 252
2017-07-27 10:30 | 243 | 243
2017-07-27 11:00 | 237 | 237
2017-07-27 11:30 | 233 | 233
2017-07-27 12:00 | 231 | 231
2017-07-27 12:30 | 231 | 231
2017-07-27 13:00 | 232 | 232
2017-07-27 13:30 | 237 | 237
2017-07-27 14:00 | 243 | 243
2017-07-27 14:30 | 250 | 250
2017-07-27 15:00 | 259 | 259
2017-07-27 15:30 | 274 | 274
2017-07-27 16:00 | 292 | 290
2017-07-27 16:30 | 310 | 307
2017-07-27 17:00 | 327 | 326
2017-07-27 17:30 | 345 | 345
2017-07-27 18:00 | 352 | 352
2017-07-27 18:30 | 352 | 352
2017-07-27 19:00 | 350 | 350
2017-07-27 19:30 | 353 | 352
2017-07-27 20:00 | 349 | 347
2017-07-27 20:30 | 337 | 334
2017-07-27 21:00 | 322 | 318
2017-07-27 21:30 | 298 | 296
2017-07-27 22:00 | 286 | 286
2017-07-27 22:30 | 277 | 277
2017-07-27 23:00 | 267 | 267
2017-07-27 23:30 | 247 | 246
2017-07-28 | 229 | 228
2017-07-28 00:30 | 218 | 217
2017-07-28 01:00 | 209 | 208
2017-07-28 01:30 | 200 | 199
2017-07-28 02:00 | 194 | 193
2017-07-28 02:30 | 191 | 190
2017-07-28 03:00 | 190 | 189
2017-07-28 03:30 | 190 | 188
2017-07-28 04:00 | 196 | 195
2017-07-28 04:30 | 210 | 209
2017-07-28 05:00 | 226 | 225
2017-07-28 05:30 | 242 | 242
2017-07-28 06:00 | 274 | 274
2017-07-28 06:30 | 308 | 305
2017-07-28 07:00 | 329 | 325
2017-07-28 07:30 | 329 | 325
2017-07-28 08:00 | 316 | 312
2017-07-28 08:30 | 299 | 294
2017-07-28 09:00 | 292 | 288
2017-07-28 09:30 | 286 | 281
2017-07-28 10:00 | 278 | 277
2017-07-28 10:30 | 261 | 261
2017-07-28 11:00 | 259 | 258
2017-07-28 11:30 | 254 | 253
2017-07-28 12:00 | 238 | 237
2017-07-28 12:30 | 229 | 228
2017-07-28 13:00 | 216 | 215
2017-07-28 13:30 | 220 | 219
2017-07-28 14:00 | 225 | 224
2017-07-28 14:30 | 230 | 229
2017-07-28 15:00 | 239 | 238
2017-07-28 15:30 | 249 | 248
2017-07-28 16:00 | 256 | 255
2017-07-28 16:30 | 267 | 266
2017-07-28 17:00 | 277 | 276
2017-07-28 17:30 | 296 | 292
2017-07-28 18:00 | 300 | 294
2017-07-28 18:30 | 301 | 295
2017-07-28 19:00 | 297 | 290
2017-07-28 19:30 | 297 | 290
2017-07-28 20:00 | 288 | 286
2017-07-28 20:30 | 278 | 275
2017-07-28 21:00 | 268 | 264
2017-07-28 21:30 | 261 | 256
2017-07-28 22:00 | 247 | 245
2017-07-28 22:30 | 243 | 241
2017-07-28 23:00 | 233 | 231
2017-07-28 23:30 | 223 | 220
2017-07-29 | 205 | 201
2017-07-29 00:30 | 200 | 195
2017-07-29 01:00 | 193 | 187
2017-07-29 01:30 | 185 | 179
2017-07-29 02:00 | 179 | 173
2017-07-29 02:30 | 175 | 168
2017-07-29 03:00 | 174 | 167
2017-07-29 03:30 | 174 | 166
2017-07-29 04:00 | 175 | 168
2017-07-29 04:30 | 177 | 170
2017-07-29 05:00 | 184 | 178
2017-07-29 05:30 | 193 | 188
2017-07-29 06:00 | 207 | 203
2017-07-29 06:30 | 223 | 220
2017-07-29 07:00 | 242 | 240
2017-07-29 07:30 | 250 | 249
2017-07-29 08:00 | 252 | 251
2017-07-29 08:30 | 247 | 247
2017-07-29 09:00 | 239 | 238
2017-07-29 09:30 | 229 | 228
2017-07-29 10:00 | 218 | 217
2017-07-29 10:30 | 209 | 208
2017-07-29 11:00 | 201 | 200
2017-07-29 11:30 | 195 | 194
2017-07-29 12:00 | 192 | 190
2017-07-29 12:30 | 188 | 187
2017-07-29 13:00 | 189 | 188
2017-07-29 13:30 | 192 | 191
2017-07-29 14:00 | 198 | 197
2017-07-29 14:30 | 204 | 203
2017-07-29 15:00 | 214 | 213
2017-07-29 15:30 | 225 | 225
2017-07-29 16:00 | 240 | 240
2017-07-29 16:30 | 259 | 258
2017-07-29 17:00 | 277 | 275
2017-07-29 17:30 | 291 | 289
2017-07-29 18:00 | 289 | 288
2017-07-29 18:30 | 287 | 285
2017-07-29 19:00 | 287 | 284
2017-07-29 19:30 | 285 | 283
2017-07-29 20:00 | 283 | 281
2017-07-29 20:30 | 275 | 272
2017-07-29 21:00 | 259 | 257
2017-07-29 21:30 | 253 | 252
2017-07-29 22:00 | 250 | 250
2017-07-29 22:30 | 251 | 251
2017-07-29 23:00 | 243 | 243
2017-07-29 23:30 | 225 | 224
2017-07-30 | 208 | 206
2017-07-30 00:30 | 197 | 195
2017-07-30 01:00 | 187 | 186
2017-07-30 01:30 | 179 | 178
2017-07-30 02:00 | 173 | 172
2017-07-30 02:30 | 171 | 169
2017-07-30 03:00 | 170 | 168
2017-07-30 03:30 | 169 | 167
2017-07-30 04:00 | 170 | 168
2017-07-30 04:30 | 172 | 171
2017-07-30 05:00 | 177 | 176
2017-07-30 05:30 | 184 | 183
2017-07-30 06:00 | 194 | 193
2017-07-30 06:30 | 206 | 206
2017-07-30 07:00 | 222 | 222
2017-07-30 07:30 | 232 | 231
2017-07-30 08:00 | 238 | 238
2017-07-30 08:30 | 237 | 237
2017-07-30 09:00 | 231 | 231
2017-07-30 09:30 | 222 | 222
2017-07-30 10:00 | 211 | 211
2017-07-30 10:30 | 202 | 202
2017-07-30 11:00 | 194 | 194
2017-07-30 11:30 | 188 | 188
2017-07-30 12:00 | 185 | 185
2017-07-30 12:30 | 183 | 183
2017-07-30 13:00 | 184 | 184
2017-07-30 13:30 | 188 | 188
2017-07-30 14:00 | 194 | 194
2017-07-30 14:30 | 202 | 202
2017-07-30 15:00 | 212 | 212
2017-07-30 15:30 | 223 | 223
2017-07-30 16:00 | 237 | 237
2017-07-30 16:30 | 255 | 254
2017-07-30 17:00 | 265 | 263
2017-07-30 17:30 | 275 | 274
2017-07-30 18:00 | 275 | 274
2017-07-30 18:30 | 276 | 275
2017-07-30 19:00 | 274 | 273
2017-07-30 19:30 | 272 | 270
2017-07-30 20:00 | 268 | 267
2017-07-30 20:30 | 263 | 263
2017-07-30 21:00 | 253 | 253
2017-07-30 21:30 | 242 | 242
2017-07-30 22:00 | 239 | 237
2017-07-30 22:30 | 238 | 237
2017-07-30 23:00 | 228 | 227
2017-07-30 23:30 | 213 | 211
2017-07-31 | 199 | 196
2017-07-31 00:30 | 187 | 185
2017-07-31 01:00 | 178 | 176
2017-07-31 01:30 | 171 | 169
2017-07-31 02:00 | 167 | 165
2017-07-31 02:30 | 164 | 162
2017-07-31 03:00 | 164 | 162
2017-07-31 03:30 | 165 | 164
2017-07-31 04:00 | 171 | 169
2017-07-31 04:30 | 179 | 177
2017-07-31 05:00 | 193 | 192
2017-07-31 05:30 | 212 | 212
2017-07-31 06:00 | 234 | 234
2017-07-31 06:30 | 260 | 260
2017-07-31 07:00 | 276 | 276
2017-07-31 07:30 | 310 | 309
2017-07-31 08:00 | 305 | 305
2017-07-31 08:30 | 294 | 294
2017-07-31 09:00 | 283 | 283
2017-07-31 09:30 | 270 | 269
2017-07-31 10:00 | 259 | 258
2017-07-31 10:30 | 251 | 250
2017-07-31 11:00 | 245 | 245
2017-07-31 11:30 | 243 | 243
2017-07-31 12:00 | 241 | 241
2017-07-31 12:30 | 242 | 241
2017-07-31 13:00 | 244 | 243
2017-07-31 13:30 | 250 | 249
2017-07-31 14:00 | 257 | 256
2017-07-31 14:30 | 263 | 263
2017-07-31 15:00 | 272 | 272
2017-07-31 15:30 | 285 | 284
2017-07-31 16:00 | 299 | 298
2017-07-31 16:30 | 316 | 315
2017-07-31 17:00 | 336 | 336
2017-07-31 17:30 | 356 | 356
2017-07-31 18:00 | 358 | 358
2017-07-31 18:30 | 355 | 354
2017-07-31 19:00 | 346 | 346
2017-07-31 19:30 | 339 | 338
2017-07-31 20:00 | 331 | 330
2017-07-31 20:30 | 317 | 315
2017-07-31 21:00 | 302 | 299
2017-07-31 21:30 | 287 | 283
2017-07-31 22:00 | 279 | 276
2017-07-31 22:30 | 274 | 271
2017-07-31 23:00 | 256 | 255
2017-07-31 23:30 | 237 | 237
2017-08-01 | 221 | 220
2017-08-01 00:30 | 210 | 209
2017-08-01 01:00 | 202 | 201
2017-08-01 01:30 | 194 | 192
2017-08-01 02:00 | 189 | 187
2017-08-01 02:30 | 185 | 184
2017-08-01 03:00 | 184 | 182
2017-08-01 03:30 | 185 | 183
2017-08-01 04:00 | 191 | 190
2017-08-01 04:30 | 199 | 198
2017-08-01 05:00 | 216 | 215
2017-08-01 05:30 | 239 | 239
2017-08-01 06:00 | 275 | 273
2017-08-01 06:30 | 283 | 280
2017-08-01 07:00 | 300 | 299
2017-08-01 07:30 | 296 | 296
2017-08-01 08:00 | 279 | 278
2017-08-01 08:30 | 261 | 260
2017-08-01 09:00 | 249 | 248
2017-08-01 09:30 | 235 | 234
2017-08-01 10:00 | 228 | 226
2017-08-01 10:30 | 219 | 218
2017-08-01 11:00 | 213 | 212
2017-08-01 11:30 | 210 | 208
2017-08-01 12:00 | 205 | 205
2017-08-01 12:30 | 202 | 202
2017-08-01 13:00 | 204 | 204
2017-08-01 13:30 | 209 | 209
2017-08-01 14:00 | 216 | 216
2017-08-01 14:30 | 222 | 222
2017-08-01 15:00 | 231 | 231
2017-08-01 15:30 | 245 | 245
2017-08-01 16:00 | 262 | 262
2017-08-01 16:30 | 288 | 287
2017-08-01 17:00 | 312 | 311
2017-08-01 17:30 | 338 | 338
2017-08-01 18:00 | 351 | 348
2017-08-01 18:30 | 349 | 346
2017-08-01 19:00 | 341 | 337
2017-08-01 19:30 | 336 | 331
2017-08-01 20:00 | 329 | 324
2017-08-01 20:30 | 306 | 304
2017-08-01 21:00 | 290 | 289
2017-08-01 21:30 | 274 | 271
2017-08-01 22:00 | 267 | 262
2017-08-01 22:30 | 262 | 256
2017-08-01 23:00 | 248 | 240
2017-08-01 23:30 | 228 | 220
2017-08-02 | 203 | 200
2017-08-02 00:30 | 193 | 189
2017-08-02 01:00 | 184 | 180
2017-08-02 01:30 | 176 | 171
2017-08-02 02:00 | 170 | 165
2017-08-02 02:30 | 167 | 161
2017-08-02 03:00 | 166 | 160
2017-08-02 03:30 | 167 | 161
2017-08-02 04:00 | 172 | 167
2017-08-02 04:30 | 181 | 176
2017-08-02 05:00 | 198 | 195
2017-08-02 05:30 | 223 | 220
2017-08-02 06:00 | 261 | 257
2017-08-02 06:30 | 294 | 288
2017-08-02 07:00 | 319 | 315
2017-08-02 07:30 | 316 | 312
2017-08-02 08:00 | 297 | 291
2017-08-02 08:30 | 278 | 271
2017-08-02 09:00 | 263 | 256
2017-08-02 09:30 | 242 | 240
2017-08-02 10:00 | 232 | 230
2017-08-02 10:30 | 222 | 220
2017-08-02 11:00 | 217 | 215
2017-08-02 11:30 | 212 | 210
2017-08-02 12:00 | 212 | 210
2017-08-02 12:30 | 223 | 221
2017-08-02 13:00 | 227 | 225
2017-08-02 13:30 | 230 | 228
2017-08-02 14:00 | 236 | 234
2017-08-02 14:30 | 242 | 240
2017-08-02 15:00 | 252 | 249
2017-08-02 15:30 | 264 | 261
2017-08-02 16:00 | 280 | 278
2017-08-02 16:30 | 304 | 301
2017-08-02 17:00 | 324 | 322
2017-08-02 17:30 | 351 | 350
2017-08-02 18:00 | 358 | 357
2017-08-02 18:30 | 358 | 357
2017-08-02 19:00 | 350 | 349
2017-08-02 19:30 | 345 | 343
2017-08-02 20:00 | 339 | 337
2017-08-02 20:30 | 325 | 322
2017-08-02 21:00 | 308 | 305
2017-08-02 21:30 | 290 | 285
2017-08-02 22:00 | 278 | 276
2017-08-02 22:30 | 267 | 267
2017-08-02 23:00 | 249 | 248
2017-08-02 23:30 | 225 | 223
2017-08-03 | 204 | 202
2017-08-03 00:30 | 192 | 189
2017-08-03 01:00 | 181 | 178
2017-08-03 01:30 | 169 | 168
2017-08-03 02:00 | 164 | 162
2017-08-03 02:30 | 161 | 159
2017-08-03 03:00 | 161 | 159
2017-08-03 03:30 | 163 | 162
2017-08-03 04:00 | 169 | 167
2017-08-03 04:30 | 177 | 176
2017-08-03 05:00 | 194 | 194
2017-08-03 05:30 | 217 | 217
2017-08-03 06:00 | 251 | 251
2017-08-03 06:30 | 282 | 282
2017-08-03 07:00 | 306 | 306
2017-08-03 07:30 | 302 | 302
2017-08-03 08:00 | 287 | 287
2017-08-03 08:30 | 272 | 272
2017-08-03 09:00 | 257 | 257
2017-08-03 09:30 | 247 | 247
2017-08-03 10:00 | 239 | 239
2017-08-03 10:30 | 226 | 226
2017-08-03 11:00 | 224 | 224
2017-08-03 11:30 | 220 | 220
2017-08-03 12:00 | 233 | 233
2017-08-03 12:30 | 230 | 230
2017-08-03 13:00 | 228 | 228
2017-08-03 13:30 | 225 | 224
2017-08-03 14:00 | 232 | 232
2017-08-03 14:30 | 234 | 234
2017-08-03 15:00 | 240 | 240
2017-08-03 15:30 | 250 | 250
2017-08-03 16:00 | 263 | 263
2017-08-03 16:30 | 282 | 282
2017-08-03 17:00 | 328 | 328
2017-08-03 17:30 | 355 | 355
2017-08-03 18:00 | 369 | 367
2017-08-03 18:30 | 364 | 361
2017-08-03 19:00 | 359 | 355
2017-08-03 19:30 | 359 | 354
2017-08-03 20:00 | 354 | 349
2017-08-03 20:30 | 339 | 335
2017-08-03 21:00 | 316 | 314
2017-08-03 21:30 | 297 | 296
2017-08-03 22:00 | 289 | 289
2017-08-03 22:30 | 283 | 283
2017-08-03 23:00 | 268 | 267
2017-08-03 23:30 | 248 | 247
2017-08-04 | 229 | 228
2017-08-04 00:30 | 217 | 215
2017-08-04 01:00 | 209 | 207
2017-08-04 01:30 | 201 | 198
2017-08-04 02:00 | 192 | 190
2017-08-04 02:30 | 188 | 186
2017-08-04 03:00 | 188 | 187
2017-08-04 03:30 | 189 | 187
2017-08-04 04:00 | 192 | 191
2017-08-04 04:30 | 200 | 199
2017-08-04 05:00 | 215 | 215
2017-08-04 05:30 | 234 | 234
2017-08-04 06:00 | 262 | 262
2017-08-04 06:30 | 291 | 291
2017-08-04 07:00 | 316 | 314
2017-08-04 07:30 | 314 | 313
2017-08-04 08:00 | 302 | 300
2017-08-04 08:30 | 285 | 284
2017-08-04 09:00 | 272 | 271
2017-08-04 09:30 | 260 | 260
2017-08-04 10:00 | 252 | 252
2017-08-04 10:30 | 244 | 243
2017-08-04 11:00 | 236 | 236
2017-08-04 11:30 | 232 | 232
2017-08-04 12:00 | 229 | 229
2017-08-04 12:30 | 229 | 229
2017-08-04 13:00 | 231 | 231
2017-08-04 13:30 | 235 | 235
2017-08-04 14:00 | 243 | 243
2017-08-04 14:30 | 252 | 252
2017-08-04 15:00 | 284 | 284
2017-08-04 15:30 | 308 | 308
2017-08-04 16:00 | 320 | 318
2017-08-04 16:30 | 332 | 331
2017-08-04 17:00 | 340 | 339
2017-08-04 17:30 | 350 | 349
2017-08-04 18:00 | 345 | 344
2017-08-04 18:30 | 347 | 347
2017-08-04 19:00 | 344 | 343
2017-08-04 19:30 | 343 | 343
2017-08-04 20:00 | 337 | 336
2017-08-04 20:30 | 328 | 328
2017-08-04 21:00 | 308 | 307
2017-08-04 21:30 | 295 | 295
2017-08-04 22:00 | 290 | 290
2017-08-04 22:30 | 287 | 287
2017-08-04 23:00 | 272 | 271
2017-08-04 23:30 | 251 | 251
2017-08-05 | 234 | 234
2017-08-05 00:30 | 222 | 221
2017-08-05 01:00 | 213 | 211
2017-08-05 01:30 | 204 | 202
2017-08-05 02:00 | 198 | 196
2017-08-05 02:30 | 194 | 192
2017-08-05 03:00 | 193 | 191
2017-08-05 03:30 | 192 | 190
2017-08-05 04:00 | 193 | 191
2017-08-05 04:30 | 198 | 196
2017-08-05 05:00 | 206 | 205
2017-08-05 05:30 | 216 | 215
2017-08-05 06:00 | 230 | 230
2017-08-05 06:30 | 249 | 248
2017-08-05 07:00 | 268 | 268
2017-08-05 07:30 | 279 | 279
2017-08-05 08:00 | 281 | 280
2017-08-05 08:30 | 275 | 275
2017-08-05 09:00 | 266 | 266
2017-08-05 09:30 | 253 | 253
2017-08-05 10:00 | 241 | 241
2017-08-05 10:30 | 230 | 229
2017-08-05 11:00 | 220 | 220
2017-08-05 11:30 | 213 | 213
2017-08-05 12:00 | 207 | 207
2017-08-05 12:30 | 205 | 205
2017-08-05 13:00 | 206 | 206
2017-08-05 13:30 | 211 | 210
2017-08-05 14:00 | 206 | 205
2017-08-05 14:30 | 197 | 196
2017-08-05 15:00 | 210 | 209
2017-08-05 15:30 | 220 | 220
2017-08-05 16:00 | 234 | 234
2017-08-05 16:30 | 251 | 251
2017-08-05 17:00 | 268 | 266
2017-08-05 17:30 | 288 | 285
2017-08-05 18:00 | 293 | 289
2017-08-05 18:30 | 294 | 290
2017-08-05 19:00 | 286 | 282
2017-08-05 19:30 | 285 | 282
2017-08-05 20:00 | 283 | 280
2017-08-05 20:30 | 275 | 273
2017-08-05 21:00 | 265 | 265
2017-08-05 21:30 | 256 | 255
2017-08-05 22:00 | 251 | 250
2017-08-05 22:30 | 252 | 251
2017-08-05 23:00 | 241 | 240
2017-08-05 23:30 | 224 | 222
2017-08-06 | 208 | 205
2017-08-06 00:30 | 195 | 194
2017-08-06 01:00 | 187 | 186
2017-08-06 01:30 | 179 | 178
2017-08-06 02:00 | 174 | 173
2017-08-06 02:30 | 169 | 168
2017-08-06 03:00 | 166 | 164
2017-08-06 03:30 | 166 | 164
2017-08-06 04:00 | 166 | 164
2017-08-06 04:30 | 169 | 167
2017-08-06 05:00 | 177 | 176
2017-08-06 05:30 | 183 | 182
2017-08-06 06:00 | 194 | 194
2017-08-06 06:30 | 206 | 205
2017-08-06 07:00 | 225 | 225
2017-08-06 07:30 | 239 | 239
2017-08-06 08:00 | 243 | 243
2017-08-06 08:30 | 243 | 243
2017-08-06 09:00 | 233 | 233
2017-08-06 09:30 | 224 | 224
2017-08-06 10:00 | 215 | 215
2017-08-06 10:30 | 205 | 205
2017-08-06 11:00 | 198 | 198
2017-08-06 11:30 | 194 | 194
2017-08-06 12:00 | 190 | 190
2017-08-06 12:30 | 186 | 186
2017-08-06 13:00 | 186 | 186
2017-08-06 13:30 | 189 | 189
2017-08-06 14:00 | 195 | 195
2017-08-06 14:30 | 202 | 201
2017-08-06 15:00 | 213 | 213
2017-08-06 15:30 | 226 | 226
2017-08-06 16:00 | 237 | 237
2017-08-06 16:30 | 254 | 254
2017-08-06 17:00 | 275 | 273
2017-08-06 17:30 | 288 | 287
2017-08-06 18:00 | 290 | 290
2017-08-06 18:30 | 290 | 289
2017-08-06 19:00 | 284 | 283
2017-08-06 19:30 | 281 | 280
2017-08-06 20:00 | 277 | 276
2017-08-06 20:30 | 266 | 265
2017-08-06 21:00 | 255 | 253
2017-08-06 21:30 | 243 | 241
2017-08-06 22:00 | 234 | 233
2017-08-06 22:30 | 233 | 233
2017-08-06 23:00 | 224 | 223
2017-08-06 23:30 | 208 | 207
2017-08-07 | 193 | 192
2017-08-07 00:30 | 183 | 182
2017-08-07 01:00 | 175 | 174
2017-08-07 01:30 | 168 | 167
2017-08-07 02:00 | 163 | 162
2017-08-07 02:30 | 161 | 160
2017-08-07 03:00 | 161 | 159
2017-08-07 03:30 | 163 | 161
2017-08-07 04:00 | 167 | 165
2017-08-07 04:30 | 173 | 172
2017-08-07 05:00 | 186 | 185
2017-08-07 05:30 | 202 | 202
2017-08-07 06:00 | 228 | 227
2017-08-07 06:30 | 253 | 252
2017-08-07 07:00 | 270 | 270
2017-08-07 07:30 | 275 | 274
2017-08-07 08:00 | 269 | 268
2017-08-07 08:30 | 255 | 254
2017-08-07 09:00 | 246 | 245
2017-08-07 09:30 | 245 | 245
2017-08-07 10:00 | 240 | 239
2017-08-07 10:30 | 235 | 234
2017-08-07 11:00 | 232 | 232
2017-08-07 11:30 | 225 | 225
2017-08-07 12:00 | 222 | 222
2017-08-07 12:30 | 221 | 220
2017-08-07 13:00 | 219 | 219
2017-08-07 13:30 | 223 | 222
2017-08-07 14:00 | 228 | 227
2017-08-07 14:30 | 232 | 232
2017-08-07 15:00 | 240 | 239
2017-08-07 15:30 | 251 | 250
2017-08-07 16:00 | 263 | 262
2017-08-07 16:30 | 278 | 278
2017-08-07 17:00 | 291 | 291
2017-08-07 17:30 | 312 | 311
2017-08-07 18:00 | 318 | 316
2017-08-07 18:30 | 314 | 312
2017-08-07 19:00 | 304 | 303
2017-08-07 19:30 | 296 | 296
2017-08-07 20:00 | 290 | 290
2017-08-07 20:30 | 278 | 278
2017-08-07 21:00 | 264 | 264
2017-08-07 21:30 | 250 | 250
2017-08-07 22:00 | 246 | 246
2017-08-07 22:30 | 244 | 244
2017-08-07 23:00 | 230 | 230
2017-08-07 23:30 | 212 | 211
2017-08-08 | 197 | 197
2017-08-08 00:30 | 188 | 187
2017-08-08 01:00 | 179 | 179
2017-08-08 01:30 | 172 | 172
2017-08-08 02:00 | 167 | 167
2017-08-08 02:30 | 164 | 163
2017-08-08 03:00 | 163 | 163
2017-08-08 03:30 | 165 | 164
2017-08-08 04:00 | 169 | 169
2017-08-08 04:30 | 176 | 176
2017-08-08 05:00 | 191 | 191
2017-08-08 05:30 | 211 | 211
2017-08-08 06:00 | 240 | 240
2017-08-08 06:30 | 268 | 267
2017-08-08 07:00 | 286 | 286
2017-08-08 07:30 | 282 | 282
2017-08-08 08:00 | 268 | 268
2017-08-08 08:30 | 253 | 253
2017-08-08 09:00 | 241 | 241
2017-08-08 09:30 | 232 | 232
2017-08-08 10:00 | 223 | 223
2017-08-08 10:30 | 215 | 215
2017-08-08 11:00 | 210 | 210
2017-08-08 11:30 | 206 | 206
2017-08-08 12:00 | 205 | 205
2017-08-08 12:30 | 205 | 205
2017-08-08 13:00 | 206 | 206
2017-08-08 13:30 | 212 | 212
2017-08-08 14:00 | 218 | 218
2017-08-08 14:30 | 223 | 223
2017-08-08 15:00 | 232 | 232
2017-08-08 15:30 | 243 | 243
2017-08-08 16:00 | 258 | 258
2017-08-08 16:30 | 274 | 274
2017-08-08 17:00 | 292 | 292
2017-08-08 17:30 | 309 | 309
2017-08-08 18:00 | 315 | 315
2017-08-08 18:30 | 313 | 313
2017-08-08 19:00 | 310 | 310
2017-08-08 19:30 | 312 | 312
2017-08-08 20:00 | 308 | 308
2017-08-08 20:30 | 295 | 295
2017-08-08 21:00 | 282 | 281
2017-08-08 21:30 | 266 | 266
2017-08-08 22:00 | 260 | 259
2017-08-08 22:30 | 253 | 252
2017-08-08 23:00 | 239 | 239
2017-08-08 23:30 | 221 | 221
2017-08-09 | 205 | 205
2017-08-09 00:30 | 195 | 194
2017-08-09 01:00 | 188 | 187
2017-08-09 01:30 | 180 | 179
2017-08-09 02:00 | 176 | 174
2017-08-09 02:30 | 172 | 171
2017-08-09 03:00 | 172 | 171
2017-08-09 03:30 | 173 | 172
2017-08-09 04:00 | 179 | 177
2017-08-09 04:30 | 187 | 186
2017-08-09 05:00 | 204 | 204
2017-08-09 05:30 | 227 | 227
2017-08-09 06:00 | 261 | 260
2017-08-09 06:30 | 283 | 282
2017-08-09 07:00 | 302 | 302
2017-08-09 07:30 | 306 | 306
2017-08-09 08:00 | 289 | 289
2017-08-09 08:30 | 269 | 269
2017-08-09 09:00 | 254 | 254
2017-08-09 09:30 | 241 | 240
2017-08-09 10:00 | 231 | 230
2017-08-09 10:30 | 221 | 221
2017-08-09 11:00 | 215 | 214
2017-08-09 11:30 | 211 | 210
2017-08-09 12:00 | 206 | 206
2017-08-09 12:30 | 205 | 205
2017-08-09 13:00 | 207 | 206
2017-08-09 13:30 | 211 | 210
2017-08-09 14:00 | 216 | 216
2017-08-09 14:30 | 222 | 221
2017-08-09 15:00 | 239 | 238
2017-08-09 15:30 | 248 | 247
2017-08-09 16:00 | 256 | 256
2017-08-09 16:30 | 272 | 271
2017-08-09 17:00 | 285 | 285
2017-08-09 17:30 | 304 | 303
2017-08-09 18:00 | 308 | 306
2017-08-09 18:30 | 310 | 309
2017-08-09 19:00 | 310 | 308
2017-08-09 19:30 | 311 | 309
2017-08-09 20:00 | 309 | 306
2017-08-09 20:30 | 303 | 300
2017-08-09 21:00 | 288 | 287
2017-08-09 21:30 | 275 | 273
2017-08-09 22:00 | 257 | 257
2017-08-09 22:30 | 251 | 251
2017-08-09 23:00 | 240 | 240
2017-08-09 23:30 | 222 | 221
2017-08-10 | 207 | 206
2017-08-10 00:30 | 197 | 196
2017-08-10 01:00 | 188 | 187
2017-08-10 01:30 | 181 | 179
2017-08-10 02:00 | 175 | 174
2017-08-10 02:30 | 172 | 171
2017-08-10 03:00 | 171 | 170
2017-08-10 03:30 | 172 | 171
2017-08-10 04:00 | 178 | 177
2017-08-10 04:30 | 186 | 185
2017-08-10 05:00 | 202 | 202
2017-08-10 05:30 | 220 | 220
2017-08-10 06:00 | 253 | 253
2017-08-10 06:30 | 278 | 277
2017-08-10 07:00 | 294 | 294
2017-08-10 07:30 | 298 | 298
2017-08-10 08:00 | 285 | 284
2017-08-10 08:30 | 266 | 265
2017-08-10 09:00 | 252 | 251
2017-08-10 09:30 | 241 | 241
2017-08-10 10:00 | 229 | 229
2017-08-10 10:30 | 220 | 220
2017-08-10 11:00 | 213 | 213
2017-08-10 11:30 | 208 | 207
2017-08-10 12:00 | 206 | 206
2017-08-10 12:30 | 206 | 206
2017-08-10 13:00 | 208 | 208
2017-08-10 13:30 | 219 | 218
2017-08-10 14:00 | 230 | 230
2017-08-10 14:30 | 235 | 234
2017-08-10 15:00 | 238 | 237
2017-08-10 15:30 | 246 | 246
2017-08-10 16:00 | 258 | 258
2017-08-10 16:30 | 271 | 271
2017-08-10 17:00 | 284 | 284
2017-08-10 17:30 | 299 | 298
2017-08-10 18:00 | 306 | 301
2017-08-10 18:30 | 308 | 302
2017-08-10 19:00 | 306 | 299
2017-08-10 19:30 | 308 | 301
2017-08-10 20:00 | 300 | 296
2017-08-10 20:30 | 285 | 284
2017-08-10 21:00 | 274 | 273
2017-08-10 21:30 | 263 | 262
2017-08-10 22:00 | 248 | 248
2017-08-10 22:30 | 246 | 246
2017-08-10 23:00 | 234 | 234
2017-08-10 23:30 | 218 | 218
2017-08-11 | 201 | 201
2017-08-11 00:30 | 192 | 191
2017-08-11 01:00 | 183 | 183
2017-08-11 01:30 | 177 | 176
2017-08-11 02:00 | 172 | 171
2017-08-11 02:30 | 169 | 167
2017-08-11 03:00 | 168 | 167
2017-08-11 03:30 | 169 | 168
2017-08-11 04:00 | 173 | 172
2017-08-11 04:30 | 179 | 178
2017-08-11 05:00 | 193 | 192
2017-08-11 05:30 | 211 | 211
2017-08-11 06:00 | 238 | 238
2017-08-11 06:30 | 257 | 257
2017-08-11 07:00 | 271 | 271
2017-08-11 07:30 | 276 | 275
2017-08-11 08:00 | 265 | 265
2017-08-11 08:30 | 253 | 252
2017-08-11 09:00 | 242 | 242
2017-08-11 09:30 | 233 | 233
2017-08-11 10:00 | 226 | 226
2017-08-11 10:30 | 220 | 220
2017-08-11 11:00 | 217 | 216
2017-08-11 11:30 | 213 | 212
2017-08-11 12:00 | 211 | 210
2017-08-11 12:30 | 210 | 210
2017-08-11 13:00 | 211 | 211
2017-08-11 13:30 | 217 | 216
2017-08-11 14:00 | 224 | 223
2017-08-11 14:30 | 229 | 229
2017-08-11 15:00 | 237 | 236
2017-08-11 15:30 | 249 | 248
2017-08-11 16:00 | 257 | 256
2017-08-11 16:30 | 267 | 267
2017-08-11 17:00 | 275 | 274
2017-08-11 17:30 | 282 | 282
2017-08-11 18:00 | 283 | 283
2017-08-11 18:30 | 283 | 283
2017-08-11 19:00 | 278 | 278
2017-08-11 19:30 | 278 | 278
2017-08-11 20:00 | 277 | 276
2017-08-11 20:30 | 272 | 270
2017-08-11 21:00 | 259 | 259
2017-08-11 21:30 | 248 | 248
2017-08-11 22:00 | 244 | 244
2017-08-11 22:30 | 242 | 242
2017-08-11 23:00 | 230 | 230
2017-08-11 23:30 | 217 | 217
2017-08-12 | 201 | 201
2017-08-12 00:30 | 191 | 190
2017-08-12 01:00 | 182 | 181
2017-08-12 01:30 | 174 | 173
2017-08-12 02:00 | 169 | 168
2017-08-12 02:30 | 166 | 165
2017-08-12 03:00 | 165 | 163
2017-08-12 03:30 | 164 | 162
2017-08-12 04:00 | 166 | 164
2017-08-12 04:30 | 168 | 166
2017-08-12 05:00 | 175 | 173
2017-08-12 05:30 | 183 | 182
2017-08-12 06:00 | 195 | 194
2017-08-12 06:30 | 209 | 208
2017-08-12 07:00 | 223 | 223
2017-08-12 07:30 | 230 | 230
2017-08-12 08:00 | 233 | 233
2017-08-12 08:30 | 230 | 230
2017-08-12 09:00 | 223 | 223
2017-08-12 09:30 | 216 | 216
2017-08-12 10:00 | 222 | 221
2017-08-12 10:30 | 241 | 241
2017-08-12 11:00 | 228 | 227
2017-08-12 11:30 | 206 | 206
2017-08-12 12:00 | 215 | 214
2017-08-12 12:30 | 209 | 209
2017-08-12 13:00 | 217 | 217
2017-08-12 13:30 | 211 | 211
2017-08-12 14:00 | 214 | 214
2017-08-12 14:30 | 210 | 210
2017-08-12 15:00 | 217 | 217
2017-08-12 15:30 | 227 | 227
2017-08-12 16:00 | 238 | 238
2017-08-12 16:30 | 254 | 253
2017-08-12 17:00 | 268 | 264
2017-08-12 17:30 | 279 | 277
2017-08-12 18:00 | 281 | 278
2017-08-12 18:30 | 279 | 277
2017-08-12 19:00 | 275 | 272
2017-08-12 19:30 | 269 | 268
2017-08-12 20:00 | 263 | 262
2017-08-12 20:30 | 252 | 252
2017-08-12 21:00 | 244 | 244
2017-08-12 21:30 | 235 | 235
2017-08-12 22:00 | 236 | 236
2017-08-12 22:30 | 237 | 237
2017-08-12 23:00 | 225 | 225
2017-08-12 23:30 | 209 | 209
2017-08-13 | 194 | 193
2017-08-13 00:30 | 183 | 182
2017-08-13 01:00 | 176 | 174
2017-08-13 01:30 | 168 | 167
2017-08-13 02:00 | 163 | 162
2017-08-13 02:30 | 161 | 159
2017-08-13 03:00 | 160 | 158
2017-08-13 03:30 | 159 | 157
2017-08-13 04:00 | 160 | 158
2017-08-13 04:30 | 161 | 159
2017-08-13 05:00 | 165 | 164
2017-08-13 05:30 | 171 | 169
2017-08-13 06:00 | 178 | 177
2017-08-13 06:30 | 186 | 185
2017-08-13 07:00 | 197 | 196
2017-08-13 07:30 | 206 | 206
2017-08-13 08:00 | 214 | 213
2017-08-13 08:30 | 214 | 214
2017-08-13 09:00 | 212 | 212
2017-08-13 09:30 | 209 | 209
2017-08-13 10:00 | 205 | 205
2017-08-13 10:30 | 191 | 191
2017-08-13 11:00 | 195 | 195
2017-08-13 11:30 | 191 | 191
2017-08-13 12:00 | 188 | 188
2017-08-13 12:30 | 188 | 188
2017-08-13 13:00 | 187 | 187
2017-08-13 13:30 | 192 | 192
2017-08-13 14:00 | 198 | 198
2017-08-13 14:30 | 207 | 207
2017-08-13 15:00 | 217 | 217
2017-08-13 15:30 | 227 | 227
2017-08-13 16:00 | 237 | 237
2017-08-13 16:30 | 253 | 252
2017-08-13 17:00 | 264 | 263
2017-08-13 17:30 | 276 | 276
2017-08-13 18:00 | 277 | 277
2017-08-13 18:30 | 276 | 276
2017-08-13 19:00 | 270 | 270
2017-08-13 19:30 | 269 | 268
2017-08-13 20:00 | 264 | 264
2017-08-13 20:30 | 256 | 256
2017-08-13 21:00 | 245 | 245
2017-08-13 21:30 | 234 | 234
2017-08-13 22:00 | 231 | 231
2017-08-13 22:30 | 230 | 230
2017-08-13 23:00 | 218 | 218
2017-08-13 23:30 | 202 | 201
2017-08-14 | 186 | 185
2017-08-14 00:30 | 178 | 176
2017-08-14 01:00 | 171 | 170
2017-08-14 01:30 | 165 | 163
2017-08-14 02:00 | 161 | 159
2017-08-14 02:30 | 158 | 156
2017-08-14 03:00 | 159 | 157
2017-08-14 03:30 | 160 | 158
2017-08-14 04:00 | 164 | 163
2017-08-14 04:30 | 170 | 168
2017-08-14 05:00 | 182 | 181
2017-08-14 05:30 | 199 | 198
2017-08-14 06:00 | 223 | 223
2017-08-14 06:30 | 246 | 246
2017-08-14 07:00 | 270 | 269
2017-08-14 07:30 | 268 | 267
2017-08-14 08:00 | 263 | 263
2017-08-14 08:30 | 250 | 250
2017-08-14 09:00 | 242 | 241
2017-08-14 09:30 | 237 | 237
2017-08-14 10:00 | 235 | 235
2017-08-14 10:30 | 231 | 231
2017-08-14 11:00 | 226 | 225
2017-08-14 11:30 | 220 | 220
2017-08-14 12:00 | 216 | 216
2017-08-14 12:30 | 225 | 225
2017-08-14 13:00 | 230 | 230
2017-08-14 13:30 | 235 | 235
2017-08-14 14:00 | 237 | 237
2017-08-14 14:30 | 233 | 233
2017-08-14 15:00 | 239 | 239
2017-08-14 15:30 | 250 | 249
2017-08-14 16:00 | 262 | 262
2017-08-14 16:30 | 276 | 276
2017-08-14 17:00 | 289 | 289
2017-08-14 17:30 | 304 | 304
2017-08-14 18:00 | 305 | 304
2017-08-14 18:30 | 303 | 301
2017-08-14 19:00 | 296 | 294
2017-08-14 19:30 | 291 | 291
2017-08-14 20:00 | 286 | 285
2017-08-14 20:30 | 272 | 271
2017-08-14 21:00 | 260 | 258
2017-08-14 21:30 | 248 | 245
2017-08-14 22:00 | 242 | 240
2017-08-14 22:30 | 236 | 236
2017-08-14 23:00 | 223 | 223
2017-08-14 23:30 | 206 | 206
2017-08-15 | 190 | 190
2017-08-15 00:30 | 182 | 181
2017-08-15 01:00 | 175 | 174
2017-08-15 01:30 | 169 | 167
2017-08-15 02:00 | 165 | 163
2017-08-15 02:30 | 163 | 161
2017-08-15 03:00 | 162 | 160
2017-08-15 03:30 | 163 | 161
2017-08-15 04:00 | 167 | 166
2017-08-15 04:30 | 174 | 172
2017-08-15 05:00 | 186 | 186
2017-08-15 05:30 | 205 | 205
2017-08-15 06:00 | 234 | 233
2017-08-15 06:30 | 254 | 253
2017-08-15 07:00 | 268 | 268
2017-08-15 07:30 | 270 | 270
2017-08-15 08:00 | 258 | 258
2017-08-15 08:30 | 244 | 244
2017-08-15 09:00 | 236 | 236
2017-08-15 09:30 | 227 | 227
2017-08-15 10:00 | 221 | 221
2017-08-15 10:30 | 217 | 217
2017-08-15 11:00 | 213 | 213
2017-08-15 11:30 | 212 | 212
2017-08-15 12:00 | 210 | 210
2017-08-15 12:30 | 210 | 210
2017-08-15 13:00 | 213 | 213
2017-08-15 13:30 | 218 | 218
2017-08-15 14:00 | 224 | 224
2017-08-15 14:30 | 229 | 229
2017-08-15 15:00 | 237 | 237
2017-08-15 15:30 | 248 | 248
2017-08-15 16:00 | 261 | 261
2017-08-15 16:30 | 274 | 274
2017-08-15 17:00 | 288 | 287
2017-08-15 17:30 | 302 | 301
2017-08-15 18:00 | 305 | 304
2017-08-15 18:30 | 302 | 301
2017-08-15 19:00 | 298 | 296
2017-08-15 19:30 | 297 | 295
2017-08-15 20:00 | 288 | 288
2017-08-15 20:30 | 270 | 270
2017-08-15 21:00 | 254 | 254
2017-08-15 21:30 | 245 | 245
2017-08-15 22:00 | 237 | 237
2017-08-15 22:30 | 233 | 233
2017-08-15 23:00 | 224 | 224
2017-08-15 23:30 | 207 | 207
2017-08-16 | 191 | 191
2017-08-16 00:30 | 181 | 180
2017-08-16 01:00 | 175 | 174
2017-08-16 01:30 | 169 | 167
2017-08-16 02:00 | 165 | 164
2017-08-16 02:30 | 161 | 159
2017-08-16 03:00 | 159 | 157
2017-08-16 03:30 | 160 | 159
2017-08-16 04:00 | 161 | 160
2017-08-16 04:30 | 166 | 165
2017-08-16 05:00 | 179 | 179
2017-08-16 05:30 | 194 | 194
2017-08-16 06:00 | 217 | 217
2017-08-16 06:30 | 239 | 239
2017-08-16 07:00 | 256 | 256
2017-08-16 07:30 | 259 | 259
2017-08-16 08:00 | 255 | 255
2017-08-16 08:30 | 245 | 245
2017-08-16 09:00 | 238 | 238
2017-08-16 09:30 | 231 | 231
2017-08-16 10:00 | 227 | 227
2017-08-16 10:30 | 222 | 222
2017-08-16 11:00 | 220 | 220
2017-08-16 11:30 | 218 | 218
2017-08-16 12:00 | 219 | 219
2017-08-16 12:30 | 219 | 219
2017-08-16 13:00 | 223 | 223
2017-08-16 13:30 | 230 | 230
2017-08-16 14:00 | 222 | 222
2017-08-16 14:30 | 235 | 235
2017-08-16 15:00 | 242 | 242
2017-08-16 15:30 | 249 | 249
2017-08-16 16:00 | 259 | 259
2017-08-16 16:30 | 268 | 268
2017-08-16 17:00 | 272 | 272
2017-08-16 17:30 | 278 | 278
2017-08-16 18:00 | 279 | 279
2017-08-16 18:30 | 278 | 278
2017-08-16 19:00 | 274 | 273
2017-08-16 19:30 | 274 | 273
2017-08-16 20:00 | 271 | 270
2017-08-16 20:30 | 260 | 259
2017-08-16 21:00 | 239 | 239
2017-08-16 21:30 | 226 | 226
2017-08-16 22:00 | 221 | 221
2017-08-16 22:30 | 218 | 217
2017-08-16 23:00 | 208 | 208
2017-08-16 23:30 | 202 | 201
2017-08-17 | 189 | 188
2017-08-17 00:30 | 181 | 180
2017-08-17 01:00 | 174 | 173
2017-08-17 01:30 | 168 | 167
2017-08-17 02:00 | 164 | 162
2017-08-17 02:30 | 162 | 160
2017-08-17 03:00 | 161 | 159
2017-08-17 03:30 | 161 | 160
2017-08-17 04:00 | 163 | 162
2017-08-17 04:30 | 170 | 169
2017-08-17 05:00 | 181 | 181
2017-08-17 05:30 | 200 | 199
2017-08-17 06:00 | 217 | 217
2017-08-17 06:30 | 233 | 233
2017-08-17 07:00 | 248 | 247
2017-08-17 07:30 | 252 | 251
2017-08-17 08:00 | 252 | 251
2017-08-17 08:30 | 249 | 249
2017-08-17 09:00 | 243 | 243
2017-08-17 09:30 | 238 | 238
2017-08-17 10:00 | 235 | 235
2017-08-17 10:30 | 232 | 232
2017-08-17 11:00 | 230 | 230
2017-08-17 11:30 | 230 | 230
2017-08-17 12:00 | 231 | 231
2017-08-17 12:30 | 234 | 234
2017-08-17 13:00 | 238 | 238
2017-08-17 13:30 | 242 | 242
2017-08-17 14:00 | 244 | 244
2017-08-17 14:30 | 247 | 247
2017-08-17 15:00 | 254 | 254
2017-08-17 15:30 | 267 | 267
2017-08-17 16:00 | 273 | 273
2017-08-17 16:30 | 281 | 281
2017-08-17 17:00 | 286 | 286
2017-08-17 17:30 | 299 | 298
2017-08-17 18:00 | 300 | 299
2017-08-17 18:30 | 300 | 300
2017-08-17 19:00 | 297 | 296
2017-08-17 19:30 | 296 | 294
2017-08-17 20:00 | 292 | 291
2017-08-17 20:30 | 278 | 278
2017-08-17 21:00 | 264 | 263
2017-08-17 21:30 | 247 | 246
2017-08-17 22:00 | 241 | 241
2017-08-17 22:30 | 238 | 238
2017-08-17 23:00 | 224 | 223
2017-08-17 23:30 | 205 | 205
2017-08-18 | 189 | 189
2017-08-18 00:30 | 180 | 179
2017-08-18 01:00 | 174 | 173
2017-08-18 01:30 | 168 | 166
2017-08-18 02:00 | 164 | 162
2017-08-18 02:30 | 161 | 160
2017-08-18 03:00 | 160 | 159
2017-08-18 03:30 | 161 | 160
2017-08-18 04:00 | 165 | 164
2017-08-18 04:30 | 171 | 170
2017-08-18 05:00 | 183 | 182
2017-08-18 05:30 | 198 | 198
2017-08-18 06:00 | 220 | 220
2017-08-18 06:30 | 242 | 242
2017-08-18 07:00 | 255 | 255
2017-08-18 07:30 | 255 | 255
2017-08-18 08:00 | 248 | 248
2017-08-18 08:30 | 238 | 238
2017-08-18 09:00 | 231 | 231
2017-08-18 09:30 | 225 | 225
2017-08-18 10:00 | 220 | 220
2017-08-18 10:30 | 214 | 214
2017-08-18 11:00 | 211 | 211
2017-08-18 11:30 | 209 | 209
2017-08-18 12:00 | 209 | 209
2017-08-18 12:30 | 210 | 210
2017-08-18 13:00 | 212 | 212
2017-08-18 13:30 | 216 | 216
2017-08-18 14:00 | 222 | 222
2017-08-18 14:30 | 226 | 226
2017-08-18 15:00 | 234 | 234
2017-08-18 15:30 | 244 | 244
2017-08-18 16:00 | 256 | 256
2017-08-18 16:30 | 267 | 267
2017-08-18 17:00 | 274 | 274
2017-08-18 17:30 | 285 | 285
2017-08-18 18:00 | 290 | 289
2017-08-18 18:30 | 290 | 290
2017-08-18 19:00 | 280 | 280
2017-08-18 19:30 | 277 | 277
2017-08-18 20:00 | 273 | 273
2017-08-18 20:30 | 262 | 262
2017-08-18 21:00 | 252 | 252
2017-08-18 21:30 | 241 | 241
2017-08-18 22:00 | 240 | 240
2017-08-18 22:30 | 240 | 239
2017-08-18 23:00 | 227 | 227
2017-08-18 23:30 | 209 | 209
2017-08-19 | 193 | 193
2017-08-19 00:30 | 184 | 183
2017-08-19 01:00 | 177 | 175
2017-08-19 01:30 | 169 | 168
2017-08-19 02:00 | 164 | 163
2017-08-19 02:30 | 161 | 160
2017-08-19 03:00 | 160 | 158
2017-08-19 03:30 | 159 | 159
2017-08-19 04:00 | 161 | 161
2017-08-19 04:30 | 164 | 164
2017-08-19 05:00 | 170 | 170
2017-08-19 05:30 | 179 | 179
2017-08-19 06:00 | 190 | 190
2017-08-19 06:30 | 202 | 202
2017-08-19 07:00 | 216 | 216
2017-08-19 07:30 | 223 | 222
2017-08-19 08:00 | 226 | 225
2017-08-19 08:30 | 225 | 225
2017-08-19 09:00 | 220 | 220
2017-08-19 09:30 | 211 | 211
2017-08-19 10:00 | 203 | 202
2017-08-19 10:30 | 194 | 194
2017-08-19 11:00 | 186 | 186
2017-08-19 11:30 | 180 | 180
2017-08-19 12:00 | 176 | 176
2017-08-19 12:30 | 175 | 175
2017-08-19 13:00 | 175 | 175
2017-08-19 13:30 | 180 | 180
2017-08-19 14:00 | 186 | 186
2017-08-19 14:30 | 193 | 193
2017-08-19 15:00 | 203 | 203
2017-08-19 15:30 | 214 | 214
2017-08-19 16:00 | 229 | 229
2017-08-19 16:30 | 245 | 245
2017-08-19 17:00 | 262 | 261
2017-08-19 17:30 | 280 | 280
2017-08-19 18:00 | 289 | 288
2017-08-19 18:30 | 290 | 289
2017-08-19 19:00 | 283 | 283
2017-08-19 19:30 | 281 | 280
2017-08-19 20:00 | 276 | 275
2017-08-19 20:30 | 266 | 265
2017-08-19 21:00 | 256 | 256
2017-08-19 21:30 | 247 | 247
2017-08-19 22:00 | 247 | 247
2017-08-19 22:30 | 248 | 248
2017-08-19 23:00 | 236 | 236
2017-08-19 23:30 | 218 | 218
2017-08-20 | 201 | 201
2017-08-20 00:30 | 190 | 189
2017-08-20 01:00 | 181 | 180
2017-08-20 01:30 | 173 | 172
2017-08-20 02:00 | 168 | 167
2017-08-20 02:30 | 167 | 165
2017-08-20 03:00 | 166 | 164
2017-08-20 03:30 | 166 | 164
2017-08-20 04:00 | 167 | 165
2017-08-20 04:30 | 168 | 166
2017-08-20 05:00 | 172 | 170
2017-08-20 05:30 | 178 | 177
2017-08-20 06:00 | 187 | 185
2017-08-20 06:30 | 198 | 197
2017-08-20 07:00 | 209 | 209
2017-08-20 07:30 | 217 | 217
2017-08-20 08:00 | 222 | 222
2017-08-20 08:30 | 222 | 222
2017-08-20 09:00 | 217 | 217
2017-08-20 09:30 | 211 | 211
2017-08-20 10:00 | 201 | 201
2017-08-20 10:30 | 192 | 192
2017-08-20 11:00 | 184 | 184
2017-08-20 11:30 | 179 | 179
2017-08-20 12:00 | 175 | 175
2017-08-20 12:30 | 174 | 173
2017-08-20 13:00 | 175 | 175
2017-08-20 13:30 | 177 | 177
2017-08-20 14:00 | 185 | 185
2017-08-20 14:30 | 193 | 193
2017-08-20 15:00 | 203 | 203
2017-08-20 15:30 | 215 | 215
2017-08-20 16:00 | 231 | 231
2017-08-20 16:30 | 250 | 250
2017-08-20 17:00 | 271 | 270
2017-08-20 17:30 | 294 | 293
2017-08-20 18:00 | 307 | 303
2017-08-20 18:30 | 303 | 300
2017-08-20 19:00 | 299 | 295
2017-08-20 19:30 | 297 | 293
2017-08-20 20:00 | 290 | 287
2017-08-20 20:30 | 276 | 274
2017-08-20 21:00 | 263 | 261
2017-08-20 21:30 | 249 | 247
2017-08-20 22:00 | 242 | 242
2017-08-20 22:30 | 240 | 240
2017-08-20 23:00 | 227 | 227
2017-08-20 23:30 | 210 | 210
2017-08-21 | 195 | 194
2017-08-21 00:30 | 185 | 184
2017-08-21 01:00 | 177 | 176
2017-08-21 01:30 | 170 | 169
2017-08-21 02:00 | 166 | 165
2017-08-21 02:30 | 164 | 162
2017-08-21 03:00 | 164 | 162
2017-08-21 03:30 | 166 | 164
2017-08-21 04:00 | 171 | 169
2017-08-21 04:30 | 178 | 177
2017-08-21 05:00 | 194 | 193
2017-08-21 05:30 | 215 | 215
2017-08-21 06:00 | 244 | 244
2017-08-21 06:30 | 271 | 270
2017-08-21 07:00 | 281 | 281
2017-08-21 07:30 | 313 | 312
2017-08-21 08:00 | 302 | 302
2017-08-21 08:30 | 285 | 285
2017-08-21 09:00 | 280 | 279
2017-08-21 09:30 | 277 | 277
2017-08-21 10:00 | 275 | 275
2017-08-21 10:30 | 247 | 246
2017-08-21 11:00 | 245 | 245
2017-08-21 11:30 | 241 | 241
2017-08-21 12:00 | 241 | 240
2017-08-21 12:30 | 250 | 250
2017-08-21 13:00 | 253 | 253
2017-08-21 13:30 | 260 | 260
2017-08-21 14:00 | 260 | 260
2017-08-21 14:30 | 263 | 263
2017-08-21 15:00 | 273 | 273
2017-08-21 15:30 | 293 | 293
2017-08-21 16:00 | 303 | 303
2017-08-21 16:30 | 314 | 314
2017-08-21 17:00 | 332 | 331
2017-08-21 17:30 | 353 | 351
2017-08-21 18:00 | 353 | 351
2017-08-21 18:30 | 352 | 350
2017-08-21 19:00 | 346 | 343
2017-08-21 19:30 | 344 | 341
2017-08-21 20:00 | 337 | 335
2017-08-21 20:30 | 319 | 317
2017-08-21 21:00 | 302 | 300
2017-08-21 21:30 | 285 | 282
2017-08-21 22:00 | 276 | 274
2017-08-21 22:30 | 271 | 270
2017-08-21 23:00 | 258 | 256
2017-08-21 23:30 | 236 | 236
2017-08-22 | 220 | 219
2017-08-22 00:30 | 209 | 208
2017-08-22 01:00 | 201 | 200
2017-08-22 01:30 | 192 | 191
2017-08-22 02:00 | 186 | 184
2017-08-22 02:30 | 182 | 180
2017-08-22 03:00 | 179 | 179
2017-08-22 03:30 | 182 | 181
2017-08-22 04:00 | 187 | 187
2017-08-22 04:30 | 193 | 193
2017-08-22 05:00 | 209 | 209
2017-08-22 05:30 | 229 | 229
2017-08-22 06:00 | 260 | 259
2017-08-22 06:30 | 282 | 282
2017-08-22 07:00 | 298 | 297
2017-08-22 07:30 | 302 | 302
2017-08-22 08:00 | 295 | 294
2017-08-22 08:30 | 279 | 279
2017-08-22 09:00 | 266 | 266
2017-08-22 09:30 | 259 | 259
2017-08-22 10:00 | 255 | 255
2017-08-22 10:30 | 249 | 248
2017-08-22 11:00 | 245 | 245
2017-08-22 11:30 | 245 | 244
2017-08-22 12:00 | 241 | 241
2017-08-22 12:30 | 241 | 241
2017-08-22 13:00 | 244 | 244
2017-08-22 13:30 | 255 | 254
2017-08-22 14:00 | 258 | 258
2017-08-22 14:30 | 263 | 262
2017-08-22 15:00 | 268 | 267
2017-08-22 15:30 | 279 | 279
2017-08-22 16:00 | 293 | 293
2017-08-22 16:30 | 309 | 309
2017-08-22 17:00 | 319 | 319
2017-08-22 17:30 | 332 | 331
2017-08-22 18:00 | 336 | 334
2017-08-22 18:30 | 337 | 335
2017-08-22 19:00 | 330 | 327
2017-08-22 19:30 | 331 | 327
2017-08-22 20:00 | 327 | 323
2017-08-22 20:30 | 310 | 308
2017-08-22 21:00 | 294 | 293
2017-08-22 21:30 | 278 | 277
2017-08-22 22:00 | 272 | 271
2017-08-22 22:30 | 268 | 267
2017-08-22 23:00 | 251 | 251
2017-08-22 23:30 | 233 | 232
2017-08-23 | 217 | 216
2017-08-23 00:30 | 206 | 204
2017-08-23 01:00 | 197 | 196
2017-08-23 01:30 | 189 | 188
2017-08-23 02:00 | 183 | 181
2017-08-23 02:30 | 178 | 176
2017-08-23 03:00 | 176 | 175
2017-08-23 03:30 | 178 | 177
2017-08-23 04:00 | 182 | 182
2017-08-23 04:30 | 189 | 189
2017-08-23 05:00 | 204 | 204
2017-08-23 05:30 | 224 | 224
2017-08-23 06:00 | 248 | 248
2017-08-23 06:30 | 265 | 265
2017-08-23 07:00 | 282 | 281
2017-08-23 07:30 | 286 | 285
2017-08-23 08:00 | 284 | 283
2017-08-23 08:30 | 281 | 280
2017-08-23 09:00 | 277 | 277
2017-08-23 09:30 | 272 | 271
2017-08-23 10:00 | 270 | 269
2017-08-23 10:30 | 263 | 262
2017-08-23 11:00 | 256 | 255
2017-08-23 11:30 | 247 | 247
2017-08-23 12:00 | 241 | 241
2017-08-23 12:30 | 240 | 240
2017-08-23 13:00 | 243 | 243
2017-08-23 13:30 | 248 | 248
2017-08-23 14:00 | 255 | 255
2017-08-23 14:30 | 261 | 261
2017-08-23 15:00 | 268 | 268
2017-08-23 15:30 | 280 | 280
2017-08-23 16:00 | 287 | 287
2017-08-23 16:30 | 297 | 297
2017-08-23 17:00 | 309 | 309
2017-08-23 17:30 | 323 | 323
2017-08-23 18:00 | 325 | 325
2017-08-23 18:30 | 325 | 325
2017-08-23 19:00 | 318 | 317
2017-08-23 19:30 | 320 | 320
2017-08-23 20:00 | 317 | 316
2017-08-23 20:30 | 303 | 302
2017-08-23 21:00 | 285 | 283
2017-08-23 21:30 | 272 | 271
2017-08-23 22:00 | 259 | 259
2017-08-23 22:30 | 253 | 253
2017-08-23 23:00 | 246 | 246
2017-08-23 23:30 | 232 | 231
2017-08-24 | 215 | 214
2017-08-24 00:30 | 205 | 204
2017-08-24 01:00 | 197 | 196
2017-08-24 01:30 | 190 | 189
2017-08-24 02:00 | 185 | 184
2017-08-24 02:30 | 181 | 180
2017-08-24 03:00 | 181 | 179
2017-08-24 03:30 | 182 | 180
2017-08-24 04:00 | 186 | 185
2017-08-24 04:30 | 193 | 191
2017-08-24 05:00 | 206 | 206
2017-08-24 05:30 | 224 | 224
2017-08-24 06:00 | 250 | 250
2017-08-24 06:30 | 272 | 272
2017-08-24 07:00 | 294 | 294
2017-08-24 07:30 | 307 | 305
2017-08-24 08:00 | 302 | 299
2017-08-24 08:30 | 311 | 309
2017-08-24 09:00 | 300 | 298
2017-08-24 09:30 | 284 | 282
2017-08-24 10:00 | 293 | 291
2017-08-24 10:30 | 291 | 288
2017-08-24 11:00 | 282 | 279
2017-08-24 11:30 | 279 | 277
2017-08-24 12:00 | 259 | 259
2017-08-24 12:30 | 248 | 248
2017-08-24 13:00 | 243 | 243
2017-08-24 13:30 | 250 | 249
2017-08-24 14:00 | 254 | 254
2017-08-24 14:30 | 257 | 257
2017-08-24 15:00 | 273 | 272
2017-08-24 15:30 | 285 | 285
2017-08-24 16:00 | 303 | 303
2017-08-24 16:30 | 313 | 312
2017-08-24 17:00 | 320 | 319
2017-08-24 17:30 | 337 | 336
2017-08-24 18:00 | 351 | 347
2017-08-24 18:30 | 347 | 342
2017-08-24 19:00 | 340 | 336
2017-08-24 19:30 | 335 | 334
2017-08-24 20:00 | 328 | 326
2017-08-24 20:30 | 315 | 313
2017-08-24 21:00 | 300 | 298
2017-08-24 21:30 | 281 | 280
2017-08-24 22:00 | 275 | 274
2017-08-24 22:30 | 271 | 270
2017-08-24 23:00 | 258 | 257
2017-08-24 23:30 | 238 | 237
2017-08-25 | 222 | 219
2017-08-25 00:30 | 210 | 208
2017-08-25 01:00 | 203 | 200
2017-08-25 01:30 | 193 | 192
2017-08-25 02:00 | 188 | 186
2017-08-25 02:30 | 185 | 183
2017-08-25 03:00 | 183 | 182
2017-08-25 03:30 | 185 | 183
2017-08-25 04:00 | 189 | 187
2017-08-25 04:30 | 196 | 194
2017-08-25 05:00 | 210 | 210
2017-08-25 05:30 | 230 | 230
2017-08-25 06:00 | 256 | 256
2017-08-25 06:30 | 277 | 277
2017-08-25 07:00 | 294 | 293
2017-08-25 07:30 | 293 | 292
2017-08-25 08:00 | 281 | 281
2017-08-25 08:30 | 269 | 269
2017-08-25 09:00 | 260 | 260
2017-08-25 09:30 | 254 | 254
2017-08-25 10:00 | 246 | 246
2017-08-25 10:30 | 239 | 239
2017-08-25 11:00 | 237 | 237
2017-08-25 11:30 | 236 | 236
2017-08-25 12:00 | 241 | 241
2017-08-25 12:30 | 241 | 240
2017-08-25 13:00 | 243 | 243
2017-08-25 13:30 | 241 | 241
2017-08-25 14:00 | 243 | 243
2017-08-25 14:30 | 243 | 243
2017-08-25 15:00 | 251 | 251
2017-08-25 15:30 | 265 | 265
2017-08-25 16:00 | 279 | 279
2017-08-25 16:30 | 296 | 296
2017-08-25 17:00 | 309 | 309
2017-08-25 17:30 | 329 | 329
2017-08-25 18:00 | 337 | 333
2017-08-25 18:30 | 337 | 334
2017-08-25 19:00 | 331 | 327
2017-08-25 19:30 | 326 | 325
2017-08-25 20:00 | 322 | 321
2017-08-25 20:30 | 312 | 312
2017-08-25 21:00 | 299 | 298
2017-08-25 21:30 | 286 | 285
2017-08-25 22:00 | 283 | 283
2017-08-25 22:30 | 281 | 281
2017-08-25 23:00 | 266 | 265
2017-08-25 23:30 | 245 | 244
2017-08-26 | 228 | 226
2017-08-26 00:30 | 214 | 212
2017-08-26 01:00 | 206 | 205
2017-08-26 01:30 | 198 | 196
2017-08-26 02:00 | 191 | 189
2017-08-26 02:30 | 185 | 184
2017-08-26 03:00 | 183 | 183
2017-08-26 03:30 | 183 | 182
2017-08-26 04:00 | 184 | 184
2017-08-26 04:30 | 187 | 186
2017-08-26 05:00 | 195 | 194
2017-08-26 05:30 | 204 | 204
2017-08-26 06:00 | 216 | 216
2017-08-26 06:30 | 232 | 232
2017-08-26 07:00 | 245 | 245
2017-08-26 07:30 | 251 | 251
2017-08-26 08:00 | 254 | 253
2017-08-26 08:30 | 251 | 251
2017-08-26 09:00 | 244 | 244
2017-08-26 09:30 | 235 | 235
2017-08-26 10:00 | 226 | 225
2017-08-26 10:30 | 216 | 216
2017-08-26 11:00 | 210 | 209
2017-08-26 11:30 | 206 | 205
2017-08-26 12:00 | 192 | 192
2017-08-26 12:30 | 184 | 183
2017-08-26 13:00 | 188 | 188
2017-08-26 13:30 | 195 | 194
2017-08-26 14:00 | 200 | 200
2017-08-26 14:30 | 204 | 204
2017-08-26 15:00 | 211 | 211
2017-08-26 15:30 | 219 | 219
2017-08-26 16:00 | 232 | 232
2017-08-26 16:30 | 248 | 248
2017-08-26 17:00 | 260 | 260
2017-08-26 17:30 | 268 | 268
2017-08-26 18:00 | 272 | 271
2017-08-26 18:30 | 272 | 271
2017-08-26 19:00 | 267 | 266
2017-08-26 19:30 | 268 | 267
2017-08-26 20:00 | 266 | 266
2017-08-26 20:30 | 258 | 258
2017-08-26 21:00 | 251 | 251
2017-08-26 21:30 | 242 | 242
2017-08-26 22:00 | 240 | 240
2017-08-26 22:30 | 234 | 234
2017-08-26 23:00 | 226 | 225
2017-08-26 23:30 | 213 | 213
2017-08-27 | 197 | 196
2017-08-27 00:30 | 187 | 185
2017-08-27 01:00 | 179 | 177
2017-08-27 01:30 | 170 | 169
2017-08-27 02:00 | 164 | 164
2017-08-27 02:30 | 162 | 161
2017-08-27 03:00 | 161 | 160
2017-08-27 03:30 | 160 | 160
2017-08-27 04:00 | 160 | 160
2017-08-27 04:30 | 162 | 162
2017-08-27 05:00 | 167 | 166
2017-08-27 05:30 | 173 | 173
2017-08-27 06:00 | 180 | 179
2017-08-27 06:30 | 188 | 188
2017-08-27 07:00 | 199 | 199
2017-08-27 07:30 | 208 | 208
2017-08-27 08:00 | 209 | 209
2017-08-27 08:30 | 211 | 210
2017-08-27 09:00 | 210 | 209
2017-08-27 09:30 | 207 | 206
2017-08-27 10:00 | 202 | 201
2017-08-27 10:30 | 207 | 207
2017-08-27 11:00 | 210 | 209
2017-08-27 11:30 | 198 | 197
2017-08-27 12:00 | 188 | 188
2017-08-27 12:30 | 187 | 187
2017-08-27 13:00 | 202 | 201
2017-08-27 13:30 | 202 | 201
2017-08-27 14:00 | 209 | 209
2017-08-27 14:30 | 208 | 208
2017-08-27 15:00 | 213 | 213
2017-08-27 15:30 | 222 | 221
2017-08-27 16:00 | 229 | 228
2017-08-27 16:30 | 242 | 242
2017-08-27 17:00 | 250 | 250
2017-08-27 17:30 | 264 | 264
2017-08-27 18:00 | 271 | 270
2017-08-27 18:30 | 272 | 271
2017-08-27 19:00 | 264 | 264
2017-08-27 19:30 | 264 | 263
2017-08-27 20:00 | 266 | 265
2017-08-27 20:30 | 257 | 257
2017-08-27 21:00 | 248 | 248
2017-08-27 21:30 | 237 | 237
2017-08-27 22:00 | 231 | 231
2017-08-27 22:30 | 227 | 227
2017-08-27 23:00 | 218 | 218
2017-08-27 23:30 | 204 | 203
2017-08-28 | 189 | 188
2017-08-28 00:30 | 181 | 179
2017-08-28 01:00 | 172 | 172
2017-08-28 01:30 | 166 | 166
2017-08-28 02:00 | 163 | 163
2017-08-28 02:30 | 161 | 160
2017-08-28 03:00 | 161 | 161
2017-08-28 03:30 | 162 | 162
2017-08-28 04:00 | 168 | 168
2017-08-28 04:30 | 176 | 176
2017-08-28 05:00 | 191 | 191
2017-08-28 05:30 | 210 | 210
2017-08-28 06:00 | 238 | 238
2017-08-28 06:30 | 264 | 264
2017-08-28 07:00 | 277 | 276
2017-08-28 07:30 | 305 | 305
2017-08-28 08:00 | 288 | 288
2017-08-28 08:30 | 271 | 271
2017-08-28 09:00 | 260 | 260
2017-08-28 09:30 | 249 | 249
2017-08-28 10:00 | 240 | 240
2017-08-28 10:30 | 233 | 233
2017-08-28 11:00 | 227 | 227
2017-08-28 11:30 | 224 | 224
2017-08-28 12:00 | 223 | 223
2017-08-28 12:30 | 223 | 223
2017-08-28 13:00 | 225 | 225
2017-08-28 13:30 | 230 | 230
2017-08-28 14:00 | 237 | 237
2017-08-28 14:30 | 243 | 243
2017-08-28 15:00 | 252 | 252
2017-08-28 15:30 | 266 | 266
2017-08-28 16:00 | 283 | 283
2017-08-28 16:30 | 304 | 303
2017-08-28 17:00 | 325 | 325
2017-08-28 17:30 | 350 | 350
2017-08-28 18:00 | 364 | 363
2017-08-28 18:30 | 366 | 364
2017-08-28 19:00 | 350 | 349
2017-08-28 19:30 | 343 | 343
2017-08-28 20:00 | 336 | 336
2017-08-28 20:30 | 321 | 320
2017-08-28 21:00 | 302 | 302
2017-08-28 21:30 | 286 | 286
2017-08-28 22:00 | 279 | 279
2017-08-28 22:30 | 276 | 276
2017-08-28 23:00 | 259 | 259
2017-08-28 23:30 | 240 | 240
2017-08-29 | 223 | 222
2017-08-29 00:30 | 211 | 210
2017-08-29 01:00 | 203 | 202
2017-08-29 01:30 | 195 | 195
2017-08-29 02:00 | 190 | 189
2017-08-29 02:30 | 186 | 186
2017-08-29 03:00 | 185 | 185
2017-08-29 03:30 | 186 | 186
2017-08-29 04:00 | 191 | 191
2017-08-29 04:30 | 200 | 199
2017-08-29 05:00 | 217 | 216
2017-08-29 05:30 | 240 | 239
2017-08-29 06:00 | 273 | 273
2017-08-29 06:30 | 300 | 299
2017-08-29 07:00 | 317 | 316
2017-08-29 07:30 | 319 | 314
2017-08-29 08:00 | 301 | 295
2017-08-29 08:30 | 281 | 276
2017-08-29 09:00 | 268 | 263
2017-08-29 09:30 | 252 | 250
2017-08-29 10:00 | 241 | 241
2017-08-29 10:30 | 230 | 230
2017-08-29 11:00 | 218 | 217
2017-08-29 11:30 | 217 | 216
2017-08-29 12:00 | 217 | 216
2017-08-29 12:30 | 217 | 216
2017-08-29 13:00 | 221 | 220
2017-08-29 13:30 | 228 | 227
2017-08-29 14:00 | 239 | 238
2017-08-29 14:30 | 247 | 246
2017-08-29 15:00 | 257 | 256
2017-08-29 15:30 | 269 | 268
2017-08-29 16:00 | 284 | 283
2017-08-29 16:30 | 303 | 302
2017-08-29 17:00 | 323 | 321
2017-08-29 17:30 | 347 | 343
2017-08-29 18:00 | 360 | 358
2017-08-29 18:30 | 361 | 358
2017-08-29 19:00 | 347 | 345
2017-08-29 19:30 | 337 | 337
2017-08-29 20:00 | 330 | 330
2017-08-29 20:30 | 313 | 313
2017-08-29 21:00 | 298 | 297
2017-08-29 21:30 | 281 | 281
2017-08-29 22:00 | 274 | 274
2017-08-29 22:30 | 270 | 270
2017-08-29 23:00 | 255 | 255
2017-08-29 23:30 | 235 | 234
2017-08-30 | 218 | 217
2017-08-30 00:30 | 208 | 206
2017-08-30 01:00 | 199 | 198
2017-08-30 01:30 | 190 | 190
2017-08-30 02:00 | 185 | 184
2017-08-30 02:30 | 183 | 182
2017-08-30 03:00 | 182 | 181
2017-08-30 03:30 | 183 | 183
2017-08-30 04:00 | 188 | 188
2017-08-30 04:30 | 196 | 196
2017-08-30 05:00 | 213 | 213
2017-08-30 05:30 | 235 | 235
2017-08-30 06:00 | 262 | 262
2017-08-30 06:30 | 284 | 284
2017-08-30 07:00 | 295 | 295
2017-08-30 07:30 | 294 | 294
2017-08-30 08:00 | 276 | 276
2017-08-30 08:30 | 277 | 277
2017-08-30 09:00 | 266 | 265
2017-08-30 09:30 | 257 | 257
2017-08-30 10:00 | 249 | 249
2017-08-30 10:30 | 241 | 241
2017-08-30 11:00 | 234 | 234
2017-08-30 11:30 | 226 | 225
2017-08-30 12:00 | 223 | 222
2017-08-30 12:30 | 222 | 222
2017-08-30 13:00 | 225 | 225
2017-08-30 13:30 | 229 | 229
2017-08-30 14:00 | 237 | 236
2017-08-30 14:30 | 243 | 242
2017-08-30 15:00 | 253 | 252
2017-08-30 15:30 | 268 | 267
2017-08-30 16:00 | 282 | 281
2017-08-30 16:30 | 300 | 298
2017-08-30 17:00 | 316 | 314
2017-08-30 17:30 | 325 | 325
2017-08-30 18:00 | 335 | 333
2017-08-30 18:30 | 337 | 335
2017-08-30 19:00 | 331 | 328
2017-08-30 19:30 | 328 | 326
2017-08-30 20:00 | 322 | 322
2017-08-30 20:30 | 310 | 309
2017-08-30 21:00 | 293 | 292
2017-08-30 21:30 | 275 | 275
2017-08-30 22:00 | 262 | 262
2017-08-30 22:30 | 257 | 257
2017-08-30 23:00 | 248 | 248
2017-08-30 23:30 | 232 | 231
2017-08-31 | 216 | 215
2017-08-31 00:30 | 206 | 204
2017-08-31 01:00 | 197 | 196
2017-08-31 01:30 | 189 | 189
2017-08-31 02:00 | 184 | 183
2017-08-31 02:30 | 181 | 180
2017-08-31 03:00 | 180 | 179
2017-08-31 03:30 | 182 | 182
2017-08-31 04:00 | 188 | 187
2017-08-31 04:30 | 195 | 194
2017-08-31 05:00 | 211 | 211
2017-08-31 05:30 | 231 | 231
2017-08-31 06:00 | 258 | 258
2017-08-31 06:30 | 282 | 282
2017-08-31 07:00 | 294 | 293
2017-08-31 07:30 | 293 | 292
2017-08-31 08:00 | 280 | 280
2017-08-31 08:30 | 265 | 264
2017-08-31 09:00 | 254 | 253
2017-08-31 09:30 | 243 | 242
2017-08-31 10:00 | 237 | 236
2017-08-31 10:30 | 236 | 235
2017-08-31 11:00 | 218 | 218
2017-08-31 11:30 | 215 | 215
2017-08-31 12:00 | 219 | 218
2017-08-31 12:30 | 230 | 229
2017-08-31 13:00 | 232 | 232
2017-08-31 13:30 | 234 | 234
2017-08-31 14:00 | 243 | 243
2017-08-31 14:30 | 244 | 244
2017-08-31 15:00 | 249 | 249
2017-08-31 15:30 | 260 | 260
2017-08-31 16:00 | 277 | 277
2017-08-31 16:30 | 295 | 295
2017-08-31 17:00 | 313 | 313
2017-08-31 17:30 | 329 | 329
2017-08-31 18:00 | 341 | 339
2017-08-31 18:30 | 338 | 335
2017-08-31 19:00 | 333 | 330
2017-08-31 19:30 | 331 | 329
2017-08-31 20:00 | 330 | 328
2017-08-31 20:30 | 315 | 315
2017-08-31 21:00 | 303 | 302
2017-08-31 21:30 | 287 | 286
2017-08-31 22:00 | 280 | 278
2017-08-31 22:30 | 273 | 273
2017-08-31 23:00 | 259 | 259
2017-08-31 23:30 | 239 | 238
2017-09-01 | 221 | 220
2017-09-01 00:30 | 210 | 208
2017-09-01 01:00 | 202 | 200
2017-09-01 01:30 | 192 | 191
2017-09-01 02:00 | 186 | 185
2017-09-01 02:30 | 182 | 182
2017-09-01 03:00 | 181 | 181
2017-09-01 03:30 | 182 | 181
2017-09-01 04:00 | 185 | 185
2017-09-01 04:30 | 190 | 190
2017-09-01 05:00 | 201 | 200
2017-09-01 05:30 | 213 | 213
2017-09-01 06:00 | 229 | 229
2017-09-01 06:30 | 241 | 241
2017-09-01 07:00 | 252 | 252
2017-09-01 07:30 | 256 | 256
2017-09-01 08:00 | 254 | 254
2017-09-01 08:30 | 255 | 255
2017-09-01 09:00 | 251 | 251
2017-09-01 09:30 | 240 | 240
2017-09-01 10:00 | 234 | 234
2017-09-01 10:30 | 228 | 228
2017-09-01 11:00 | 202 | 201
2017-09-01 11:30 | 198 | 198
2017-09-01 12:00 | 191 | 190
2017-09-01 12:30 | 185 | 184
2017-09-01 13:00 | 184 | 184
2017-09-01 13:30 | 188 | 188
2017-09-01 14:00 | 193 | 193
2017-09-01 14:30 | 200 | 199
2017-09-01 15:00 | 209 | 209
2017-09-01 15:30 | 221 | 220
2017-09-01 16:00 | 234 | 234
2017-09-01 16:30 | 249 | 248
2017-09-01 17:00 | 259 | 259
2017-09-01 17:30 | 276 | 276
2017-09-01 18:00 | 286 | 285
2017-09-01 18:30 | 280 | 280
2017-09-01 19:00 | 276 | 275
2017-09-01 19:30 | 275 | 274
2017-09-01 20:00 | 272 | 272
2017-09-01 20:30 | 264 | 264
2017-09-01 21:00 | 255 | 255
2017-09-01 21:30 | 246 | 246
2017-09-01 22:00 | 245 | 245
2017-09-01 22:30 | 242 | 242
2017-09-01 23:00 | 232 | 232
2017-09-01 23:30 | 215 | 215
2017-09-02 | 198 | 198
2017-09-02 00:30 | 189 | 189
2017-09-02 01:00 | 181 | 180
2017-09-02 01:30 | 172 | 172
2017-09-02 02:00 | 167 | 167
2017-09-02 02:30 | 164 | 164
2017-09-02 03:00 | 162 | 162
2017-09-02 03:30 | 161 | 161
2017-09-02 04:00 | 164 | 164
2017-09-02 04:30 | 167 | 167
2017-09-02 05:00 | 174 | 174
2017-09-02 05:30 | 183 | 183
2017-09-02 06:00 | 194 | 194
2017-09-02 06:30 | 204 | 204
2017-09-02 07:00 | 216 | 215
2017-09-02 07:30 | 220 | 219
2017-09-02 08:00 | 222 | 221
2017-09-02 08:30 | 219 | 219
2017-09-02 09:00 | 213 | 213
2017-09-02 09:30 | 207 | 207
2017-09-02 10:00 | 203 | 203
2017-09-02 10:30 | 201 | 201
2017-09-02 11:00 | 193 | 193
2017-09-02 11:30 | 186 | 186
2017-09-02 12:00 | 181 | 181
2017-09-02 12:30 | 178 | 178
2017-09-02 13:00 | 178 | 178
2017-09-02 13:30 | 182 | 182
2017-09-02 14:00 | 189 | 189
2017-09-02 14:30 | 194 | 194
2017-09-02 15:00 | 203 | 203
2017-09-02 15:30 | 213 | 213
2017-09-02 16:00 | 227 | 227
2017-09-02 16:30 | 242 | 241
2017-09-02 17:00 | 252 | 251
2017-09-02 17:30 | 260 | 259
2017-09-02 18:00 | 263 | 262
2017-09-02 18:30 | 267 | 266
2017-09-02 19:00 | 259 | 257
2017-09-02 19:30 | 260 | 258
2017-09-02 20:00 | 253 | 252
2017-09-02 20:30 | 243 | 242
2017-09-02 21:00 | 239 | 238
2017-09-02 21:30 | 234 | 233
2017-09-02 22:00 | 227 | 226
2017-09-02 22:30 | 226 | 224
2017-09-02 23:00 | 217 | 216
2017-09-02 23:30 | 208 | 206
2017-09-03 | 198 | 195
2017-09-03 00:30 | 188 | 185
2017-09-03 01:00 | 179 | 176
2017-09-03 01:30 | 170 | 168
2017-09-03 02:00 | 165 | 163
2017-09-03 02:30 | 164 | 162
2017-09-03 03:00 | 162 | 160
2017-09-03 03:30 | 161 | 159
2017-09-03 04:00 | 164 | 162
2017-09-03 04:30 | 166 | 164
2017-09-03 05:00 | 169 | 167
2017-09-03 05:30 | 174 | 172
2017-09-03 06:00 | 181 | 179
2017-09-03 06:30 | 187 | 185
2017-09-03 07:00 | 195 | 194
2017-09-03 07:30 | 201 | 200
2017-09-03 08:00 | 209 | 208
2017-09-03 08:30 | 210 | 210
2017-09-03 09:00 | 209 | 209
2017-09-03 09:30 | 205 | 205
2017-09-03 10:00 | 200 | 200
2017-09-03 10:30 | 193 | 193
2017-09-03 11:00 | 189 | 189
2017-09-03 11:30 | 182 | 182
2017-09-03 12:00 | 177 | 177
2017-09-03 12:30 | 178 | 178
2017-09-03 13:00 | 179 | 179
2017-09-03 13:30 | 184 | 184
2017-09-03 14:00 | 189 | 189
2017-09-03 14:30 | 197 | 197
2017-09-03 15:00 | 207 | 207
2017-09-03 15:30 | 216 | 216
2017-09-03 16:00 | 224 | 224
2017-09-03 16:30 | 231 | 231
2017-09-03 17:00 | 235 | 234
2017-09-03 17:30 | 248 | 247
2017-09-03 18:00 | 254 | 252
2017-09-03 18:30 | 255 | 253
2017-09-03 19:00 | 254 | 252
2017-09-03 19:30 | 253 | 251
2017-09-03 20:00 | 251 | 249
2017-09-03 20:30 | 245 | 242
2017-09-03 21:00 | 238 | 237
2017-09-03 21:30 | 232 | 231
2017-09-03 22:00 | 223 | 221
2017-09-03 22:30 | 220 | 219
2017-09-03 23:00 | 213 | 211
2017-09-03 23:30 | 203 | 201
2017-09-04 | 190 | 186
2017-09-04 00:30 | 180 | 176
2017-09-04 01:00 | 174 | 169
2017-09-04 01:30 | 164 | 161
2017-09-04 02:00 | 159 | 157
2017-09-04 02:30 | 159 | 157
2017-09-04 03:00 | 159 | 158
2017-09-04 03:30 | 161 | 159
2017-09-04 04:00 | 165 | 163
2017-09-04 04:30 | 171 | 170
2017-09-04 05:00 | 179 | 178
2017-09-04 05:30 | 184 | 183
2017-09-04 06:00 | 203 | 203
2017-09-04 06:30 | 221 | 221
2017-09-04 07:00 | 236 | 236
2017-09-04 07:30 | 244 | 244
2017-09-04 08:00 | 241 | 241
2017-09-04 08:30 | 238 | 238
2017-09-04 09:00 | 234 | 234
2017-09-04 09:30 | 229 | 229
2017-09-04 10:00 | 226 | 226
2017-09-04 10:30 | 220 | 220
2017-09-04 11:00 | 219 | 219
2017-09-04 11:30 | 222 | 221
2017-09-04 12:00 | 223 | 223
2017-09-04 12:30 | 226 | 225
2017-09-04 13:00 | 229 | 229
2017-09-04 13:30 | 234 | 233
2017-09-04 14:00 | 242 | 241
2017-09-04 14:30 | 244 | 243
2017-09-04 15:00 | 245 | 244
2017-09-04 15:30 | 252 | 250
2017-09-04 16:00 | 262 | 261
2017-09-04 16:30 | 272 | 271
2017-09-04 17:00 | 277 | 275
2017-09-04 17:30 | 281 | 279
2017-09-04 18:00 | 282 | 281
2017-09-04 18:30 | 279 | 278
2017-09-04 19:00 | 273 | 271
2017-09-04 19:30 | 271 | 269
2017-09-04 20:00 | 268 | 264
2017-09-04 20:30 | 260 | 258
2017-09-04 21:00 | 252 | 249
2017-09-04 21:30 | 243 | 240
2017-09-04 22:00 | 229 | 228
2017-09-04 22:30 | 225 | 224
2017-09-04 23:00 | 217 | 215
2017-09-04 23:30 | 205 | 203
2017-09-05 | 191 | 188
2017-09-05 00:30 | 186 | 183
2017-09-05 01:00 | 180 | 176
2017-09-05 01:30 | 174 | 170
2017-09-05 02:00 | 171 | 167
2017-09-05 02:30 | 166 | 164
2017-09-05 03:00 | 163 | 160
2017-09-05 03:30 | 163 | 161
2017-09-05 04:00 | 168 | 166
2017-09-05 04:30 | 172 | 171
2017-09-05 05:00 | 186 | 185
2017-09-05 05:30 | 201 | 201
2017-09-05 06:00 | 223 | 223
2017-09-05 06:30 | 238 | 238
2017-09-05 07:00 | 249 | 249
2017-09-05 07:30 | 250 | 249
2017-09-05 08:00 | 245 | 242
2017-09-05 08:30 | 234 | 232
2017-09-05 09:00 | 227 | 225
2017-09-05 09:30 | 222 | 221
2017-09-05 10:00 | 216 | 215
2017-09-05 10:30 | 212 | 210
2017-09-05 11:00 | 210 | 208
2017-09-05 11:30 | 208 | 206
2017-09-05 12:00 | 204 | 204
2017-09-05 12:30 | 206 | 206
2017-09-05 13:00 | 209 | 209
2017-09-05 13:30 | 215 | 215
2017-09-05 14:00 | 222 | 222
2017-09-05 14:30 | 229 | 229
2017-09-05 15:00 | 236 | 236
2017-09-05 15:30 | 249 | 249
2017-09-05 16:00 | 260 | 257
2017-09-05 16:30 | 267 | 264
2017-09-05 17:00 | 270 | 267
2017-09-05 17:30 | 281 | 278
2017-09-05 18:00 | 294 | 289
2017-09-05 18:30 | 292 | 288
2017-09-05 19:00 | 283 | 280
2017-09-05 19:30 | 280 | 279
2017-09-05 20:00 | 275 | 274
2017-09-05 20:30 | 266 | 265
2017-09-05 21:00 | 251 | 251
2017-09-05 21:30 | 241 | 240
2017-09-05 22:00 | 231 | 230
2017-09-05 22:30 | 227 | 226
2017-09-05 23:00 | 220 | 218
2017-09-05 23:30 | 204 | 201
2017-09-06 | 190 | 187
2017-09-06 00:30 | 181 | 178
2017-09-06 01:00 | 175 | 171
2017-09-06 01:30 | 169 | 165
2017-09-06 02:00 | 162 | 160
2017-09-06 02:30 | 160 | 158
2017-09-06 03:00 | 160 | 158
2017-09-06 03:30 | 162 | 160
2017-09-06 04:00 | 166 | 164
2017-09-06 04:30 | 172 | 171
2017-09-06 05:00 | 186 | 185
2017-09-06 05:30 | 202 | 201
2017-09-06 06:00 | 219 | 219
2017-09-06 06:30 | 231 | 231
2017-09-06 07:00 | 243 | 243
2017-09-06 07:30 | 246 | 245
2017-09-06 08:00 | 239 | 238
2017-09-06 08:30 | 227 | 227
2017-09-06 09:00 | 220 | 219
2017-09-06 09:30 | 212 | 211
2017-09-06 10:00 | 207 | 207
2017-09-06 10:30 | 203 | 202
2017-09-06 11:00 | 200 | 200
2017-09-06 11:30 | 199 | 199
2017-09-06 12:00 | 199 | 199
2017-09-06 12:30 | 201 | 201
2017-09-06 13:00 | 204 | 204
2017-09-06 13:30 | 210 | 210
2017-09-06 14:00 | 218 | 218
2017-09-06 14:30 | 224 | 224
2017-09-06 15:00 | 233 | 233
2017-09-06 15:30 | 245 | 245
2017-09-06 16:00 | 255 | 254
2017-09-06 16:30 | 262 | 262
2017-09-06 17:00 | 268 | 268
2017-09-06 17:30 | 280 | 280
2017-09-06 18:00 | 292 | 290
2017-09-06 18:30 | 292 | 290
2017-09-06 19:00 | 287 | 284
2017-09-06 19:30 | 288 | 285
2017-09-06 20:00 | 278 | 277
2017-09-06 20:30 | 267 | 267
2017-09-06 21:00 | 256 | 256
2017-09-06 21:30 | 243 | 243
2017-09-06 22:00 | 237 | 236
2017-09-06 22:30 | 233 | 232
2017-09-06 23:00 | 221 | 220
2017-09-06 23:30 | 205 | 203
2017-09-07 | 191 | 188
2017-09-07 00:30 | 182 | 178
2017-09-07 01:00 | 176 | 172
2017-09-07 01:30 | 169 | 165
2017-09-07 02:00 | 166 | 161
2017-09-07 02:30 | 163 | 158
2017-09-07 03:00 | 163 | 158
2017-09-07 03:30 | 164 | 159
2017-09-07 04:00 | 168 | 163
2017-09-07 04:30 | 174 | 170
2017-09-07 05:00 | 188 | 185
2017-09-07 05:30 | 198 | 196
2017-09-07 06:00 | 217 | 215
2017-09-07 06:30 | 237 | 233
2017-09-07 07:00 | 252 | 248
2017-09-07 07:30 | 250 | 247
2017-09-07 08:00 | 239 | 236
2017-09-07 08:30 | 228 | 226
2017-09-07 09:00 | 218 | 216
2017-09-07 09:30 | 214 | 212
2017-09-07 10:00 | 211 | 209
2017-09-07 10:30 | 208 | 207
2017-09-07 11:00 | 207 | 205
2017-09-07 11:30 | 203 | 202
2017-09-07 12:00 | 202 | 200
2017-09-07 12:30 | 199 | 199
2017-09-07 13:00 | 203 | 203
2017-09-07 13:30 | 208 | 208
2017-09-07 14:00 | 215 | 215
2017-09-07 14:30 | 221 | 221
2017-09-07 15:00 | 229 | 229
2017-09-07 15:30 | 241 | 241
2017-09-07 16:00 | 254 | 253
2017-09-07 16:30 | 266 | 264
2017-09-07 17:00 | 275 | 273
2017-09-07 17:30 | 289 | 287
2017-09-07 18:00 | 293 | 292
2017-09-07 18:30 | 295 | 294
2017-09-07 19:00 | 292 | 290
2017-09-07 19:30 | 290 | 288
2017-09-07 20:00 | 284 | 282
2017-09-07 20:30 | 273 | 271
2017-09-07 21:00 | 260 | 258
2017-09-07 21:30 | 245 | 244
2017-09-07 22:00 | 241 | 240
2017-09-07 22:30 | 237 | 236
2017-09-07 23:00 | 225 | 224
2017-09-07 23:30 | 207 | 206
2017-09-08 | 191 | 189
2017-09-08 00:30 | 182 | 179
2017-09-08 01:00 | 175 | 172
2017-09-08 01:30 | 171 | 167
2017-09-08 02:00 | 167 | 164
2017-09-08 02:30 | 166 | 162
2017-09-08 03:00 | 164 | 160
2017-09-08 03:30 | 164 | 160
2017-09-08 04:00 | 169 | 165
2017-09-08 04:30 | 175 | 172
2017-09-08 05:00 | 189 | 187
2017-09-08 05:30 | 202 | 201
2017-09-08 06:00 | 225 | 224
2017-09-08 06:30 | 241 | 240
2017-09-08 07:00 | 257 | 257
2017-09-08 07:30 | 256 | 256
2017-09-08 08:00 | 245 | 245
2017-09-08 08:30 | 231 | 231
2017-09-08 09:00 | 222 | 222
2017-09-08 09:30 | 213 | 213
2017-09-08 10:00 | 209 | 209
2017-09-08 10:30 | 204 | 204
2017-09-08 11:00 | 202 | 202
2017-09-08 11:30 | 200 | 199
2017-09-08 12:00 | 199 | 198
2017-09-08 12:30 | 200 | 199
2017-09-08 13:00 | 202 | 202
2017-09-08 13:30 | 205 | 205
2017-09-08 14:00 | 210 | 210
2017-09-08 14:30 | 215 | 215
2017-09-08 15:00 | 223 | 223
2017-09-08 15:30 | 235 | 235
2017-09-08 16:00 | 250 | 248
2017-09-08 16:30 | 261 | 259
2017-09-08 17:00 | 267 | 264
2017-09-08 17:30 | 275 | 273
2017-09-08 18:00 | 282 | 279
2017-09-08 18:30 | 284 | 282
2017-09-08 19:00 | 281 | 278
2017-09-08 19:30 | 276 | 275
2017-09-08 20:00 | 275 | 273
2017-09-08 20:30 | 265 | 263
2017-09-08 21:00 | 254 | 253
2017-09-08 21:30 | 244 | 244
2017-09-08 22:00 | 243 | 242
2017-09-08 22:30 | 243 | 242
2017-09-08 23:00 | 231 | 229
2017-09-08 23:30 | 213 | 211
2017-09-09 | 197 | 194
2017-09-09 00:30 | 187 | 184
2017-09-09 01:00 | 180 | 176
2017-09-09 01:30 | 172 | 170
2017-09-09 02:00 | 168 | 166
2017-09-09 02:30 | 165 | 163
2017-09-09 03:00 | 164 | 162
2017-09-09 03:30 | 163 | 160
2017-09-09 04:00 | 164 | 162
2017-09-09 04:30 | 167 | 165
2017-09-09 05:00 | 174 | 173
2017-09-09 05:30 | 182 | 181
2017-09-09 06:00 | 194 | 193
2017-09-09 06:30 | 202 | 202
2017-09-09 07:00 | 211 | 210
2017-09-09 07:30 | 214 | 214
2017-09-09 08:00 | 215 | 215
2017-09-09 08:30 | 213 | 213
2017-09-09 09:00 | 208 | 208
2017-09-09 09:30 | 200 | 200
2017-09-09 10:00 | 193 | 193
2017-09-09 10:30 | 187 | 187
2017-09-09 11:00 | 182 | 182
2017-09-09 11:30 | 178 | 178
2017-09-09 12:00 | 174 | 174
2017-09-09 12:30 | 173 | 173
2017-09-09 13:00 | 175 | 175
2017-09-09 13:30 | 180 | 180
2017-09-09 14:00 | 186 | 186
2017-09-09 14:30 | 196 | 195
2017-09-09 15:00 | 207 | 207
2017-09-09 15:30 | 219 | 219
2017-09-09 16:00 | 231 | 231
2017-09-09 16:30 | 245 | 245
2017-09-09 17:00 | 256 | 255
2017-09-09 17:30 | 267 | 267
2017-09-09 18:00 | 273 | 273
2017-09-09 18:30 | 273 | 273
2017-09-09 19:00 | 267 | 267
2017-09-09 19:30 | 263 | 263
2017-09-09 20:00 | 258 | 258
2017-09-09 20:30 | 249 | 249
2017-09-09 21:00 | 241 | 240
2017-09-09 21:30 | 233 | 233
2017-09-09 22:00 | 224 | 224
2017-09-09 22:30 | 224 | 223
2017-09-09 23:00 | 216 | 216
2017-09-09 23:30 | 208 | 208
2017-09-10 | 192 | 192
2017-09-10 00:30 | 182 | 182
2017-09-10 01:00 | 173 | 173
2017-09-10 01:30 | 166 | 166
2017-09-10 02:00 | 162 | 162
2017-09-10 02:30 | 158 | 158
2017-09-10 03:00 | 157 | 157
2017-09-10 03:30 | 156 | 156
2017-09-10 04:00 | 157 | 156
2017-09-10 04:30 | 158 | 158
2017-09-10 05:00 | 164 | 163
2017-09-10 05:30 | 170 | 169
2017-09-10 06:00 | 176 | 176
2017-09-10 06:30 | 180 | 180
2017-09-10 07:00 | 187 | 186
2017-09-10 07:30 | 192 | 191
2017-09-10 08:00 | 197 | 195
2017-09-10 08:30 | 199 | 197
2017-09-10 09:00 | 197 | 195
2017-09-10 09:30 | 195 | 193
2017-09-10 10:00 | 191 | 189
2017-09-10 10:30 | 188 | 185
2017-09-10 11:00 | 183 | 180
2017-09-10 11:30 | 179 | 176
2017-09-10 12:00 | 175 | 172
2017-09-10 12:30 | 175 | 172
2017-09-10 13:00 | 176 | 174
2017-09-10 13:30 | 180 | 178
2017-09-10 14:00 | 186 | 184
2017-09-10 14:30 | 195 | 192
2017-09-10 15:00 | 205 | 202
2017-09-10 15:30 | 216 | 215
2017-09-10 16:00 | 229 | 228
2017-09-10 16:30 | 241 | 240
2017-09-10 17:00 | 253 | 253
2017-09-10 17:30 | 263 | 263
2017-09-10 18:00 | 270 | 270
2017-09-10 18:30 | 273 | 273
2017-09-10 19:00 | 265 | 265
2017-09-10 19:30 | 260 | 260
2017-09-10 20:00 | 260 | 260
2017-09-10 20:30 | 251 | 251
2017-09-10 21:00 | 241 | 241
2017-09-10 21:30 | 231 | 231
2017-09-10 22:00 | 227 | 227
2017-09-10 22:30 | 226 | 226
2017-09-10 23:00 | 215 | 215
2017-09-10 23:30 | 200 | 200
2017-09-11 | 185 | 185
2017-09-11 00:30 | 176 | 176
2017-09-11 01:00 | 169 | 169
2017-09-11 01:30 | 163 | 163
2017-09-11 02:00 | 160 | 160
2017-09-11 02:30 | 158 | 158
2017-09-11 03:00 | 160 | 159
2017-09-11 03:30 | 158 | 158
2017-09-11 04:00 | 163 | 162
2017-09-11 04:30 | 169 | 168
2017-09-11 05:00 | 184 | 183
2017-09-11 05:30 | 196 | 195
2017-09-11 06:00 | 214 | 213
2017-09-11 06:30 | 231 | 231
2017-09-11 07:00 | 240 | 239
2017-09-11 07:30 | 244 | 243
2017-09-11 08:00 | 240 | 238
2017-09-11 08:30 | 230 | 227
2017-09-11 09:00 | 224 | 222
2017-09-11 09:30 | 218 | 215
2017-09-11 10:00 | 213 | 210
2017-09-11 10:30 | 210 | 207
2017-09-11 11:00 | 207 | 204
2017-09-11 11:30 | 208 | 204
2017-09-11 12:00 | 210 | 207
2017-09-11 12:30 | 213 | 209
2017-09-11 13:00 | 216 | 213
2017-09-11 13:30 | 219 | 216
2017-09-11 14:00 | 225 | 221
2017-09-11 14:30 | 231 | 229
2017-09-11 15:00 | 239 | 239
2017-09-11 15:30 | 249 | 249
2017-09-11 16:00 | 257 | 257
2017-09-11 16:30 | 260 | 260
2017-09-11 17:00 | 268 | 268
2017-09-11 17:30 | 282 | 281
2017-09-11 18:00 | 286 | 286
2017-09-11 18:30 | 282 | 282
2017-09-11 19:00 | 274 | 274
2017-09-11 19:30 | 269 | 269
2017-09-11 20:00 | 266 | 265
2017-09-11 20:30 | 257 | 256
2017-09-11 21:00 | 240 | 240
2017-09-11 21:30 | 229 | 229
2017-09-11 22:00 | 220 | 220
2017-09-11 22:30 | 217 | 217
2017-09-11 23:00 | 208 | 208
2017-09-11 23:30 | 197 | 197
2017-09-12 | 183 | 183
2017-09-12 00:30 | 179 | 179
2017-09-12 01:00 | 174 | 174
2017-09-12 01:30 | 167 | 167
2017-09-12 02:00 | 163 | 163
2017-09-12 02:30 | 160 | 160
2017-09-12 03:00 | 160 | 160
2017-09-12 03:30 | 161 | 161
2017-09-12 04:00 | 165 | 164
2017-09-12 04:30 | 170 | 170
2017-09-12 05:00 | 183 | 183
2017-09-12 05:30 | 194 | 194
2017-09-12 06:00 | 214 | 214
2017-09-12 06:30 | 227 | 227
2017-09-12 07:00 | 245 | 245
2017-09-12 07:30 | 245 | 245
2017-09-12 08:00 | 240 | 240
2017-09-12 08:30 | 232 | 232
2017-09-12 09:00 | 225 | 225
2017-09-12 09:30 | 220 | 220
2017-09-12 10:00 | 219 | 219
2017-09-12 10:30 | 217 | 216
2017-09-12 11:00 | 216 | 216
2017-09-12 11:30 | 220 | 219
2017-09-12 12:00 | 220 | 220
2017-09-12 12:30 | 222 | 221
2017-09-12 13:00 | 227 | 226
2017-09-12 13:30 | 230 | 229
2017-09-12 14:00 | 238 | 238
2017-09-12 14:30 | 246 | 245
2017-09-12 15:00 | 252 | 252
2017-09-12 15:30 | 255 | 255
2017-09-12 16:00 | 258 | 257
2017-09-12 16:30 | 268 | 267
2017-09-12 17:00 | 273 | 273
2017-09-12 17:30 | 279 | 279
2017-09-12 18:00 | 284 | 284
2017-09-12 18:30 | 284 | 280
2017-09-12 19:00 | 278 | 275
2017-09-12 19:30 | 276 | 274
2017-09-12 20:00 | 271 | 269
2017-09-12 20:30 | 257 | 256
2017-09-12 21:00 | 244 | 244
2017-09-12 21:30 | 233 | 233
2017-09-12 22:00 | 225 | 224
2017-09-12 22:30 | 222 | 221
2017-09-12 23:00 | 212 | 210
2017-09-12 23:30 | 202 | 200
2017-09-13 | 190 | 187
2017-09-13 00:30 | 182 | 178
2017-09-13 01:00 | 176 | 172
2017-09-13 01:30 | 171 | 166
2017-09-13 02:00 | 166 | 162
2017-09-13 02:30 | 161 | 159
2017-09-13 03:00 | 160 | 158
2017-09-13 03:30 | 161 | 159
2017-09-13 04:00 | 166 | 164
2017-09-13 04:30 | 171 | 169
2017-09-13 05:00 | 183 | 182
2017-09-13 05:30 | 195 | 194
2017-09-13 06:00 | 210 | 209
2017-09-13 06:30 | 220 | 220
2017-09-13 07:00 | 229 | 229
2017-09-13 07:30 | 233 | 233
2017-09-13 08:00 | 231 | 231
2017-09-13 08:30 | 229 | 229
2017-09-13 09:00 | 228 | 228
2017-09-13 09:30 | 225 | 225
2017-09-13 10:00 | 225 | 225
2017-09-13 10:30 | 223 | 222
2017-09-13 11:00 | 222 | 221
2017-09-13 11:30 | 222 | 222
2017-09-13 12:00 | 223 | 223
2017-09-13 12:30 | 223 | 223
2017-09-13 13:00 | 228 | 227
2017-09-13 13:30 | 232 | 232
2017-09-13 14:00 | 239 | 238
2017-09-13 14:30 | 244 | 243
2017-09-13 15:00 | 249 | 249
2017-09-13 15:30 | 253 | 252
2017-09-13 16:00 | 259 | 258
2017-09-13 16:30 | 269 | 268
2017-09-13 17:00 | 270 | 269
2017-09-13 17:30 | 279 | 279
2017-09-13 18:00 | 281 | 280
2017-09-13 18:30 | 278 | 277
2017-09-13 19:00 | 275 | 273
2017-09-13 19:30 | 272 | 271
2017-09-13 20:00 | 266 | 264
2017-09-13 20:30 | 250 | 249
2017-09-13 21:00 | 240 | 239
2017-09-13 21:30 | 235 | 233
2017-09-13 22:00 | 220 | 218
2017-09-13 22:30 | 213 | 210
2017-09-13 23:00 | 202 | 198
2017-09-13 23:30 | 193 | 188
2017-09-14 | 179 | 176
2017-09-14 00:30 | 176 | 175
2017-09-14 01:00 | 174 | 173
2017-09-14 01:30 | 168 | 167
2017-09-14 02:00 | 165 | 163
2017-09-14 02:30 | 163 | 161
2017-09-14 03:00 | 162 | 161
2017-09-14 03:30 | 162 | 161
2017-09-14 04:00 | 167 | 165
2017-09-14 04:30 | 172 | 171
2017-09-14 05:00 | 184 | 184
2017-09-14 05:30 | 195 | 194
2017-09-14 06:00 | 213 | 213
2017-09-14 06:30 | 219 | 219
2017-09-14 07:00 | 240 | 239
2017-09-14 07:30 | 256 | 255
2017-09-14 08:00 | 268 | 267
2017-09-14 08:30 | 261 | 261
2017-09-14 09:00 | 251 | 251
2017-09-14 09:30 | 246 | 246
2017-09-14 10:00 | 233 | 233
2017-09-14 10:30 | 215 | 215
2017-09-14 11:00 | 208 | 207
2017-09-14 11:30 | 220 | 219
2017-09-14 12:00 | 221 | 220
2017-09-14 12:30 | 225 | 225
2017-09-14 13:00 | 227 | 226
2017-09-14 13:30 | 224 | 223
2017-09-14 14:00 | 221 | 220
2017-09-14 14:30 | 220 | 220
2017-09-14 15:00 | 229 | 229
2017-09-14 15:30 | 240 | 239
2017-09-14 16:00 | 241 | 240
2017-09-14 16:30 | 250 | 249
2017-09-14 17:00 | 253 | 253
2017-09-14 17:30 | 265 | 265
2017-09-14 18:00 | 272 | 272
2017-09-14 18:30 | 273 | 273
2017-09-14 19:00 | 270 | 269
2017-09-14 19:30 | 270 | 269
2017-09-14 20:00 | 268 | 268
2017-09-14 20:30 | 259 | 259
2017-09-14 21:00 | 245 | 245
2017-09-14 21:30 | 239 | 238
2017-09-14 22:00 | 230 | 230
2017-09-14 22:30 | 229 | 229
2017-09-14 23:00 | 220 | 219
2017-09-14 23:30 | 208 | 207
2017-09-15 | 192 | 191
2017-09-15 00:30 | 186 | 184
2017-09-15 01:00 | 184 | 182
2017-09-15 01:30 | 181 | 179
2017-09-15 02:00 | 173 | 171
2017-09-15 02:30 | 169 | 166
2017-09-15 03:00 | 166 | 163
2017-09-15 03:30 | 166 | 163
2017-09-15 04:00 | 169 | 167
2017-09-15 04:30 | 178 | 176
2017-09-15 05:00 | 186 | 185
2017-09-15 05:30 | 192 | 191
2017-09-15 06:00 | 207 | 206
2017-09-15 06:30 | 213 | 213
2017-09-15 07:00 | 227 | 227
2017-09-15 07:30 | 234 | 234
2017-09-15 08:00 | 232 | 232
2017-09-15 08:30 | 225 | 225
2017-09-15 09:00 | 223 | 223
2017-09-15 09:30 | 219 | 219
2017-09-15 10:00 | 217 | 217
2017-09-15 10:30 | 216 | 215
2017-09-15 11:00 | 216 | 216
2017-09-15 11:30 | 215 | 214
2017-09-15 12:00 | 211 | 211
2017-09-15 12:30 | 210 | 210
2017-09-15 13:00 | 212 | 212
2017-09-15 13:30 | 214 | 214
2017-09-15 14:00 | 220 | 220
2017-09-15 14:30 | 221 | 221
2017-09-15 15:00 | 223 | 223
2017-09-15 15:30 | 231 | 231
2017-09-15 16:00 | 238 | 238
2017-09-15 16:30 | 241 | 241
2017-09-15 17:00 | 244 | 244
2017-09-15 17:30 | 253 | 253
2017-09-15 18:00 | 261 | 261
2017-09-15 18:30 | 265 | 264
2017-09-15 19:00 | 262 | 261
2017-09-15 19:30 | 264 | 262
2017-09-15 20:00 | 261 | 261
2017-09-15 20:30 | 252 | 252
2017-09-15 21:00 | 248 | 247
2017-09-15 21:30 | 243 | 243
2017-09-15 22:00 | 229 | 229
2017-09-15 22:30 | 223 | 223
2017-09-15 23:00 | 213 | 212
2017-09-15 23:30 | 205 | 204
2017-09-16 | 196 | 195
2017-09-16 00:30 | 189 | 187
2017-09-16 01:00 | 184 | 181
2017-09-16 01:30 | 182 | 180
2017-09-16 02:00 | 181 | 178
2017-09-16 02:30 | 180 | 178
2017-09-16 03:00 | 180 | 178
2017-09-16 03:30 | 178 | 176
2017-09-16 04:00 | 180 | 178
2017-09-16 04:30 | 179 | 176
2017-09-16 05:00 | 182 | 180
2017-09-16 05:30 | 184 | 182
2017-09-16 06:00 | 196 | 194
2017-09-16 06:30 | 202 | 201
2017-09-16 07:00 | 213 | 212
2017-09-16 07:30 | 221 | 221
2017-09-16 08:00 | 227 | 227
2017-09-16 08:30 | 228 | 228
2017-09-16 09:00 | 226 | 225
2017-09-16 09:30 | 221 | 221
2017-09-16 10:00 | 216 | 215
2017-09-16 10:30 | 209 | 208
2017-09-16 11:00 | 203 | 203
2017-09-16 11:30 | 200 | 200
2017-09-16 12:00 | 198 | 197
2017-09-16 12:30 | 197 | 197
2017-09-16 13:00 | 199 | 199
2017-09-16 13:30 | 204 | 203
2017-09-16 14:00 | 210 | 209
2017-09-16 14:30 | 215 | 215
2017-09-16 15:00 | 221 | 221
2017-09-16 15:30 | 227 | 227
2017-09-16 16:00 | 235 | 234
2017-09-16 16:30 | 238 | 238
2017-09-16 17:00 | 239 | 239
2017-09-16 17:30 | 253 | 252
2017-09-16 18:00 | 259 | 257
2017-09-16 18:30 | 261 | 260
2017-09-16 19:00 | 258 | 256
2017-09-16 19:30 | 254 | 252
2017-09-16 20:00 | 251 | 251
2017-09-16 20:30 | 247 | 247
2017-09-16 21:00 | 239 | 238
2017-09-16 21:30 | 233 | 232
2017-09-16 22:00 | 224 | 223
2017-09-16 22:30 | 220 | 218
2017-09-16 23:00 | 210 | 207
2017-09-16 23:30 | 202 | 199
2017-09-17 | 195 | 191
2017-09-17 00:30 | 193 | 189
2017-09-17 01:00 | 189 | 184
2017-09-17 01:30 | 182 | 178
2017-09-17 02:00 | 178 | 173
2017-09-17 02:30 | 177 | 172
2017-09-17 03:00 | 177 | 172
2017-09-17 03:30 | 180 | 175
2017-09-17 04:00 | 179 | 174
2017-09-17 04:30 | 180 | 175
2017-09-17 05:00 | 182 | 178
2017-09-17 05:30 | 180 | 177
2017-09-17 06:00 | 194 | 192
2017-09-17 06:30 | 201 | 199
2017-09-17 07:00 | 215 | 214
2017-09-17 07:30 | 221 | 220
2017-09-17 08:00 | 230 | 230
2017-09-17 08:30 | 233 | 233
2017-09-17 09:00 | 229 | 229
2017-09-17 09:30 | 231 | 231
2017-09-17 10:00 | 221 | 221
2017-09-17 10:30 | 209 | 209
2017-09-17 11:00 | 203 | 203
2017-09-17 11:30 | 202 | 201
2017-09-17 12:00 | 203 | 203
2017-09-17 12:30 | 203 | 203
2017-09-17 13:00 | 200 | 200
2017-09-17 13:30 | 208 | 208
2017-09-17 14:00 | 212 | 212
2017-09-17 14:30 | 215 | 215
2017-09-17 15:00 | 224 | 223
2017-09-17 15:30 | 231 | 231
2017-09-17 16:00 | 231 | 230
2017-09-17 16:30 | 232 | 231
2017-09-17 17:00 | 237 | 237
2017-09-17 17:30 | 252 | 251
2017-09-17 18:00 | 266 | 263
2017-09-17 18:30 | 265 | 262
2017-09-17 19:00 | 262 | 259
2017-09-17 19:30 | 258 | 254
2017-09-17 20:00 | 253 | 251
2017-09-17 20:30 | 244 | 241
2017-09-17 21:00 | 236 | 235
2017-09-17 21:30 | 230 | 229
2017-09-17 22:00 | 223 | 222
2017-09-17 22:30 | 221 | 220
2017-09-17 23:00 | 213 | 211
2017-09-17 23:30 | 200 | 197
2017-09-18 | 186 | 182
2017-09-18 00:30 | 177 | 173
2017-09-18 01:00 | 171 | 167
2017-09-18 01:30 | 166 | 161
2017-09-18 02:00 | 163 | 158
2017-09-18 02:30 | 161 | 156
2017-09-18 03:00 | 162 | 157
2017-09-18 03:30 | 163 | 158
2017-09-18 04:00 | 166 | 162
2017-09-18 04:30 | 172 | 168
2017-09-18 05:00 | 184 | 181
2017-09-18 05:30 | 196 | 194
2017-09-18 06:00 | 209 | 208
2017-09-18 06:30 | 220 | 219
2017-09-18 07:00 | 233 | 233
2017-09-18 07:30 | 238 | 238
2017-09-18 08:00 | 239 | 239
2017-09-18 08:30 | 237 | 237
2017-09-18 09:00 | 237 | 236
2017-09-18 09:30 | 232 | 231
2017-09-18 10:00 | 227 | 227
2017-09-18 10:30 | 220 | 220
2017-09-18 11:00 | 214 | 214
2017-09-18 11:30 | 211 | 211
2017-09-18 12:00 | 208 | 208
2017-09-18 12:30 | 208 | 208
2017-09-18 13:00 | 210 | 210
2017-09-18 13:30 | 215 | 215
2017-09-18 14:00 | 221 | 221
2017-09-18 14:30 | 227 | 227
2017-09-18 15:00 | 236 | 236
2017-09-18 15:30 | 239 | 239
2017-09-18 16:00 | 246 | 246
2017-09-18 16:30 | 254 | 254
2017-09-18 17:00 | 254 | 254
2017-09-18 17:30 | 264 | 264
2017-09-18 18:00 | 273 | 273
2017-09-18 18:30 | 272 | 272
2017-09-18 19:00 | 268 | 268
2017-09-18 19:30 | 269 | 269
2017-09-18 20:00 | 262 | 262
2017-09-18 20:30 | 255 | 255
2017-09-18 21:00 | 248 | 248
2017-09-18 21:30 | 241 | 241
2017-09-18 22:00 | 233 | 233
2017-09-18 22:30 | 227 | 227
2017-09-18 23:00 | 214 | 214
2017-09-18 23:30 | 202 | 202
2017-09-19 | 188 | 188
2017-09-19 00:30 | 181 | 180
2017-09-19 01:00 | 173 | 173
2017-09-19 01:30 | 167 | 167
2017-09-19 02:00 | 162 | 162
2017-09-19 02:30 | 159 | 159
2017-09-19 03:00 | 159 | 159
2017-09-19 03:30 | 159 | 159
2017-09-19 04:00 | 164 | 164
2017-09-19 04:30 | 170 | 170
2017-09-19 05:00 | 182 | 182
2017-09-19 05:30 | 195 | 195
2017-09-19 06:00 | 211 | 211
2017-09-19 06:30 | 220 | 219
2017-09-19 07:00 | 231 | 231
2017-09-19 07:30 | 233 | 233
2017-09-19 08:00 | 231 | 231
2017-09-19 08:30 | 228 | 227
2017-09-19 09:00 | 224 | 224
2017-09-19 09:30 | 218 | 217
2017-09-19 10:00 | 215 | 214
2017-09-19 10:30 | 212 | 212
2017-09-19 11:00 | 209 | 209
2017-09-19 11:30 | 212 | 212
2017-09-19 12:00 | 212 | 212
2017-09-19 12:30 | 215 | 215
2017-09-19 13:00 | 219 | 219
2017-09-19 13:30 | 226 | 226
2017-09-19 14:00 | 233 | 233
2017-09-19 14:30 | 240 | 240
2017-09-19 15:00 | 243 | 243
2017-09-19 15:30 | 250 | 250
2017-09-19 16:00 | 259 | 259
2017-09-19 16:30 | 265 | 265
2017-09-19 17:00 | 268 | 268
2017-09-19 17:30 | 276 | 276
2017-09-19 18:00 | 282 | 282
2017-09-19 18:30 | 282 | 281
2017-09-19 19:00 | 277 | 275
2017-09-19 19:30 | 276 | 274
2017-09-19 20:00 | 269 | 267
2017-09-19 20:30 | 261 | 260
2017-09-19 21:00 | 253 | 253
2017-09-19 21:30 | 244 | 243
2017-09-19 22:00 | 237 | 236
2017-09-19 22:30 | 235 | 235
2017-09-19 23:00 | 222 | 221
2017-09-19 23:30 | 206 | 205
2017-09-20 | 191 | 190
2017-09-20 00:30 | 183 | 182
2017-09-20 01:00 | 176 | 175
2017-09-20 01:30 | 169 | 168
2017-09-20 02:00 | 164 | 163
2017-09-20 02:30 | 162 | 161
2017-09-20 03:00 | 161 | 161
2017-09-20 03:30 | 162 | 162
2017-09-20 04:00 | 165 | 165
2017-09-20 04:30 | 171 | 171
2017-09-20 05:00 | 182 | 182
2017-09-20 05:30 | 194 | 194
2017-09-20 06:00 | 212 | 212
2017-09-20 06:30 | 222 | 222
2017-09-20 07:00 | 234 | 234
2017-09-20 07:30 | 248 | 248
2017-09-20 08:00 | 254 | 254
2017-09-20 08:30 | 250 | 250
2017-09-20 09:00 | 246 | 246
2017-09-20 09:30 | 239 | 238
2017-09-20 10:00 | 238 | 238
2017-09-20 10:30 | 233 | 233
2017-09-20 11:00 | 229 | 229
2017-09-20 11:30 | 229 | 229
2017-09-20 12:00 | 228 | 228
2017-09-20 12:30 | 229 | 229
2017-09-20 13:00 | 233 | 233
2017-09-20 13:30 | 240 | 240
2017-09-20 14:00 | 246 | 246
2017-09-20 14:30 | 253 | 253
2017-09-20 15:00 | 262 | 262
2017-09-20 15:30 | 272 | 272
2017-09-20 16:00 | 287 | 285
2017-09-20 16:30 | 294 | 292
2017-09-20 17:00 | 297 | 294
2017-09-20 17:30 | 304 | 301
2017-09-20 18:00 | 310 | 308
2017-09-20 18:30 | 304 | 302
2017-09-20 19:00 | 299 | 296
2017-09-20 19:30 | 295 | 292
2017-09-20 20:00 | 292 | 288
2017-09-20 20:30 | 279 | 278
2017-09-20 21:00 | 268 | 267
2017-09-20 21:30 | 260 | 258
2017-09-20 22:00 | 247 | 244
2017-09-20 22:30 | 246 | 243
2017-09-20 23:00 | 240 | 237
2017-09-20 23:30 | 224 | 221
2017-09-21 | 206 | 203
2017-09-21 00:30 | 198 | 194
2017-09-21 01:00 | 191 | 188
2017-09-21 01:30 | 182 | 180
2017-09-21 02:00 | 177 | 175
2017-09-21 02:30 | 175 | 172
2017-09-21 03:00 | 175 | 172
2017-09-21 03:30 | 175 | 173
2017-09-21 04:00 | 179 | 177
2017-09-21 04:30 | 185 | 183
2017-09-21 05:00 | 198 | 197
2017-09-21 05:30 | 211 | 209
2017-09-21 06:00 | 226 | 225
2017-09-21 06:30 | 236 | 235
2017-09-21 07:00 | 250 | 250
2017-09-21 07:30 | 253 | 252
2017-09-21 08:00 | 255 | 255
2017-09-21 08:30 | 257 | 257
2017-09-21 09:00 | 263 | 263
2017-09-21 09:30 | 260 | 259
2017-09-21 10:00 | 259 | 258
2017-09-21 10:30 | 251 | 251
2017-09-21 11:00 | 248 | 247
2017-09-21 11:30 | 245 | 244
2017-09-21 12:00 | 242 | 241
2017-09-21 12:30 | 242 | 241
2017-09-21 13:00 | 244 | 243
2017-09-21 13:30 | 248 | 247
2017-09-21 14:00 | 254 | 253
2017-09-21 14:30 | 259 | 258
2017-09-21 15:00 | 247 | 246
2017-09-21 15:30 | 255 | 254
2017-09-21 16:00 | 265 | 264
2017-09-21 16:30 | 274 | 273
2017-09-21 17:00 | 277 | 275
2017-09-21 17:30 | 283 | 281
2017-09-21 18:00 | 289 | 288
2017-09-21 18:30 | 290 | 289
2017-09-21 19:00 | 285 | 283
2017-09-21 19:30 | 283 | 281
2017-09-21 20:00 | 278 | 276
2017-09-21 20:30 | 270 | 269
2017-09-21 21:00 | 259 | 258
2017-09-21 21:30 | 245 | 243
2017-09-21 22:00 | 238 | 236
2017-09-21 22:30 | 236 | 234
2017-09-21 23:00 | 224 | 223
2017-09-21 23:30 | 207 | 205
2017-09-22 | 192 | 190
2017-09-22 00:30 | 182 | 180
2017-09-22 01:00 | 175 | 174
2017-09-22 01:30 | 169 | 168
2017-09-22 02:00 | 165 | 164
2017-09-22 02:30 | 163 | 162
2017-09-22 03:00 | 163 | 162
2017-09-22 03:30 | 164 | 163
2017-09-22 04:00 | 169 | 167
2017-09-22 04:30 | 174 | 173
2017-09-22 05:00 | 187 | 186
2017-09-22 05:30 | 197 | 197
2017-09-22 06:00 | 214 | 214
2017-09-22 06:30 | 225 | 225
2017-09-22 07:00 | 239 | 239
2017-09-22 07:30 | 244 | 244
2017-09-22 08:00 | 246 | 246
2017-09-22 08:30 | 245 | 245
2017-09-22 09:00 | 246 | 246
2017-09-22 09:30 | 241 | 241
2017-09-22 10:00 | 238 | 238
2017-09-22 10:30 | 236 | 235
2017-09-22 11:00 | 235 | 234
2017-09-22 11:30 | 236 | 235
2017-09-22 12:00 | 236 | 235
2017-09-22 12:30 | 237 | 237
2017-09-22 13:00 | 241 | 240
2017-09-22 13:30 | 241 | 241
2017-09-22 14:00 | 245 | 245
2017-09-22 14:30 | 248 | 247
2017-09-22 15:00 | 251 | 250
2017-09-22 15:30 | 258 | 257
2017-09-22 16:00 | 264 | 263
2017-09-22 16:30 | 273 | 272
2017-09-22 17:00 | 269 | 268
2017-09-22 17:30 | 276 | 274
2017-09-22 18:00 | 278 | 276
2017-09-22 18:30 | 277 | 276
2017-09-22 19:00 | 270 | 268
2017-09-22 19:30 | 265 | 262
2017-09-22 20:00 | 260 | 260
2017-09-22 20:30 | 250 | 249
2017-09-22 21:00 | 241 | 240
2017-09-22 21:30 | 238 | 237
2017-09-22 22:00 | 232 | 229
2017-09-22 22:30 | 226 | 223
2017-09-22 23:00 | 218 | 215
2017-09-22 23:30 | 208 | 204
2017-09-23 | 193 | 190
2017-09-23 00:30 | 185 | 182
2017-09-23 01:00 | 178 | 174
2017-09-23 01:30 | 171 | 168
2017-09-23 02:00 | 165 | 163
2017-09-23 02:30 | 162 | 160
2017-09-23 03:00 | 160 | 158
2017-09-23 03:30 | 159 | 158
2017-09-23 04:00 | 160 | 159
2017-09-23 04:30 | 163 | 162
2017-09-23 05:00 | 169 | 168
2017-09-23 05:30 | 173 | 172
2017-09-23 06:00 | 182 | 181
2017-09-23 06:30 | 188 | 187
2017-09-23 07:00 | 197 | 197
2017-09-23 07:30 | 205 | 205
2017-09-23 08:00 | 211 | 211
2017-09-23 08:30 | 214 | 214
2017-09-23 09:00 | 215 | 215
2017-09-23 09:30 | 212 | 212
2017-09-23 10:00 | 209 | 209
2017-09-23 10:30 | 206 | 206
2017-09-23 11:00 | 205 | 205
2017-09-23 11:30 | 204 | 204
2017-09-23 12:00 | 205 | 205
2017-09-23 12:30 | 207 | 206
2017-09-23 13:00 | 210 | 210
2017-09-23 13:30 | 216 | 216
2017-09-23 14:00 | 223 | 223
2017-09-23 14:30 | 230 | 230
2017-09-23 15:00 | 240 | 239
2017-09-23 15:30 | 250 | 250
2017-09-23 16:00 | 251 | 250
2017-09-23 16:30 | 254 | 254
2017-09-23 17:00 | 250 | 250
2017-09-23 17:30 | 257 | 256
2017-09-23 18:00 | 265 | 265
2017-09-23 18:30 | 263 | 263
2017-09-23 19:00 | 254 | 254
2017-09-23 19:30 | 250 | 249
2017-09-23 20:00 | 243 | 243
2017-09-23 20:30 | 234 | 234
2017-09-23 21:00 | 228 | 228
2017-09-23 21:30 | 227 | 226
2017-09-23 22:00 | 224 | 224
2017-09-23 22:30 | 224 | 223
2017-09-23 23:00 | 215 | 214
2017-09-23 23:30 | 206 | 204
2017-09-24 | 192 | 190
2017-09-24 00:30 | 182 | 180
2017-09-24 01:00 | 176 | 173
2017-09-24 01:30 | 169 | 166
2017-09-24 02:00 | 164 | 162
2017-09-24 02:30 | 162 | 160
2017-09-24 03:00 | 161 | 159
2017-09-24 03:30 | 158 | 157
2017-09-24 04:00 | 159 | 157
2017-09-24 04:30 | 159 | 158
2017-09-24 05:00 | 164 | 163
2017-09-24 05:30 | 167 | 165
2017-09-24 06:00 | 172 | 171
2017-09-24 06:30 | 177 | 176
2017-09-24 07:00 | 184 | 184
2017-09-24 07:30 | 190 | 189
2017-09-24 08:00 | 198 | 198
2017-09-24 08:30 | 201 | 201
2017-09-24 09:00 | 204 | 204
2017-09-24 09:30 | 207 | 206
2017-09-24 10:00 | 207 | 206
2017-09-24 10:30 | 203 | 202
2017-09-24 11:00 | 201 | 200
2017-09-24 11:30 | 202 | 202
2017-09-24 12:00 | 203 | 202
2017-09-24 12:30 | 205 | 205
2017-09-24 13:00 | 206 | 206
2017-09-24 13:30 | 184 | 183
2017-09-24 14:00 | 187 | 186
2017-09-24 14:30 | 207 | 207
2017-09-24 15:00 | 230 | 230
2017-09-24 15:30 | 209 | 208
2017-09-24 16:00 | 216 | 215
2017-09-24 16:30 | 241 | 240
2017-09-24 17:00 | 240 | 239
2017-09-24 17:30 | 246 | 245
2017-09-24 18:00 | 262 | 259
2017-09-24 18:30 | 262 | 258
2017-09-24 19:00 | 254 | 252
2017-09-24 19:30 | 248 | 248
2017-09-24 20:00 | 244 | 244
2017-09-24 20:30 | 238 | 238
2017-09-24 21:00 | 230 | 229
2017-09-24 21:30 | 222 | 222
2017-09-24 22:00 | 218 | 217
2017-09-24 22:30 | 213 | 212
2017-09-24 23:00 | 206 | 205
2017-09-24 23:30 | 197 | 195
2017-09-25 | 184 | 183
2017-09-25 00:30 | 177 | 176
2017-09-25 01:00 | 172 | 171
2017-09-25 01:30 | 166 | 165
2017-09-25 02:00 | 161 | 160
2017-09-25 02:30 | 159 | 157
2017-09-25 03:00 | 159 | 158
2017-09-25 03:30 | 161 | 160
2017-09-25 04:00 | 167 | 166
2017-09-25 04:30 | 174 | 173
2017-09-25 05:00 | 185 | 184
2017-09-25 05:30 | 193 | 192
2017-09-25 06:00 | 204 | 204
2017-09-25 06:30 | 211 | 211
2017-09-25 07:00 | 222 | 222
2017-09-25 07:30 | 233 | 233
2017-09-25 08:00 | 238 | 237
2017-09-25 08:30 | 240 | 240
2017-09-25 09:00 | 245 | 245
2017-09-25 09:30 | 236 | 236
2017-09-25 10:00 | 238 | 238
2017-09-25 10:30 | 239 | 239
2017-09-25 11:00 | 241 | 240
2017-09-25 11:30 | 240 | 239
2017-09-25 12:00 | 241 | 240
2017-09-25 12:30 | 248 | 247
2017-09-25 13:00 | 243 | 243
2017-09-25 13:30 | 249 | 249
2017-09-25 14:00 | 254 | 254
2017-09-25 14:30 | 261 | 261
2017-09-25 15:00 | 264 | 264
2017-09-25 15:30 | 268 | 268
2017-09-25 16:00 | 270 | 270
2017-09-25 16:30 | 273 | 273
2017-09-25 17:00 | 282 | 282
2017-09-25 17:30 | 285 | 285
2017-09-25 18:00 | 290 | 289
2017-09-25 18:30 | 289 | 289
2017-09-25 19:00 | 276 | 275
2017-09-25 19:30 | 276 | 275
2017-09-25 20:00 | 273 | 271
2017-09-25 20:30 | 261 | 260
2017-09-25 21:00 | 243 | 243
2017-09-25 21:30 | 232 | 232
2017-09-25 22:00 | 225 | 225
2017-09-25 22:30 | 224 | 224
2017-09-25 23:00 | 210 | 209
2017-09-25 23:30 | 200 | 199
2017-09-26 | 190 | 188
2017-09-26 00:30 | 182 | 181
2017-09-26 01:00 | 178 | 178
2017-09-26 01:30 | 173 | 173
2017-09-26 02:00 | 168 | 167
2017-09-26 02:30 | 168 | 167
2017-09-26 03:00 | 161 | 160
2017-09-26 03:30 | 161 | 160
2017-09-26 04:00 | 166 | 165
2017-09-26 04:30 | 167 | 166
2017-09-26 05:00 | 179 | 178
2017-09-26 05:30 | 185 | 185
2017-09-26 06:00 | 195 | 195
2017-09-26 06:30 | 207 | 207
2017-09-26 07:00 | 220 | 220
2017-09-26 07:30 | 225 | 224
2017-09-26 08:00 | 230 | 230
2017-09-26 08:30 | 246 | 246
2017-09-26 09:00 | 247 | 247
2017-09-26 09:30 | 265 | 265
2017-09-26 10:00 | 252 | 252
2017-09-26 10:30 | 245 | 245
2017-09-26 11:00 | 240 | 239
2017-09-26 11:30 | 244 | 244
2017-09-26 12:00 | 249 | 248
2017-09-26 12:30 | 243 | 243
2017-09-26 13:00 | 243 | 243
2017-09-26 13:30 | 250 | 249
2017-09-26 14:00 | 253 | 253
2017-09-26 14:30 | 248 | 248
2017-09-26 15:00 | 252 | 252
2017-09-26 15:30 | 257 | 257
2017-09-26 16:00 | 266 | 266
2017-09-26 16:30 | 276 | 276
2017-09-26 17:00 | 282 | 281
2017-09-26 17:30 | 289 | 288
2017-09-26 18:00 | 299 | 299
2017-09-26 18:30 | 301 | 300
2017-09-26 19:00 | 289 | 288
2017-09-26 19:30 | 282 | 281
2017-09-26 20:00 | 273 | 272
2017-09-26 20:30 | 261 | 260
2017-09-26 21:00 | 249 | 249
2017-09-26 21:30 | 236 | 236
2017-09-26 22:00 | 228 | 228
2017-09-26 22:30 | 223 | 223
2017-09-26 23:00 | 208 | 208
2017-09-26 23:30 | 188 | 188
2017-09-27 | 175 | 175
2017-09-27 00:30 | 168 | 168
2017-09-27 01:00 | 162 | 162
2017-09-27 01:30 | 158 | 158
2017-09-27 02:00 | 156 | 156
2017-09-27 02:30 | 156 | 155
2017-09-27 03:00 | 156 | 155
2017-09-27 03:30 | 159 | 159
2017-09-27 04:00 | 164 | 164
2017-09-27 04:30 | 168 | 168
2017-09-27 05:00 | 173 | 172
2017-09-27 05:30 | 178 | 178
2017-09-27 06:00 | 202 | 202
2017-09-27 06:30 | 220 | 220
2017-09-27 07:00 | 241 | 241
2017-09-27 07:30 | 251 | 251
2017-09-27 08:00 | 244 | 244
2017-09-27 08:30 | 244 | 243
2017-09-27 09:00 | 251 | 251
2017-09-27 09:30 | 254 | 254
2017-09-27 10:00 | 257 | 257
2017-09-27 10:30 | 251 | 251
2017-09-27 11:00 | 247 | 247
2017-09-27 11:30 | 251 | 251
2017-09-27 12:00 | 250 | 250
2017-09-27 12:30 | 247 | 247
2017-09-27 13:00 | 251 | 251
2017-09-27 13:30 | 254 | 254
2017-09-27 14:00 | 265 | 265
2017-09-27 14:30 | 261 | 261
2017-09-27 15:00 | 258 | 258
2017-09-27 15:30 | 261 | 261
2017-09-27 16:00 | 272 | 272
2017-09-27 16:30 | 278 | 278
2017-09-27 17:00 | 281 | 281
2017-09-27 17:30 | 291 | 290
2017-09-27 18:00 | 292 | 292
2017-09-27 18:30 | 291 | 291
2017-09-27 19:00 | 287 | 286
2017-09-27 19:30 | 281 | 281
2017-09-27 20:00 | 270 | 270
2017-09-27 20:30 | 259 | 259
2017-09-27 21:00 | 244 | 243
2017-09-27 21:30 | 231 | 231
2017-09-27 22:00 | 228 | 228
2017-09-27 22:30 | 227 | 227
2017-09-27 23:00 | 218 | 218
2017-09-27 23:30 | 209 | 209
2017-09-28 | 188 | 188
2017-09-28 00:30 | 182 | 182
2017-09-28 01:00 | 181 | 181
2017-09-28 01:30 | 176 | 176
2017-09-28 02:00 | 150 | 150
2017-09-28 02:30 | 154 | 154
2017-09-28 03:00 | 164 | 164
2017-09-28 03:30 | 162 | 162
2017-09-28 04:00 | 166 | 166
2017-09-28 04:30 | 176 | 176
2017-09-28 05:00 | 183 | 183
2017-09-28 05:30 | 186 | 186
2017-09-28 06:00 | 197 | 197
2017-09-28 06:30 | 216 | 216
2017-09-28 07:00 | 232 | 232
2017-09-28 07:30 | 239 | 239
2017-09-28 08:00 | 244 | 244
2017-09-28 08:30 | 249 | 249
2017-09-28 09:00 | 251 | 251
2017-09-28 09:30 | 249 | 249
2017-09-28 10:00 | 249 | 249
2017-09-28 10:30 | 250 | 249
2017-09-28 11:00 | 250 | 249
2017-09-28 11:30 | 250 | 249
2017-09-28 12:00 | 253 | 253
2017-09-28 12:30 | 255 | 255
2017-09-28 13:00 | 258 | 257
2017-09-28 13:30 | 264 | 263
2017-09-28 14:00 | 270 | 270
2017-09-28 14:30 | 280 | 279
2017-09-28 15:00 | 288 | 288
2017-09-28 15:30 | 297 | 296
2017-09-28 16:00 | 306 | 306
2017-09-28 16:30 | 312 | 312
2017-09-28 17:00 | 311 | 310
2017-09-28 17:30 | 314 | 313
2017-09-28 18:00 | 324 | 323
2017-09-28 18:30 | 325 | 324
2017-09-28 19:00 | 313 | 312
2017-09-28 19:30 | 304 | 304
2017-09-28 20:00 | 298 | 298
2017-09-28 20:30 | 287 | 287
2017-09-28 21:00 | 276 | 276
2017-09-28 21:30 | 273 | 271
2017-09-28 22:00 | 267 | 266
2017-09-28 22:30 | 262 | 260
2017-09-28 23:00 | 233 | 230
2017-09-28 23:30 | 217 | 213
2017-09-29 | 199 | 199
2017-09-29 00:30 | 190 | 189
2017-09-29 01:00 | 182 | 181
2017-09-29 01:30 | 182 | 181
2017-09-29 02:00 | 179 | 178
2017-09-29 02:30 | 180 | 178
2017-09-29 03:00 | 180 | 179
2017-09-29 03:30 | 183 | 181
2017-09-29 04:00 | 189 | 187
2017-09-29 04:30 | 191 | 190
2017-09-29 05:00 | 200 | 199
2017-09-29 05:30 | 204 | 203
2017-09-29 06:00 | 214 | 214
2017-09-29 06:30 | 218 | 218
2017-09-29 07:00 | 225 | 225
2017-09-29 07:30 | 242 | 242
2017-09-29 08:00 | 255 | 254
2017-09-29 08:30 | 263 | 262
2017-09-29 09:00 | 271 | 270
2017-09-29 09:30 | 268 | 268
2017-09-29 10:00 | 269 | 269
2017-09-29 10:30 | 274 | 274
2017-09-29 11:00 | 276 | 275
2017-09-29 11:30 | 268 | 266
2017-09-29 12:00 | 268 | 266
2017-09-29 12:30 | 274 | 273
2017-09-29 13:00 | 272 | 270
2017-09-29 13:30 | 279 | 277
2017-09-29 14:00 | 286 | 282
2017-09-29 14:30 | 288 | 282
2017-09-29 15:00 | 288 | 283
2017-09-29 15:30 | 282 | 278
2017-09-29 16:00 | 283 | 279
2017-09-29 16:30 | 281 | 279
2017-09-29 17:00 | 277 | 275
2017-09-29 17:30 | 276 | 274
2017-09-29 18:00 | 281 | 279
2017-09-29 18:30 | 279 | 277
2017-09-29 19:00 | 273 | 271
2017-09-29 19:30 | 266 | 265
2017-09-29 20:00 | 257 | 257
2017-09-29 20:30 | 247 | 247
2017-09-29 21:00 | 234 | 233
2017-09-29 21:30 | 227 | 226
2017-09-29 22:00 | 219 | 219
2017-09-29 22:30 | 217 | 217
2017-09-29 23:00 | 203 | 203
2017-09-29 23:30 | 192 | 192
2017-09-30 | 183 | 183
2017-09-30 00:30 | 179 | 179
2017-09-30 01:00 | 176 | 176
2017-09-30 01:30 | 170 | 170
2017-09-30 02:00 | 161 | 161
2017-09-30 02:30 | 158 | 158
2017-09-30 03:00 | 157 | 156
2017-09-30 03:30 | 155 | 155
2017-09-30 04:00 | 154 | 154
2017-09-30 04:30 | 156 | 156
2017-09-30 05:00 | 163 | 162
2017-09-30 05:30 | 166 | 166
2017-09-30 06:00 | 173 | 173
2017-09-30 06:30 | 180 | 180
2017-09-30 07:00 | 193 | 193
2017-09-30 07:30 | 204 | 204
2017-09-30 08:00 | 211 | 210
2017-09-30 08:30 | 225 | 225
2017-09-30 09:00 | 233 | 233
2017-09-30 09:30 | 219 | 219
2017-09-30 10:00 | 225 | 225
2017-09-30 10:30 | 219 | 219
2017-09-30 11:00 | 216 | 216
2017-09-30 11:30 | 217 | 217
2017-09-30 12:00 | 214 | 214
2017-09-30 12:30 | 212 | 212
2017-09-30 13:00 | 214 | 214
2017-09-30 13:30 | 215 | 215
2017-09-30 14:00 | 220 | 220
2017-09-30 14:30 | 224 | 224
2017-09-30 15:00 | 225 | 224
2017-09-30 15:30 | 229 | 228
2017-09-30 16:00 | 232 | 232
2017-09-30 16:30 | 237 | 236
2017-09-30 17:00 | 233 | 233
2017-09-30 17:30 | 233 | 233
2017-09-30 18:00 | 240 | 240
2017-09-30 18:30 | 243 | 243
2017-09-30 19:00 | 236 | 236
2017-09-30 19:30 | 232 | 232
2017-09-30 20:00 | 228 | 228
2017-09-30 20:30 | 221 | 221
2017-09-30 21:00 | 218 | 218
2017-09-30 21:30 | 210 | 209
2017-09-30 22:00 | 205 | 205
2017-09-30 22:30 | 204 | 203
2017-09-30 23:00 | 193 | 192
2017-09-30 23:30 | 186 | 185
2017-10-01 | 177 | 175
2017-10-01 00:30 | 176 | 174
2017-10-01 01:00 | 172 | 170
2017-10-01 01:30 | 167 | 164
2017-10-01 02:00 | 161 | 158
2017-10-01 02:30 | 160 | 157
2017-10-01 03:00 | 156 | 153
2017-10-01 03:30 | 157 | 154
2017-10-01 04:00 | 158 | 155
2017-10-01 04:30 | 160 | 157
2017-10-01 05:00 | 165 | 162
2017-10-01 05:30 | 165 | 162
2017-10-01 06:00 | 175 | 172
2017-10-01 06:30 | 179 | 177
2017-10-01 07:00 | 192 | 191
2017-10-01 07:30 | 202 | 201
2017-10-01 08:00 | 198 | 197
2017-10-01 08:30 | 197 | 196
2017-10-01 09:00 | 197 | 197
2017-10-01 09:30 | 201 | 201
2017-10-01 10:00 | 207 | 207
2017-10-01 10:30 | 217 | 216
2017-10-01 11:00 | 214 | 213
2017-10-01 11:30 | 220 | 219
2017-10-01 12:00 | 219 | 219
2017-10-01 12:30 | 217 | 217
2017-10-01 13:00 | 216 | 216
2017-10-01 13:30 | 217 | 216
2017-10-01 14:00 | 218 | 217
2017-10-01 14:30 | 219 | 218
2017-10-01 15:00 | 218 | 217
2017-10-01 15:30 | 220 | 219
2017-10-01 16:00 | 228 | 227
2017-10-01 16:30 | 234 | 233
2017-10-01 17:00 | 236 | 235
2017-10-01 17:30 | 238 | 238
2017-10-01 18:00 | 236 | 236
2017-10-01 18:30 | 238 | 238
2017-10-01 19:00 | 230 | 230
2017-10-01 19:30 | 230 | 230
2017-10-01 20:00 | 223 | 221
2017-10-01 20:30 | 219 | 217
2017-10-01 21:00 | 212 | 210
2017-10-01 21:30 | 210 | 208
2017-10-01 22:00 | 203 | 201
2017-10-01 22:30 | 197 | 195
2017-10-01 23:00 | 189 | 185
2017-10-01 23:30 | 180 | 175
2017-10-02 | 169 | 167
2017-10-02 00:30 | 167 | 164
2017-10-02 01:00 | 167 | 164
2017-10-02 01:30 | 163 | 160
2017-10-02 02:00 | 160 | 157
2017-10-02 02:30 | 158 | 154
2017-10-02 03:00 | 158 | 155
2017-10-02 03:30 | 157 | 153
2017-10-02 04:00 | 159 | 156
2017-10-02 04:30 | 161 | 158
2017-10-02 05:00 | 166 | 164
2017-10-02 05:30 | 170 | 168
2017-10-02 06:00 | 179 | 177
2017-10-02 06:30 | 188 | 187
2017-10-02 07:00 | 200 | 199
2017-10-02 07:30 | 213 | 212
2017-10-02 08:00 | 222 | 222
2017-10-02 08:30 | 226 | 226
2017-10-02 09:00 | 226 | 226
2017-10-02 09:30 | 225 | 225
2017-10-02 10:00 | 231 | 231
2017-10-02 10:30 | 227 | 227
2017-10-02 11:00 | 226 | 226
2017-10-02 11:30 | 227 | 227
2017-10-02 12:00 | 219 | 218
2017-10-02 12:30 | 217 | 216
2017-10-02 13:00 | 215 | 214
2017-10-02 13:30 | 214 | 213
2017-10-02 14:00 | 219 | 219
2017-10-02 14:30 | 217 | 216
2017-10-02 15:00 | 216 | 215
2017-10-02 15:30 | 222 | 222
2017-10-02 16:00 | 228 | 228
2017-10-02 16:30 | 238 | 238
2017-10-02 17:00 | 245 | 245
2017-10-02 17:30 | 250 | 250
2017-10-02 18:00 | 253 | 251
2017-10-02 18:30 | 251 | 249
2017-10-02 19:00 | 244 | 241
2017-10-02 19:30 | 243 | 240
2017-10-02 20:00 | 235 | 234
2017-10-02 20:30 | 221 | 221
2017-10-02 21:00 | 213 | 213
2017-10-02 21:30 | 207 | 206
2017-10-02 22:00 | 199 | 198
2017-10-02 22:30 | 195 | 194
2017-10-02 23:00 | 184 | 183
2017-10-02 23:30 | 173 | 171
2017-10-03 | 160 | 158
2017-10-03 00:30 | 156 | 152
2017-10-03 01:00 | 153 | 150
2017-10-03 01:30 | 146 | 143
2017-10-03 02:00 | 144 | 141
2017-10-03 02:30 | 138 | 134
2017-10-03 03:00 | 138 | 134
2017-10-03 03:30 | 141 | 137
2017-10-03 04:00 | 147 | 143
2017-10-03 04:30 | 158 | 155
2017-10-03 05:00 | 169 | 168
2017-10-03 05:30 | 178 | 176
2017-10-03 06:00 | 189 | 189
2017-10-03 06:30 | 207 | 206
2017-10-03 07:00 | 227 | 227
2017-10-03 07:30 | 236 | 236
2017-10-03 08:00 | 238 | 238
2017-10-03 08:30 | 234 | 233
2017-10-03 09:00 | 226 | 224
2017-10-03 09:30 | 220 | 218
2017-10-03 10:00 | 224 | 222
2017-10-03 10:30 | 224 | 223
2017-10-03 11:00 | 217 | 216
2017-10-03 11:30 | 208 | 206
2017-10-03 12:00 | 216 | 214
2017-10-03 12:30 | 222 | 221
2017-10-03 13:00 | 224 | 223
2017-10-03 13:30 | 220 | 219
2017-10-03 14:00 | 217 | 215
2017-10-03 14:30 | 217 | 216
2017-10-03 15:00 | 223 | 221
2017-10-03 15:30 | 231 | 229
2017-10-03 16:00 | 240 | 238
2017-10-03 16:30 | 248 | 246
2017-10-03 17:00 | 257 | 255
2017-10-03 17:30 | 265 | 263
2017-10-03 18:00 | 271 | 269
2017-10-03 18:30 | 270 | 268
2017-10-03 19:00 | 262 | 260
2017-10-03 19:30 | 260 | 258
2017-10-03 20:00 | 248 | 245
2017-10-03 20:30 | 237 | 233
2017-10-03 21:00 | 229 | 225
2017-10-03 21:30 | 218 | 215
2017-10-03 22:00 | 213 | 211
2017-10-03 22:30 | 206 | 204
2017-10-03 23:00 | 190 | 188
2017-10-03 23:30 | 178 | 174
2017-10-04 | 169 | 165
2017-10-04 00:30 | 160 | 158
2017-10-04 01:00 | 155 | 153
2017-10-04 01:30 | 146 | 143
2017-10-04 02:00 | 141 | 138
2017-10-04 02:30 | 141 | 138
2017-10-04 03:00 | 144 | 141
2017-10-04 03:30 | 147 | 144
2017-10-04 04:00 | 150 | 147
2017-10-04 04:30 | 154 | 151
2017-10-04 05:00 | 161 | 159
2017-10-04 05:30 | 173 | 172
2017-10-04 06:00 | 183 | 183
2017-10-04 06:30 | 198 | 198
2017-10-04 07:00 | 214 | 214
2017-10-04 07:30 | 222 | 222
2017-10-04 08:00 | 217 | 217
2017-10-04 08:30 | 214 | 214
2017-10-04 09:00 | 220 | 220
2017-10-04 09:30 | 225 | 224
2017-10-04 10:00 | 230 | 229
2017-10-04 10:30 | 217 | 215
2017-10-04 11:00 | 205 | 203
2017-10-04 11:30 | 204 | 201
2017-10-04 12:00 | 201 | 199
2017-10-04 12:30 | 203 | 200
2017-10-04 13:00 | 203 | 201
2017-10-04 13:30 | 208 | 206
2017-10-04 14:00 | 216 | 215
2017-10-04 14:30 | 227 | 225
2017-10-04 15:00 | 233 | 232
2017-10-04 15:30 | 238 | 236
2017-10-04 16:00 | 245 | 243
2017-10-04 16:30 | 254 | 251
2017-10-04 17:00 | 259 | 256
2017-10-04 17:30 | 267 | 264
2017-10-04 18:00 | 274 | 272
2017-10-04 18:30 | 274 | 272
2017-10-04 19:00 | 267 | 265
2017-10-04 19:30 | 259 | 257
2017-10-04 20:00 | 250 | 249
2017-10-04 20:30 | 238 | 238
2017-10-04 21:00 | 231 | 230
2017-10-04 21:30 | 217 | 216
2017-10-04 22:00 | 211 | 211
2017-10-04 22:30 | 208 | 208
2017-10-04 23:00 | 198 | 197
2017-10-04 23:30 | 183 | 182
2017-10-05 | 172 | 170
2017-10-05 00:30 | 166 | 164
2017-10-05 01:00 | 162 | 159
2017-10-05 01:30 | 157 | 154
2017-10-05 02:00 | 150 | 147
2017-10-05 02:30 | 148 | 145
2017-10-05 03:00 | 150 | 148
2017-10-05 03:30 | 154 | 151
2017-10-05 04:00 | 156 | 154
2017-10-05 04:30 | 159 | 157
2017-10-05 05:00 | 177 | 175
2017-10-05 05:30 | 186 | 184
2017-10-05 06:00 | 191 | 190
2017-10-05 06:30 | 202 | 202
2017-10-05 07:00 | 211 | 211
2017-10-05 07:30 | 221 | 220
2017-10-05 08:00 | 224 | 222
2017-10-05 08:30 | 221 | 220
2017-10-05 09:00 | 249 | 248
2017-10-05 09:30 | 250 | 249
2017-10-05 10:00 | 247 | 246
2017-10-05 10:30 | 244 | 244
2017-10-05 11:00 | 241 | 241
2017-10-05 11:30 | 235 | 235
2017-10-05 12:00 | 217 | 216
2017-10-05 12:30 | 220 | 220
2017-10-05 13:00 | 222 | 221
2017-10-05 13:30 | 225 | 224
2017-10-05 14:00 | 230 | 229
2017-10-05 14:30 | 239 | 238
2017-10-05 15:00 | 243 | 242
2017-10-05 15:30 | 252 | 251
2017-10-05 16:00 | 257 | 256
2017-10-05 16:30 | 265 | 264
2017-10-05 17:00 | 268 | 266
2017-10-05 17:30 | 274 | 273
2017-10-05 18:00 | 279 | 279
2017-10-05 18:30 | 283 | 283
2017-10-05 19:00 | 273 | 273
2017-10-05 19:30 | 270 | 270
2017-10-05 20:00 | 266 | 266
2017-10-05 20:30 | 258 | 258
2017-10-05 21:00 | 244 | 244
2017-10-05 21:30 | 235 | 235
2017-10-05 22:00 | 229 | 229
2017-10-05 22:30 | 221 | 221
2017-10-05 23:00 | 212 | 212
2017-10-05 23:30 | 193 | 193
2017-10-06 | 181 | 181
2017-10-06 00:30 | 176 | 176
2017-10-06 01:00 | 174 | 174
2017-10-06 01:30 | 170 | 170
2017-10-06 02:00 | 167 | 166
2017-10-06 02:30 | 163 | 163
2017-10-06 03:00 | 160 | 160
2017-10-06 03:30 | 166 | 166
2017-10-06 04:00 | 166 | 166
2017-10-06 04:30 | 173 | 173
2017-10-06 05:00 | 179 | 179
2017-10-06 05:30 | 189 | 189
2017-10-06 06:00 | 201 | 201
2017-10-06 06:30 | 223 | 222
2017-10-06 07:00 | 237 | 237
2017-10-06 07:30 | 246 | 246
2017-10-06 08:00 | 247 | 247
2017-10-06 08:30 | 245 | 244
2017-10-06 09:00 | 245 | 244
2017-10-06 09:30 | 253 | 253
2017-10-06 10:00 | 255 | 255
2017-10-06 10:30 | 243 | 243
2017-10-06 11:00 | 236 | 236
2017-10-06 11:30 | 239 | 239
2017-10-06 12:00 | 240 | 240
2017-10-06 12:30 | 244 | 244
2017-10-06 13:00 | 259 | 259
2017-10-06 13:30 | 270 | 270
2017-10-06 14:00 | 288 | 287
2017-10-06 14:30 | 288 | 287
2017-10-06 15:00 | 278 | 277
2017-10-06 15:30 | 272 | 272
2017-10-06 16:00 | 277 | 277
2017-10-06 16:30 | 275 | 275
2017-10-06 17:00 | 274 | 274
2017-10-06 17:30 | 272 | 272
2017-10-06 18:00 | 276 | 276
2017-10-06 18:30 | 280 | 280
2017-10-06 19:00 | 271 | 271
2017-10-06 19:30 | 269 | 269
2017-10-06 20:00 | 263 | 263
2017-10-06 20:30 | 250 | 249
2017-10-06 21:00 | 237 | 236
2017-10-06 21:30 | 224 | 223
2017-10-06 22:00 | 223 | 223
2017-10-06 22:30 | 221 | 221
2017-10-06 23:00 | 202 | 202
2017-10-06 23:30 | 188 | 188
2017-10-07 | 175 | 175
2017-10-07 00:30 | 163 | 163
2017-10-07 01:00 | 161 | 161
2017-10-07 01:30 | 158 | 158
2017-10-07 02:00 | 156 | 156
2017-10-07 02:30 | 159 | 159
2017-10-07 03:00 | 160 | 160
2017-10-07 03:30 | 162 | 162
2017-10-07 04:00 | 164 | 163
2017-10-07 04:30 | 165 | 165
2017-10-07 05:00 | 167 | 167
2017-10-07 05:30 | 171 | 171
2017-10-07 06:00 | 177 | 177
2017-10-07 06:30 | 185 | 185
2017-10-07 07:00 | 201 | 201
2017-10-07 07:30 | 219 | 218
2017-10-07 08:00 | 213 | 213
2017-10-07 08:30 | 213 | 213
2017-10-07 09:00 | 217 | 217
2017-10-07 09:30 | 222 | 222
2017-10-07 10:00 | 220 | 220
2017-10-07 10:30 | 202 | 201
2017-10-07 11:00 | 206 | 205
2017-10-07 11:30 | 215 | 214
2017-10-07 12:00 | 213 | 212
2017-10-07 12:30 | 220 | 219
2017-10-07 13:00 | 221 | 221
2017-10-07 13:30 | 217 | 216
2017-10-07 14:00 | 217 | 216
2017-10-07 14:30 | 214 | 213
2017-10-07 15:00 | 220 | 219
2017-10-07 15:30 | 218 | 218
2017-10-07 16:00 | 224 | 224
2017-10-07 16:30 | 231 | 230
2017-10-07 17:00 | 232 | 232
2017-10-07 17:30 | 234 | 234
2017-10-07 18:00 | 240 | 240
2017-10-07 18:30 | 243 | 243
2017-10-07 19:00 | 237 | 237
2017-10-07 19:30 | 233 | 233
2017-10-07 20:00 | 227 | 226
2017-10-07 20:30 | 222 | 221
2017-10-07 21:00 | 217 | 216
2017-10-07 21:30 | 212 | 212
2017-10-07 22:00 | 207 | 207
2017-10-07 22:30 | 206 | 206
2017-10-07 23:00 | 196 | 196
2017-10-07 23:30 | 186 | 186
2017-10-08 | 174 | 174
2017-10-08 00:30 | 169 | 168
2017-10-08 01:00 | 163 | 163
2017-10-08 01:30 | 157 | 157
2017-10-08 02:00 | 152 | 152
2017-10-08 02:30 | 152 | 152
2017-10-08 03:00 | 151 | 151
2017-10-08 03:30 | 151 | 151
2017-10-08 04:00 | 146 | 146
2017-10-08 04:30 | 145 | 145
2017-10-08 05:00 | 149 | 149
2017-10-08 05:30 | 156 | 156
2017-10-08 06:00 | 168 | 168
2017-10-08 06:30 | 180 | 180
2017-10-08 07:00 | 194 | 194
2017-10-08 07:30 | 202 | 202
2017-10-08 08:00 | 202 | 202
2017-10-08 08:30 | 202 | 202
2017-10-08 09:00 | 209 | 208
2017-10-08 09:30 | 212 | 212
2017-10-08 10:00 | 224 | 223
2017-10-08 10:30 | 225 | 224
2017-10-08 11:00 | 220 | 220
2017-10-08 11:30 | 214 | 214
2017-10-08 12:00 | 194 | 194
2017-10-08 12:30 | 197 | 196
2017-10-08 13:00 | 199 | 199
2017-10-08 13:30 | 203 | 203
2017-10-08 14:00 | 216 | 216
2017-10-08 14:30 | 225 | 225
2017-10-08 15:00 | 231 | 231
2017-10-08 15:30 | 230 | 230
2017-10-08 16:00 | 229 | 229
2017-10-08 16:30 | 235 | 235
2017-10-08 17:00 | 236 | 236
2017-10-08 17:30 | 242 | 242
2017-10-08 18:00 | 254 | 253
2017-10-08 18:30 | 255 | 253
2017-10-08 19:00 | 246 | 244
2017-10-08 19:30 | 241 | 241
2017-10-08 20:00 | 235 | 235
2017-10-08 20:30 | 225 | 224
2017-10-08 21:00 | 218 | 217
2017-10-08 21:30 | 214 | 213
2017-10-08 22:00 | 210 | 208
2017-10-08 22:30 | 207 | 206
2017-10-08 23:00 | 199 | 197
2017-10-08 23:30 | 192 | 189
2017-10-09 | 181 | 178
2017-10-09 00:30 | 173 | 169
2017-10-09 01:00 | 167 | 163
2017-10-09 01:30 | 160 | 158
2017-10-09 02:00 | 158 | 156
2017-10-09 02:30 | 152 | 149
2017-10-09 03:00 | 154 | 152
2017-10-09 03:30 | 155 | 153
2017-10-09 04:00 | 163 | 162
2017-10-09 04:30 | 168 | 167
2017-10-09 05:00 | 180 | 179
2017-10-09 05:30 | 193 | 192
2017-10-09 06:00 | 203 | 203
2017-10-09 06:30 | 236 | 235
2017-10-09 07:00 | 258 | 256
2017-10-09 07:30 | 270 | 269
2017-10-09 08:00 | 273 | 273
2017-10-09 08:30 | 260 | 260
2017-10-09 09:00 | 239 | 239
2017-10-09 09:30 | 240 | 240
2017-10-09 10:00 | 234 | 234
2017-10-09 10:30 | 233 | 233
2017-10-09 11:00 | 237 | 237
2017-10-09 11:30 | 249 | 249
2017-10-09 12:00 | 247 | 247
2017-10-09 12:30 | 248 | 247
2017-10-09 13:00 | 253 | 253
2017-10-09 13:30 | 272 | 272
2017-10-09 14:00 | 282 | 282
2017-10-09 14:30 | 288 | 288
2017-10-09 15:00 | 296 | 295
2017-10-09 15:30 | 309 | 309
2017-10-09 16:00 | 316 | 316
2017-10-09 16:30 | 321 | 321
2017-10-09 17:00 | 320 | 320
2017-10-09 17:30 | 319 | 319
2017-10-09 18:00 | 328 | 328
2017-10-09 18:30 | 331 | 331
2017-10-09 19:00 | 319 | 319
2017-10-09 19:30 | 310 | 309
2017-10-09 20:00 | 299 | 298
2017-10-09 20:30 | 285 | 283
2017-10-09 21:00 | 270 | 267
2017-10-09 21:30 | 237 | 234
2017-10-09 22:00 | 224 | 224
2017-10-09 22:30 | 218 | 218
2017-10-09 23:00 | 210 | 209
2017-10-09 23:30 | 198 | 197
2017-10-10 | 184 | 182
2017-10-10 00:30 | 175 | 173
2017-10-10 01:00 | 171 | 168
2017-10-10 01:30 | 167 | 164
2017-10-10 02:00 | 167 | 163
2017-10-10 02:30 | 164 | 161
2017-10-10 03:00 | 162 | 159
2017-10-10 03:30 | 165 | 161
2017-10-10 04:00 | 166 | 162
2017-10-10 04:30 | 172 | 169
2017-10-10 05:00 | 179 | 176
2017-10-10 05:30 | 195 | 193
2017-10-10 06:00 | 207 | 207
2017-10-10 06:30 | 219 | 219
2017-10-10 07:00 | 238 | 238
2017-10-10 07:30 | 249 | 248
2017-10-10 08:00 | 254 | 254
2017-10-10 08:30 | 258 | 258
2017-10-10 09:00 | 256 | 256
2017-10-10 09:30 | 280 | 280
2017-10-10 10:00 | 279 | 279
2017-10-10 10:30 | 267 | 266
2017-10-10 11:00 | 273 | 273
2017-10-10 11:30 | 262 | 262
2017-10-10 12:00 | 275 | 275
2017-10-10 12:30 | 284 | 284
2017-10-10 13:00 | 270 | 269
2017-10-10 13:30 | 282 | 282
2017-10-10 14:00 | 300 | 299
2017-10-10 14:30 | 299 | 299
2017-10-10 15:00 | 305 | 305
2017-10-10 15:30 | 317 | 316
2017-10-10 16:00 | 326 | 326
2017-10-10 16:30 | 330 | 329
2017-10-10 17:00 | 328 | 326
2017-10-10 17:30 | 328 | 326
2017-10-10 18:00 | 333 | 331
2017-10-10 18:30 | 332 | 331
2017-10-10 19:00 | 322 | 320
2017-10-10 19:30 | 315 | 313
2017-10-10 20:00 | 299 | 298
2017-10-10 20:30 | 290 | 289
2017-10-10 21:00 | 277 | 275
2017-10-10 21:30 | 239 | 238
2017-10-10 22:00 | 229 | 229
2017-10-10 22:30 | 225 | 224
2017-10-10 23:00 | 209 | 208
2017-10-10 23:30 | 201 | 201
2017-10-11 | 188 | 188
2017-10-11 00:30 | 171 | 171
2017-10-11 01:00 | 167 | 166
2017-10-11 01:30 | 156 | 155
2017-10-11 02:00 | 154 | 153
2017-10-11 02:30 | 148 | 147
2017-10-11 03:00 | 146 | 146
2017-10-11 03:30 | 148 | 148
2017-10-11 04:00 | 154 | 154
2017-10-11 04:30 | 158 | 158
2017-10-11 05:00 | 173 | 173
2017-10-11 05:30 | 193 | 193
2017-10-11 06:00 | 208 | 208
2017-10-11 06:30 | 232 | 232
2017-10-11 07:00 | 274 | 272
2017-10-11 07:30 | 286 | 283
2017-10-11 08:00 | 291 | 289
2017-10-11 08:30 | 294 | 292
2017-10-11 09:00 | 298 | 297
2017-10-11 09:30 | 299 | 298
2017-10-11 10:00 | 298 | 297
2017-10-11 10:30 | 291 | 290
2017-10-11 11:00 | 279 | 277
2017-10-11 11:30 | 274 | 273
2017-10-11 12:00 | 278 | 277
2017-10-11 12:30 | 280 | 279
2017-10-11 13:00 | 285 | 285
2017-10-11 13:30 | 292 | 291
2017-10-11 14:00 | 293 | 292
2017-10-11 14:30 | 298 | 297
2017-10-11 15:00 | 315 | 313
2017-10-11 15:30 | 314 | 312
2017-10-11 16:00 | 313 | 311
2017-10-11 16:30 | 320 | 318
2017-10-11 17:00 | 322 | 320
2017-10-11 17:30 | 321 | 319
2017-10-11 18:00 | 325 | 323
2017-10-11 18:30 | 326 | 325
2017-10-11 19:00 | 315 | 313
2017-10-11 19:30 | 306 | 305
2017-10-11 20:00 | 297 | 296
2017-10-11 20:30 | 281 | 280
2017-10-11 21:00 | 265 | 265
2017-10-11 21:30 | 251 | 251
2017-10-11 22:00 | 239 | 239
2017-10-11 22:30 | 239 | 239
2017-10-11 23:00 | 228 | 228
2017-10-11 23:30 | 209 | 209
2017-10-12 | 194 | 193
2017-10-12 00:30 | 183 | 183
2017-10-12 01:00 | 161 | 161
2017-10-12 01:30 | 149 | 148
2017-10-12 02:00 | 153 | 152
2017-10-12 02:30 | 152 | 151
2017-10-12 03:00 | 143 | 142
2017-10-12 03:30 | 143 | 142
2017-10-12 04:00 | 146 | 145
2017-10-12 04:30 | 151 | 151
2017-10-12 05:00 | 172 | 172
2017-10-12 05:30 | 205 | 205
2017-10-12 06:00 | 229 | 229
2017-10-12 06:30 | 248 | 248
2017-10-12 07:00 | 270 | 270
2017-10-12 07:30 | 285 | 285
2017-10-12 08:00 | 291 | 291
2017-10-12 08:30 | 292 | 292
2017-10-12 09:00 | 296 | 295
2017-10-12 09:30 | 297 | 296
2017-10-12 10:00 | 300 | 299
2017-10-12 10:30 | 297 | 296
2017-10-12 11:00 | 289 | 288
2017-10-12 11:30 | 291 | 290
2017-10-12 12:00 | 292 | 290
2017-10-12 12:30 | 290 | 289
2017-10-12 13:00 | 288 | 287
2017-10-12 13:30 | 288 | 286
2017-10-12 14:00 | 290 | 289
2017-10-12 14:30 | 287 | 286
2017-10-12 15:00 | 285 | 283
2017-10-12 15:30 | 294 | 292
2017-10-12 16:00 | 299 | 298
2017-10-12 16:30 | 302 | 300
2017-10-12 17:00 | 305 | 303
2017-10-12 17:30 | 309 | 307
2017-10-12 18:00 | 318 | 316
2017-10-12 18:30 | 322 | 320
2017-10-12 19:00 | 311 | 310
2017-10-12 19:30 | 305 | 304
2017-10-12 20:00 | 297 | 295
2017-10-12 20:30 | 281 | 281
2017-10-12 21:00 | 266 | 266
2017-10-12 21:30 | 250 | 250
2017-10-12 22:00 | 239 | 239
2017-10-12 22:30 | 240 | 239
2017-10-12 23:00 | 228 | 227
2017-10-12 23:30 | 209 | 207
2017-10-13 | 193 | 191
2017-10-13 00:30 | 181 | 178
2017-10-13 01:00 | 164 | 161
2017-10-13 01:30 | 154 | 152
2017-10-13 02:00 | 152 | 150
2017-10-13 02:30 | 151 | 150
2017-10-13 03:00 | 146 | 145
2017-10-13 03:30 | 146 | 144
2017-10-13 04:00 | 146 | 144
2017-10-13 04:30 | 153 | 152
2017-10-13 05:00 | 175 | 174
2017-10-13 05:30 | 206 | 205
2017-10-13 06:00 | 222 | 222
2017-10-13 06:30 | 239 | 239
2017-10-13 07:00 | 256 | 255
2017-10-13 07:30 | 258 | 258
2017-10-13 08:00 | 262 | 262
2017-10-13 08:30 | 263 | 263
2017-10-13 09:00 | 265 | 265
2017-10-13 09:30 | 265 | 265
2017-10-13 10:00 | 267 | 267
2017-10-13 10:30 | 268 | 267
2017-10-13 11:00 | 270 | 270
2017-10-13 11:30 | 273 | 273
2017-10-13 12:00 | 276 | 275
2017-10-13 12:30 | 271 | 270
2017-10-13 13:00 | 275 | 275
2017-10-13 13:30 | 280 | 280
2017-10-13 14:00 | 280 | 279
2017-10-13 14:30 | 293 | 293
2017-10-13 15:00 | 306 | 305
2017-10-13 15:30 | 312 | 311
2017-10-13 16:00 | 313 | 313
2017-10-13 16:30 | 311 | 310
2017-10-13 17:00 | 305 | 305
2017-10-13 17:30 | 303 | 303
2017-10-13 18:00 | 309 | 309
2017-10-13 18:30 | 312 | 312
2017-10-13 19:00 | 304 | 304
2017-10-13 19:30 | 301 | 301
2017-10-13 20:00 | 295 | 292
2017-10-13 20:30 | 275 | 274
2017-10-13 21:00 | 261 | 260
2017-10-13 21:30 | 246 | 245
2017-10-13 22:00 | 237 | 237
2017-10-13 22:30 | 239 | 239
2017-10-13 23:00 | 226 | 226
2017-10-13 23:30 | 206 | 206
2017-10-14 | 191 | 191
2017-10-14 00:30 | 179 | 179
2017-10-14 01:00 | 166 | 166
2017-10-14 01:30 | 161 | 161
2017-10-14 02:00 | 157 | 157
2017-10-14 02:30 | 154 | 154
2017-10-14 03:00 | 152 | 152
2017-10-14 03:30 | 151 | 151
2017-10-14 04:00 | 156 | 156
2017-10-14 04:30 | 160 | 160
2017-10-14 05:00 | 166 | 165
2017-10-14 05:30 | 191 | 191
2017-10-14 06:00 | 212 | 212
2017-10-14 06:30 | 201 | 201
2017-10-14 07:00 | 211 | 211
2017-10-14 07:30 | 224 | 224
2017-10-14 08:00 | 238 | 238
2017-10-14 08:30 | 256 | 256
2017-10-14 09:00 | 268 | 267
2017-10-14 09:30 | 267 | 266
2017-10-14 10:00 | 269 | 268
2017-10-14 10:30 | 262 | 262
2017-10-14 11:00 | 255 | 255
2017-10-14 11:30 | 253 | 252
2017-10-14 12:00 | 243 | 242
2017-10-14 12:30 | 237 | 236
2017-10-14 13:00 | 235 | 235
2017-10-14 13:30 | 242 | 242
2017-10-14 14:00 | 243 | 242
2017-10-14 14:30 | 241 | 240
2017-10-14 15:00 | 244 | 243
2017-10-14 15:30 | 250 | 249
2017-10-14 16:00 | 259 | 258
2017-10-14 16:30 | 271 | 270
2017-10-14 17:00 | 272 | 271
2017-10-14 17:30 | 274 | 273
2017-10-14 18:00 | 276 | 275
2017-10-14 18:30 | 274 | 274
2017-10-14 19:00 | 264 | 264
2017-10-14 19:30 | 257 | 257
2017-10-14 20:00 | 244 | 244
2017-10-14 20:30 | 240 | 240
2017-10-14 21:00 | 232 | 232
2017-10-14 21:30 | 220 | 220
2017-10-14 22:00 | 217 | 217
2017-10-14 22:30 | 218 | 218
2017-10-14 23:00 | 206 | 206
2017-10-14 23:30 | 192 | 191
2017-10-15 | 186 | 185
2017-10-15 00:30 | 178 | 177
2017-10-15 01:00 | 172 | 170
2017-10-15 01:30 | 164 | 163
2017-10-15 02:00 | 164 | 164
2017-10-15 02:30 | 163 | 162
2017-10-15 03:00 | 163 | 163
2017-10-15 03:30 | 164 | 163
2017-10-15 04:00 | 164 | 164
2017-10-15 04:30 | 167 | 166
2017-10-15 05:00 | 171 | 170
2017-10-15 05:30 | 186 | 186
2017-10-15 06:00 | 189 | 189
2017-10-15 06:30 | 190 | 189
2017-10-15 07:00 | 201 | 201
2017-10-15 07:30 | 218 | 218
2017-10-15 08:00 | 227 | 227
2017-10-15 08:30 | 233 | 233
2017-10-15 09:00 | 233 | 233
2017-10-15 09:30 | 236 | 236
2017-10-15 10:00 | 245 | 245
2017-10-15 10:30 | 244 | 244
2017-10-15 11:00 | 230 | 230
2017-10-15 11:30 | 235 | 235
2017-10-15 12:00 | 231 | 231
2017-10-15 12:30 | 237 | 237
2017-10-15 13:00 | 243 | 243
2017-10-15 13:30 | 242 | 242
2017-10-15 14:00 | 246 | 246
2017-10-15 14:30 | 249 | 249
2017-10-15 15:00 | 253 | 253
2017-10-15 15:30 | 254 | 254
2017-10-15 16:00 | 256 | 256
2017-10-15 16:30 | 264 | 264
2017-10-15 17:00 | 266 | 266
2017-10-15 17:30 | 271 | 270
2017-10-15 18:00 | 279 | 279
2017-10-15 18:30 | 279 | 279
2017-10-15 19:00 | 270 | 270
2017-10-15 19:30 | 264 | 263
2017-10-15 20:00 | 264 | 264
2017-10-15 20:30 | 261 | 260
2017-10-15 21:00 | 251 | 250
2017-10-15 21:30 | 243 | 243
2017-10-15 22:00 | 237 | 237
2017-10-15 22:30 | 235 | 235
2017-10-15 23:00 | 226 | 226
2017-10-15 23:30 | 215 | 214
2017-10-16 | 201 | 201
2017-10-16 00:30 | 196 | 195
2017-10-16 01:00 | 192 | 191
2017-10-16 01:30 | 187 | 186
2017-10-16 02:00 | 182 | 181
2017-10-16 02:30 | 179 | 177
2017-10-16 03:00 | 181 | 180
2017-10-16 03:30 | 183 | 181
2017-10-16 04:00 | 185 | 184
2017-10-16 04:30 | 192 | 191
2017-10-16 05:00 | 204 | 203
2017-10-16 05:30 | 222 | 222
2017-10-16 06:00 | 246 | 245
2017-10-16 06:30 | 265 | 265
2017-10-16 07:00 | 282 | 282
2017-10-16 07:30 | 289 | 289
2017-10-16 08:00 | 295 | 295
2017-10-16 08:30 | 302 | 302
2017-10-16 09:00 | 305 | 303
2017-10-16 09:30 | 296 | 294
2017-10-16 10:00 | 297 | 295
2017-10-16 10:30 | 286 | 284
2017-10-16 11:00 | 266 | 264
2017-10-16 11:30 | 252 | 252
2017-10-16 12:00 | 253 | 253
2017-10-16 12:30 | 252 | 252
2017-10-16 13:00 | 253 | 253
2017-10-16 13:30 | 254 | 254
2017-10-16 14:00 | 255 | 254
2017-10-16 14:30 | 261 | 261
2017-10-16 15:00 | 263 | 262
2017-10-16 15:30 | 264 | 264
2017-10-16 16:00 | 271 | 271
2017-10-16 16:30 | 284 | 284
2017-10-16 17:00 | 291 | 290
2017-10-16 17:30 | 297 | 296
2017-10-16 18:00 | 304 | 303
2017-10-16 18:30 | 303 | 302
2017-10-16 19:00 | 291 | 289
2017-10-16 19:30 | 285 | 283
2017-10-16 20:00 | 281 | 278
2017-10-16 20:30 | 277 | 273
2017-10-16 21:00 | 267 | 264
2017-10-16 21:30 | 250 | 249
2017-10-16 22:00 | 241 | 239
2017-10-16 22:30 | 239 | 236
2017-10-16 23:00 | 230 | 227
2017-10-16 23:30 | 216 | 213
2017-10-17 | 203 | 200
2017-10-17 00:30 | 195 | 192
2017-10-17 01:00 | 190 | 187
2017-10-17 01:30 | 185 | 181
2017-10-17 02:00 | 183 | 179
2017-10-17 02:30 | 176 | 172
2017-10-17 03:00 | 184 | 180
2017-10-17 03:30 | 185 | 181
2017-10-17 04:00 | 185 | 182
2017-10-17 04:30 | 187 | 184
2017-10-17 05:00 | 195 | 192
2017-10-17 05:30 | 207 | 205
2017-10-17 06:00 | 225 | 224
2017-10-17 06:30 | 241 | 239
2017-10-17 07:00 | 260 | 258
2017-10-17 07:30 | 265 | 265
2017-10-17 08:00 | 282 | 282
2017-10-17 08:30 | 278 | 278
2017-10-17 09:00 | 283 | 283
2017-10-17 09:30 | 278 | 278
2017-10-17 10:00 | 270 | 270
2017-10-17 10:30 | 278 | 278
2017-10-17 11:00 | 275 | 275
2017-10-17 11:30 | 261 | 261
2017-10-17 12:00 | 273 | 273
2017-10-17 12:30 | 264 | 263
2017-10-17 13:00 | 266 | 265
2017-10-17 13:30 | 265 | 265
2017-10-17 14:00 | 262 | 262
2017-10-17 14:30 | 261 | 261
2017-10-17 15:00 | 262 | 262
2017-10-17 15:30 | 269 | 269
2017-10-17 16:00 | 278 | 278
2017-10-17 16:30 | 286 | 286
2017-10-17 17:00 | 291 | 291
2017-10-17 17:30 | 294 | 294
2017-10-17 18:00 | 298 | 298
2017-10-17 18:30 | 300 | 299
2017-10-17 19:00 | 289 | 288
2017-10-17 19:30 | 281 | 281
2017-10-17 20:00 | 273 | 273
2017-10-17 20:30 | 260 | 260
2017-10-17 21:00 | 249 | 249
2017-10-17 21:30 | 240 | 240
2017-10-17 22:00 | 227 | 227
2017-10-17 22:30 | 226 | 226
2017-10-17 23:00 | 219 | 218
2017-10-17 23:30 | 209 | 208
2017-10-18 | 194 | 193
2017-10-18 00:30 | 185 | 184
2017-10-18 01:00 | 180 | 178
2017-10-18 01:30 | 179 | 177
2017-10-18 02:00 | 175 | 173
2017-10-18 02:30 | 177 | 175
2017-10-18 03:00 | 153 | 150
2017-10-18 03:30 | 170 | 168
2017-10-18 04:00 | 175 | 173
2017-10-18 04:30 | 185 | 183
2017-10-18 05:00 | 194 | 193
2017-10-18 05:30 | 209 | 208
2017-10-18 06:00 | 234 | 233
2017-10-18 06:30 | 250 | 248
2017-10-18 07:00 | 261 | 260
2017-10-18 07:30 | 263 | 262
2017-10-18 08:00 | 264 | 264
2017-10-18 08:30 | 265 | 265
2017-10-18 09:00 | 272 | 271
2017-10-18 09:30 | 269 | 268
2017-10-18 10:00 | 270 | 269
2017-10-18 10:30 | 270 | 270
2017-10-18 11:00 | 261 | 260
2017-10-18 11:30 | 253 | 252
2017-10-18 12:00 | 247 | 246
2017-10-18 12:30 | 247 | 246
2017-10-18 13:00 | 255 | 254
2017-10-18 13:30 | 251 | 250
2017-10-18 14:00 | 257 | 256
2017-10-18 14:30 | 265 | 264
2017-10-18 15:00 | 272 | 271
2017-10-18 15:30 | 277 | 276
2017-10-18 16:00 | 279 | 278
2017-10-18 16:30 | 292 | 290
2017-10-18 17:00 | 299 | 297
2017-10-18 17:30 | 303 | 302
2017-10-18 18:00 | 308 | 307
2017-10-18 18:30 | 309 | 308
2017-10-18 19:00 | 301 | 299
2017-10-18 19:30 | 290 | 288
2017-10-18 20:00 | 282 | 279
2017-10-18 20:30 | 273 | 269
2017-10-18 21:00 | 255 | 254
2017-10-18 21:30 | 248 | 247
2017-10-18 22:00 | 249 | 249
2017-10-18 22:30 | 239 | 239
2017-10-18 23:00 | 229 | 228
2017-10-18 23:30 | 214 | 212
2017-10-19 | 198 | 196
2017-10-19 00:30 | 195 | 192
2017-10-19 01:00 | 190 | 187
2017-10-19 01:30 | 188 | 185
2017-10-19 02:00 | 188 | 184
2017-10-19 02:30 | 184 | 180
2017-10-19 03:00 | 185 | 181
2017-10-19 03:30 | 187 | 183
2017-10-19 04:00 | 191 | 188
2017-10-19 04:30 | 196 | 194
2017-10-19 05:00 | 204 | 201
2017-10-19 05:30 | 212 | 209
2017-10-19 06:00 | 227 | 225
2017-10-19 06:30 | 245 | 241
2017-10-19 07:00 | 251 | 248
2017-10-19 07:30 | 252 | 250
2017-10-19 08:00 | 253 | 251
2017-10-19 08:30 | 258 | 257
2017-10-19 09:00 | 259 | 258
2017-10-19 09:30 | 258 | 258
2017-10-19 10:00 | 256 | 256
2017-10-19 10:30 | 253 | 252
2017-10-19 11:00 | 251 | 251
2017-10-19 11:30 | 252 | 252
2017-10-19 12:00 | 247 | 247
2017-10-19 12:30 | 254 | 253
2017-10-19 13:00 | 252 | 251
2017-10-19 13:30 | 255 | 255
2017-10-19 14:00 | 259 | 259
2017-10-19 14:30 | 261 | 260
2017-10-19 15:00 | 267 | 267
2017-10-19 15:30 | 278 | 277
2017-10-19 16:00 | 286 | 282
2017-10-19 16:30 | 290 | 286
2017-10-19 17:00 | 288 | 285
2017-10-19 17:30 | 296 | 294
2017-10-19 18:00 | 301 | 299
2017-10-19 18:30 | 306 | 304
2017-10-19 19:00 | 301 | 299
2017-10-19 19:30 | 295 | 293
2017-10-19 20:00 | 280 | 280
2017-10-19 20:30 | 269 | 269
2017-10-19 21:00 | 257 | 257
2017-10-19 21:30 | 249 | 249
2017-10-19 22:00 | 244 | 244
2017-10-19 22:30 | 239 | 239
2017-10-19 23:00 | 225 | 225
2017-10-19 23:30 | 218 | 217
2017-10-20 | 203 | 203
2017-10-20 00:30 | 197 | 196
2017-10-20 01:00 | 192 | 191
2017-10-20 01:30 | 190 | 189
2017-10-20 02:00 | 187 | 186
2017-10-20 02:30 | 185 | 184
2017-10-20 03:00 | 186 | 185
2017-10-20 03:30 | 189 | 188
2017-10-20 04:00 | 190 | 189
2017-10-20 04:30 | 193 | 192
2017-10-20 05:00 | 201 | 200
2017-10-20 05:30 | 224 | 224
2017-10-20 06:00 | 241 | 241
2017-10-20 06:30 | 259 | 257
2017-10-20 07:00 | 268 | 266
2017-10-20 07:30 | 274 | 273
2017-10-20 08:00 | 276 | 276
2017-10-20 08:30 | 272 | 272
2017-10-20 09:00 | 275 | 274
2017-10-20 09:30 | 278 | 278
2017-10-20 10:00 | 281 | 281
2017-10-20 10:30 | 285 | 285
2017-10-20 11:00 | 278 | 278
2017-10-20 11:30 | 273 | 273
2017-10-20 12:00 | 271 | 271
2017-10-20 12:30 | 270 | 270
2017-10-20 13:00 | 276 | 276
2017-10-20 13:30 | 276 | 276
2017-10-20 14:00 | 274 | 274
2017-10-20 14:30 | 273 | 273
2017-10-20 15:00 | 276 | 276
2017-10-20 15:30 | 284 | 284
2017-10-20 16:00 | 294 | 294
2017-10-20 16:30 | 297 | 297
2017-10-20 17:00 | 276 | 275
2017-10-20 17:30 | 276 | 275
2017-10-20 18:00 | 285 | 284
2017-10-20 18:30 | 286 | 285
2017-10-20 19:00 | 281 | 280
2017-10-20 19:30 | 279 | 279
2017-10-20 20:00 | 274 | 274
2017-10-20 20:30 | 264 | 264
2017-10-20 21:00 | 257 | 256
2017-10-20 21:30 | 250 | 250
2017-10-20 22:00 | 245 | 244
2017-10-20 22:30 | 244 | 243
2017-10-20 23:00 | 231 | 230
2017-10-20 23:30 | 221 | 219
2017-10-21 | 208 | 206
2017-10-21 00:30 | 203 | 200
2017-10-21 01:00 | 200 | 197
2017-10-21 01:30 | 195 | 192
2017-10-21 02:00 | 192 | 189
2017-10-21 02:30 | 187 | 183
2017-10-21 03:00 | 184 | 180
2017-10-21 03:30 | 187 | 183
2017-10-21 04:00 | 190 | 187
2017-10-21 04:30 | 194 | 190
2017-10-21 05:00 | 198 | 194
2017-10-21 05:30 | 203 | 199
2017-10-21 06:00 | 214 | 212
2017-10-21 06:30 | 224 | 222
2017-10-21 07:00 | 243 | 241
2017-10-21 07:30 | 253 | 252
2017-10-21 08:00 | 262 | 261
2017-10-21 08:30 | 269 | 268
2017-10-21 09:00 | 279 | 277
2017-10-21 09:30 | 273 | 272
2017-10-21 10:00 | 266 | 265
2017-10-21 10:30 | 264 | 263
2017-10-21 11:00 | 264 | 262
2017-10-21 11:30 | 264 | 262
2017-10-21 12:00 | 261 | 258
2017-10-21 12:30 | 254 | 252
2017-10-21 13:00 | 252 | 251
2017-10-21 13:30 | 253 | 252
2017-10-21 14:00 | 251 | 250
2017-10-21 14:30 | 251 | 250
2017-10-21 15:00 | 249 | 248
2017-10-21 15:30 | 252 | 251
2017-10-21 16:00 | 256 | 254
2017-10-21 16:30 | 265 | 263
2017-10-21 17:00 | 267 | 265
2017-10-21 17:30 | 268 | 267
2017-10-21 18:00 | 274 | 274
2017-10-21 18:30 | 282 | 281
2017-10-21 19:00 | 275 | 274
2017-10-21 19:30 | 271 | 270
2017-10-21 20:00 | 263 | 262
2017-10-21 20:30 | 254 | 253
2017-10-21 21:00 | 246 | 246
2017-10-21 21:30 | 240 | 240
2017-10-21 22:00 | 238 | 238
2017-10-21 22:30 | 238 | 238
2017-10-21 23:00 | 229 | 229
2017-10-21 23:30 | 219 | 219
2017-10-22 | 202 | 201
2017-10-22 00:30 | 197 | 196
2017-10-22 01:00 | 193 | 191
2017-10-22 01:30 | 188 | 187
2017-10-22 02:00 | 185 | 183
2017-10-22 02:30 | 182 | 180
2017-10-22 03:00 | 182 | 181
2017-10-22 03:30 | 182 | 180
2017-10-22 04:00 | 183 | 181
2017-10-22 04:30 | 184 | 182
2017-10-22 05:00 | 185 | 183
2017-10-22 05:30 | 188 | 186
2017-10-22 06:00 | 188 | 186
2017-10-22 06:30 | 188 | 186
2017-10-22 07:00 | 197 | 196
2017-10-22 07:30 | 203 | 203
2017-10-22 08:00 | 206 | 206
2017-10-22 08:30 | 207 | 207
2017-10-22 09:00 | 208 | 208
2017-10-22 09:30 | 207 | 207
2017-10-22 10:00 | 207 | 207
2017-10-22 10:30 | 213 | 213
2017-10-22 11:00 | 217 | 217
2017-10-22 11:30 | 218 | 218
2017-10-22 12:00 | 218 | 218
2017-10-22 12:30 | 216 | 215
2017-10-22 13:00 | 208 | 208
2017-10-22 13:30 | 207 | 206
2017-10-22 14:00 | 209 | 208
2017-10-22 14:30 | 216 | 215
2017-10-22 15:00 | 223 | 222
2017-10-22 15:30 | 236 | 235
2017-10-22 16:00 | 245 | 244
2017-10-22 16:30 | 257 | 256
2017-10-22 17:00 | 264 | 263
2017-10-22 17:30 | 269 | 269
2017-10-22 18:00 | 279 | 279
2017-10-22 18:30 | 284 | 282
2017-10-22 19:00 | 277 | 275
2017-10-22 19:30 | 274 | 271
2017-10-22 20:00 | 271 | 268
2017-10-22 20:30 | 261 | 259
2017-10-22 21:00 | 250 | 248
2017-10-22 21:30 | 239 | 239
2017-10-22 22:00 | 235 | 235
2017-10-22 22:30 | 236 | 236
2017-10-22 23:00 | 229 | 228
2017-10-22 23:30 | 218 | 217
2017-10-23 | 204 | 203
2017-10-23 00:30 | 194 | 193
2017-10-23 01:00 | 187 | 185
2017-10-23 01:30 | 183 | 181
2017-10-23 02:00 | 180 | 179
2017-10-23 02:30 | 179 | 178
2017-10-23 03:00 | 179 | 177
2017-10-23 03:30 | 179 | 177
2017-10-23 04:00 | 186 | 184
2017-10-23 04:30 | 192 | 190
2017-10-23 05:00 | 201 | 200
2017-10-23 05:30 | 215 | 214
2017-10-23 06:00 | 237 | 236
2017-10-23 06:30 | 256 | 256
2017-10-23 07:00 | 265 | 264
2017-10-23 07:30 | 267 | 267
2017-10-23 08:00 | 258 | 258
2017-10-23 08:30 | 252 | 251
2017-10-23 09:00 | 260 | 260
2017-10-23 09:30 | 290 | 290
2017-10-23 10:00 | 309 | 309
2017-10-23 10:30 | 314 | 314
2017-10-23 11:00 | 308 | 307
2017-10-23 11:30 | 303 | 303
2017-10-23 12:00 | 287 | 287
2017-10-23 12:30 | 282 | 282
2017-10-23 13:00 | 274 | 274
2017-10-23 13:30 | 261 | 260
2017-10-23 14:00 | 256 | 256
2017-10-23 14:30 | 255 | 254
2017-10-23 15:00 | 275 | 274
2017-10-23 15:30 | 285 | 284
2017-10-23 16:00 | 288 | 287
2017-10-23 16:30 | 301 | 300
2017-10-23 17:00 | 302 | 301
2017-10-23 17:30 | 289 | 287
2017-10-23 18:00 | 298 | 297
2017-10-23 18:30 | 301 | 300
2017-10-23 19:00 | 295 | 293
2017-10-23 19:30 | 294 | 292
2017-10-23 20:00 | 291 | 289
2017-10-23 20:30 | 275 | 274
2017-10-23 21:00 | 263 | 262
2017-10-23 21:30 | 255 | 254
2017-10-23 22:00 | 247 | 245
2017-10-23 22:30 | 242 | 241
2017-10-23 23:00 | 230 | 228
2017-10-23 23:30 | 219 | 217
2017-10-24 | 207 | 204
2017-10-24 00:30 | 203 | 200
2017-10-24 01:00 | 195 | 191
2017-10-24 01:30 | 190 | 186
2017-10-24 02:00 | 188 | 184
2017-10-24 02:30 | 187 | 182
2017-10-24 03:00 | 188 | 184
2017-10-24 03:30 | 189 | 185
2017-10-24 04:00 | 193 | 188
2017-10-24 04:30 | 198 | 194
2017-10-24 05:00 | 210 | 206
2017-10-24 05:30 | 224 | 221
2017-10-24 06:00 | 238 | 237
2017-10-24 06:30 | 250 | 250
2017-10-24 07:00 | 260 | 260
2017-10-24 07:30 | 257 | 257
2017-10-24 08:00 | 251 | 251
2017-10-24 08:30 | 245 | 244
2017-10-24 09:00 | 244 | 244
2017-10-24 09:30 | 242 | 242
2017-10-24 10:00 | 238 | 238
2017-10-24 10:30 | 237 | 237
2017-10-24 11:00 | 237 | 237
2017-10-24 11:30 | 238 | 238
2017-10-24 12:00 | 238 | 238
2017-10-24 12:30 | 240 | 240
2017-10-24 13:00 | 244 | 244
2017-10-24 13:30 | 247 | 246
2017-10-24 14:00 | 251 | 251
2017-10-24 14:30 | 254 | 254
2017-10-24 15:00 | 276 | 275
2017-10-24 15:30 | 248 | 247
2017-10-24 16:00 | 250 | 250
2017-10-24 16:30 | 263 | 263
2017-10-24 17:00 | 313 | 312
2017-10-24 17:30 | 316 | 316
2017-10-24 18:00 | 327 | 327
2017-10-24 18:30 | 327 | 326
2017-10-24 19:00 | 295 | 294
2017-10-24 19:30 | 278 | 278
2017-10-24 20:00 | 265 | 265
2017-10-24 20:30 | 272 | 272
2017-10-24 21:00 | 262 | 262
2017-10-24 21:30 | 252 | 252
2017-10-24 22:00 | 241 | 240
2017-10-24 22:30 | 231 | 230
2017-10-24 23:00 | 221 | 221
2017-10-24 23:30 | 212 | 211
2017-10-25 | 201 | 200
2017-10-25 00:30 | 200 | 200
2017-10-25 01:00 | 191 | 189
2017-10-25 01:30 | 187 | 186
2017-10-25 02:00 | 184 | 182
2017-10-25 02:30 | 183 | 181
2017-10-25 03:00 | 183 | 181
2017-10-25 03:30 | 184 | 183
2017-10-25 04:00 | 187 | 186
2017-10-25 04:30 | 187 | 186
2017-10-25 05:00 | 204 | 202
2017-10-25 05:30 | 216 | 215
2017-10-25 06:00 | 232 | 232
2017-10-25 06:30 | 243 | 243
2017-10-25 07:00 | 258 | 257
2017-10-25 07:30 | 279 | 276
2017-10-25 08:00 | 275 | 273
2017-10-25 08:30 | 268 | 266
2017-10-25 09:00 | 265 | 264
2017-10-25 09:30 | 264 | 263
2017-10-25 10:00 | 264 | 263
2017-10-25 10:30 | 265 | 264
2017-10-25 11:00 | 266 | 265
2017-10-25 11:30 | 267 | 266
2017-10-25 12:00 | 274 | 273
2017-10-25 12:30 | 282 | 281
2017-10-25 13:00 | 288 | 287
2017-10-25 13:30 | 287 | 287
2017-10-25 14:00 | 298 | 297
2017-10-25 14:30 | 306 | 305
2017-10-25 15:00 | 312 | 311
2017-10-25 15:30 | 314 | 313
2017-10-25 16:00 | 303 | 302
2017-10-25 16:30 | 312 | 310
2017-10-25 17:00 | 318 | 316
2017-10-25 17:30 | 320 | 317
2017-10-25 18:00 | 326 | 324
2017-10-25 18:30 | 332 | 330
2017-10-25 19:00 | 307 | 304
2017-10-25 19:30 | 294 | 292
2017-10-25 20:00 | 288 | 286
2017-10-25 20:30 | 278 | 277
2017-10-25 21:00 | 266 | 265
2017-10-25 21:30 | 253 | 252
2017-10-25 22:00 | 241 | 240
2017-10-25 22:30 | 233 | 232
2017-10-25 23:00 | 222 | 221
2017-10-25 23:30 | 212 | 212
2017-10-26 | 201 | 200
2017-10-26 00:30 | 196 | 195
2017-10-26 01:00 | 192 | 190
2017-10-26 01:30 | 189 | 187
2017-10-26 02:00 | 186 | 185
2017-10-26 02:30 | 176 | 174
2017-10-26 03:00 | 163 | 160
2017-10-26 03:30 | 164 | 162
2017-10-26 04:00 | 169 | 167
2017-10-26 04:30 | 173 | 172
2017-10-26 05:00 | 182 | 181
2017-10-26 05:30 | 195 | 194
2017-10-26 06:00 | 208 | 208
2017-10-26 06:30 | 223 | 223
2017-10-26 07:00 | 237 | 236
2017-10-26 07:30 | 238 | 238
2017-10-26 08:00 | 236 | 236
2017-10-26 08:30 | 234 | 233
2017-10-26 09:00 | 240 | 240
2017-10-26 09:30 | 244 | 244
2017-10-26 10:00 | 247 | 247
2017-10-26 10:30 | 245 | 245
2017-10-26 11:00 | 247 | 246
2017-10-26 11:30 | 251 | 251
2017-10-26 12:00 | 255 | 255
2017-10-26 12:30 | 259 | 259
2017-10-26 13:00 | 264 | 264
2017-10-26 13:30 | 270 | 269
2017-10-26 14:00 | 278 | 277
2017-10-26 14:30 | 280 | 280
2017-10-26 15:00 | 291 | 291
2017-10-26 15:30 | 309 | 309
2017-10-26 16:00 | 321 | 321
2017-10-26 16:30 | 325 | 325
2017-10-26 17:00 | 327 | 326
2017-10-26 17:30 | 323 | 322
2017-10-26 18:00 | 313 | 312
2017-10-26 18:30 | 312 | 311
2017-10-26 19:00 | 302 | 302
2017-10-26 19:30 | 301 | 300
2017-10-26 20:00 | 295 | 294
2017-10-26 20:30 | 284 | 283
2017-10-26 21:00 | 277 | 275
2017-10-26 21:30 | 265 | 264
2017-10-26 22:00 | 250 | 249
2017-10-26 22:30 | 239 | 238
2017-10-26 23:00 | 223 | 222
2017-10-26 23:30 | 212 | 210
2017-10-27 | 204 | 203
2017-10-27 00:30 | 196 | 196
2017-10-27 01:00 | 190 | 189
2017-10-27 01:30 | 185 | 184
2017-10-27 02:00 | 184 | 183
2017-10-27 02:30 | 184 | 183
2017-10-27 03:00 | 184 | 182
2017-10-27 03:30 | 186 | 185
2017-10-27 04:00 | 187 | 186
2017-10-27 04:30 | 188 | 187
2017-10-27 05:00 | 198 | 197
2017-10-27 05:30 | 218 | 218
2017-10-27 06:00 | 241 | 240
2017-10-27 06:30 | 255 | 254
2017-10-27 07:00 | 267 | 267
2017-10-27 07:30 | 268 | 268
2017-10-27 08:00 | 267 | 266
2017-10-27 08:30 | 263 | 262
2017-10-27 09:00 | 261 | 261
2017-10-27 09:30 | 258 | 258
2017-10-27 10:00 | 258 | 258
2017-10-27 10:30 | 260 | 259
2017-10-27 11:00 | 260 | 259
2017-10-27 11:30 | 262 | 261
2017-10-27 12:00 | 264 | 263
2017-10-27 12:30 | 270 | 269
2017-10-27 13:00 | 274 | 273
2017-10-27 13:30 | 282 | 281
2017-10-27 14:00 | 291 | 291
2017-10-27 14:30 | 300 | 300
2017-10-27 15:00 | 303 | 303
2017-10-27 15:30 | 308 | 307
2017-10-27 16:00 | 309 | 308
2017-10-27 16:30 | 300 | 298
2017-10-27 17:00 | 293 | 292
2017-10-27 17:30 | 307 | 306
2017-10-27 18:00 | 291 | 290
2017-10-27 18:30 | 294 | 293
2017-10-27 19:00 | 289 | 287
2017-10-27 19:30 | 285 | 284
2017-10-27 20:00 | 276 | 276
2017-10-27 20:30 | 268 | 268
2017-10-27 21:00 | 257 | 257
2017-10-27 21:30 | 243 | 243
2017-10-27 22:00 | 236 | 236
2017-10-27 22:30 | 232 | 232
2017-10-27 23:00 | 220 | 220
2017-10-27 23:30 | 212 | 212
2017-10-28 | 193 | 193
2017-10-28 00:30 | 185 | 184
2017-10-28 01:00 | 182 | 181
2017-10-28 01:30 | 177 | 176
2017-10-28 02:00 | 175 | 174
2017-10-28 02:30 | 172 | 171
2017-10-28 03:00 | 170 | 169
2017-10-28 03:30 | 171 | 170
2017-10-28 04:00 | 175 | 174
2017-10-28 04:30 | 173 | 172
2017-10-28 05:00 | 178 | 176
2017-10-28 05:30 | 198 | 197
2017-10-28 06:00 | 177 | 176
2017-10-28 06:30 | 180 | 180
2017-10-28 07:00 | 190 | 190
2017-10-28 07:30 | 196 | 196
2017-10-28 08:00 | 203 | 203
2017-10-28 08:30 | 206 | 206
2017-10-28 09:00 | 207 | 207
2017-10-28 09:30 | 207 | 206
2017-10-28 10:00 | 207 | 207
2017-10-28 10:30 | 208 | 208
2017-10-28 11:00 | 205 | 205
2017-10-28 11:30 | 210 | 210
2017-10-28 12:00 | 212 | 211
2017-10-28 12:30 | 212 | 212
2017-10-28 13:00 | 211 | 210
2017-10-28 13:30 | 216 | 215
2017-10-28 14:00 | 223 | 222
2017-10-28 14:30 | 230 | 229
2017-10-28 15:00 | 240 | 239
2017-10-28 15:30 | 253 | 251
2017-10-28 16:00 | 263 | 262
2017-10-28 16:30 | 271 | 270
2017-10-28 17:00 | 274 | 272
2017-10-28 17:30 | 277 | 275
2017-10-28 18:00 | 283 | 281
2017-10-28 18:30 | 285 | 283
2017-10-28 19:00 | 278 | 276
2017-10-28 19:30 | 278 | 275
2017-10-28 20:00 | 268 | 267
2017-10-28 20:30 | 259 | 259
2017-10-28 21:00 | 248 | 248
2017-10-28 21:30 | 240 | 240
2017-10-28 22:00 | 235 | 234
2017-10-28 22:30 | 233 | 233
2017-10-28 23:00 | 220 | 220
2017-10-28 23:30 | 206 | 206
2017-10-29 | 196 | 196
2017-10-29 00:30 | 189 | 189
2017-10-29 01:00 | 182 | 182
2017-10-29 01:30 | 177 | 177
2017-10-29 02:00 | 174 | 174
2017-10-29 02:30 | 167 | 167
2017-10-29 03:00 | 153 | 153
2017-10-29 03:30 | 131 | 130
2017-10-29 04:00 | 163 | 163
2017-10-29 04:30 | 168 | 168
2017-10-29 05:00 | 169 | 168
2017-10-29 05:30 | 192 | 192
2017-10-29 06:00 | 173 | 173
2017-10-29 06:30 | 169 | 169
2017-10-29 07:00 | 181 | 181
2017-10-29 07:30 | 185 | 185
2017-10-29 08:00 | 195 | 194
2017-10-29 08:30 | 170 | 170
2017-10-29 09:00 | 175 | 174
2017-10-29 09:30 | 205 | 205
2017-10-29 10:00 | 208 | 208
2017-10-29 10:30 | 195 | 195
2017-10-29 11:00 | 217 | 216
2017-10-29 11:30 | 220 | 220
2017-10-29 12:00 | 222 | 222
2017-10-29 12:30 | 228 | 228
2017-10-29 13:00 | 235 | 235
2017-10-29 13:30 | 244 | 244
2017-10-29 14:00 | 254 | 254
2017-10-29 14:30 | 265 | 265
2017-10-29 15:00 | 282 | 278
2017-10-29 15:30 | 291 | 288
2017-10-29 16:00 | 302 | 299
2017-10-29 16:30 | 311 | 308
2017-10-29 17:00 | 314 | 310
2017-10-29 17:30 | 316 | 312
2017-10-29 18:00 | 321 | 318
2017-10-29 18:30 | 328 | 325
2017-10-29 19:00 | 312 | 311
2017-10-29 19:30 | 300 | 300
2017-10-29 20:00 | 291 | 290
2017-10-29 20:30 | 273 | 273
2017-10-29 21:00 | 258 | 258
2017-10-29 21:30 | 236 | 236
2017-10-29 22:00 | 227 | 226
2017-10-29 22:30 | 224 | 224
2017-10-29 23:00 | 213 | 212
2017-10-29 23:30 | 206 | 205
2017-10-30 | 186 | 185
2017-10-30 00:30 | 185 | 184
2017-10-30 01:00 | 180 | 179
2017-10-30 01:30 | 177 | 176
2017-10-30 02:00 | 176 | 175
2017-10-30 02:30 | 176 | 175
2017-10-30 03:00 | 176 | 175
2017-10-30 03:30 | 177 | 177
2017-10-30 04:00 | 183 | 182
2017-10-30 04:30 | 185 | 184
2017-10-30 05:00 | 194 | 193
2017-10-30 05:30 | 221 | 220
2017-10-30 06:00 | 218 | 218
2017-10-30 06:30 | 236 | 236
2017-10-30 07:00 | 253 | 253
2017-10-30 07:30 | 259 | 259
2017-10-30 08:00 | 266 | 266
2017-10-30 08:30 | 283 | 283
2017-10-30 09:00 | 287 | 286
2017-10-30 09:30 | 278 | 278
2017-10-30 10:00 | 281 | 281
2017-10-30 10:30 | 283 | 283
2017-10-30 11:00 | 293 | 293
2017-10-30 11:30 | 299 | 299
2017-10-30 12:00 | 292 | 292
2017-10-30 12:30 | 292 | 292
2017-10-30 13:00 | 294 | 294
2017-10-30 13:30 | 305 | 305
2017-10-30 14:00 | 332 | 331
2017-10-30 14:30 | 331 | 331
2017-10-30 15:00 | 323 | 322
2017-10-30 15:30 | 319 | 317
2017-10-30 16:00 | 325 | 324
2017-10-30 16:30 | 337 | 335
2017-10-30 17:00 | 337 | 335
2017-10-30 17:30 | 332 | 330
2017-10-30 18:00 | 335 | 334
2017-10-30 18:30 | 341 | 340
2017-10-30 19:00 | 329 | 328
2017-10-30 19:30 | 317 | 317
2017-10-30 20:00 | 306 | 306
2017-10-30 20:30 | 293 | 293
2017-10-30 21:00 | 281 | 281
2017-10-30 21:30 | 268 | 267
2017-10-30 22:00 | 260 | 259
2017-10-30 22:30 | 253 | 252
2017-10-30 23:00 | 233 | 232
2017-10-30 23:30 | 218 | 216
2017-10-31 | 204 | 203
2017-10-31 00:30 | 200 | 200
2017-10-31 01:00 | 194 | 193
2017-10-31 01:30 | 188 | 187
2017-10-31 02:00 | 185 | 185
2017-10-31 02:30 | 186 | 185
2017-10-31 03:00 | 187 | 186
2017-10-31 03:30 | 189 | 189
2017-10-31 04:00 | 192 | 192
2017-10-31 04:30 | 189 | 188
2017-10-31 05:00 | 199 | 199
2017-10-31 05:30 | 209 | 208
2017-10-31 06:00 | 217 | 217
2017-10-31 06:30 | 232 | 232
2017-10-31 07:00 | 252 | 251
2017-10-31 07:30 | 258 | 257
2017-10-31 08:00 | 268 | 268
2017-10-31 08:30 | 266 | 265
2017-10-31 09:00 | 266 | 266
2017-10-31 09:30 | 260 | 260
2017-10-31 10:00 | 257 | 257
2017-10-31 10:30 | 254 | 254
2017-10-31 11:00 | 249 | 249
2017-10-31 11:30 | 246 | 246
2017-10-31 12:00 | 245 | 244
2017-10-31 12:30 | 244 | 244
2017-10-31 13:00 | 248 | 248
2017-10-31 13:30 | 253 | 253
2017-10-31 14:00 | 260 | 260
2017-10-31 14:30 | 268 | 267
2017-10-31 15:00 | 279 | 277
2017-10-31 15:30 | 283 | 281
2017-10-31 16:00 | 294 | 292
2017-10-31 16:30 | 301 | 299
2017-10-31 17:00 | 308 | 306
2017-10-31 17:30 | 306 | 304
2017-10-31 18:00 | 308 | 307
2017-10-31 18:30 | 315 | 314
2017-10-31 19:00 | 308 | 307
2017-10-31 19:30 | 306 | 305
2017-10-31 20:00 | 297 | 297
2017-10-31 20:30 | 281 | 281
2017-10-31 21:00 | 268 | 268
2017-10-31 21:30 | 258 | 258
2017-10-31 22:00 | 246 | 246
2017-10-31 22:30 | 237 | 237
2017-10-31 23:00 | 219 | 219
2017-10-31 23:30 | 204 | 203
2017-11-01 | 194 | 192
2017-11-01 00:30 | 189 | 188
2017-11-01 01:00 | 184 | 183
2017-11-01 01:30 | 181 | 180
2017-11-01 02:00 | 178 | 178
2017-11-01 02:30 | 177 | 176
2017-11-01 03:00 | 177 | 177
2017-11-01 03:30 | 186 | 185
2017-11-01 04:00 | 189 | 188
2017-11-01 04:30 | 187 | 187
2017-11-01 05:00 | 193 | 193
2017-11-01 05:30 | 202 | 202
2017-11-01 06:00 | 243 | 243
2017-11-01 06:30 | 256 | 255
2017-11-01 07:00 | 261 | 261
2017-11-01 07:30 | 278 | 278
2017-11-01 08:00 | 266 | 265
2017-11-01 08:30 | 262 | 262
2017-11-01 09:00 | 258 | 258
2017-11-01 09:30 | 260 | 260
2017-11-01 10:00 | 272 | 272
2017-11-01 10:30 | 260 | 260
2017-11-01 11:00 | 267 | 267
2017-11-01 11:30 | 258 | 258
2017-11-01 12:00 | 250 | 250
2017-11-01 12:30 | 242 | 242
2017-11-01 13:00 | 244 | 244
2017-11-01 13:30 | 250 | 250
2017-11-01 14:00 | 252 | 252
2017-11-01 14:30 | 255 | 255
2017-11-01 15:00 | 260 | 260
2017-11-01 15:30 | 270 | 270
2017-11-01 16:00 | 280 | 280
2017-11-01 16:30 | 303 | 303
2017-11-01 17:00 | 303 | 303
2017-11-01 17:30 | 303 | 302
2017-11-01 18:00 | 308 | 308
2017-11-01 18:30 | 319 | 319
2017-11-01 19:00 | 310 | 309
2017-11-01 19:30 | 296 | 296
2017-11-01 20:00 | 292 | 292
2017-11-01 20:30 | 280 | 279
2017-11-01 21:00 | 268 | 268
2017-11-01 21:30 | 255 | 255
2017-11-01 22:00 | 240 | 240
2017-11-01 22:30 | 231 | 231
2017-11-01 23:00 | 219 | 218
2017-11-01 23:30 | 206 | 205
2017-11-02 | 196 | 195
2017-11-02 00:30 | 201 | 199
2017-11-02 01:00 | 197 | 196
2017-11-02 01:30 | 194 | 193
2017-11-02 02:00 | 192 | 191
2017-11-02 02:30 | 191 | 189
2017-11-02 03:00 | 193 | 191
2017-11-02 03:30 | 192 | 190
2017-11-02 04:00 | 194 | 193
2017-11-02 04:30 | 189 | 188
2017-11-02 05:00 | 197 | 196
2017-11-02 05:30 | 208 | 207
2017-11-02 06:00 | 227 | 227
2017-11-02 06:30 | 248 | 247
2017-11-02 07:00 | 264 | 264
2017-11-02 07:30 | 271 | 271
2017-11-02 08:00 | 269 | 269
2017-11-02 08:30 | 270 | 270
2017-11-02 09:00 | 274 | 274
2017-11-02 09:30 | 272 | 272
2017-11-02 10:00 | 271 | 271
2017-11-02 10:30 | 268 | 268
2017-11-02 11:00 | 265 | 265
2017-11-02 11:30 | 264 | 264
2017-11-02 12:00 | 267 | 267
2017-11-02 12:30 | 270 | 270
2017-11-02 13:00 | 277 | 277
2017-11-02 13:30 | 286 | 286
2017-11-02 14:00 | 291 | 291
2017-11-02 14:30 | 298 | 298
2017-11-02 15:00 | 298 | 298
2017-11-02 15:30 | 309 | 309
2017-11-02 16:00 | 315 | 315
2017-11-02 16:30 | 320 | 319
2017-11-02 17:00 | 318 | 318
2017-11-02 17:30 | 319 | 318
2017-11-02 18:00 | 322 | 321
2017-11-02 18:30 | 334 | 333
2017-11-02 19:00 | 326 | 323
2017-11-02 19:30 | 320 | 320
2017-11-02 20:00 | 313 | 313
2017-11-02 20:30 | 298 | 298
2017-11-02 21:00 | 286 | 286
2017-11-02 21:30 | 279 | 279
2017-11-02 22:00 | 270 | 270
2017-11-02 22:30 | 260 | 260
2017-11-02 23:00 | 242 | 241
2017-11-02 23:30 | 230 | 229
2017-11-03 | 219 | 218
2017-11-03 00:30 | 213 | 212
2017-11-03 01:00 | 210 | 208
2017-11-03 01:30 | 205 | 203
2017-11-03 02:00 | 204 | 202
2017-11-03 02:30 | 205 | 203
2017-11-03 03:00 | 206 | 204
2017-11-03 03:30 | 210 | 209
2017-11-03 04:00 | 213 | 212
2017-11-03 04:30 | 211 | 210
2017-11-03 05:00 | 194 | 194
2017-11-03 05:30 | 206 | 205
2017-11-03 06:00 | 219 | 219
2017-11-03 06:30 | 242 | 242
2017-11-03 07:00 | 271 | 271
2017-11-03 07:30 | 278 | 277
2017-11-03 08:00 | 280 | 280
2017-11-03 08:30 | 286 | 286
2017-11-03 09:00 | 288 | 288
2017-11-03 09:30 | 282 | 282
2017-11-03 10:00 | 284 | 284
2017-11-03 10:30 | 283 | 283
2017-11-03 11:00 | 280 | 280
2017-11-03 11:30 | 275 | 275
2017-11-03 12:00 | 287 | 287
2017-11-03 12:30 | 288 | 288
2017-11-03 13:00 | 277 | 277
2017-11-03 13:30 | 278 | 278
2017-11-03 14:00 | 286 | 286
2017-11-03 14:30 | 296 | 296
2017-11-03 15:00 | 298 | 298
2017-11-03 15:30 | 307 | 307
2017-11-03 16:00 | 310 | 309
2017-11-03 16:30 | 315 | 315
2017-11-03 17:00 | 314 | 314
2017-11-03 17:30 | 311 | 310
2017-11-03 18:00 | 312 | 311
2017-11-03 18:30 | 319 | 319
2017-11-03 19:00 | 313 | 313
2017-11-03 19:30 | 311 | 310
2017-11-03 20:00 | 306 | 306
2017-11-03 20:30 | 301 | 300
2017-11-03 21:00 | 294 | 293
2017-11-03 21:30 | 281 | 280
2017-11-03 22:00 | 267 | 266
2017-11-03 22:30 | 253 | 253
2017-11-03 23:00 | 234 | 234
2017-11-03 23:30 | 223 | 223
2017-11-04 | 215 | 215
2017-11-04 00:30 | 210 | 209
2017-11-04 01:00 | 202 | 201
2017-11-04 01:30 | 196 | 196
2017-11-04 02:00 | 195 | 194
2017-11-04 02:30 | 194 | 194
2017-11-04 03:00 | 198 | 197
2017-11-04 03:30 | 198 | 198
2017-11-04 04:00 | 202 | 201
2017-11-04 04:30 | 201 | 200
2017-11-04 05:00 | 205 | 204
2017-11-04 05:30 | 207 | 206
2017-11-04 06:00 | 215 | 215
2017-11-04 06:30 | 222 | 222
2017-11-04 07:00 | 231 | 231
2017-11-04 07:30 | 240 | 240
2017-11-04 08:00 | 247 | 247
2017-11-04 08:30 | 253 | 252
2017-11-04 09:00 | 243 | 242
2017-11-04 09:30 | 243 | 243
2017-11-04 10:00 | 251 | 250
2017-11-04 10:30 | 239 | 239
2017-11-04 11:00 | 249 | 249
2017-11-04 11:30 | 233 | 233
2017-11-04 12:00 | 231 | 230
2017-11-04 12:30 | 252 | 251
2017-11-04 13:00 | 248 | 247
2017-11-04 13:30 | 253 | 252
2017-11-04 14:00 | 248 | 247
2017-11-04 14:30 | 263 | 262
2017-11-04 15:00 | 265 | 264
2017-11-04 15:30 | 273 | 272
2017-11-04 16:00 | 280 | 279
2017-11-04 16:30 | 296 | 295
2017-11-04 17:00 | 298 | 296
2017-11-04 17:30 | 299 | 297
2017-11-04 18:00 | 302 | 301
2017-11-04 18:30 | 310 | 309
2017-11-04 19:00 | 302 | 301
2017-11-04 19:30 | 293 | 291
2017-11-04 20:00 | 283 | 283
2017-11-04 20:30 | 277 | 276
2017-11-04 21:00 | 270 | 270
2017-11-04 21:30 | 266 | 265
2017-11-04 22:00 | 260 | 259
2017-11-04 22:30 | 251 | 251
2017-11-04 23:00 | 239 | 239
2017-11-04 23:30 | 227 | 227
2017-11-05 | 215 | 215
2017-11-05 00:30 | 209 | 209
2017-11-05 01:00 | 207 | 207
2017-11-05 01:30 | 202 | 202
2017-11-05 02:00 | 199 | 199
2017-11-05 02:30 | 201 | 201
2017-11-05 03:00 | 204 | 203
2017-11-05 03:30 | 205 | 205
2017-11-05 04:00 | 204 | 204
2017-11-05 04:30 | 204 | 203
2017-11-05 05:00 | 214 | 214
2017-11-05 05:30 | 217 | 217
2017-11-05 06:00 | 216 | 215
2017-11-05 06:30 | 223 | 223
2017-11-05 07:00 | 244 | 244
2017-11-05 07:30 | 252 | 251
2017-11-05 08:00 | 253 | 253
2017-11-05 08:30 | 256 | 256
2017-11-05 09:00 | 256 | 256
2017-11-05 09:30 | 261 | 261
2017-11-05 10:00 | 245 | 245
2017-11-05 10:30 | 227 | 227
2017-11-05 11:00 | 260 | 260
2017-11-05 11:30 | 249 | 249
2017-11-05 12:00 | 250 | 250
2017-11-05 12:30 | 252 | 252
2017-11-05 13:00 | 257 | 257
2017-11-05 13:30 | 260 | 260
2017-11-05 14:00 | 263 | 262
2017-11-05 14:30 | 263 | 263
2017-11-05 15:00 | 274 | 273
2017-11-05 15:30 | 273 | 272
2017-11-05 16:00 | 287 | 286
2017-11-05 16:30 | 301 | 299
2017-11-05 17:00 | 308 | 306
2017-11-05 17:30 | 311 | 308
2017-11-05 18:00 | 316 | 314
2017-11-05 18:30 | 321 | 319
2017-11-05 19:00 | 310 | 308
2017-11-05 19:30 | 301 | 300
2017-11-05 20:00 | 292 | 291
2017-11-05 20:30 | 277 | 277
2017-11-05 21:00 | 263 | 263
2017-11-05 21:30 | 250 | 249
2017-11-05 22:00 | 248 | 247
2017-11-05 22:30 | 245 | 244
2017-11-05 23:00 | 228 | 227
2017-11-05 23:30 | 209 | 207
2017-11-06 | 197 | 195
2017-11-06 00:30 | 192 | 191
2017-11-06 01:00 | 187 | 186
2017-11-06 01:30 | 183 | 182
2017-11-06 02:00 | 181 | 179
2017-11-06 02:30 | 182 | 181
2017-11-06 03:00 | 187 | 186
2017-11-06 03:30 | 191 | 190
2017-11-06 04:00 | 199 | 198
2017-11-06 04:30 | 188 | 187
2017-11-06 05:00 | 197 | 197
2017-11-06 05:30 | 207 | 206
2017-11-06 06:00 | 230 | 230
2017-11-06 06:30 | 254 | 254
2017-11-06 07:00 | 269 | 268
2017-11-06 07:30 | 271 | 271
2017-11-06 08:00 | 284 | 284
2017-11-06 08:30 | 287 | 287
2017-11-06 09:00 | 294 | 293
2017-11-06 09:30 | 285 | 283
2017-11-06 10:00 | 281 | 280
2017-11-06 10:30 | 293 | 292
2017-11-06 11:00 | 287 | 286
2017-11-06 11:30 | 292 | 292
2017-11-06 12:00 | 285 | 284
2017-11-06 12:30 | 284 | 283
2017-11-06 13:00 | 294 | 293
2017-11-06 13:30 | 283 | 282
2017-11-06 14:00 | 291 | 290
2017-11-06 14:30 | 298 | 297
2017-11-06 15:00 | 305 | 304
2017-11-06 15:30 | 315 | 314
2017-11-06 16:00 | 320 | 319
2017-11-06 16:30 | 333 | 331
2017-11-06 17:00 | 333 | 332
2017-11-06 17:30 | 332 | 330
2017-11-06 18:00 | 338 | 335
2017-11-06 18:30 | 345 | 344
2017-11-06 19:00 | 335 | 332
2017-11-06 19:30 | 329 | 326
2017-11-06 20:00 | 320 | 317
2017-11-06 20:30 | 307 | 303
2017-11-06 21:00 | 285 | 284
2017-11-06 21:30 | 261 | 258
2017-11-06 22:00 | 252 | 250
2017-11-06 22:30 | 245 | 244
2017-11-06 23:00 | 230 | 229
2017-11-06 23:30 | 218 | 217
2017-11-07 | 206 | 205
2017-11-07 00:30 | 202 | 200
2017-11-07 01:00 | 196 | 193
2017-11-07 01:30 | 188 | 186
2017-11-07 02:00 | 185 | 184
2017-11-07 02:30 | 186 | 186
2017-11-07 03:00 | 187 | 186
2017-11-07 03:30 | 190 | 189
2017-11-07 04:00 | 191 | 190
2017-11-07 04:30 | 195 | 194
2017-11-07 05:00 | 205 | 204
2017-11-07 05:30 | 215 | 214
2017-11-07 06:00 | 233 | 233
2017-11-07 06:30 | 245 | 245
2017-11-07 07:00 | 264 | 264
2017-11-07 07:30 | 270 | 270
2017-11-07 08:00 | 271 | 271
2017-11-07 08:30 | 279 | 279
2017-11-07 09:00 | 288 | 288
2017-11-07 09:30 | 291 | 291
2017-11-07 10:00 | 296 | 295
2017-11-07 10:30 | 299 | 297
2017-11-07 11:00 | 286 | 284
2017-11-07 11:30 | 268 | 266
2017-11-07 12:00 | 249 | 249
2017-11-07 12:30 | 257 | 256
2017-11-07 13:00 | 262 | 262
2017-11-07 13:30 | 275 | 275
2017-11-07 14:00 | 272 | 272
2017-11-07 14:30 | 275 | 275
2017-11-07 15:00 | 281 | 281
2017-11-07 15:30 | 288 | 287
2017-11-07 16:00 | 294 | 293
2017-11-07 16:30 | 303 | 302
2017-11-07 17:00 | 298 | 297
2017-11-07 17:30 | 295 | 294
2017-11-07 18:00 | 301 | 300
2017-11-07 18:30 | 309 | 308
2017-11-07 19:00 | 305 | 304
2017-11-07 19:30 | 305 | 304
2017-11-07 20:00 | 294 | 294
2017-11-07 20:30 | 281 | 281
2017-11-07 21:00 | 272 | 271
2017-11-07 21:30 | 263 | 263
2017-11-07 22:00 | 253 | 253
2017-11-07 22:30 | 250 | 250
2017-11-07 23:00 | 239 | 239
2017-11-07 23:30 | 227 | 227
2017-11-08 | 216 | 216
2017-11-08 00:30 | 210 | 210
2017-11-08 01:00 | 205 | 205
2017-11-08 01:30 | 202 | 202
2017-11-08 02:00 | 201 | 201
2017-11-08 02:30 | 200 | 200
2017-11-08 03:00 | 202 | 201
2017-11-08 03:30 | 203 | 203
2017-11-08 04:00 | 205 | 204
2017-11-08 04:30 | 205 | 205
2017-11-08 05:00 | 211 | 211
2017-11-08 05:30 | 221 | 221
2017-11-08 06:00 | 234 | 234
2017-11-08 06:30 | 252 | 252
2017-11-08 07:00 | 262 | 262
2017-11-08 07:30 | 258 | 258
2017-11-08 08:00 | 269 | 268
2017-11-08 08:30 | 272 | 272
2017-11-08 09:00 | 267 | 267
2017-11-08 09:30 | 263 | 263
2017-11-08 10:00 | 266 | 266
2017-11-08 10:30 | 268 | 267
2017-11-08 11:00 | 263 | 262
2017-11-08 11:30 | 272 | 271
2017-11-08 12:00 | 273 | 272
2017-11-08 12:30 | 266 | 266
2017-11-08 13:00 | 268 | 268
2017-11-08 13:30 | 277 | 276
2017-11-08 14:00 | 263 | 263
2017-11-08 14:30 | 254 | 254
2017-11-08 15:00 | 258 | 258
2017-11-08 15:30 | 270 | 270
2017-11-08 16:00 | 277 | 277
2017-11-08 16:30 | 284 | 284
2017-11-08 17:00 | 286 | 286
2017-11-08 17:30 | 286 | 286
2017-11-08 18:00 | 295 | 294
2017-11-08 18:30 | 307 | 307
2017-11-08 19:00 | 299 | 298
2017-11-08 19:30 | 295 | 294
2017-11-08 20:00 | 287 | 285
2017-11-08 20:30 | 276 | 275
2017-11-08 21:00 | 266 | 265
2017-11-08 21:30 | 254 | 254
2017-11-08 22:00 | 248 | 247
2017-11-08 22:30 | 244 | 243
2017-11-08 23:00 | 228 | 227
2017-11-08 23:30 | 214 | 212
2017-11-09 | 202 | 199
2017-11-09 00:30 | 198 | 195
2017-11-09 01:00 | 193 | 190
2017-11-09 01:30 | 188 | 185
2017-11-09 02:00 | 187 | 183
2017-11-09 02:30 | 186 | 183
2017-11-09 03:00 | 187 | 184
2017-11-09 03:30 | 192 | 189
2017-11-09 04:00 | 200 | 197
2017-11-09 04:30 | 199 | 196
2017-11-09 05:00 | 206 | 203
2017-11-09 05:30 | 217 | 215
2017-11-09 06:00 | 231 | 230
2017-11-09 06:30 | 243 | 242
2017-11-09 07:00 | 255 | 255
2017-11-09 07:30 | 255 | 255
2017-11-09 08:00 | 259 | 259
2017-11-09 08:30 | 268 | 268
2017-11-09 09:00 | 261 | 261
2017-11-09 09:30 | 260 | 259
2017-11-09 10:00 | 260 | 259
2017-11-09 10:30 | 252 | 252
2017-11-09 11:00 | 260 | 260
2017-11-09 11:30 | 256 | 256
2017-11-09 12:00 | 257 | 256
2017-11-09 12:30 | 239 | 238
2017-11-09 13:00 | 246 | 245
2017-11-09 13:30 | 256 | 255
2017-11-09 14:00 | 259 | 258
2017-11-09 14:30 | 263 | 263
2017-11-09 15:00 | 268 | 268
2017-11-09 15:30 | 281 | 281
2017-11-09 16:00 | 288 | 288
2017-11-09 16:30 | 299 | 298
2017-11-09 17:00 | 303 | 302
2017-11-09 17:30 | 305 | 305
2017-11-09 18:00 | 309 | 309
2017-11-09 18:30 | 318 | 318
2017-11-09 19:00 | 312 | 312
2017-11-09 19:30 | 309 | 308
2017-11-09 20:00 | 295 | 294
2017-11-09 20:30 | 278 | 277
2017-11-09 21:00 | 266 | 265
2017-11-09 21:30 | 257 | 255
2017-11-09 22:00 | 255 | 254
2017-11-09 22:30 | 245 | 243
2017-11-09 23:00 | 226 | 223
2017-11-09 23:30 | 215 | 211
2017-11-10 | 200 | 196
2017-11-10 00:30 | 191 | 188
2017-11-10 01:00 | 189 | 186
2017-11-10 01:30 | 185 | 182
2017-11-10 02:00 | 183 | 180
2017-11-10 02:30 | 183 | 180
2017-11-10 03:00 | 186 | 182
2017-11-10 03:30 | 191 | 188
2017-11-10 04:00 | 195 | 192
2017-11-10 04:30 | 195 | 192
2017-11-10 05:00 | 202 | 199
2017-11-10 05:30 | 211 | 209
2017-11-10 06:00 | 225 | 224
2017-11-10 06:30 | 238 | 238
2017-11-10 07:00 | 254 | 253
2017-11-10 07:30 | 259 | 256
2017-11-10 08:00 | 269 | 267
2017-11-10 08:30 | 277 | 275
2017-11-10 09:00 | 272 | 270
2017-11-10 09:30 | 268 | 265
2017-11-10 10:00 | 263 | 259
2017-11-10 10:30 | 259 | 256
2017-11-10 11:00 | 245 | 242
2017-11-10 11:30 | 243 | 240
2017-11-10 12:00 | 238 | 235
2017-11-10 12:30 | 238 | 235
2017-11-10 13:00 | 241 | 238
2017-11-10 13:30 | 246 | 243
2017-11-10 14:00 | 244 | 241
2017-11-10 14:30 | 246 | 243
2017-11-10 15:00 | 251 | 248
2017-11-10 15:30 | 256 | 253
2017-11-10 16:00 | 263 | 259
2017-11-10 16:30 | 267 | 264
2017-11-10 17:00 | 268 | 265
2017-11-10 17:30 | 265 | 262
2017-11-10 18:00 | 268 | 265
2017-11-10 18:30 | 277 | 275
2017-11-10 19:00 | 273 | 271
2017-11-10 19:30 | 266 | 265
2017-11-10 20:00 | 258 | 257
2017-11-10 20:30 | 250 | 249
2017-11-10 21:00 | 243 | 242
2017-11-10 21:30 | 234 | 233
2017-11-10 22:00 | 233 | 233
2017-11-10 22:30 | 230 | 229
2017-11-10 23:00 | 220 | 219
2017-11-10 23:30 | 207 | 205
2017-11-11 | 194 | 192
2017-11-11 00:30 | 190 | 188
2017-11-11 01:00 | 185 | 183
2017-11-11 01:30 | 181 | 179
2017-11-11 02:00 | 182 | 180
2017-11-11 02:30 | 180 | 177
2017-11-11 03:00 | 183 | 181
2017-11-11 03:30 | 187 | 185
2017-11-11 04:00 | 190 | 187
2017-11-11 04:30 | 185 | 182
2017-11-11 05:00 | 188 | 185
2017-11-11 05:30 | 191 | 188
2017-11-11 06:00 | 196 | 193
2017-11-11 06:30 | 207 | 206
2017-11-11 07:00 | 222 | 221
2017-11-11 07:30 | 236 | 235
2017-11-11 08:00 | 241 | 241
2017-11-11 08:30 | 238 | 238
2017-11-11 09:00 | 241 | 241
2017-11-11 09:30 | 238 | 237
2017-11-11 10:00 | 232 | 232
2017-11-11 10:30 | 226 | 226
2017-11-11 11:00 | 225 | 224
2017-11-11 11:30 | 218 | 217
2017-11-11 12:00 | 217 | 216
2017-11-11 12:30 | 233 | 232
2017-11-11 13:00 | 230 | 229
2017-11-11 13:30 | 226 | 225
2017-11-11 14:00 | 231 | 230
2017-11-11 14:30 | 234 | 233
2017-11-11 15:00 | 237 | 236
2017-11-11 15:30 | 239 | 238
2017-11-11 16:00 | 243 | 242
2017-11-11 16:30 | 245 | 244
2017-11-11 17:00 | 246 | 245
2017-11-11 17:30 | 248 | 247
2017-11-11 18:00 | 255 | 254
2017-11-11 18:30 | 261 | 261
2017-11-11 19:00 | 257 | 256
2017-11-11 19:30 | 252 | 252
2017-11-11 20:00 | 246 | 245
2017-11-11 20:30 | 236 | 235
2017-11-11 21:00 | 228 | 227
2017-11-11 21:30 | 223 | 221
2017-11-11 22:00 | 222 | 219
2017-11-11 22:30 | 221 | 218
2017-11-11 23:00 | 211 | 207
2017-11-11 23:30 | 203 | 198
2017-11-12 | 190 | 187
2017-11-12 00:30 | 187 | 184
2017-11-12 01:00 | 182 | 179
2017-11-12 01:30 | 178 | 175
2017-11-12 02:00 | 176 | 173
2017-11-12 02:30 | 176 | 172
2017-11-12 03:00 | 178 | 175
2017-11-12 03:30 | 187 | 185
2017-11-12 04:00 | 187 | 184
2017-11-12 04:30 | 185 | 181
2017-11-12 05:00 | 195 | 192
2017-11-12 05:30 | 190 | 187
2017-11-12 06:00 | 181 | 178
2017-11-12 06:30 | 210 | 208
2017-11-12 07:00 | 219 | 218
2017-11-12 07:30 | 224 | 224
2017-11-12 08:00 | 229 | 229
2017-11-12 08:30 | 223 | 223
2017-11-12 09:00 | 212 | 212
2017-11-12 09:30 | 214 | 213
2017-11-12 10:00 | 217 | 216
2017-11-12 10:30 | 214 | 213
2017-11-12 11:00 | 207 | 207
2017-11-12 11:30 | 206 | 206
2017-11-12 12:00 | 205 | 204
2017-11-12 12:30 | 205 | 204
2017-11-12 13:00 | 206 | 206
2017-11-12 13:30 | 213 | 212
2017-11-12 14:00 | 218 | 217
2017-11-12 14:30 | 219 | 218
2017-11-12 15:00 | 218 | 217
2017-11-12 15:30 | 228 | 227
2017-11-12 16:00 | 235 | 234
2017-11-12 16:30 | 242 | 241
2017-11-12 17:00 | 246 | 245
2017-11-12 17:30 | 250 | 249
2017-11-12 18:00 | 256 | 255
2017-11-12 18:30 | 268 | 265
2017-11-12 19:00 | 265 | 262
2017-11-12 19:30 | 259 | 256
2017-11-12 20:00 | 252 | 250
2017-11-12 20:30 | 240 | 239
2017-11-12 21:00 | 231 | 231
2017-11-12 21:30 | 225 | 224
2017-11-12 22:00 | 224 | 223
2017-11-12 22:30 | 224 | 223
2017-11-12 23:00 | 215 | 214
2017-11-12 23:30 | 206 | 205
2017-11-13 | 197 | 194
2017-11-13 00:30 | 184 | 182
2017-11-13 01:00 | 181 | 178
2017-11-13 01:30 | 184 | 181
2017-11-13 02:00 | 183 | 180
2017-11-13 02:30 | 184 | 182
2017-11-13 03:00 | 187 | 184
2017-11-13 03:30 | 194 | 192
2017-11-13 04:00 | 182 | 179
2017-11-13 04:30 | 186 | 183
2017-11-13 05:00 | 199 | 197
2017-11-13 05:30 | 207 | 205
2017-11-13 06:00 | 219 | 218
2017-11-13 06:30 | 231 | 231
2017-11-13 07:00 | 240 | 240
2017-11-13 07:30 | 247 | 247
2017-11-13 08:00 | 248 | 248
2017-11-13 08:30 | 246 | 246
2017-11-13 09:00 | 246 | 246
2017-11-13 09:30 | 242 | 242
2017-11-13 10:00 | 243 | 243
2017-11-13 10:30 | 246 | 245
2017-11-13 11:00 | 237 | 236
2017-11-13 11:30 | 243 | 243
2017-11-13 12:00 | 245 | 244
2017-11-13 12:30 | 246 | 245
2017-11-13 13:00 | 242 | 242
2017-11-13 13:30 | 245 | 244
2017-11-13 14:00 | 246 | 245
2017-11-13 14:30 | 257 | 257
2017-11-13 15:00 | 269 | 269
2017-11-13 15:30 | 279 | 278
2017-11-13 16:00 | 289 | 288
2017-11-13 16:30 | 295 | 294
2017-11-13 17:00 | 291 | 290
2017-11-13 17:30 | 290 | 289
2017-11-13 18:00 | 291 | 291
2017-11-13 18:30 | 299 | 299
2017-11-13 19:00 | 295 | 295
2017-11-13 19:30 | 292 | 292
2017-11-13 20:00 | 282 | 282
2017-11-13 20:30 | 267 | 266
2017-11-13 21:00 | 255 | 255
2017-11-13 21:30 | 244 | 244
2017-11-13 22:00 | 234 | 234
2017-11-13 22:30 | 230 | 229
2017-11-13 23:00 | 218 | 218
2017-11-13 23:30 | 203 | 202
2017-11-14 | 194 | 193
2017-11-14 00:30 | 182 | 180
2017-11-14 01:00 | 176 | 174
2017-11-14 01:30 | 175 | 173
2017-11-14 02:00 | 175 | 173
2017-11-14 02:30 | 172 | 170
2017-11-14 03:00 | 173 | 170
2017-11-14 03:30 | 174 | 171
2017-11-14 04:00 | 178 | 176
2017-11-14 04:30 | 179 | 176
2017-11-14 05:00 | 187 | 184
2017-11-14 05:30 | 195 | 193
2017-11-14 06:00 | 209 | 208
2017-11-14 06:30 | 223 | 222
2017-11-14 07:00 | 233 | 233
2017-11-14 07:30 | 237 | 237
2017-11-14 08:00 | 238 | 237
2017-11-14 08:30 | 233 | 233
2017-11-14 09:00 | 238 | 238
2017-11-14 09:30 | 235 | 234
2017-11-14 10:00 | 237 | 236
2017-11-14 10:30 | 234 | 234
2017-11-14 11:00 | 229 | 228
2017-11-14 11:30 | 232 | 231
2017-11-14 12:00 | 231 | 230
2017-11-14 12:30 | 229 | 229
2017-11-14 13:00 | 234 | 233
2017-11-14 13:30 | 237 | 237
2017-11-14 14:00 | 241 | 240
2017-11-14 14:30 | 249 | 249
2017-11-14 15:00 | 255 | 254
2017-11-14 15:30 | 266 | 265
2017-11-14 16:00 | 270 | 269
2017-11-14 16:30 | 274 | 273
2017-11-14 17:00 | 275 | 274
2017-11-14 17:30 | 277 | 275
2017-11-14 18:00 | 280 | 278
2017-11-14 18:30 | 290 | 288
2017-11-14 19:00 | 281 | 281
2017-11-14 19:30 | 278 | 277
2017-11-14 20:00 | 271 | 270
2017-11-14 20:30 | 258 | 258
2017-11-14 21:00 | 251 | 251
2017-11-14 21:30 | 245 | 244
2017-11-14 22:00 | 238 | 237
2017-11-14 22:30 | 232 | 232
2017-11-14 23:00 | 219 | 218
2017-11-14 23:30 | 208 | 207
2017-11-15 | 191 | 189
2017-11-15 00:30 | 186 | 184
2017-11-15 01:00 | 181 | 179
2017-11-15 01:30 | 179 | 176
2017-11-15 02:00 | 176 | 173
2017-11-15 02:30 | 175 | 172
2017-11-15 03:00 | 176 | 173
2017-11-15 03:30 | 175 | 173
2017-11-15 04:00 | 180 | 178
2017-11-15 04:30 | 183 | 181
2017-11-15 05:00 | 191 | 189
2017-11-15 05:30 | 201 | 200
2017-11-15 06:00 | 213 | 213
2017-11-15 06:30 | 226 | 226
2017-11-15 07:00 | 245 | 243
2017-11-15 07:30 | 252 | 250
2017-11-15 08:00 | 253 | 251
2017-11-15 08:30 | 252 | 251
2017-11-15 09:00 | 248 | 247
2017-11-15 09:30 | 245 | 244
2017-11-15 10:00 | 245 | 245
2017-11-15 10:30 | 240 | 239
2017-11-15 11:00 | 241 | 241
2017-11-15 11:30 | 241 | 240
2017-11-15 12:00 | 246 | 245
2017-11-15 12:30 | 255 | 255
2017-11-15 13:00 | 255 | 255
2017-11-15 13:30 | 253 | 253
2017-11-15 14:00 | 269 | 269
2017-11-15 14:30 | 260 | 259
2017-11-15 15:00 | 256 | 254
2017-11-15 15:30 | 258 | 257
2017-11-15 16:00 | 267 | 265
2017-11-15 16:30 | 274 | 272
2017-11-15 17:00 | 275 | 274
2017-11-15 17:30 | 276 | 274
2017-11-15 18:00 | 280 | 277
2017-11-15 18:30 | 292 | 290
2017-11-15 19:00 | 285 | 283
2017-11-15 19:30 | 280 | 278
2017-11-15 20:00 | 272 | 269
2017-11-15 20:30 | 257 | 257
2017-11-15 21:00 | 251 | 250
2017-11-15 21:30 | 238 | 238
2017-11-15 22:00 | 228 | 227
2017-11-15 22:30 | 221 | 220
2017-11-15 23:00 | 211 | 210
2017-11-15 23:30 | 202 | 200
2017-11-16 | 189 | 187
2017-11-16 00:30 | 181 | 180
2017-11-16 01:00 | 180 | 178
2017-11-16 01:30 | 175 | 173
2017-11-16 02:00 | 174 | 172
2017-11-16 02:30 | 175 | 173
2017-11-16 03:00 | 179 | 178
2017-11-16 03:30 | 184 | 182
2017-11-16 04:00 | 186 | 185
2017-11-16 04:30 | 188 | 186
2017-11-16 05:00 | 195 | 193
2017-11-16 05:30 | 205 | 204
2017-11-16 06:00 | 217 | 217
2017-11-16 06:30 | 231 | 230
2017-11-16 07:00 | 247 | 246
2017-11-16 07:30 | 257 | 255
2017-11-16 08:00 | 269 | 268
2017-11-16 08:30 | 268 | 267
2017-11-16 09:00 | 267 | 266
2017-11-16 09:30 | 270 | 268
2017-11-16 10:00 | 266 | 263
2017-11-16 10:30 | 264 | 262
2017-11-16 11:00 | 256 | 254
2017-11-16 11:30 | 257 | 255
2017-11-16 12:00 | 255 | 253
2017-11-16 12:30 | 265 | 263
2017-11-16 13:00 | 275 | 273
2017-11-16 13:30 | 279 | 277
2017-11-16 14:00 | 288 | 285
2017-11-16 14:30 | 285 | 283
2017-11-16 15:00 | 281 | 278
2017-11-16 15:30 | 276 | 272
2017-11-16 16:00 | 279 | 274
2017-11-16 16:30 | 285 | 280
2017-11-16 17:00 | 286 | 281
2017-11-16 17:30 | 281 | 278
2017-11-16 18:00 | 286 | 284
2017-11-16 18:30 | 295 | 293
2017-11-16 19:00 | 288 | 286
2017-11-16 19:30 | 284 | 281
2017-11-16 20:00 | 272 | 268
2017-11-16 20:30 | 262 | 258
2017-11-16 21:00 | 257 | 252
2017-11-16 21:30 | 248 | 242
2017-11-16 22:00 | 238 | 234
2017-11-16 22:30 | 226 | 225
2017-11-16 23:00 | 210 | 209
2017-11-16 23:30 | 202 | 202
2017-11-17 | 192 | 191
2017-11-17 00:30 | 189 | 187
2017-11-17 01:00 | 186 | 185
2017-11-17 01:30 | 181 | 180
2017-11-17 02:00 | 180 | 179
2017-11-17 02:30 | 180 | 178
2017-11-17 03:00 | 180 | 178
2017-11-17 03:30 | 180 | 179
2017-11-17 04:00 | 182 | 180
2017-11-17 04:30 | 182 | 180
2017-11-17 05:00 | 187 | 185
2017-11-17 05:30 | 199 | 198
2017-11-17 06:00 | 211 | 211
2017-11-17 06:30 | 223 | 223
2017-11-17 07:00 | 248 | 247
2017-11-17 07:30 | 263 | 262
2017-11-17 08:00 | 271 | 270
2017-11-17 08:30 | 269 | 268
2017-11-17 09:00 | 264 | 263
2017-11-17 09:30 | 264 | 264
2017-11-17 10:00 | 260 | 259
2017-11-17 10:30 | 247 | 247
2017-11-17 11:00 | 243 | 243
2017-11-17 11:30 | 244 | 244
2017-11-17 12:00 | 248 | 248
2017-11-17 12:30 | 251 | 251
2017-11-17 13:00 | 255 | 255
2017-11-17 13:30 | 256 | 256
2017-11-17 14:00 | 258 | 258
2017-11-17 14:30 | 258 | 258
2017-11-17 15:00 | 262 | 262
2017-11-17 15:30 | 266 | 266
2017-11-17 16:00 | 270 | 269
2017-11-17 16:30 | 272 | 271
2017-11-17 17:00 | 270 | 269
2017-11-17 17:30 | 269 | 268
2017-11-17 18:00 | 271 | 270
2017-11-17 18:30 | 277 | 277
2017-11-17 19:00 | 270 | 269
2017-11-17 19:30 | 269 | 268
2017-11-17 20:00 | 265 | 264
2017-11-17 20:30 | 257 | 255
2017-11-17 21:00 | 253 | 250
2017-11-17 21:30 | 245 | 241
2017-11-17 22:00 | 242 | 241
2017-11-17 22:30 | 237 | 236
2017-11-17 23:00 | 223 | 221
2017-11-17 23:30 | 214 | 212
2017-11-18 | 202 | 200
2017-11-18 00:30 | 196 | 193
2017-11-18 01:00 | 192 | 188
2017-11-18 01:30 | 188 | 185
2017-11-18 02:00 | 186 | 182
2017-11-18 02:30 | 186 | 182
2017-11-18 03:00 | 187 | 183
2017-11-18 03:30 | 187 | 183
2017-11-18 04:00 | 188 | 184
2017-11-18 04:30 | 187 | 183
2017-11-18 05:00 | 189 | 184
2017-11-18 05:30 | 199 | 195
2017-11-18 06:00 | 206 | 203
2017-11-18 06:30 | 216 | 214
2017-11-18 07:00 | 233 | 231
2017-11-18 07:30 | 243 | 242
2017-11-18 08:00 | 249 | 248
2017-11-18 08:30 | 253 | 253
2017-11-18 09:00 | 261 | 261
2017-11-18 09:30 | 267 | 267
2017-11-18 10:00 | 263 | 263
2017-11-18 10:30 | 259 | 259
2017-11-18 11:00 | 260 | 260
2017-11-18 11:30 | 259 | 259
2017-11-18 12:00 | 253 | 253
2017-11-18 12:30 | 253 | 253
2017-11-18 13:00 | 251 | 251
2017-11-18 13:30 | 249 | 249
2017-11-18 14:00 | 248 | 248
2017-11-18 14:30 | 251 | 251
2017-11-18 15:00 | 249 | 249
2017-11-18 15:30 | 254 | 254
2017-11-18 16:00 | 259 | 259
2017-11-18 16:30 | 260 | 260
2017-11-18 17:00 | 260 | 260
2017-11-18 17:30 | 258 | 258
2017-11-18 18:00 | 261 | 261
2017-11-18 18:30 | 269 | 269
2017-11-18 19:00 | 264 | 264
2017-11-18 19:30 | 262 | 262
2017-11-18 20:00 | 255 | 255
2017-11-18 20:30 | 248 | 248
2017-11-18 21:00 | 244 | 243
2017-11-18 21:30 | 239 | 238
2017-11-18 22:00 | 239 | 238
2017-11-18 22:30 | 234 | 233
2017-11-18 23:00 | 222 | 220
2017-11-18 23:30 | 215 | 213
2017-11-19 | 205 | 202
2017-11-19 00:30 | 200 | 197
2017-11-19 01:00 | 194 | 191
2017-11-19 01:30 | 189 | 185
2017-11-19 02:00 | 185 | 181
2017-11-19 02:30 | 184 | 180
2017-11-19 03:00 | 186 | 182
2017-11-19 03:30 | 185 | 181
2017-11-19 04:00 | 184 | 181
2017-11-19 04:30 | 183 | 181
2017-11-19 05:00 | 183 | 181
2017-11-19 05:30 | 191 | 189
2017-11-19 06:00 | 194 | 192
2017-11-19 06:30 | 191 | 190
2017-11-19 07:00 | 206 | 205
2017-11-19 07:30 | 221 | 221
2017-11-19 08:00 | 234 | 234
2017-11-19 08:30 | 235 | 235
2017-11-19 09:00 | 227 | 227
2017-11-19 09:30 | 233 | 233
2017-11-19 10:00 | 230 | 230
2017-11-19 10:30 | 229 | 228
2017-11-19 11:00 | 230 | 230
2017-11-19 11:30 | 230 | 230
2017-11-19 12:00 | 224 | 224
2017-11-19 12:30 | 217 | 216
2017-11-19 13:00 | 223 | 223
2017-11-19 13:30 | 230 | 230
2017-11-19 14:00 | 232 | 232
2017-11-19 14:30 | 228 | 227
2017-11-19 15:00 | 232 | 231
2017-11-19 15:30 | 242 | 242
2017-11-19 16:00 | 244 | 244
2017-11-19 16:30 | 246 | 246
2017-11-19 17:00 | 247 | 247
2017-11-19 17:30 | 250 | 250
2017-11-19 18:00 | 262 | 261
2017-11-19 18:30 | 274 | 274
2017-11-19 19:00 | 271 | 270
2017-11-19 19:30 | 268 | 267
2017-11-19 20:00 | 258 | 257
2017-11-19 20:30 | 250 | 248
2017-11-19 21:00 | 244 | 241
2017-11-19 21:30 | 236 | 233
2017-11-19 22:00 | 233 | 229
2017-11-19 22:30 | 227 | 223
2017-11-19 23:00 | 220 | 217
2017-11-19 23:30 | 212 | 209
2017-11-20 | 204 | 201
2017-11-20 00:30 | 200 | 197
2017-11-20 01:00 | 193 | 190
2017-11-20 01:30 | 189 | 184
2017-11-20 02:00 | 190 | 186
2017-11-20 02:30 | 187 | 183
2017-11-20 03:00 | 187 | 182
2017-11-20 03:30 | 187 | 183
2017-11-20 04:00 | 192 | 187
2017-11-20 04:30 | 193 | 188
2017-11-20 05:00 | 200 | 196
2017-11-20 05:30 | 205 | 202
2017-11-20 06:00 | 216 | 214
2017-11-20 06:30 | 233 | 228
2017-11-20 07:00 | 242 | 236
2017-11-20 07:30 | 246 | 242
2017-11-20 08:00 | 250 | 247
2017-11-20 08:30 | 250 | 247
2017-11-20 09:00 | 252 | 250
2017-11-20 09:30 | 246 | 244
2017-11-20 10:00 | 247 | 245
2017-11-20 10:30 | 244 | 243
2017-11-20 11:00 | 248 | 248
2017-11-20 11:30 | 244 | 244
2017-11-20 12:00 | 241 | 241
2017-11-20 12:30 | 244 | 244
2017-11-20 13:00 | 244 | 244
2017-11-20 13:30 | 256 | 256
2017-11-20 14:00 | 252 | 252
2017-11-20 14:30 | 252 | 251
2017-11-20 15:00 | 261 | 260
2017-11-20 15:30 | 271 | 270
2017-11-20 16:00 | 279 | 278
2017-11-20 16:30 | 290 | 289
2017-11-20 17:00 | 294 | 293
2017-11-20 17:30 | 294 | 292
2017-11-20 18:00 | 297 | 295
2017-11-20 18:30 | 308 | 307
2017-11-20 19:00 | 301 | 299
2017-11-20 19:30 | 294 | 293
2017-11-20 20:00 | 287 | 285
2017-11-20 20:30 | 273 | 272
2017-11-20 21:00 | 257 | 257
2017-11-20 21:30 | 247 | 247
2017-11-20 22:00 | 241 | 241
2017-11-20 22:30 | 239 | 239
2017-11-20 23:00 | 224 | 224
2017-11-20 23:30 | 212 | 212
2017-11-21 | 200 | 200
2017-11-21 00:30 | 194 | 194
2017-11-21 01:00 | 190 | 190
2017-11-21 01:30 | 187 | 187
2017-11-21 02:00 | 183 | 183
2017-11-21 02:30 | 182 | 182
2017-11-21 03:00 | 183 | 182
2017-11-21 03:30 | 183 | 183
2017-11-21 04:00 | 185 | 185
2017-11-21 04:30 | 186 | 186
2017-11-21 05:00 | 193 | 193
2017-11-21 05:30 | 204 | 204
2017-11-21 06:00 | 221 | 221
2017-11-21 06:30 | 232 | 232
2017-11-21 07:00 | 247 | 247
2017-11-21 07:30 | 254 | 254
2017-11-21 08:00 | 260 | 260
2017-11-21 08:30 | 254 | 254
2017-11-21 09:00 | 242 | 242
2017-11-21 09:30 | 244 | 244
2017-11-21 10:00 | 251 | 251
2017-11-21 10:30 | 250 | 250
2017-11-21 11:00 | 260 | 260
2017-11-21 11:30 | 261 | 261
2017-11-21 12:00 | 251 | 251
2017-11-21 12:30 | 261 | 261
2017-11-21 13:00 | 254 | 254
2017-11-21 13:30 | 256 | 256
2017-11-21 14:00 | 252 | 252
2017-11-21 14:30 | 249 | 249
2017-11-21 15:00 | 253 | 253
2017-11-21 15:30 | 269 | 269
2017-11-21 16:00 | 292 | 291
2017-11-21 16:30 | 305 | 300
2017-11-21 17:00 | 309 | 304
2017-11-21 17:30 | 311 | 306
2017-11-21 18:00 | 310 | 308
2017-11-21 18:30 | 311 | 310
2017-11-21 19:00 | 308 | 308
2017-11-21 19:30 | 308 | 307
2017-11-21 20:00 | 293 | 291
2017-11-21 20:30 | 272 | 271
2017-11-21 21:00 | 257 | 256
2017-11-21 21:30 | 247 | 246
2017-11-21 22:00 | 241 | 240
2017-11-21 22:30 | 232 | 231
2017-11-21 23:00 | 219 | 218
2017-11-21 23:30 | 211 | 211
2017-11-22 | 203 | 203
2017-11-22 00:30 | 201 | 200
2017-11-22 01:00 | 191 | 189
2017-11-22 01:30 | 186 | 185
2017-11-22 02:00 | 183 | 182
2017-11-22 02:30 | 182 | 181
2017-11-22 03:00 | 183 | 182
2017-11-22 03:30 | 181 | 179
2017-11-22 04:00 | 164 | 162
2017-11-22 04:30 | 188 | 186
2017-11-22 05:00 | 194 | 193
2017-11-22 05:30 | 203 | 202
2017-11-22 06:00 | 220 | 220
2017-11-22 06:30 | 233 | 233
2017-11-22 07:00 | 248 | 248
2017-11-22 07:30 | 250 | 249
2017-11-22 08:00 | 254 | 254
2017-11-22 08:30 | 258 | 258
2017-11-22 09:00 | 256 | 256
2017-11-22 09:30 | 251 | 250
2017-11-22 10:00 | 250 | 249
2017-11-22 10:30 | 252 | 252
2017-11-22 11:00 | 251 | 250
2017-11-22 11:30 | 254 | 253
2017-11-22 12:00 | 256 | 255
2017-11-22 12:30 | 253 | 253
2017-11-22 13:00 | 255 | 254
2017-11-22 13:30 | 258 | 257
2017-11-22 14:00 | 270 | 269
2017-11-22 14:30 | 266 | 265
2017-11-22 15:00 | 262 | 261
2017-11-22 15:30 | 276 | 274
2017-11-22 16:00 | 283 | 281
2017-11-22 16:30 | 298 | 296
2017-11-22 17:00 | 295 | 293
2017-11-22 17:30 | 297 | 294
2017-11-22 18:00 | 295 | 293
2017-11-22 18:30 | 304 | 303
2017-11-22 19:00 | 312 | 310
2017-11-22 19:30 | 311 | 309
2017-11-22 20:00 | 291 | 288
2017-11-22 20:30 | 270 | 269
2017-11-22 21:00 | 260 | 260
2017-11-22 21:30 | 250 | 250
2017-11-22 22:00 | 244 | 243
2017-11-22 22:30 | 239 | 239
2017-11-22 23:00 | 227 | 227
2017-11-22 23:30 | 217 | 217
2017-11-23 | 205 | 204
2017-11-23 00:30 | 198 | 197
2017-11-23 01:00 | 191 | 190
2017-11-23 01:30 | 187 | 186
2017-11-23 02:00 | 186 | 184
2017-11-23 02:30 | 186 | 184
2017-11-23 03:00 | 187 | 185
2017-11-23 03:30 | 187 | 185
2017-11-23 04:00 | 191 | 189
2017-11-23 04:30 | 192 | 190
2017-11-23 05:00 | 198 | 197
2017-11-23 05:30 | 207 | 206
2017-11-23 06:00 | 221 | 221
2017-11-23 06:30 | 233 | 233
2017-11-23 07:00 | 246 | 246
2017-11-23 07:30 | 250 | 250
2017-11-23 08:00 | 255 | 254
2017-11-23 08:30 | 254 | 253
2017-11-23 09:00 | 256 | 255
2017-11-23 09:30 | 254 | 253
2017-11-23 10:00 | 254 | 253
2017-11-23 10:30 | 256 | 256
2017-11-23 11:00 | 256 | 256
2017-11-23 11:30 | 252 | 252
2017-11-23 12:00 | 253 | 253
2017-11-23 12:30 | 253 | 253
2017-11-23 13:00 | 252 | 251
2017-11-23 13:30 | 255 | 255
2017-11-23 14:00 | 264 | 263
2017-11-23 14:30 | 276 | 276
2017-11-23 15:00 | 278 | 278
2017-11-23 15:30 | 283 | 283
2017-11-23 16:00 | 288 | 288
2017-11-23 16:30 | 296 | 295
2017-11-23 17:00 | 297 | 296
2017-11-23 17:30 | 296 | 295
2017-11-23 18:00 | 295 | 293
2017-11-23 18:30 | 303 | 301
2017-11-23 19:00 | 300 | 299
2017-11-23 19:30 | 297 | 295
2017-11-23 20:00 | 288 | 286
2017-11-23 20:30 | 275 | 272
2017-11-23 21:00 | 265 | 262
2017-11-23 21:30 | 252 | 251
2017-11-23 22:00 | 245 | 244
2017-11-23 22:30 | 238 | 237
2017-11-23 23:00 | 220 | 220
2017-11-23 23:30 | 209 | 208
2017-11-24 | 200 | 198
2017-11-24 00:30 | 195 | 194
2017-11-24 01:00 | 188 | 186
2017-11-24 01:30 | 184 | 182
2017-11-24 02:00 | 185 | 184
2017-11-24 02:30 | 185 | 184
2017-11-24 03:00 | 184 | 183
2017-11-24 03:30 | 185 | 184
2017-11-24 04:00 | 187 | 185
2017-11-24 04:30 | 190 | 188
2017-11-24 05:00 | 198 | 196
2017-11-24 05:30 | 203 | 201
2017-11-24 06:00 | 217 | 216
2017-11-24 06:30 | 236 | 236
2017-11-24 07:00 | 252 | 252
2017-11-24 07:30 | 260 | 259
2017-11-24 08:00 | 269 | 268
2017-11-24 08:30 | 270 | 270
2017-11-24 09:00 | 263 | 263
2017-11-24 09:30 | 263 | 263
2017-11-24 10:00 | 261 | 261
2017-11-24 10:30 | 262 | 262
2017-11-24 11:00 | 262 | 262
2017-11-24 11:30 | 261 | 261
2017-11-24 12:00 | 262 | 262
2017-11-24 12:30 | 265 | 265
2017-11-24 13:00 | 266 | 266
2017-11-24 13:30 | 273 | 273
2017-11-24 14:00 | 274 | 274
2017-11-24 14:30 | 281 | 281
2017-11-24 15:00 | 281 | 281
2017-11-24 15:30 | 287 | 287
2017-11-24 16:00 | 294 | 293
2017-11-24 16:30 | 297 | 297
2017-11-24 17:00 | 295 | 295
2017-11-24 17:30 | 295 | 293
2017-11-24 18:00 | 293 | 291
2017-11-24 18:30 | 298 | 297
2017-11-24 19:00 | 294 | 293
2017-11-24 19:30 | 291 | 289
2017-11-24 20:00 | 279 | 277
2017-11-24 20:30 | 273 | 270
2017-11-24 21:00 | 274 | 272
2017-11-24 21:30 | 275 | 272
2017-11-24 22:00 | 266 | 262
2017-11-24 22:30 | 260 | 260
2017-11-24 23:00 | 250 | 250
2017-11-24 23:30 | 233 | 233
2017-11-25 | 219 | 218
2017-11-25 00:30 | 205 | 205
2017-11-25 01:00 | 192 | 191
2017-11-25 01:30 | 185 | 184
2017-11-25 02:00 | 185 | 184
2017-11-25 02:30 | 186 | 185
2017-11-25 03:00 | 187 | 186
2017-11-25 03:30 | 186 | 185
2017-11-25 04:00 | 184 | 182
2017-11-25 04:30 | 183 | 181
2017-11-25 05:00 | 188 | 186
2017-11-25 05:30 | 194 | 193
2017-11-25 06:00 | 201 | 200
2017-11-25 06:30 | 208 | 207
2017-11-25 07:00 | 218 | 218
2017-11-25 07:30 | 232 | 232
2017-11-25 08:00 | 240 | 240
2017-11-25 08:30 | 247 | 247
2017-11-25 09:00 | 255 | 254
2017-11-25 09:30 | 252 | 251
2017-11-25 10:00 | 250 | 249
2017-11-25 10:30 | 248 | 247
2017-11-25 11:00 | 248 | 248
2017-11-25 11:30 | 245 | 244
2017-11-25 12:00 | 246 | 245
2017-11-25 12:30 | 242 | 242
2017-11-25 13:00 | 242 | 241
2017-11-25 13:30 | 248 | 247
2017-11-25 14:00 | 256 | 256
2017-11-25 14:30 | 261 | 260
2017-11-25 15:00 | 273 | 273
2017-11-25 15:30 | 282 | 282
2017-11-25 16:00 | 278 | 277
2017-11-25 16:30 | 287 | 286
2017-11-25 17:00 | 281 | 280
2017-11-25 17:30 | 282 | 281
2017-11-25 18:00 | 281 | 279
2017-11-25 18:30 | 286 | 285
2017-11-25 19:00 | 283 | 282
2017-11-25 19:30 | 284 | 283
2017-11-25 20:00 | 276 | 274
2017-11-25 20:30 | 267 | 265
2017-11-25 21:00 | 264 | 261
2017-11-25 21:30 | 259 | 256
2017-11-25 22:00 | 263 | 259
2017-11-25 22:30 | 255 | 252
2017-11-25 23:00 | 237 | 234
2017-11-25 23:30 | 222 | 222
2017-11-26 | 216 | 215
2017-11-26 00:30 | 208 | 207
2017-11-26 01:00 | 198 | 197
2017-11-26 01:30 | 192 | 191
2017-11-26 02:00 | 191 | 190
2017-11-26 02:30 | 189 | 188
2017-11-26 03:00 | 186 | 185
2017-11-26 03:30 | 188 | 187
2017-11-26 04:00 | 188 | 186
2017-11-26 04:30 | 188 | 186
2017-11-26 05:00 | 191 | 189
2017-11-26 05:30 | 193 | 192
2017-11-26 06:00 | 198 | 196
2017-11-26 06:30 | 201 | 200
2017-11-26 07:00 | 211 | 211
2017-11-26 07:30 | 221 | 221
2017-11-26 08:00 | 236 | 236
2017-11-26 08:30 | 242 | 242
2017-11-26 09:00 | 247 | 247
2017-11-26 09:30 | 251 | 251
2017-11-26 10:00 | 254 | 254
2017-11-26 10:30 | 250 | 250
2017-11-26 11:00 | 243 | 243
2017-11-26 11:30 | 238 | 238
2017-11-26 12:00 | 237 | 237
2017-11-26 12:30 | 239 | 239
2017-11-26 13:00 | 243 | 243
2017-11-26 13:30 | 250 | 249
2017-11-26 14:00 | 257 | 256
2017-11-26 14:30 | 259 | 259
2017-11-26 15:00 | 264 | 263
2017-11-26 15:30 | 279 | 278
2017-11-26 16:00 | 279 | 278
2017-11-26 16:30 | 287 | 286
2017-11-26 17:00 | 282 | 281
2017-11-26 17:30 | 281 | 279
2017-11-26 18:00 | 280 | 279
2017-11-26 18:30 | 285 | 284
2017-11-26 19:00 | 281 | 281
2017-11-26 19:30 | 278 | 277
2017-11-26 20:00 | 263 | 263
2017-11-26 20:30 | 257 | 257
2017-11-26 21:00 | 246 | 246
2017-11-26 21:30 | 238 | 238
2017-11-26 22:00 | 239 | 238
2017-11-26 22:30 | 233 | 232
2017-11-26 23:00 | 220 | 219
2017-11-26 23:30 | 211 | 210
2017-11-27 | 202 | 202
2017-11-27 00:30 | 197 | 196
2017-11-27 01:00 | 191 | 190
2017-11-27 01:30 | 188 | 186
2017-11-27 02:00 | 185 | 183
2017-11-27 02:30 | 187 | 186
2017-11-27 03:00 | 186 | 185
2017-11-27 03:30 | 190 | 189
2017-11-27 04:00 | 195 | 195
2017-11-27 04:30 | 194 | 193
2017-11-27 05:00 | 202 | 201
2017-11-27 05:30 | 217 | 217
2017-11-27 06:00 | 236 | 236
2017-11-27 06:30 | 251 | 251
2017-11-27 07:00 | 268 | 267
2017-11-27 07:30 | 274 | 273
2017-11-27 08:00 | 284 | 284
2017-11-27 08:30 | 282 | 282
2017-11-27 09:00 | 281 | 281
2017-11-27 09:30 | 280 | 280
2017-11-27 10:00 | 285 | 285
2017-11-27 10:30 | 288 | 287
2017-11-27 11:00 | 292 | 292
2017-11-27 11:30 | 292 | 292
2017-11-27 12:00 | 289 | 289
2017-11-27 12:30 | 286 | 286
2017-11-27 13:00 | 287 | 287
2017-11-27 13:30 | 292 | 292
2017-11-27 14:00 | 295 | 295
2017-11-27 14:30 | 300 | 300
2017-11-27 15:00 | 305 | 305
2017-11-27 15:30 | 308 | 308
2017-11-27 16:00 | 315 | 315
2017-11-27 16:30 | 319 | 319
2017-11-27 17:00 | 314 | 314
2017-11-27 17:30 | 311 | 311
2017-11-27 18:00 | 305 | 305
2017-11-27 18:30 | 314 | 314
2017-11-27 19:00 | 309 | 309
2017-11-27 19:30 | 306 | 306
2017-11-27 20:00 | 296 | 295
2017-11-27 20:30 | 284 | 284
2017-11-27 21:00 | 271 | 271
2017-11-27 21:30 | 260 | 260
2017-11-27 22:00 | 254 | 254
2017-11-27 22:30 | 242 | 241
2017-11-27 23:00 | 223 | 222
2017-11-27 23:30 | 211 | 210
2017-11-28 | 197 | 197
2017-11-28 00:30 | 194 | 194
2017-11-28 01:00 | 190 | 190
2017-11-28 01:30 | 187 | 187
2017-11-28 02:00 | 183 | 183
2017-11-28 02:30 | 181 | 181
2017-11-28 03:00 | 178 | 178
2017-11-28 03:30 | 194 | 193
2017-11-28 04:00 | 202 | 202
2017-11-28 04:30 | 199 | 199
2017-11-28 05:00 | 214 | 213
2017-11-28 05:30 | 226 | 226
2017-11-28 06:00 | 247 | 246
2017-11-28 06:30 | 262 | 261
2017-11-28 07:00 | 282 | 281
2017-11-28 07:30 | 291 | 291
2017-11-28 08:00 | 297 | 297
2017-11-28 08:30 | 298 | 298
2017-11-28 09:00 | 303 | 303
2017-11-28 09:30 | 302 | 302
2017-11-28 10:00 | 303 | 303
2017-11-28 10:30 | 304 | 304
2017-11-28 11:00 | 305 | 305
2017-11-28 11:30 | 307 | 306
2017-11-28 12:00 | 314 | 313
2017-11-28 12:30 | 323 | 323
2017-11-28 13:00 | 328 | 328
2017-11-28 13:30 | 331 | 330
2017-11-28 14:00 | 329 | 329
2017-11-28 14:30 | 329 | 328
2017-11-28 15:00 | 343 | 340
2017-11-28 15:30 | 347 | 345
2017-11-28 16:00 | 352 | 350
2017-11-28 16:30 | 359 | 356
2017-11-28 17:00 | 356 | 353
2017-11-28 17:30 | 355 | 351
2017-11-28 18:00 | 354 | 350
2017-11-28 18:30 | 345 | 342
2017-11-28 19:00 | 331 | 327
2017-11-28 19:30 | 329 | 325
2017-11-28 20:00 | 318 | 316
2017-11-28 20:30 | 304 | 304
2017-11-28 21:00 | 285 | 285
2017-11-28 21:30 | 266 | 265
2017-11-28 22:00 | 260 | 259
2017-11-28 22:30 | 252 | 252
2017-11-28 23:00 | 231 | 231
2017-11-28 23:30 | 216 | 214
2017-11-29 | 206 | 204
2017-11-29 00:30 | 201 | 198
2017-11-29 01:00 | 201 | 199
2017-11-29 01:30 | 199 | 197
2017-11-29 02:00 | 200 | 197
2017-11-29 02:30 | 199 | 196
2017-11-29 03:00 | 200 | 197
2017-11-29 03:30 | 203 | 200
2017-11-29 04:00 | 206 | 204
2017-11-29 04:30 | 206 | 204
2017-11-29 05:00 | 213 | 211
2017-11-29 05:30 | 223 | 222
2017-11-29 06:00 | 244 | 244
2017-11-29 06:30 | 262 | 261
2017-11-29 07:00 | 279 | 278
2017-11-29 07:30 | 284 | 284
2017-11-29 08:00 | 297 | 297
2017-11-29 08:30 | 303 | 302
2017-11-29 09:00 | 305 | 304
2017-11-29 09:30 | 296 | 295
2017-11-29 10:00 | 295 | 293
2017-11-29 10:30 | 297 | 295
2017-11-29 11:00 | 296 | 295
2017-11-29 11:30 | 292 | 290
2017-11-29 12:00 | 289 | 288
2017-11-29 12:30 | 296 | 294
2017-11-29 13:00 | 302 | 300
2017-11-29 13:30 | 312 | 310
2017-11-29 14:00 | 313 | 311
2017-11-29 14:30 | 320 | 317
2017-11-29 15:00 | 308 | 305
2017-11-29 15:30 | 310 | 307
2017-11-29 16:00 | 314 | 310
2017-11-29 16:30 | 320 | 315
2017-11-29 17:00 | 312 | 307
2017-11-29 17:30 | 317 | 313
2017-11-29 18:00 | 318 | 316
2017-11-29 18:30 | 320 | 319
2017-11-29 19:00 | 318 | 318
2017-11-29 19:30 | 315 | 315
2017-11-29 20:00 | 304 | 303
2017-11-29 20:30 | 290 | 289
2017-11-29 21:00 | 279 | 277
2017-11-29 21:30 | 269 | 266
2017-11-29 22:00 | 262 | 260
2017-11-29 22:30 | 258 | 255
2017-11-29 23:00 | 236 | 236
2017-11-29 23:30 | 217 | 217
2017-11-30 | 208 | 207
2017-11-30 00:30 | 203 | 203
2017-11-30 01:00 | 200 | 199
2017-11-30 01:30 | 196 | 195
2017-11-30 02:00 | 194 | 193
2017-11-30 02:30 | 193 | 191
2017-11-30 03:00 | 191 | 189
2017-11-30 03:30 | 200 | 199
2017-11-30 04:00 | 205 | 204
2017-11-30 04:30 | 209 | 208
2017-11-30 05:00 | 217 | 217
2017-11-30 05:30 | 230 | 229
2017-11-30 06:00 | 267 | 266
2017-11-30 06:30 | 294 | 294
2017-11-30 07:00 | 297 | 296
2017-11-30 07:30 | 323 | 322
2017-11-30 08:00 | 330 | 329
2017-11-30 08:30 | 328 | 328
2017-11-30 09:00 | 336 | 335
2017-11-30 09:30 | 350 | 346
2017-11-30 10:00 | 353 | 350
2017-11-30 10:30 | 344 | 341
2017-11-30 11:00 | 341 | 338
2017-11-30 11:30 | 338 | 335
2017-11-30 12:00 | 322 | 319
2017-11-30 12:30 | 332 | 328
2017-11-30 13:00 | 339 | 335
2017-11-30 13:30 | 355 | 352
2017-11-30 14:00 | 364 | 361
2017-11-30 14:30 | 373 | 370
2017-11-30 15:00 | 361 | 357
2017-11-30 15:30 | 368 | 363
2017-11-30 16:00 | 355 | 351
2017-11-30 16:30 | 351 | 347
2017-11-30 17:00 | 346 | 340
2017-11-30 17:30 | 329 | 325
2017-11-30 18:00 | 310 | 308
2017-11-30 18:30 | 314 | 314
2017-11-30 19:00 | 309 | 309
2017-11-30 19:30 | 307 | 307
2017-11-30 20:00 | 303 | 303
2017-11-30 20:30 | 290 | 290
2017-11-30 21:00 | 277 | 277
2017-11-30 21:30 | 269 | 268
2017-11-30 22:00 | 264 | 262
2017-11-30 22:30 | 253 | 252
2017-11-30 23:00 | 236 | 235
2017-11-30 23:30 | 227 | 226
2017-12-01 | 214 | 212
2017-12-01 00:30 | 207 | 205
2017-12-01 01:00 | 201 | 198
2017-12-01 01:30 | 199 | 197
2017-12-01 02:00 | 198 | 197
2017-12-01 02:30 | 196 | 195
2017-12-01 03:00 | 194 | 193
2017-12-01 03:30 | 196 | 195
2017-12-01 04:00 | 203 | 202
2017-12-01 04:30 | 203 | 202
2017-12-01 05:00 | 212 | 211
2017-12-01 05:30 | 222 | 222
2017-12-01 06:00 | 240 | 240
2017-12-01 06:30 | 251 | 251
2017-12-01 07:00 | 270 | 269
2017-12-01 07:30 | 272 | 271
2017-12-01 08:00 | 286 | 285
2017-12-01 08:30 | 288 | 288
2017-12-01 09:00 | 288 | 288
2017-12-01 09:30 | 291 | 291
2017-12-01 10:00 | 295 | 295
2017-12-01 10:30 | 298 | 298
2017-12-01 11:00 | 288 | 288
2017-12-01 11:30 | 283 | 283
2017-12-01 12:00 | 282 | 282
2017-12-01 12:30 | 284 | 284
2017-12-01 13:00 | 286 | 286
2017-12-01 13:30 | 293 | 293
2017-12-01 14:00 | 295 | 295
2017-12-01 14:30 | 301 | 301
2017-12-01 15:00 | 310 | 310
2017-12-01 15:30 | 314 | 314
2017-12-01 16:00 | 318 | 317
2017-12-01 16:30 | 317 | 317
2017-12-01 17:00 | 308 | 307
2017-12-01 17:30 | 300 | 299
2017-12-01 18:00 | 296 | 295
2017-12-01 18:30 | 304 | 302
2017-12-01 19:00 | 303 | 302
2017-12-01 19:30 | 302 | 301
2017-12-01 20:00 | 288 | 288
2017-12-01 20:30 | 276 | 276
2017-12-01 21:00 | 270 | 269
2017-12-01 21:30 | 261 | 261
2017-12-01 22:00 | 259 | 259
2017-12-01 22:30 | 256 | 255
2017-12-01 23:00 | 243 | 241
2017-12-01 23:30 | 228 | 226
2017-12-02 | 219 | 217
2017-12-02 00:30 | 210 | 208
2017-12-02 01:00 | 201 | 200
2017-12-02 01:30 | 190 | 189
2017-12-02 02:00 | 189 | 187
2017-12-02 02:30 | 185 | 184
2017-12-02 03:00 | 181 | 180
2017-12-02 03:30 | 182 | 180
2017-12-02 04:00 | 183 | 181
2017-12-02 04:30 | 184 | 182
2017-12-02 05:00 | 189 | 187
2017-12-02 05:30 | 197 | 196
2017-12-02 06:00 | 208 | 207
2017-12-02 06:30 | 216 | 215
2017-12-02 07:00 | 223 | 223
2017-12-02 07:30 | 234 | 234
2017-12-02 08:00 | 243 | 243
2017-12-02 08:30 | 257 | 257
2017-12-02 09:00 | 272 | 272
2017-12-02 09:30 | 273 | 273
2017-12-02 10:00 | 275 | 275
2017-12-02 10:30 | 265 | 265
2017-12-02 11:00 | 248 | 247
2017-12-02 11:30 | 243 | 243
2017-12-02 12:00 | 242 | 242
2017-12-02 12:30 | 253 | 253
2017-12-02 13:00 | 253 | 252
2017-12-02 13:30 | 251 | 251
2017-12-02 14:00 | 256 | 256
2017-12-02 14:30 | 266 | 265
2017-12-02 15:00 | 277 | 277
2017-12-02 15:30 | 280 | 280
2017-12-02 16:00 | 287 | 287
2017-12-02 16:30 | 297 | 294
2017-12-02 17:00 | 299 | 295
2017-12-02 17:30 | 299 | 295
2017-12-02 18:00 | 299 | 294
2017-12-02 18:30 | 305 | 302
2017-12-02 19:00 | 301 | 297
2017-12-02 19:30 | 297 | 292
2017-12-02 20:00 | 286 | 283
2017-12-02 20:30 | 270 | 270
2017-12-02 21:00 | 263 | 262
2017-12-02 21:30 | 251 | 250
2017-12-02 22:00 | 244 | 244
2017-12-02 22:30 | 234 | 234
2017-12-02 23:00 | 224 | 224
2017-12-02 23:30 | 209 | 208
2017-12-03 | 199 | 198
2017-12-03 00:30 | 196 | 195
2017-12-03 01:00 | 189 | 188
2017-12-03 01:30 | 186 | 185
2017-12-03 02:00 | 180 | 179
2017-12-03 02:30 | 179 | 178
2017-12-03 03:00 | 179 | 178
2017-12-03 03:30 | 178 | 177
2017-12-03 04:00 | 176 | 175
2017-12-03 04:30 | 176 | 175
2017-12-03 05:00 | 171 | 171
2017-12-03 05:30 | 179 | 179
2017-12-03 06:00 | 188 | 188
2017-12-03 06:30 | 196 | 196
2017-12-03 07:00 | 205 | 205
2017-12-03 07:30 | 213 | 213
2017-12-03 08:00 | 220 | 220
2017-12-03 08:30 | 230 | 230
2017-12-03 09:00 | 238 | 238
2017-12-03 09:30 | 238 | 237
2017-12-03 10:00 | 247 | 247
2017-12-03 10:30 | 248 | 248
2017-12-03 11:00 | 255 | 254
2017-12-03 11:30 | 254 | 252
2017-12-03 12:00 | 253 | 250
2017-12-03 12:30 | 260 | 257
2017-12-03 13:00 | 265 | 262
2017-12-03 13:30 | 271 | 268
2017-12-03 14:00 | 283 | 280
2017-12-03 14:30 | 281 | 278
2017-12-03 15:00 | 277 | 275
2017-12-03 15:30 | 290 | 288
2017-12-03 16:00 | 311 | 309
2017-12-03 16:30 | 320 | 318
2017-12-03 17:00 | 322 | 319
2017-12-03 17:30 | 324 | 321
2017-12-03 18:00 | 323 | 319
2017-12-03 18:30 | 322 | 319
2017-12-03 19:00 | 319 | 316
2017-12-03 19:30 | 315 | 311
2017-12-03 20:00 | 306 | 302
2017-12-03 20:30 | 284 | 284
2017-12-03 21:00 | 272 | 272
2017-12-03 21:30 | 257 | 256
2017-12-03 22:00 | 253 | 251
2017-12-03 22:30 | 242 | 240
2017-12-03 23:00 | 227 | 224
2017-12-03 23:30 | 215 | 213
2017-12-04 | 203 | 202
2017-12-04 00:30 | 196 | 196
2017-12-04 01:00 | 191 | 191
2017-12-04 01:30 | 190 | 190
2017-12-04 02:00 | 191 | 191
2017-12-04 02:30 | 191 | 191
2017-12-04 03:00 | 191 | 191
2017-12-04 03:30 | 192 | 192
2017-12-04 04:00 | 190 | 190
2017-12-04 04:30 | 190 | 190
2017-12-04 05:00 | 197 | 197
2017-12-04 05:30 | 206 | 206
2017-12-04 06:00 | 228 | 228
2017-12-04 06:30 | 238 | 238
2017-12-04 07:00 | 261 | 261
2017-12-04 07:30 | 281 | 281
2017-12-04 08:00 | 292 | 292
2017-12-04 08:30 | 295 | 294
2017-12-04 09:00 | 281 | 281
2017-12-04 09:30 | 293 | 293
2017-12-04 10:00 | 293 | 293
2017-12-04 10:30 | 304 | 304
2017-12-04 11:00 | 317 | 317
2017-12-04 11:30 | 324 | 322
2017-12-04 12:00 | 330 | 328
2017-12-04 12:30 | 330 | 328
2017-12-04 13:00 | 329 | 327
2017-12-04 13:30 | 323 | 320
2017-12-04 14:00 | 314 | 314
2017-12-04 14:30 | 302 | 302
2017-12-04 15:00 | 294 | 294
2017-12-04 15:30 | 293 | 293
2017-12-04 16:00 | 292 | 292
2017-12-04 16:30 | 296 | 296
2017-12-04 17:00 | 300 | 300
2017-12-04 17:30 | 300 | 300
2017-12-04 18:00 | 294 | 294
2017-12-04 18:30 | 297 | 297
2017-12-04 19:00 | 293 | 293
2017-12-04 19:30 | 288 | 288
2017-12-04 20:00 | 275 | 275
2017-12-04 20:30 | 267 | 267
2017-12-04 21:00 | 255 | 254
2017-12-04 21:30 | 242 | 241
2017-12-04 22:00 | 237 | 236
2017-12-04 22:30 | 231 | 230
2017-12-04 23:00 | 219 | 219
2017-12-04 23:30 | 206 | 205
2017-12-05 | 194 | 193
2017-12-05 00:30 | 191 | 190
2017-12-05 01:00 | 188 | 186
2017-12-05 01:30 | 181 | 179
2017-12-05 02:00 | 174 | 173
2017-12-05 02:30 | 173 | 173
2017-12-05 03:00 | 175 | 175
2017-12-05 03:30 | 179 | 178
2017-12-05 04:00 | 180 | 180
2017-12-05 04:30 | 183 | 183
2017-12-05 05:00 | 192 | 192
2017-12-05 05:30 | 200 | 200
2017-12-05 06:00 | 219 | 219
2017-12-05 06:30 | 228 | 228
2017-12-05 07:00 | 240 | 240
2017-12-05 07:30 | 255 | 255
2017-12-05 08:00 | 266 | 266
2017-12-05 08:30 | 274 | 274
2017-12-05 09:00 | 273 | 273
2017-12-05 09:30 | 273 | 273
2017-12-05 10:00 | 257 | 257
2017-12-05 10:30 | 267 | 267
2017-12-05 11:00 | 279 | 279
2017-12-05 11:30 | 263 | 263
2017-12-05 12:00 | 267 | 267
2017-12-05 12:30 | 269 | 269
2017-12-05 13:00 | 266 | 266
2017-12-05 13:30 | 265 | 265
2017-12-05 14:00 | 271 | 271
2017-12-05 14:30 | 282 | 282
2017-12-05 15:00 | 293 | 293
2017-12-05 15:30 | 306 | 306
2017-12-05 16:00 | 309 | 309
2017-12-05 16:30 | 314 | 314
2017-12-05 17:00 | 314 | 313
2017-12-05 17:30 | 309 | 308
2017-12-05 18:00 | 304 | 303
2017-12-05 18:30 | 311 | 310
2017-12-05 19:00 | 304 | 303
2017-12-05 19:30 | 296 | 295
2017-12-05 20:00 | 289 | 288
2017-12-05 20:30 | 280 | 277
2017-12-05 21:00 | 267 | 264
2017-12-05 21:30 | 253 | 250
2017-12-05 22:00 | 248 | 246
2017-12-05 22:30 | 235 | 233
2017-12-05 23:00 | 213 | 212
2017-12-05 23:30 | 198 | 198
2017-12-06 | 187 | 186
2017-12-06 00:30 | 183 | 182
2017-12-06 01:00 | 181 | 180
2017-12-06 01:30 | 181 | 179
2017-12-06 02:00 | 179 | 177
2017-12-06 02:30 | 179 | 177
2017-12-06 03:00 | 180 | 178
2017-12-06 03:30 | 178 | 177
2017-12-06 04:00 | 177 | 175
2017-12-06 04:30 | 178 | 177
2017-12-06 05:00 | 187 | 186
2017-12-06 05:30 | 196 | 196
2017-12-06 06:00 | 217 | 217
2017-12-06 06:30 | 237 | 237
2017-12-06 07:00 | 255 | 255
2017-12-06 07:30 | 259 | 259
2017-12-06 08:00 | 264 | 264
2017-12-06 08:30 | 264 | 264
2017-12-06 09:00 | 266 | 266
2017-12-06 09:30 | 267 | 267
2017-12-06 10:00 | 267 | 267
2017-12-06 10:30 | 267 | 266
2017-12-06 11:00 | 259 | 258
2017-12-06 11:30 | 258 | 258
2017-12-06 12:00 | 255 | 255
2017-12-06 12:30 | 256 | 256
2017-12-06 13:00 | 262 | 261
2017-12-06 13:30 | 267 | 267
2017-12-06 14:00 | 281 | 280
2017-12-06 14:30 | 284 | 282
2017-12-06 15:00 | 290 | 287
2017-12-06 15:30 | 302 | 300
2017-12-06 16:00 | 314 | 312
2017-12-06 16:30 | 323 | 321
2017-12-06 17:00 | 325 | 322
2017-12-06 17:30 | 320 | 316
2017-12-06 18:00 | 312 | 309
2017-12-06 18:30 | 318 | 315
2017-12-06 19:00 | 317 | 315
2017-12-06 19:30 | 312 | 309
2017-12-06 20:00 | 299 | 297
2017-12-06 20:30 | 283 | 282
2017-12-06 21:00 | 272 | 270
2017-12-06 21:30 | 261 | 258
2017-12-06 22:00 | 253 | 250
2017-12-06 22:30 | 234 | 234
2017-12-06 23:00 | 217 | 217
2017-12-06 23:30 | 205 | 204
2017-12-07 | 199 | 199
2017-12-07 00:30 | 197 | 196
2017-12-07 01:00 | 188 | 187
2017-12-07 01:30 | 186 | 185
2017-12-07 02:00 | 190 | 189
2017-12-07 02:30 | 191 | 190
2017-12-07 03:00 | 193 | 191
2017-12-07 03:30 | 194 | 193
2017-12-07 04:00 | 194 | 193
2017-12-07 04:30 | 195 | 194
2017-12-07 05:00 | 197 | 196
2017-12-07 05:30 | 206 | 205
2017-12-07 06:00 | 220 | 220
2017-12-07 06:30 | 235 | 235
2017-12-07 07:00 | 248 | 248
2017-12-07 07:30 | 252 | 252
2017-12-07 08:00 | 253 | 253
2017-12-07 08:30 | 262 | 262
2017-12-07 09:00 | 269 | 268
2017-12-07 09:30 | 274 | 272
2017-12-07 10:00 | 275 | 274
2017-12-07 10:30 | 278 | 277
2017-12-07 11:00 | 283 | 282
2017-12-07 11:30 | 283 | 282
2017-12-07 12:00 | 285 | 284
2017-12-07 12:30 | 289 | 289
2017-12-07 13:00 | 296 | 295
2017-12-07 13:30 | 306 | 305
2017-12-07 14:00 | 317 | 315
2017-12-07 14:30 | 325 | 322
2017-12-07 15:00 | 333 | 331
2017-12-07 15:30 | 344 | 342
2017-12-07 16:00 | 354 | 352
2017-12-07 16:30 | 364 | 361
2017-12-07 17:00 | 365 | 362
2017-12-07 17:30 | 363 | 359
2017-12-07 18:00 | 360 | 355
2017-12-07 18:30 | 366 | 362
2017-12-07 19:00 | 366 | 362
2017-12-07 19:30 | 362 | 357
2017-12-07 20:00 | 349 | 345
2017-12-07 20:30 | 329 | 327
2017-12-07 21:00 | 309 | 308
2017-12-07 21:30 | 288 | 287
2017-12-07 22:00 | 283 | 281
2017-12-07 22:30 | 278 | 276
2017-12-07 23:00 | 257 | 255
2017-12-07 23:30 | 237 | 235
2017-12-08 | 220 | 219
2017-12-08 00:30 | 210 | 208
2017-12-08 01:00 | 203 | 201
2017-12-08 01:30 | 199 | 196
2017-12-08 02:00 | 196 | 194
2017-12-08 02:30 | 192 | 191
2017-12-08 03:00 | 192 | 191
2017-12-08 03:30 | 193 | 192
2017-12-08 04:00 | 197 | 196
2017-12-08 04:30 | 199 | 198
2017-12-08 05:00 | 208 | 207
2017-12-08 05:30 | 217 | 217
2017-12-08 06:00 | 234 | 234
2017-12-08 06:30 | 253 | 253
2017-12-08 07:00 | 269 | 269
2017-12-08 07:30 | 284 | 284
2017-12-08 08:00 | 291 | 291
2017-12-08 08:30 | 298 | 298
2017-12-08 09:00 | 306 | 306
2017-12-08 09:30 | 311 | 311
2017-12-08 10:00 | 323 | 322
2017-12-08 10:30 | 336 | 334
2017-12-08 11:00 | 354 | 351
2017-12-08 11:30 | 376 | 375
2017-12-08 12:00 | 389 | 388
2017-12-08 12:30 | 378 | 377
2017-12-08 13:00 | 351 | 350
2017-12-08 13:30 | 339 | 335
2017-12-08 14:00 | 331 | 324
2017-12-08 14:30 | 329 | 322
2017-12-08 15:00 | 319 | 316
2017-12-08 15:30 | 317 | 315
2017-12-08 16:00 | 312 | 310
2017-12-08 16:30 | 316 | 315
2017-12-08 17:00 | 317 | 315
2017-12-08 17:30 | 312 | 310
2017-12-08 18:00 | 306 | 304
2017-12-08 18:30 | 311 | 310
2017-12-08 19:00 | 309 | 309
2017-12-08 19:30 | 306 | 305
2017-12-08 20:00 | 298 | 298
2017-12-08 20:30 | 286 | 286
2017-12-08 21:00 | 277 | 277
2017-12-08 21:30 | 267 | 266
2017-12-08 22:00 | 266 | 266
2017-12-08 22:30 | 266 | 265
2017-12-08 23:00 | 248 | 248
2017-12-08 23:30 | 230 | 229
2017-12-09 | 216 | 215
2017-12-09 00:30 | 205 | 205
2017-12-09 01:00 | 198 | 197
2017-12-09 01:30 | 193 | 192
2017-12-09 02:00 | 190 | 189
2017-12-09 02:30 | 188 | 187
2017-12-09 03:00 | 187 | 186
2017-12-09 03:30 | 186 | 185
2017-12-09 04:00 | 187 | 186
2017-12-09 04:30 | 187 | 185
2017-12-09 05:00 | 190 | 188
2017-12-09 05:30 | 196 | 194
2017-12-09 06:00 | 206 | 205
2017-12-09 06:30 | 214 | 214
2017-12-09 07:00 | 225 | 225
2017-12-09 07:30 | 235 | 235
2017-12-09 08:00 | 244 | 244
2017-12-09 08:30 | 251 | 251
2017-12-09 09:00 | 253 | 253
2017-12-09 09:30 | 253 | 253
2017-12-09 10:00 | 253 | 253
2017-12-09 10:30 | 252 | 252
2017-12-09 11:00 | 252 | 252
2017-12-09 11:30 | 255 | 255
2017-12-09 12:00 | 257 | 257
2017-12-09 12:30 | 262 | 262
2017-12-09 13:00 | 268 | 268
2017-12-09 13:30 | 279 | 278
2017-12-09 14:00 | 292 | 291
2017-12-09 14:30 | 304 | 303
2017-12-09 15:00 | 317 | 316
2017-12-09 15:30 | 326 | 325
2017-12-09 16:00 | 327 | 325
2017-12-09 16:30 | 326 | 324
2017-12-09 17:00 | 321 | 319
2017-12-09 17:30 | 314 | 312
2017-12-09 18:00 | 303 | 301
2017-12-09 18:30 | 302 | 300
2017-12-09 19:00 | 296 | 295
2017-12-09 19:30 | 290 | 290
2017-12-09 20:00 | 282 | 282
2017-12-09 20:30 | 270 | 269
2017-12-09 21:00 | 261 | 261
2017-12-09 21:30 | 252 | 251
2017-12-09 22:00 | 252 | 252
2017-12-09 22:30 | 253 | 253
2017-12-09 23:00 | 237 | 237
2017-12-09 23:30 | 218 | 218
2017-12-10 | 204 | 204
2017-12-10 00:30 | 195 | 195
2017-12-10 01:00 | 188 | 188
2017-12-10 01:30 | 184 | 184
2017-12-10 02:00 | 181 | 181
2017-12-10 02:30 | 180 | 180
2017-12-10 03:00 | 179 | 179
2017-12-10 03:30 | 179 | 178
2017-12-10 04:00 | 180 | 179
2017-12-10 04:30 | 176 | 176
2017-12-10 05:00 | 178 | 178
2017-12-10 05:30 | 181 | 181
2017-12-10 06:00 | 188 | 188
2017-12-10 06:30 | 193 | 193
2017-12-10 07:00 | 200 | 200
2017-12-10 07:30 | 208 | 207
2017-12-10 08:00 | 220 | 218
2017-12-10 08:30 | 223 | 222
2017-12-10 09:00 | 228 | 227
2017-12-10 09:30 | 228 | 227
2017-12-10 10:00 | 233 | 233
2017-12-10 10:30 | 234 | 233
2017-12-10 11:00 | 228 | 227
2017-12-10 11:30 | 228 | 227
2017-12-10 12:00 | 225 | 225
2017-12-10 12:30 | 225 | 224
2017-12-10 13:00 | 229 | 228
2017-12-10 13:30 | 234 | 234
2017-12-10 14:00 | 241 | 241
2017-12-10 14:30 | 249 | 248
2017-12-10 15:00 | 259 | 259
2017-12-10 15:30 | 267 | 266
2017-12-10 16:00 | 274 | 273
2017-12-10 16:30 | 285 | 285
2017-12-10 17:00 | 293 | 291
2017-12-10 17:30 | 294 | 292
2017-12-10 18:00 | 296 | 293
2017-12-10 18:30 | 303 | 301
2017-12-10 19:00 | 306 | 304
2017-12-10 19:30 | 306 | 302
2017-12-10 20:00 | 298 | 294
2017-12-10 20:30 | 277 | 277
2017-12-10 21:00 | 267 | 267
2017-12-10 21:30 | 253 | 253
2017-12-10 22:00 | 251 | 251
2017-12-10 22:30 | 250 | 250
2017-12-10 23:00 | 233 | 232
2017-12-10 23:30 | 215 | 214
2017-12-11 | 201 | 200
2017-12-11 00:30 | 193 | 191
2017-12-11 01:00 | 187 | 185
2017-12-11 01:30 | 184 | 182
2017-12-11 02:00 | 183 | 181
2017-12-11 02:30 | 182 | 180
2017-12-11 03:00 | 183 | 181
2017-12-11 03:30 | 179 | 177
2017-12-11 04:00 | 182 | 180
2017-12-11 04:30 | 185 | 183
2017-12-11 05:00 | 195 | 193
2017-12-11 05:30 | 205 | 204
2017-12-11 06:00 | 227 | 227
2017-12-11 06:30 | 240 | 240
2017-12-11 07:00 | 254 | 254
2017-12-11 07:30 | 264 | 263
2017-12-11 08:00 | 269 | 269
2017-12-11 08:30 | 276 | 276
2017-12-11 09:00 | 283 | 283
2017-12-11 09:30 | 282 | 282
2017-12-11 10:00 | 286 | 286
2017-12-11 10:30 | 286 | 286
2017-12-11 11:00 | 285 | 285
2017-12-11 11:30 | 286 | 286
2017-12-11 12:00 | 284 | 284
2017-12-11 12:30 | 275 | 275
2017-12-11 13:00 | 272 | 272
2017-12-11 13:30 | 276 | 276
2017-12-11 14:00 | 280 | 280
2017-12-11 14:30 | 286 | 286
2017-12-11 15:00 | 294 | 294
2017-12-11 15:30 | 305 | 305
2017-12-11 16:00 | 313 | 313
2017-12-11 16:30 | 319 | 319
2017-12-11 17:00 | 320 | 319
2017-12-11 17:30 | 319 | 318
2017-12-11 18:00 | 320 | 317
2017-12-11 18:30 | 326 | 323
2017-12-11 19:00 | 326 | 323
2017-12-11 19:30 | 321 | 318
2017-12-11 20:00 | 308 | 306
2017-12-11 20:30 | 292 | 290
2017-12-11 21:00 | 279 | 277
2017-12-11 21:30 | 264 | 263
2017-12-11 22:00 | 260 | 258
2017-12-11 22:30 | 258 | 257
2017-12-11 23:00 | 240 | 239
2017-12-11 23:30 | 222 | 220
2017-12-12 | 207 | 205
2017-12-12 00:30 | 198 | 195
2017-12-12 01:00 | 191 | 188
2017-12-12 01:30 | 188 | 185
2017-12-12 02:00 | 186 | 183
2017-12-12 02:30 | 185 | 181
2017-12-12 03:00 | 185 | 181
2017-12-12 03:30 | 188 | 184
2017-12-12 04:00 | 191 | 188
2017-12-12 04:30 | 194 | 191
2017-12-12 05:00 | 204 | 201
2017-12-12 05:30 | 213 | 211
2017-12-12 06:00 | 229 | 228
2017-12-12 06:30 | 241 | 240
2017-12-12 07:00 | 254 | 254
2017-12-12 07:30 | 262 | 262
2017-12-12 08:00 | 272 | 272
2017-12-12 08:30 | 281 | 280
2017-12-12 09:00 | 287 | 286
2017-12-12 09:30 | 281 | 280
2017-12-12 10:00 | 276 | 275
2017-12-12 10:30 | 274 | 273
2017-12-12 11:00 | 267 | 266
2017-12-12 11:30 | 264 | 263
2017-12-12 12:00 | 264 | 263
2017-12-12 12:30 | 266 | 265
2017-12-12 13:00 | 269 | 268
2017-12-12 13:30 | 275 | 274
2017-12-12 14:00 | 282 | 282
2017-12-12 14:30 | 290 | 290
2017-12-12 15:00 | 299 | 299
2017-12-12 15:30 | 309 | 308
2017-12-12 16:00 | 317 | 317
2017-12-12 16:30 | 330 | 328
2017-12-12 17:00 | 334 | 329
2017-12-12 17:30 | 328 | 324
2017-12-12 18:00 | 327 | 323
2017-12-12 18:30 | 334 | 330
2017-12-12 19:00 | 334 | 330
2017-12-12 19:30 | 324 | 323
2017-12-12 20:00 | 313 | 312
2017-12-12 20:30 | 299 | 296
2017-12-12 21:00 | 286 | 283
2017-12-12 21:30 | 270 | 267
2017-12-12 22:00 | 264 | 262
2017-12-12 22:30 | 263 | 261
2017-12-12 23:00 | 246 | 243
2017-12-12 23:30 | 225 | 222
2017-12-13 | 210 | 207
2017-12-13 00:30 | 200 | 197
2017-12-13 01:00 | 193 | 190
2017-12-13 01:30 | 189 | 186
2017-12-13 02:00 | 187 | 183
2017-12-13 02:30 | 186 | 182
2017-12-13 03:00 | 187 | 183
2017-12-13 03:30 | 188 | 185
2017-12-13 04:00 | 192 | 189
2017-12-13 04:30 | 195 | 191
2017-12-13 05:00 | 203 | 200
2017-12-13 05:30 | 215 | 212
2017-12-13 06:00 | 231 | 228
2017-12-13 06:30 | 244 | 242
2017-12-13 07:00 | 260 | 258
2017-12-13 07:30 | 269 | 268
2017-12-13 08:00 | 277 | 277
2017-12-13 08:30 | 281 | 281
2017-12-13 09:00 | 281 | 281
2017-12-13 09:30 | 279 | 279
2017-12-13 10:00 | 279 | 279
2017-12-13 10:30 | 278 | 278
2017-12-13 11:00 | 279 | 279
2017-12-13 11:30 | 280 | 280
2017-12-13 12:00 | 281 | 281
2017-12-13 12:30 | 285 | 285
2017-12-13 13:00 | 289 | 288
2017-12-13 13:30 | 296 | 296
2017-12-13 14:00 | 305 | 305
2017-12-13 14:30 | 312 | 312
2017-12-13 15:00 | 322 | 322
2017-12-13 15:30 | 328 | 328
2017-12-13 16:00 | 333 | 333
2017-12-13 16:30 | 340 | 339
2017-12-13 17:00 | 339 | 339
2017-12-13 17:30 | 336 | 335
2017-12-13 18:00 | 330 | 329
2017-12-13 18:30 | 336 | 335
2017-12-13 19:00 | 336 | 336
2017-12-13 19:30 | 332 | 331
2017-12-13 20:00 | 322 | 322
2017-12-13 20:30 | 309 | 307
2017-12-13 21:00 | 293 | 292
2017-12-13 21:30 | 276 | 276
2017-12-13 22:00 | 272 | 272
2017-12-13 22:30 | 269 | 269
2017-12-13 23:00 | 249 | 249
2017-12-13 23:30 | 228 | 228
2017-12-14 | 214 | 213
2017-12-14 00:30 | 202 | 202
2017-12-14 01:00 | 195 | 194
2017-12-14 01:30 | 191 | 190
2017-12-14 02:00 | 189 | 188
2017-12-14 02:30 | 187 | 186
2017-12-14 03:00 | 187 | 186
2017-12-14 03:30 | 187 | 186
2017-12-14 04:00 | 192 | 191
2017-12-14 04:30 | 195 | 193
2017-12-14 05:00 | 203 | 202
2017-12-14 05:30 | 213 | 212
2017-12-14 06:00 | 228 | 228
2017-12-14 06:30 | 242 | 241
2017-12-14 07:00 | 259 | 259
2017-12-14 07:30 | 268 | 268
2017-12-14 08:00 | 277 | 277
2017-12-14 08:30 | 281 | 281
2017-12-14 09:00 | 289 | 289
2017-12-14 09:30 | 290 | 288
2017-12-14 10:00 | 290 | 289
2017-12-14 10:30 | 289 | 288
2017-12-14 11:00 | 289 | 288
2017-12-14 11:30 | 291 | 290
2017-12-14 12:00 | 292 | 290
2017-12-14 12:30 | 293 | 292
2017-12-14 13:00 | 299 | 298
2017-12-14 13:30 | 306 | 305
2017-12-14 14:00 | 312 | 311
2017-12-14 14:30 | 317 | 316
2017-12-14 15:00 | 325 | 324
2017-12-14 15:30 | 333 | 332
2017-12-14 16:00 | 342 | 341
2017-12-14 16:30 | 351 | 350
2017-12-14 17:00 | 352 | 350
2017-12-14 17:30 | 350 | 347
2017-12-14 18:00 | 344 | 342
2017-12-14 18:30 | 348 | 346
2017-12-14 19:00 | 348 | 346
2017-12-14 19:30 | 343 | 342
2017-12-14 20:00 | 334 | 332
2017-12-14 20:30 | 316 | 316
2017-12-14 21:00 | 301 | 301
2017-12-14 21:30 | 283 | 282
2017-12-14 22:00 | 276 | 276
2017-12-14 22:30 | 274 | 273
2017-12-14 23:00 | 255 | 254
2017-12-14 23:30 | 234 | 233
2017-12-15 | 218 | 216
2017-12-15 00:30 | 207 | 205
2017-12-15 01:00 | 197 | 196
2017-12-15 01:30 | 193 | 193
2017-12-15 02:00 | 191 | 191
2017-12-15 02:30 | 190 | 189
2017-12-15 03:00 | 190 | 189
2017-12-15 03:30 | 191 | 190
2017-12-15 04:00 | 194 | 194
2017-12-15 04:30 | 197 | 196
2017-12-15 05:00 | 207 | 206
2017-12-15 05:30 | 216 | 216
2017-12-15 06:00 | 242 | 242
2017-12-15 06:30 | 271 | 271
2017-12-15 07:00 | 294 | 294
2017-12-15 07:30 | 312 | 311
2017-12-15 08:00 | 321 | 320
2017-12-15 08:30 | 324 | 324
2017-12-15 09:00 | 328 | 328
2017-12-15 09:30 | 328 | 328
2017-12-15 10:00 | 329 | 329
2017-12-15 10:30 | 325 | 325
2017-12-15 11:00 | 323 | 323
2017-12-15 11:30 | 325 | 324
2017-12-15 12:00 | 325 | 322
2017-12-15 12:30 | 326 | 323
2017-12-15 13:00 | 317 | 314
2017-12-15 13:30 | 321 | 318
2017-12-15 14:00 | 329 | 326
2017-12-15 14:30 | 338 | 336
2017-12-15 15:00 | 338 | 335
2017-12-15 15:30 | 344 | 341
2017-12-15 16:00 | 331 | 328
2017-12-15 16:30 | 338 | 335
2017-12-15 17:00 | 336 | 333
2017-12-15 17:30 | 329 | 326
2017-12-15 18:00 | 318 | 317
2017-12-15 18:30 | 321 | 321
2017-12-15 19:00 | 321 | 321
2017-12-15 19:30 | 318 | 317
2017-12-15 20:00 | 307 | 307
2017-12-15 20:30 | 295 | 295
2017-12-15 21:00 | 285 | 285
2017-12-15 21:30 | 272 | 272
2017-12-15 22:00 | 267 | 267
2017-12-15 22:30 | 254 | 254
2017-12-15 23:00 | 240 | 240
2017-12-15 23:30 | 224 | 224
2017-12-16 | 212 | 212
2017-12-16 00:30 | 211 | 211
2017-12-16 01:00 | 202 | 202
2017-12-16 01:30 | 201 | 201
2017-12-16 02:00 | 200 | 200
2017-12-16 02:30 | 197 | 196
2017-12-16 03:00 | 197 | 196
2017-12-16 03:30 | 196 | 195
2017-12-16 04:00 | 195 | 195
2017-12-16 04:30 | 191 | 189
2017-12-16 05:00 | 195 | 194
2017-12-16 05:30 | 201 | 200
2017-12-16 06:00 | 214 | 214
2017-12-16 06:30 | 229 | 228
2017-12-16 07:00 | 240 | 239
2017-12-16 07:30 | 245 | 245
2017-12-16 08:00 | 257 | 257
2017-12-16 08:30 | 266 | 266
2017-12-16 09:00 | 279 | 279
2017-12-16 09:30 | 285 | 284
2017-12-16 10:00 | 289 | 289
2017-12-16 10:30 | 294 | 293
2017-12-16 11:00 | 291 | 290
2017-12-16 11:30 | 298 | 298
2017-12-16 12:00 | 297 | 296
2017-12-16 12:30 | 287 | 287
2017-12-16 13:00 | 293 | 292
2017-12-16 13:30 | 296 | 296
2017-12-16 14:00 | 302 | 302
2017-12-16 14:30 | 305 | 304
2017-12-16 15:00 | 311 | 310
2017-12-16 15:30 | 317 | 317
2017-12-16 16:00 | 322 | 322
2017-12-16 16:30 | 328 | 328
2017-12-16 17:00 | 318 | 317
2017-12-16 17:30 | 313 | 311
2017-12-16 18:00 | 307 | 305
2017-12-16 18:30 | 311 | 309
2017-12-16 19:00 | 308 | 307
2017-12-16 19:30 | 304 | 302
2017-12-16 20:00 | 291 | 290
2017-12-16 20:30 | 280 | 280
2017-12-16 21:00 | 273 | 273
2017-12-16 21:30 | 257 | 257
2017-12-16 22:00 | 248 | 248
2017-12-16 22:30 | 244 | 244
2017-12-16 23:00 | 234 | 233
2017-12-16 23:30 | 222 | 221
2017-12-17 | 210 | 210
2017-12-17 00:30 | 202 | 201
2017-12-17 01:00 | 194 | 194
2017-12-17 01:30 | 189 | 189
2017-12-17 02:00 | 186 | 185
2017-12-17 02:30 | 183 | 182
2017-12-17 03:00 | 181 | 181
2017-12-17 03:30 | 179 | 179
2017-12-17 04:00 | 180 | 179
2017-12-17 04:30 | 177 | 175
2017-12-17 05:00 | 178 | 177
2017-12-17 05:30 | 180 | 179
2017-12-17 06:00 | 187 | 186
2017-12-17 06:30 | 194 | 194
2017-12-17 07:00 | 204 | 204
2017-12-17 07:30 | 213 | 213
2017-12-17 08:00 | 224 | 224
2017-12-17 08:30 | 234 | 233
2017-12-17 09:00 | 238 | 238
2017-12-17 09:30 | 245 | 245
2017-12-17 10:00 | 249 | 249
2017-12-17 10:30 | 253 | 253
2017-12-17 11:00 | 253 | 253
2017-12-17 11:30 | 258 | 257
2017-12-17 12:00 | 260 | 260
2017-12-17 12:30 | 266 | 265
2017-12-17 13:00 | 269 | 268
2017-12-17 13:30 | 275 | 274
2017-12-17 14:00 | 286 | 285
2017-12-17 14:30 | 291 | 291
2017-12-17 15:00 | 295 | 295
2017-12-17 15:30 | 300 | 300
2017-12-17 16:00 | 301 | 301
2017-12-17 16:30 | 298 | 298
2017-12-17 17:00 | 294 | 293
2017-12-17 17:30 | 291 | 290
2017-12-17 18:00 | 288 | 286
2017-12-17 18:30 | 292 | 290
2017-12-17 19:00 | 291 | 290
2017-12-17 19:30 | 291 | 289
2017-12-17 20:00 | 288 | 286
2017-12-17 20:30 | 280 | 278
2017-12-17 21:00 | 270 | 269
2017-12-17 21:30 | 259 | 258
2017-12-17 22:00 | 252 | 251
2017-12-17 22:30 | 251 | 249
2017-12-17 23:00 | 237 | 236
2017-12-17 23:30 | 223 | 223
2017-12-18 | 209 | 209
2017-12-18 00:30 | 202 | 202
2017-12-18 01:00 | 196 | 196
2017-12-18 01:30 | 192 | 192
2017-12-18 02:00 | 190 | 189
2017-12-18 02:30 | 189 | 188
2017-12-18 03:00 | 189 | 188
2017-12-18 03:30 | 188 | 188
2017-12-18 04:00 | 192 | 191
2017-12-18 04:30 | 194 | 193
2017-12-18 05:00 | 202 | 201
2017-12-18 05:30 | 195 | 194
2017-12-18 06:00 | 208 | 208
2017-12-18 06:30 | 225 | 225
2017-12-18 07:00 | 245 | 245
2017-12-18 07:30 | 258 | 258
2017-12-18 08:00 | 266 | 266
2017-12-18 08:30 | 269 | 269
2017-12-18 09:00 | 274 | 273
2017-12-18 09:30 | 272 | 271
2017-12-18 10:00 | 271 | 270
2017-12-18 10:30 | 273 | 272
2017-12-18 11:00 | 273 | 273
2017-12-18 11:30 | 273 | 272
2017-12-18 12:00 | 272 | 271
2017-12-18 12:30 | 274 | 273
2017-12-18 13:00 | 278 | 278
2017-12-18 13:30 | 284 | 284
2017-12-18 14:00 | 291 | 290
2017-12-18 14:30 | 299 | 299
2017-12-18 15:00 | 324 | 323
2017-12-18 15:30 | 327 | 327
2017-12-18 16:00 | 338 | 338
2017-12-18 16:30 | 347 | 346
2017-12-18 17:00 | 344 | 343
2017-12-18 17:30 | 346 | 344
2017-12-18 18:00 | 334 | 333
2017-12-18 18:30 | 336 | 335
2017-12-18 19:00 | 332 | 332
2017-12-18 19:30 | 329 | 328
2017-12-18 20:00 | 320 | 320
2017-12-18 20:30 | 305 | 305
2017-12-18 21:00 | 291 | 291
2017-12-18 21:30 | 280 | 280
2017-12-18 22:00 | 272 | 271
2017-12-18 22:30 | 255 | 254
2017-12-18 23:00 | 239 | 238
2017-12-18 23:30 | 224 | 224
2017-12-19 | 213 | 213
2017-12-19 00:30 | 205 | 205
2017-12-19 01:00 | 198 | 198
2017-12-19 01:30 | 194 | 193
2017-12-19 02:00 | 192 | 191
2017-12-19 02:30 | 190 | 190
2017-12-19 03:00 | 190 | 189
2017-12-19 03:30 | 190 | 189
2017-12-19 04:00 | 193 | 193
2017-12-19 04:30 | 196 | 195
2017-12-19 05:00 | 204 | 203
2017-12-19 05:30 | 214 | 213
2017-12-19 06:00 | 230 | 230
2017-12-19 06:30 | 244 | 244
2017-12-19 07:00 | 264 | 264
2017-12-19 07:30 | 277 | 276
2017-12-19 08:00 | 285 | 285
2017-12-19 08:30 | 293 | 292
2017-12-19 09:00 | 296 | 295
2017-12-19 09:30 | 297 | 297
2017-12-19 10:00 | 301 | 300
2017-12-19 10:30 | 305 | 304
2017-12-19 11:00 | 308 | 307
2017-12-19 11:30 | 313 | 313
2017-12-19 12:00 | 318 | 317
2017-12-19 12:30 | 323 | 322
2017-12-19 13:00 | 332 | 332
2017-12-19 13:30 | 348 | 348
2017-12-19 14:00 | 356 | 354
2017-12-19 14:30 | 366 | 364
2017-12-19 15:00 | 395 | 393
2017-12-19 15:30 | 388 | 385
2017-12-19 16:00 | 373 | 370
2017-12-19 16:30 | 363 | 360
2017-12-19 17:00 | 369 | 365
2017-12-19 17:30 | 359 | 356
2017-12-19 18:00 | 348 | 347
2017-12-19 18:30 | 354 | 353
2017-12-19 19:00 | 354 | 352
2017-12-19 19:30 | 352 | 350
2017-12-19 20:00 | 338 | 336
2017-12-19 20:30 | 322 | 319
2017-12-19 21:00 | 303 | 302
2017-12-19 21:30 | 291 | 290
2017-12-19 22:00 | 279 | 277
2017-12-19 22:30 | 269 | 266
2017-12-19 23:00 | 246 | 245
2017-12-19 23:30 | 230 | 230
2017-12-20 | 219 | 219
2017-12-20 00:30 | 214 | 214
2017-12-20 01:00 | 210 | 210
2017-12-20 01:30 | 207 | 207
2017-12-20 02:00 | 205 | 204
2017-12-20 02:30 | 206 | 205
2017-12-20 03:00 | 206 | 206
2017-12-20 03:30 | 207 | 207
2017-12-20 04:00 | 209 | 209
2017-12-20 04:30 | 209 | 208
2017-12-20 05:00 | 214 | 214
2017-12-20 05:30 | 222 | 222
2017-12-20 06:00 | 240 | 240
2017-12-20 06:30 | 259 | 258
2017-12-20 07:00 | 286 | 285
2017-12-20 07:30 | 307 | 307
2017-12-20 08:00 | 310 | 310
2017-12-20 08:30 | 314 | 314
2017-12-20 09:00 | 322 | 320
2017-12-20 09:30 | 328 | 325
2017-12-20 10:00 | 327 | 324
2017-12-20 10:30 | 329 | 327
2017-12-20 11:00 | 329 | 327
2017-12-20 11:30 | 327 | 325
2017-12-20 12:00 | 333 | 331
2017-12-20 12:30 | 334 | 333
2017-12-20 13:00 | 344 | 343
2017-12-20 13:30 | 350 | 348
2017-12-20 14:00 | 352 | 350
2017-12-20 14:30 | 349 | 347
2017-12-20 15:00 | 347 | 345
2017-12-20 15:30 | 349 | 347
2017-12-20 16:00 | 353 | 350
2017-12-20 16:30 | 354 | 352
2017-12-20 17:00 | 347 | 346
2017-12-20 17:30 | 343 | 341
2017-12-20 18:00 | 331 | 330
2017-12-20 18:30 | 335 | 335
2017-12-20 19:00 | 338 | 337
2017-12-20 19:30 | 332 | 331
2017-12-20 20:00 | 320 | 318
2017-12-20 20:30 | 302 | 302
2017-12-20 21:00 | 296 | 296
2017-12-20 21:30 | 286 | 285
2017-12-20 22:00 | 275 | 275
2017-12-20 22:30 | 263 | 263
2017-12-20 23:00 | 245 | 245
2017-12-20 23:30 | 234 | 234
2017-12-21 | 222 | 222
2017-12-21 00:30 | 217 | 216
2017-12-21 01:00 | 207 | 207
2017-12-21 01:30 | 205 | 204
2017-12-21 02:00 | 205 | 204
2017-12-21 02:30 | 206 | 206
2017-12-21 03:00 | 207 | 206
2017-12-21 03:30 | 204 | 203
2017-12-21 04:00 | 207 | 207
2017-12-21 04:30 | 203 | 203
2017-12-21 05:00 | 204 | 203
2017-12-21 05:30 | 208 | 207
2017-12-21 06:00 | 223 | 223
2017-12-21 06:30 | 241 | 241
2017-12-21 07:00 | 261 | 261
2017-12-21 07:30 | 276 | 276
2017-12-21 08:00 | 295 | 294
2017-12-21 08:30 | 305 | 304
2017-12-21 09:00 | 301 | 301
2017-12-21 09:30 | 307 | 306
2017-12-21 10:00 | 312 | 308
2017-12-21 10:30 | 312 | 309
2017-12-21 11:00 | 312 | 308
2017-12-21 11:30 | 312 | 308
2017-12-21 12:00 | 315 | 312
2017-12-21 12:30 | 324 | 322
2017-12-21 13:00 | 328 | 326
2017-12-21 13:30 | 338 | 336
2017-12-21 14:00 | 349 | 347
2017-12-21 14:30 | 351 | 349
2017-12-21 15:00 | 339 | 336
2017-12-21 15:30 | 336 | 333
2017-12-21 16:00 | 338 | 336
2017-12-21 16:30 | 329 | 327
2017-12-21 17:00 | 333 | 330
2017-12-21 17:30 | 339 | 336
2017-12-21 18:00 | 332 | 330
2017-12-21 18:30 | 328 | 328
2017-12-21 19:00 | 338 | 337
2017-12-21 19:30 | 336 | 335
2017-12-21 20:00 | 331 | 330
2017-12-21 20:30 | 323 | 321
2017-12-21 21:00 | 307 | 305
2017-12-21 21:30 | 291 | 291
2017-12-21 22:00 | 279 | 278
2017-12-21 22:30 | 267 | 265
2017-12-21 23:00 | 244 | 244
2017-12-21 23:30 | 231 | 231
2017-12-22 | 219 | 219
2017-12-22 00:30 | 216 | 216
2017-12-22 01:00 | 213 | 213
2017-12-22 01:30 | 211 | 210
2017-12-22 02:00 | 209 | 208
2017-12-22 02:30 | 208 | 208
2017-12-22 03:00 | 207 | 207
2017-12-22 03:30 | 207 | 206
2017-12-22 04:00 | 208 | 207
2017-12-22 04:30 | 208 | 207
2017-12-22 05:00 | 213 | 212
2017-12-22 05:30 | 221 | 221
2017-12-22 06:00 | 233 | 233
2017-12-22 06:30 | 249 | 249
2017-12-22 07:00 | 267 | 266
2017-12-22 07:30 | 276 | 276
2017-12-22 08:00 | 284 | 284
2017-12-22 08:30 | 297 | 297
2017-12-22 09:00 | 297 | 296
2017-12-22 09:30 | 300 | 298
2017-12-22 10:00 | 297 | 295
2017-12-22 10:30 | 292 | 290
2017-12-22 11:00 | 290 | 288
2017-12-22 11:30 | 291 | 291
2017-12-22 12:00 | 300 | 300
2017-12-22 12:30 | 301 | 301
2017-12-22 13:00 | 295 | 295
2017-12-22 13:30 | 302 | 302
2017-12-22 14:00 | 313 | 313
2017-12-22 14:30 | 322 | 322
2017-12-22 15:00 | 318 | 318
2017-12-22 15:30 | 321 | 321
2017-12-22 16:00 | 322 | 322
2017-12-22 16:30 | 321 | 321
2017-12-22 17:00 | 314 | 313
2017-12-22 17:30 | 307 | 306
2017-12-22 18:00 | 301 | 300
2017-12-22 18:30 | 303 | 302
2017-12-22 19:00 | 303 | 302
2017-12-22 19:30 | 304 | 303
2017-12-22 20:00 | 300 | 299
2017-12-22 20:30 | 292 | 292
2017-12-22 21:00 | 286 | 286
2017-12-22 21:30 | 274 | 274
2017-12-22 22:00 | 267 | 267
2017-12-22 22:30 | 264 | 264
2017-12-22 23:00 | 248 | 248
2017-12-22 23:30 | 231 | 231
2017-12-23 | 217 | 217
2017-12-23 00:30 | 209 | 209
2017-12-23 01:00 | 201 | 201
2017-12-23 01:30 | 197 | 197
2017-12-23 02:00 | 194 | 194
2017-12-23 02:30 | 193 | 193
2017-12-23 03:00 | 193 | 193
2017-12-23 03:30 | 194 | 194
2017-12-23 04:00 | 192 | 192
2017-12-23 04:30 | 193 | 193
2017-12-23 05:00 | 195 | 195
2017-12-23 05:30 | 202 | 202
2017-12-23 06:00 | 211 | 211
2017-12-23 06:30 | 221 | 220
2017-12-23 07:00 | 225 | 224
2017-12-23 07:30 | 236 | 236
2017-12-23 08:00 | 244 | 244
2017-12-23 08:30 | 247 | 247
2017-12-23 09:00 | 256 | 256
2017-12-23 09:30 | 255 | 255
2017-12-23 10:00 | 258 | 258
2017-12-23 10:30 | 263 | 263
2017-12-23 11:00 | 271 | 271
2017-12-23 11:30 | 275 | 273
2017-12-23 12:00 | 276 | 275
2017-12-23 12:30 | 282 | 281
2017-12-23 13:00 | 280 | 279
2017-12-23 13:30 | 287 | 287
2017-12-23 14:00 | 298 | 297
2017-12-23 14:30 | 300 | 299
2017-12-23 15:00 | 313 | 313
2017-12-23 15:30 | 312 | 311
2017-12-23 16:00 | 309 | 308
2017-12-23 16:30 | 316 | 315
2017-12-23 17:00 | 319 | 319
2017-12-23 17:30 | 312 | 311
2017-12-23 18:00 | 303 | 302
2017-12-23 18:30 | 303 | 302
2017-12-23 19:00 | 308 | 307
2017-12-23 19:30 | 304 | 303
2017-12-23 20:00 | 298 | 297
2017-12-23 20:30 | 287 | 285
2017-12-23 21:00 | 268 | 268
2017-12-23 21:30 | 253 | 253
2017-12-23 22:00 | 241 | 241
2017-12-23 22:30 | 236 | 235
2017-12-23 23:00 | 215 | 215
2017-12-23 23:30 | 193 | 193
2017-12-24 | 176 | 176
2017-12-24 00:30 | 166 | 166
2017-12-24 01:00 | 157 | 157
2017-12-24 01:30 | 152 | 152
2017-12-24 02:00 | 148 | 148
2017-12-24 02:30 | 146 | 146
2017-12-24 03:00 | 144 | 144
2017-12-24 03:30 | 143 | 143
2017-12-24 04:00 | 143 | 143
2017-12-24 04:30 | 140 | 140
2017-12-24 05:00 | 141 | 141
2017-12-24 05:30 | 147 | 147
2017-12-24 06:00 | 169 | 169
2017-12-24 06:30 | 193 | 193
2017-12-24 07:00 | 204 | 204
2017-12-24 07:30 | 214 | 214
2017-12-24 08:00 | 230 | 230
2017-12-24 08:30 | 237 | 237
2017-12-24 09:00 | 246 | 246
2017-12-24 09:30 | 250 | 250
2017-12-24 10:00 | 259 | 259
2017-12-24 10:30 | 267 | 266
2017-12-24 11:00 | 272 | 271
2017-12-24 11:30 | 277 | 277
2017-12-24 12:00 | 284 | 283
2017-12-24 12:30 | 290 | 289
2017-12-24 13:00 | 296 | 295
2017-12-24 13:30 | 304 | 303
2017-12-24 14:00 | 312 | 311
2017-12-24 14:30 | 299 | 299
2017-12-24 15:00 | 298 | 298
2017-12-24 15:30 | 306 | 305
2017-12-24 16:00 | 313 | 311
2017-12-24 16:30 | 317 | 315
2017-12-24 17:00 | 317 | 316
2017-12-24 17:30 | 314 | 312
2017-12-24 18:00 | 304 | 303
2017-12-24 18:30 | 301 | 300
2017-12-24 19:00 | 302 | 302
2017-12-24 19:30 | 302 | 302
2017-12-24 20:00 | 298 | 297
2017-12-24 20:30 | 283 | 283
2017-12-24 21:00 | 275 | 275
2017-12-24 21:30 | 259 | 259
2017-12-24 22:00 | 253 | 253
2017-12-24 22:30 | 247 | 246
2017-12-24 23:00 | 225 | 224
2017-12-24 23:30 | 203 | 202
2017-12-25 | 183 | 183
2017-12-25 00:30 | 170 | 170
2017-12-25 01:00 | 162 | 162
2017-12-25 01:30 | 156 | 156
2017-12-25 02:00 | 152 | 152
2017-12-25 02:30 | 149 | 148
2017-12-25 03:00 | 147 | 147
2017-12-25 03:30 | 146 | 146
2017-12-25 04:00 | 147 | 147
2017-12-25 04:30 | 148 | 148
2017-12-25 05:00 | 151 | 151
2017-12-25 05:30 | 157 | 157
2017-12-25 06:00 | 171 | 171
2017-12-25 06:30 | 195 | 194
2017-12-25 07:00 | 235 | 235
2017-12-25 07:30 | 247 | 247
2017-12-25 08:00 | 255 | 255
2017-12-25 08:30 | 262 | 262
2017-12-25 09:00 | 267 | 267
2017-12-25 09:30 | 273 | 272
2017-12-25 10:00 | 277 | 277
2017-12-25 10:30 | 281 | 281
2017-12-25 11:00 | 284 | 284
2017-12-25 11:30 | 287 | 287
2017-12-25 12:00 | 289 | 289
2017-12-25 12:30 | 292 | 292
2017-12-25 13:00 | 294 | 294
2017-12-25 13:30 | 298 | 298
2017-12-25 14:00 | 301 | 301
2017-12-25 14:30 | 283 | 283
2017-12-25 15:00 | 286 | 286
2017-12-25 15:30 | 303 | 302
2017-12-25 16:00 | 313 | 311
2017-12-25 16:30 | 313 | 310
2017-12-25 17:00 | 303 | 301
2017-12-25 17:30 | 298 | 297
2017-12-25 18:00 | 291 | 290
2017-12-25 18:30 | 278 | 278
2017-12-25 19:00 | 264 | 264
2017-12-25 19:30 | 256 | 255
2017-12-25 20:00 | 248 | 247
2017-12-25 20:30 | 237 | 236
2017-12-25 21:00 | 229 | 229
2017-12-25 21:30 | 217 | 217
2017-12-25 22:00 | 218 | 218
2017-12-25 22:30 | 216 | 216
2017-12-25 23:00 | 197 | 197
2017-12-25 23:30 | 179 | 179
2017-12-26 | 171 | 171
2017-12-26 00:30 | 190 | 190
2017-12-26 01:00 | 185 | 184
2017-12-26 01:30 | 182 | 181
2017-12-26 02:00 | 179 | 179
2017-12-26 02:30 | 177 | 177
2017-12-26 03:00 | 176 | 175
2017-12-26 03:30 | 175 | 174
2017-12-26 04:00 | 176 | 176
2017-12-26 04:30 | 175 | 175
2017-12-26 05:00 | 177 | 177
2017-12-26 05:30 | 180 | 180
2017-12-26 06:00 | 190 | 189
2017-12-26 06:30 | 197 | 196
2017-12-26 07:00 | 210 | 209
2017-12-26 07:30 | 225 | 222
2017-12-26 08:00 | 235 | 234
2017-12-26 08:30 | 239 | 239
2017-12-26 09:00 | 233 | 233
2017-12-26 09:30 | 229 | 229
2017-12-26 10:00 | 229 | 229
2017-12-26 10:30 | 234 | 234
2017-12-26 11:00 | 249 | 248
2017-12-26 11:30 | 248 | 248
2017-12-26 12:00 | 256 | 256
2017-12-26 12:30 | 264 | 264
2017-12-26 13:00 | 257 | 257
2017-12-26 13:30 | 262 | 262
2017-12-26 14:00 | 266 | 266
2017-12-26 14:30 | 271 | 271
2017-12-26 15:00 | 285 | 285
2017-12-26 15:30 | 262 | 262
2017-12-26 16:00 | 247 | 247
2017-12-26 16:30 | 254 | 254
2017-12-26 17:00 | 256 | 255
2017-12-26 17:30 | 251 | 251
2017-12-26 18:00 | 247 | 246
2017-12-26 18:30 | 250 | 250
2017-12-26 19:00 | 246 | 245
2017-12-26 19:30 | 241 | 240
2017-12-26 20:00 | 231 | 231
2017-12-26 20:30 | 221 | 221
2017-12-26 21:00 | 213 | 213
2017-12-26 21:30 | 201 | 201
2017-12-26 22:00 | 201 | 201
2017-12-26 22:30 | 201 | 201
2017-12-26 23:00 | 184 | 183
2017-12-26 23:30 | 165 | 165
2017-12-27 | 154 | 154
2017-12-27 00:30 | 161 | 161
2017-12-27 01:00 | 174 | 174
2017-12-27 01:30 | 170 | 170
2017-12-27 02:00 | 168 | 168
2017-12-27 02:30 | 166 | 166
2017-12-27 03:00 | 166 | 165
2017-12-27 03:30 | 166 | 165
2017-12-27 04:00 | 168 | 168
2017-12-27 04:30 | 170 | 170
2017-12-27 05:00 | 174 | 174
2017-12-27 05:30 | 179 | 179
2017-12-27 06:00 | 191 | 190
2017-12-27 06:30 | 203 | 202
2017-12-27 07:00 | 217 | 217
2017-12-27 07:30 | 227 | 227
2017-12-27 08:00 | 238 | 238
2017-12-27 08:30 | 244 | 244
2017-12-27 09:00 | 256 | 256
2017-12-27 09:30 | 262 | 262
2017-12-27 10:00 | 261 | 261
2017-12-27 10:30 | 254 | 254
2017-12-27 11:00 | 245 | 245
2017-12-27 11:30 | 244 | 244
2017-12-27 12:00 | 249 | 249
2017-12-27 12:30 | 256 | 256
2017-12-27 13:00 | 266 | 266
2017-12-27 13:30 | 255 | 255
2017-12-27 14:00 | 252 | 252
2017-12-27 14:30 | 259 | 259
2017-12-27 15:00 | 263 | 263
2017-12-27 15:30 | 261 | 261
2017-12-27 16:00 | 271 | 271
2017-12-27 16:30 | 282 | 281
2017-12-27 17:00 | 275 | 275
2017-12-27 17:30 | 272 | 272
2017-12-27 18:00 | 270 | 270
2017-12-27 18:30 | 270 | 270
2017-12-27 19:00 | 269 | 269
2017-12-27 19:30 | 269 | 269
2017-12-27 20:00 | 258 | 258
2017-12-27 20:30 | 250 | 250
2017-12-27 21:00 | 243 | 242
2017-12-27 21:30 | 234 | 234
2017-12-27 22:00 | 227 | 227
2017-12-27 22:30 | 224 | 224
2017-12-27 23:00 | 210 | 210
2017-12-27 23:30 | 200 | 200
2017-12-28 | 190 | 190
2017-12-28 00:30 | 185 | 185
2017-12-28 01:00 | 174 | 174
2017-12-28 01:30 | 170 | 170
2017-12-28 02:00 | 170 | 169
2017-12-28 02:30 | 172 | 172
2017-12-28 03:00 | 173 | 173
2017-12-28 03:30 | 176 | 175
2017-12-28 04:00 | 179 | 179
2017-12-28 04:30 | 175 | 175
2017-12-28 05:00 | 178 | 178
2017-12-28 05:30 | 180 | 180
2017-12-28 06:00 | 188 | 188
2017-12-28 06:30 | 195 | 194
2017-12-28 07:00 | 211 | 210
2017-12-28 07:30 | 223 | 222
2017-12-28 08:00 | 237 | 236
2017-12-28 08:30 | 251 | 251
2017-12-28 09:00 | 264 | 264
2017-12-28 09:30 | 263 | 263
2017-12-28 10:00 | 253 | 253
2017-12-28 10:30 | 249 | 249
2017-12-28 11:00 | 248 | 247
2017-12-28 11:30 | 251 | 251
2017-12-28 12:00 | 250 | 250
2017-12-28 12:30 | 257 | 257
2017-12-28 13:00 | 266 | 266
2017-12-28 13:30 | 274 | 274
2017-12-28 14:00 | 286 | 286
2017-12-28 14:30 | 296 | 296
2017-12-28 15:00 | 298 | 298
2017-12-28 15:30 | 308 | 308
2017-12-28 16:00 | 313 | 313
2017-12-28 16:30 | 315 | 315
2017-12-28 17:00 | 309 | 309
2017-12-28 17:30 | 311 | 311
2017-12-28 18:00 | 309 | 309
2017-12-28 18:30 | 308 | 308
2017-12-28 19:00 | 309 | 309
2017-12-28 19:30 | 313 | 313
2017-12-28 20:00 | 301 | 301
2017-12-28 20:30 | 290 | 290
2017-12-28 21:00 | 282 | 281
2017-12-28 21:30 | 272 | 270
2017-12-28 22:00 | 256 | 255
2017-12-28 22:30 | 248 | 247
2017-12-28 23:00 | 231 | 231
2017-12-28 23:30 | 216 | 216
2017-12-29 | 205 | 205
2017-12-29 00:30 | 203 | 203
2017-12-29 01:00 | 195 | 195
2017-12-29 01:30 | 190 | 190
2017-12-29 02:00 | 185 | 185
2017-12-29 02:30 | 185 | 185
2017-12-29 03:00 | 185 | 185
2017-12-29 03:30 | 184 | 184
2017-12-29 04:00 | 191 | 191
2017-12-29 04:30 | 190 | 190
2017-12-29 05:00 | 191 | 191
2017-12-29 05:30 | 192 | 192
2017-12-29 06:00 | 201 | 201
2017-12-29 06:30 | 212 | 211
2017-12-29 07:00 | 235 | 235
2017-12-29 07:30 | 255 | 255
2017-12-29 08:00 | 265 | 265
2017-12-29 08:30 | 273 | 273
2017-12-29 09:00 | 281 | 281
2017-12-29 09:30 | 286 | 286
2017-12-29 10:00 | 287 | 287
2017-12-29 10:30 | 291 | 290
2017-12-29 11:00 | 288 | 288
2017-12-29 11:30 | 293 | 292
2017-12-29 12:00 | 300 | 300
2017-12-29 12:30 | 299 | 299
2017-12-29 13:00 | 298 | 298
2017-12-29 13:30 | 301 | 300
2017-12-29 14:00 | 302 | 301
2017-12-29 14:30 | 308 | 308
2017-12-29 15:00 | 305 | 305
2017-12-29 15:30 | 307 | 306
2017-12-29 16:00 | 313 | 312
2017-12-29 16:30 | 312 | 310
2017-12-29 17:00 | 312 | 310
2017-12-29 17:30 | 314 | 312
2017-12-29 18:00 | 304 | 302
2017-12-29 18:30 | 309 | 308
2017-12-29 19:00 | 313 | 312
2017-12-29 19:30 | 309 | 308
2017-12-29 20:00 | 298 | 296
2017-12-29 20:30 | 285 | 284
2017-12-29 21:00 | 271 | 270
2017-12-29 21:30 | 259 | 258
2017-12-29 22:00 | 253 | 251
2017-12-29 22:30 | 247 | 246
2017-12-29 23:00 | 233 | 232
2017-12-29 23:30 | 221 | 220
2017-12-30 | 201 | 199
2017-12-30 00:30 | 196 | 194
2017-12-30 01:00 | 187 | 185
2017-12-30 01:30 | 179 | 176
2017-12-30 02:00 | 176 | 172
2017-12-30 02:30 | 176 | 172
2017-12-30 03:00 | 177 | 173
2017-12-30 03:30 | 178 | 173
2017-12-30 04:00 | 174 | 169
2017-12-30 04:30 | 171 | 166
2017-12-30 05:00 | 172 | 166
2017-12-30 05:30 | 180 | 176
2017-12-30 06:00 | 188 | 184
2017-12-30 06:30 | 193 | 191
2017-12-30 07:00 | 205 | 204
2017-12-30 07:30 | 214 | 213
2017-12-30 08:00 | 230 | 228
2017-12-30 08:30 | 242 | 240
2017-12-30 09:00 | 240 | 239
2017-12-30 09:30 | 230 | 229
2017-12-30 10:00 | 245 | 244
2017-12-30 10:30 | 257 | 257
2017-12-30 11:00 | 255 | 255
2017-12-30 11:30 | 246 | 246
2017-12-30 12:00 | 253 | 252
2017-12-30 12:30 | 281 | 279
2017-12-30 13:00 | 284 | 283
2017-12-30 13:30 | 287 | 287
2017-12-30 14:00 | 267 | 267
2017-12-30 14:30 | 276 | 276
2017-12-30 15:00 | 282 | 282
2017-12-30 15:30 | 302 | 302
2017-12-30 16:00 | 311 | 311
2017-12-30 16:30 | 319 | 319
2017-12-30 17:00 | 318 | 318
2017-12-30 17:30 | 319 | 319
2017-12-30 18:00 | 317 | 317
2017-12-30 18:30 | 320 | 320
2017-12-30 19:00 | 320 | 320
2017-12-30 19:30 | 321 | 321
2017-12-30 20:00 | 315 | 315
2017-12-30 20:30 | 306 | 306
2017-12-30 21:00 | 293 | 292
2017-12-30 21:30 | 284 | 283
2017-12-30 22:00 | 276 | 275
2017-12-30 22:30 | 270 | 269
2017-12-30 23:00 | 257 | 257
2017-12-30 23:30 | 240 | 240
2017-12-31 | 220 | 220
2017-12-31 00:30 | 215 | 215
2017-12-31 01:00 | 208 | 208
2017-12-31 01:30 | 203 | 203
2017-12-31 02:00 | 201 | 201
2017-12-31 02:30 | 198 | 198
2017-12-31 03:00 | 199 | 199
2017-12-31 03:30 | 198 | 197
2017-12-31 04:00 | 190 | 190
2017-12-31 04:30 | 188 | 188
2017-12-31 05:00 | 191 | 191
2017-12-31 05:30 | 196 | 196
2017-12-31 06:00 | 200 | 200
2017-12-31 06:30 | 205 | 205
2017-12-31 07:00 | 214 | 213
2017-12-31 07:30 | 224 | 223
2017-12-31 08:00 | 236 | 236
2017-12-31 08:30 | 247 | 246
2017-12-31 09:00 | 257 | 257
2017-12-31 09:30 | 265 | 264
2017-12-31 10:00 | 267 | 267
2017-12-31 10:30 | 268 | 267
2017-12-31 11:00 | 265 | 265
2017-12-31 11:30 | 264 | 264
2017-12-31 12:00 | 275 | 275
2017-12-31 12:30 | 285 | 284
2017-12-31 13:00 | 294 | 293
2017-12-31 13:30 | 301 | 301
2017-12-31 14:00 | 308 | 308
2017-12-31 14:30 | 319 | 318
2017-12-31 15:00 | 332 | 332
2017-12-31 15:30 | 335 | 334
2017-12-31 16:00 | 324 | 322
2017-12-31 16:30 | 310 | 308
2017-12-31 17:00 | 300 | 299
2017-12-31 17:30 | 290 | 290
2017-12-31 18:00 | 284 | 284
2017-12-31 18:30 | 285 | 285
2017-12-31 19:00 | 287 | 287
2017-12-31 19:30 | 284 | 284
2017-12-31 20:00 | 281 | 281
2017-12-31 20:30 | 279 | 279
2017-12-31 21:00 | 277 | 277
2017-12-31 21:30 | 277 | 276
2017-12-31 22:00 | 277 | 276
2017-12-31 22:30 | 277 | 277
2017-12-31 23:00 | 267 | 266
2017-12-31 23:30 | 250 | 250
2018-01-01 | 242 | 241
2018-01-01 00:30 | 238 | 238
2018-01-01 01:00 | 230 | 230
2018-01-01 01:30 | 219 | 219
2018-01-01 02:00 | 209 | 209
2018-01-01 02:30 | 206 | 206
2018-01-01 03:00 | 204 | 204
2018-01-01 03:30 | 204 | 204
2018-01-01 04:00 | 205 | 205
2018-01-01 04:30 | 207 | 207
2018-01-01 05:00 | 207 | 207
2018-01-01 05:30 | 214 | 214
2018-01-01 06:00 | 219 | 218
2018-01-01 06:30 | 222 | 222
2018-01-01 07:00 | 241 | 241
2018-01-01 07:30 | 252 | 252
2018-01-01 08:00 | 270 | 270
2018-01-01 08:30 | 281 | 281
2018-01-01 09:00 | 293 | 292
2018-01-01 09:30 | 314 | 314
2018-01-01 10:00 | 315 | 315
2018-01-01 10:30 | 300 | 300
2018-01-01 11:00 | 302 | 301
2018-01-01 11:30 | 303 | 303
2018-01-01 12:00 | 299 | 299
2018-01-01 12:30 | 299 | 299
2018-01-01 13:00 | 311 | 311
2018-01-01 13:30 | 309 | 309
2018-01-01 14:00 | 308 | 307
2018-01-01 14:30 | 318 | 317
2018-01-01 15:00 | 316 | 316
2018-01-01 15:30 | 322 | 322
2018-01-01 16:00 | 323 | 323
2018-01-01 16:30 | 327 | 325
2018-01-01 17:00 | 327 | 325
2018-01-01 17:30 | 317 | 315
2018-01-01 18:00 | 312 | 311
2018-01-01 18:30 | 315 | 314
2018-01-01 19:00 | 310 | 309
2018-01-01 19:30 | 309 | 308
2018-01-01 20:00 | 298 | 298
2018-01-01 20:30 | 288 | 287
2018-01-01 21:00 | 274 | 272
2018-01-01 21:30 | 265 | 263
2018-01-01 22:00 | 255 | 253
2018-01-01 22:30 | 250 | 248
2018-01-01 23:00 | 231 | 228
2018-01-01 23:30 | 217 | 217
2018-01-02 | 206 | 206
2018-01-02 00:30 | 199 | 199
2018-01-02 01:00 | 195 | 195
2018-01-02 01:30 | 191 | 191
2018-01-02 02:00 | 188 | 188
2018-01-02 02:30 | 187 | 187
2018-01-02 03:00 | 186 | 186
2018-01-02 03:30 | 187 | 187
2018-01-02 04:00 | 187 | 187
2018-01-02 04:30 | 186 | 186
2018-01-02 05:00 | 189 | 189
2018-01-02 05:30 | 195 | 195
2018-01-02 06:00 | 211 | 211
2018-01-02 06:30 | 219 | 218
2018-01-02 07:00 | 245 | 245
2018-01-02 07:30 | 257 | 257
2018-01-02 08:00 | 266 | 266
2018-01-02 08:30 | 280 | 280
2018-01-02 09:00 | 286 | 286
2018-01-02 09:30 | 303 | 302
2018-01-02 10:00 | 300 | 300
2018-01-02 10:30 | 299 | 299
2018-01-02 11:00 | 302 | 302
2018-01-02 11:30 | 302 | 302
2018-01-02 12:00 | 301 | 300
2018-01-02 12:30 | 304 | 304
2018-01-02 13:00 | 322 | 321
2018-01-02 13:30 | 334 | 333
2018-01-02 14:00 | 351 | 350
2018-01-02 14:30 | 341 | 339
2018-01-02 15:00 | 330 | 328
2018-01-02 15:30 | 328 | 327
2018-01-02 16:00 | 313 | 313
2018-01-02 16:30 | 309 | 309
2018-01-02 17:00 | 303 | 303
2018-01-02 17:30 | 303 | 303
2018-01-02 18:00 | 300 | 300
2018-01-02 18:30 | 306 | 306
2018-01-02 19:00 | 293 | 293
2018-01-02 19:30 | 291 | 290
2018-01-02 20:00 | 284 | 284
2018-01-02 20:30 | 270 | 270
2018-01-02 21:00 | 259 | 259
2018-01-02 21:30 | 251 | 251
2018-01-02 22:00 | 246 | 246
2018-01-02 22:30 | 238 | 238
2018-01-02 23:00 | 221 | 221
2018-01-02 23:30 | 211 | 210
2018-01-03 | 198 | 198
2018-01-03 00:30 | 194 | 194
2018-01-03 01:00 | 190 | 190
2018-01-03 01:30 | 186 | 185
2018-01-03 02:00 | 183 | 183
2018-01-03 02:30 | 184 | 183
2018-01-03 03:00 | 182 | 182
2018-01-03 03:30 | 182 | 182
2018-01-03 04:00 | 182 | 182
2018-01-03 04:30 | 184 | 183
2018-01-03 05:00 | 191 | 190
2018-01-03 05:30 | 198 | 197
2018-01-03 06:00 | 209 | 209
2018-01-03 06:30 | 224 | 224
2018-01-03 07:00 | 247 | 247
2018-01-03 07:30 | 261 | 260
2018-01-03 08:00 | 271 | 271
2018-01-03 08:30 | 280 | 280
2018-01-03 09:00 | 285 | 285
2018-01-03 09:30 | 290 | 289
2018-01-03 10:00 | 287 | 287
2018-01-03 10:30 | 283 | 282
2018-01-03 11:00 | 280 | 279
2018-01-03 11:30 | 276 | 275
2018-01-03 12:00 | 276 | 276
2018-01-03 12:30 | 279 | 278
2018-01-03 13:00 | 274 | 274
2018-01-03 13:30 | 296 | 296
2018-01-03 14:00 | 307 | 307
2018-01-03 14:30 | 309 | 309
2018-01-03 15:00 | 305 | 304
2018-01-03 15:30 | 305 | 305
2018-01-03 16:00 | 299 | 298
2018-01-03 16:30 | 297 | 295
2018-01-03 17:00 | 296 | 294
2018-01-03 17:30 | 300 | 299
2018-01-03 18:00 | 299 | 298
2018-01-03 18:30 | 294 | 293
2018-01-03 19:00 | 294 | 294
2018-01-03 19:30 | 294 | 294
2018-01-03 20:00 | 288 | 288
2018-01-03 20:30 | 274 | 274
2018-01-03 21:00 | 263 | 263
2018-01-03 21:30 | 254 | 253
2018-01-03 22:00 | 246 | 244
2018-01-03 22:30 | 237 | 235
2018-01-03 23:00 | 220 | 220
2018-01-03 23:30 | 208 | 208
2018-01-04 | 195 | 195
2018-01-04 00:30 | 189 | 189
2018-01-04 01:00 | 186 | 186
2018-01-04 01:30 | 183 | 183
2018-01-04 02:00 | 179 | 179
2018-01-04 02:30 | 170 | 170
2018-01-04 03:00 | 177 | 177
2018-01-04 03:30 | 180 | 180
2018-01-04 04:00 | 180 | 180
2018-01-04 04:30 | 182 | 182
2018-01-04 05:00 | 186 | 186
2018-01-04 05:30 | 193 | 193
2018-01-04 06:00 | 207 | 207
2018-01-04 06:30 | 217 | 216
2018-01-04 07:00 | 234 | 233
2018-01-04 07:30 | 244 | 244
2018-01-04 08:00 | 256 | 256
2018-01-04 08:30 | 261 | 261
2018-01-04 09:00 | 266 | 266
2018-01-04 09:30 | 272 | 272
2018-01-04 10:00 | 271 | 271
2018-01-04 10:30 | 274 | 274
2018-01-04 11:00 | 273 | 273
2018-01-04 11:30 | 276 | 276
2018-01-04 12:00 | 273 | 273
2018-01-04 12:30 | 273 | 273
2018-01-04 13:00 | 275 | 275
2018-01-04 13:30 | 277 | 277
2018-01-04 14:00 | 278 | 277
2018-01-04 14:30 | 276 | 276
2018-01-04 15:00 | 275 | 275
2018-01-04 15:30 | 275 | 275
2018-01-04 16:00 | 279 | 279
2018-01-04 16:30 | 283 | 283
2018-01-04 17:00 | 281 | 281
2018-01-04 17:30 | 288 | 288
2018-01-04 18:00 | 282 | 282
2018-01-04 18:30 | 271 | 271
2018-01-04 19:00 | 275 | 275
2018-01-04 19:30 | 286 | 286
2018-01-04 20:00 | 277 | 277
2018-01-04 20:30 | 267 | 266
2018-01-04 21:00 | 256 | 255
2018-01-04 21:30 | 242 | 242
2018-01-04 22:00 | 237 | 237
2018-01-04 22:30 | 219 | 218
2018-01-04 23:00 | 204 | 203
2018-01-04 23:30 | 195 | 195
2018-01-05 | 187 | 187
2018-01-05 00:30 | 181 | 181
2018-01-05 01:00 | 178 | 178
2018-01-05 01:30 | 174 | 174
2018-01-05 02:00 | 173 | 173
2018-01-05 02:30 | 170 | 170
2018-01-05 03:00 | 172 | 172
2018-01-05 03:30 | 173 | 173
2018-01-05 04:00 | 173 | 173
2018-01-05 04:30 | 175 | 175
2018-01-05 05:00 | 181 | 181
2018-01-05 05:30 | 187 | 187
2018-01-05 06:00 | 198 | 198
2018-01-05 06:30 | 209 | 209
2018-01-05 07:00 | 226 | 226
2018-01-05 07:30 | 234 | 234
2018-01-05 08:00 | 248 | 247
2018-01-05 08:30 | 257 | 257
2018-01-05 09:00 | 268 | 267
2018-01-05 09:30 | 279 | 278
2018-01-05 10:00 | 275 | 274
2018-01-05 10:30 | 266 | 265
2018-01-05 11:00 | 262 | 262
2018-01-05 11:30 | 265 | 264
2018-01-05 12:00 | 266 | 265
2018-01-05 12:30 | 270 | 269
2018-01-05 13:00 | 273 | 273
2018-01-05 13:30 | 283 | 283
2018-01-05 14:00 | 288 | 287
2018-01-05 14:30 | 292 | 291
2018-01-05 15:00 | 295 | 294
2018-01-05 15:30 | 302 | 302
2018-01-05 16:00 | 312 | 311
2018-01-05 16:30 | 311 | 310
2018-01-05 17:00 | 301 | 300
2018-01-05 17:30 | 296 | 295
2018-01-05 18:00 | 290 | 290
2018-01-05 18:30 | 289 | 289
2018-01-05 19:00 | 287 | 287
2018-01-05 19:30 | 286 | 286
2018-01-05 20:00 | 283 | 282
2018-01-05 20:30 | 281 | 280
2018-01-05 21:00 | 270 | 269
2018-01-05 21:30 | 252 | 252
2018-01-05 22:00 | 247 | 246
2018-01-05 22:30 | 238 | 237
2018-01-05 23:00 | 227 | 225
2018-01-05 23:30 | 212 | 211
2018-01-06 | 200 | 199
2018-01-06 00:30 | 197 | 197
2018-01-06 01:00 | 192 | 192
2018-01-06 01:30 | 187 | 186
2018-01-06 02:00 | 183 | 182
2018-01-06 02:30 | 178 | 177
2018-01-06 03:00 | 174 | 173
2018-01-06 03:30 | 174 | 173
2018-01-06 04:00 | 173 | 171
2018-01-06 04:30 | 173 | 172
2018-01-06 05:00 | 176 | 174
2018-01-06 05:30 | 190 | 188
2018-01-06 06:00 | 200 | 199
2018-01-06 06:30 | 206 | 206
2018-01-06 07:00 | 217 | 217
2018-01-06 07:30 | 230 | 229
2018-01-06 08:00 | 234 | 234
2018-01-06 08:30 | 239 | 238
2018-01-06 09:00 | 244 | 244
2018-01-06 09:30 | 253 | 253
2018-01-06 10:00 | 250 | 250
2018-01-06 10:30 | 242 | 242
2018-01-06 11:00 | 245 | 245
2018-01-06 11:30 | 244 | 244
2018-01-06 12:00 | 251 | 251
2018-01-06 12:30 | 259 | 259
2018-01-06 13:00 | 264 | 263
2018-01-06 13:30 | 268 | 267
2018-01-06 14:00 | 267 | 266
2018-01-06 14:30 | 272 | 271
2018-01-06 15:00 | 286 | 285
2018-01-06 15:30 | 296 | 296
2018-01-06 16:00 | 300 | 300
2018-01-06 16:30 | 304 | 303
2018-01-06 17:00 | 304 | 303
2018-01-06 17:30 | 303 | 303
2018-01-06 18:00 | 301 | 300
2018-01-06 18:30 | 299 | 298
2018-01-06 19:00 | 299 | 298
2018-01-06 19:30 | 295 | 295
2018-01-06 20:00 | 286 | 286
2018-01-06 20:30 | 278 | 277
2018-01-06 21:00 | 269 | 269
2018-01-06 21:30 | 256 | 256
2018-01-06 22:00 | 247 | 247
2018-01-06 22:30 | 240 | 240
2018-01-06 23:00 | 223 | 223
2018-01-06 23:30 | 210 | 209
2018-01-07 | 202 | 200
2018-01-07 00:30 | 199 | 197
2018-01-07 01:00 | 196 | 194
2018-01-07 01:30 | 190 | 188
2018-01-07 02:00 | 187 | 186
2018-01-07 02:30 | 186 | 185
2018-01-07 03:00 | 185 | 184
2018-01-07 03:30 | 183 | 182
2018-01-07 04:00 | 183 | 182
2018-01-07 04:30 | 180 | 179
2018-01-07 05:00 | 185 | 183
2018-01-07 05:30 | 189 | 187
2018-01-07 06:00 | 198 | 197
2018-01-07 06:30 | 202 | 202
2018-01-07 07:00 | 212 | 212
2018-01-07 07:30 | 221 | 221
2018-01-07 08:00 | 232 | 232
2018-01-07 08:30 | 240 | 239
2018-01-07 09:00 | 245 | 244
2018-01-07 09:30 | 255 | 255
2018-01-07 10:00 | 265 | 265
2018-01-07 10:30 | 267 | 267
2018-01-07 11:00 | 266 | 266
2018-01-07 11:30 | 270 | 270
2018-01-07 12:00 | 273 | 273
2018-01-07 12:30 | 270 | 270
2018-01-07 13:00 | 270 | 269
2018-01-07 13:30 | 268 | 267
2018-01-07 14:00 | 289 | 288
2018-01-07 14:30 | 307 | 307
2018-01-07 15:00 | 315 | 314
2018-01-07 15:30 | 322 | 322
2018-01-07 16:00 | 332 | 332
2018-01-07 16:30 | 340 | 340
2018-01-07 17:00 | 345 | 344
2018-01-07 17:30 | 344 | 343
2018-01-07 18:00 | 338 | 337
2018-01-07 18:30 | 336 | 334
2018-01-07 19:00 | 333 | 332
2018-01-07 19:30 | 330 | 329
2018-01-07 20:00 | 317 | 316
2018-01-07 20:30 | 299 | 297
2018-01-07 21:00 | 283 | 283
2018-01-07 21:30 | 269 | 269
2018-01-07 22:00 | 262 | 262
2018-01-07 22:30 | 253 | 252
2018-01-07 23:00 | 228 | 228
2018-01-07 23:30 | 216 | 216
2018-01-08 | 210 | 210
2018-01-08 00:30 | 207 | 206
2018-01-08 01:00 | 199 | 199
2018-01-08 01:30 | 195 | 195
2018-01-08 02:00 | 193 | 193
2018-01-08 02:30 | 193 | 193
2018-01-08 03:00 | 191 | 191
2018-01-08 03:30 | 192 | 192
2018-01-08 04:00 | 192 | 192
2018-01-08 04:30 | 195 | 194
2018-01-08 05:00 | 199 | 198
2018-01-08 05:30 | 207 | 206
2018-01-08 06:00 | 225 | 225
2018-01-08 06:30 | 240 | 240
2018-01-08 07:00 | 263 | 263
2018-01-08 07:30 | 281 | 281
2018-01-08 08:00 | 292 | 292
2018-01-08 08:30 | 298 | 297
2018-01-08 09:00 | 302 | 301
2018-01-08 09:30 | 304 | 303
2018-01-08 10:00 | 304 | 304
2018-01-08 10:30 | 309 | 309
2018-01-08 11:00 | 312 | 312
2018-01-08 11:30 | 320 | 320
2018-01-08 12:00 | 331 | 330
2018-01-08 12:30 | 339 | 338
2018-01-08 13:00 | 346 | 346
2018-01-08 13:30 | 352 | 352
2018-01-08 14:00 | 355 | 354
2018-01-08 14:30 | 363 | 363
2018-01-08 15:00 | 367 | 367
2018-01-08 15:30 | 374 | 373
2018-01-08 16:00 | 378 | 377
2018-01-08 16:30 | 380 | 380
2018-01-08 17:00 | 380 | 379
2018-01-08 17:30 | 376 | 375
2018-01-08 18:00 | 366 | 364
2018-01-08 18:30 | 364 | 362
2018-01-08 19:00 | 361 | 359
2018-01-08 19:30 | 354 | 351
2018-01-08 20:00 | 335 | 332
2018-01-08 20:30 | 314 | 313
2018-01-08 21:00 | 299 | 298
2018-01-08 21:30 | 284 | 284
2018-01-08 22:00 | 272 | 272
2018-01-08 22:30 | 260 | 260
2018-01-08 23:00 | 241 | 240
2018-01-08 23:30 | 229 | 228
2018-01-09 | 219 | 217
2018-01-09 00:30 | 215 | 212
2018-01-09 01:00 | 209 | 206
2018-01-09 01:30 | 203 | 201
2018-01-09 02:00 | 196 | 194
2018-01-09 02:30 | 194 | 192
2018-01-09 03:00 | 192 | 190
2018-01-09 03:30 | 192 | 190
2018-01-09 04:00 | 194 | 192
2018-01-09 04:30 | 196 | 194
2018-01-09 05:00 | 200 | 198
2018-01-09 05:30 | 202 | 201
2018-01-09 06:00 | 216 | 216
2018-01-09 06:30 | 234 | 233
2018-01-09 07:00 | 253 | 253
2018-01-09 07:30 | 263 | 263
2018-01-09 08:00 | 273 | 273
2018-01-09 08:30 | 278 | 278
2018-01-09 09:00 | 284 | 284
2018-01-09 09:30 | 286 | 285
2018-01-09 10:00 | 291 | 291
2018-01-09 10:30 | 295 | 295
2018-01-09 11:00 | 294 | 294
2018-01-09 11:30 | 302 | 301
2018-01-09 12:00 | 308 | 307
2018-01-09 12:30 | 315 | 314
2018-01-09 13:00 | 320 | 320
2018-01-09 13:30 | 328 | 327
2018-01-09 14:00 | 332 | 332
2018-01-09 14:30 | 329 | 329
2018-01-09 15:00 | 333 | 332
2018-01-09 15:30 | 348 | 347
2018-01-09 16:00 | 358 | 358
2018-01-09 16:30 | 365 | 365
2018-01-09 17:00 | 362 | 361
2018-01-09 17:30 | 356 | 355
2018-01-09 18:00 | 341 | 339
2018-01-09 18:30 | 335 | 334
2018-01-09 19:00 | 327 | 326
2018-01-09 19:30 | 323 | 322
2018-01-09 20:00 | 309 | 308
2018-01-09 20:30 | 304 | 302
2018-01-09 21:00 | 290 | 290
2018-01-09 21:30 | 280 | 279
2018-01-09 22:00 | 261 | 261
2018-01-09 22:30 | 249 | 249
2018-01-09 23:00 | 232 | 232
2018-01-09 23:30 | 215 | 214
2018-01-10 | 202 | 202
2018-01-10 00:30 | 198 | 198
2018-01-10 01:00 | 194 | 193
2018-01-10 01:30 | 189 | 189
2018-01-10 02:00 | 186 | 186
2018-01-10 02:30 | 188 | 188
2018-01-10 03:00 | 188 | 188
2018-01-10 03:30 | 187 | 187
2018-01-10 04:00 | 189 | 189
2018-01-10 04:30 | 191 | 190
2018-01-10 05:00 | 198 | 197
2018-01-10 05:30 | 205 | 204
2018-01-10 06:00 | 224 | 224
2018-01-10 06:30 | 239 | 238
2018-01-10 07:00 | 266 | 266
2018-01-10 07:30 | 280 | 280
2018-01-10 08:00 | 291 | 290
2018-01-10 08:30 | 297 | 297
2018-01-10 09:00 | 305 | 304
2018-01-10 09:30 | 310 | 310
2018-01-10 10:00 | 318 | 318
2018-01-10 10:30 | 321 | 321
2018-01-10 11:00 | 314 | 314
2018-01-10 11:30 | 313 | 313
2018-01-10 12:00 | 319 | 318
2018-01-10 12:30 | 320 | 319
2018-01-10 13:00 | 322 | 322
2018-01-10 13:30 | 324 | 323
2018-01-10 14:00 | 328 | 327
2018-01-10 14:30 | 334 | 334
2018-01-10 15:00 | 335 | 335
2018-01-10 15:30 | 338 | 338
2018-01-10 16:00 | 348 | 348
2018-01-10 16:30 | 353 | 353
2018-01-10 17:00 | 355 | 355
2018-01-10 17:30 | 352 | 350
2018-01-10 18:00 | 338 | 336
2018-01-10 18:30 | 338 | 336
2018-01-10 19:00 | 338 | 336
2018-01-10 19:30 | 332 | 329
2018-01-10 20:00 | 323 | 321
2018-01-10 20:30 | 301 | 300
2018-01-10 21:00 | 294 | 292
2018-01-10 21:30 | 278 | 277
2018-01-10 22:00 | 272 | 271
2018-01-10 22:30 | 264 | 263
2018-01-10 23:00 | 239 | 239
2018-01-10 23:30 | 225 | 225
2018-01-11 | 212 | 212
2018-01-11 00:30 | 205 | 205
2018-01-11 01:00 | 201 | 201
2018-01-11 01:30 | 199 | 198
2018-01-11 02:00 | 197 | 197
2018-01-11 02:30 | 195 | 194
2018-01-11 03:00 | 196 | 195
2018-01-11 03:30 | 197 | 196
2018-01-11 04:00 | 195 | 195
2018-01-11 04:30 | 196 | 195
2018-01-11 05:00 | 201 | 201
2018-01-11 05:30 | 213 | 213
2018-01-11 06:00 | 228 | 227
2018-01-11 06:30 | 244 | 244
2018-01-11 07:00 | 275 | 275
2018-01-11 07:30 | 292 | 292
2018-01-11 08:00 | 304 | 304
2018-01-11 08:30 | 313 | 313
2018-01-11 09:00 | 318 | 318
2018-01-11 09:30 | 322 | 322
2018-01-11 10:00 | 322 | 322
2018-01-11 10:30 | 327 | 327
2018-01-11 11:00 | 344 | 344
2018-01-11 11:30 | 336 | 336
2018-01-11 12:00 | 341 | 341
2018-01-11 12:30 | 337 | 337
2018-01-11 13:00 | 346 | 346
2018-01-11 13:30 | 363 | 363
2018-01-11 14:00 | 368 | 367
2018-01-11 14:30 | 371 | 371
2018-01-11 15:00 | 376 | 375
2018-01-11 15:30 | 380 | 378
2018-01-11 16:00 | 387 | 385
2018-01-11 16:30 | 386 | 384
2018-01-11 17:00 | 393 | 391
2018-01-11 17:30 | 395 | 392
2018-01-11 18:00 | 383 | 380
2018-01-11 18:30 | 384 | 382
2018-01-11 19:00 | 384 | 382
2018-01-11 19:30 | 379 | 378
2018-01-11 20:00 | 365 | 365
2018-01-11 20:30 | 349 | 348
2018-01-11 21:00 | 329 | 328
2018-01-11 21:30 | 307 | 305
2018-01-11 22:00 | 284 | 282
2018-01-11 22:30 | 262 | 262
2018-01-11 23:00 | 250 | 250
2018-01-11 23:30 | 233 | 233
2018-01-12 | 214 | 214
2018-01-12 00:30 | 204 | 204
2018-01-12 01:00 | 196 | 196
2018-01-12 01:30 | 187 | 187
2018-01-12 02:00 | 183 | 183
2018-01-12 02:30 | 183 | 183
2018-01-12 03:00 | 184 | 184
2018-01-12 03:30 | 182 | 182
2018-01-12 04:00 | 185 | 185
2018-01-12 04:30 | 195 | 195
2018-01-12 05:00 | 199 | 199
2018-01-12 05:30 | 209 | 208
2018-01-12 06:00 | 219 | 218
2018-01-12 06:30 | 243 | 243
2018-01-12 07:00 | 281 | 280
2018-01-12 07:30 | 282 | 282
2018-01-12 08:00 | 292 | 292
2018-01-12 08:30 | 300 | 300
2018-01-12 09:00 | 316 | 315
2018-01-12 09:30 | 317 | 317
2018-01-12 10:00 | 313 | 313
2018-01-12 10:30 | 312 | 312
2018-01-12 11:00 | 316 | 315
2018-01-12 11:30 | 319 | 316
2018-01-12 12:00 | 322 | 320
2018-01-12 12:30 | 325 | 323
2018-01-12 13:00 | 331 | 329
2018-01-12 13:30 | 337 | 336
2018-01-12 14:00 | 346 | 345
2018-01-12 14:30 | 353 | 352
2018-01-12 15:00 | 360 | 359
2018-01-12 15:30 | 367 | 366
2018-01-12 16:00 | 372 | 371
2018-01-12 16:30 | 380 | 379
2018-01-12 17:00 | 377 | 376
2018-01-12 17:30 | 365 | 362
2018-01-12 18:00 | 352 | 350
2018-01-12 18:30 | 348 | 346
2018-01-12 19:00 | 346 | 344
2018-01-12 19:30 | 340 | 340
2018-01-12 20:00 | 334 | 333
2018-01-12 20:30 | 314 | 314
2018-01-12 21:00 | 303 | 303
2018-01-12 21:30 | 289 | 289
2018-01-12 22:00 | 280 | 280
2018-01-12 22:30 | 264 | 264
2018-01-12 23:00 | 244 | 244
2018-01-12 23:30 | 228 | 228
2018-01-13 | 217 | 217
2018-01-13 00:30 | 211 | 211
2018-01-13 01:00 | 211 | 211
2018-01-13 01:30 | 205 | 204
2018-01-13 02:00 | 201 | 201
2018-01-13 02:30 | 198 | 198
2018-01-13 03:00 | 196 | 195
2018-01-13 03:30 | 195 | 194
2018-01-13 04:00 | 195 | 195
2018-01-13 04:30 | 196 | 196
2018-01-13 05:00 | 198 | 197
2018-01-13 05:30 | 204 | 204
2018-01-13 06:00 | 218 | 218
2018-01-13 06:30 | 233 | 233
2018-01-13 07:00 | 251 | 251
2018-01-13 07:30 | 267 | 267
2018-01-13 08:00 | 275 | 274
2018-01-13 08:30 | 281 | 281
2018-01-13 09:00 | 292 | 292
2018-01-13 09:30 | 302 | 302
2018-01-13 10:00 | 311 | 311
2018-01-13 10:30 | 312 | 311
2018-01-13 11:00 | 313 | 312
2018-01-13 11:30 | 320 | 320
2018-01-13 12:00 | 337 | 337
2018-01-13 12:30 | 345 | 344
2018-01-13 13:00 | 336 | 335
2018-01-13 13:30 | 353 | 353
2018-01-13 14:00 | 352 | 352
2018-01-13 14:30 | 361 | 361
2018-01-13 15:00 | 373 | 373
2018-01-13 15:30 | 383 | 382
2018-01-13 16:00 | 390 | 389
2018-01-13 16:30 | 397 | 396
2018-01-13 17:00 | 393 | 391
2018-01-13 17:30 | 384 | 382
2018-01-13 18:00 | 377 | 375
2018-01-13 18:30 | 377 | 375
2018-01-13 19:00 | 373 | 372
2018-01-13 19:30 | 367 | 365
2018-01-13 20:00 | 355 | 352
2018-01-13 20:30 | 341 | 337
2018-01-13 21:00 | 325 | 321
2018-01-13 21:30 | 301 | 299
2018-01-13 22:00 | 294 | 292
2018-01-13 22:30 | 285 | 284
2018-01-13 23:00 | 259 | 259
2018-01-13 23:30 | 237 | 236
2018-01-14 | 220 | 219
2018-01-14 00:30 | 218 | 216
2018-01-14 01:00 | 211 | 210
2018-01-14 01:30 | 204 | 203
2018-01-14 02:00 | 199 | 198
2018-01-14 02:30 | 196 | 195
2018-01-14 03:00 | 194 | 193
2018-01-14 03:30 | 189 | 189
2018-01-14 04:00 | 189 | 189
2018-01-14 04:30 | 188 | 188
2018-01-14 05:00 | 188 | 187
2018-01-14 05:30 | 192 | 191
2018-01-14 06:00 | 200 | 200
2018-01-14 06:30 | 212 | 212
2018-01-14 07:00 | 227 | 227
2018-01-14 07:30 | 248 | 248
2018-01-14 08:00 | 268 | 268
2018-01-14 08:30 | 290 | 290
2018-01-14 09:00 | 310 | 310
2018-01-14 09:30 | 317 | 317
2018-01-14 10:00 | 313 | 313
2018-01-14 10:30 | 308 | 308
2018-01-14 11:00 | 309 | 309
2018-01-14 11:30 | 319 | 318
2018-01-14 12:00 | 328 | 327
2018-01-14 12:30 | 338 | 337
2018-01-14 13:00 | 342 | 341
2018-01-14 13:30 | 337 | 336
2018-01-14 14:00 | 344 | 343
2018-01-14 14:30 | 340 | 338
2018-01-14 15:00 | 335 | 332
2018-01-14 15:30 | 325 | 321
2018-01-14 16:00 | 307 | 305
2018-01-14 16:30 | 294 | 294
2018-01-14 17:00 | 284 | 284
2018-01-14 17:30 | 273 | 273
2018-01-14 18:00 | 266 | 266
2018-01-14 18:30 | 265 | 265
2018-01-14 19:00 | 261 | 261
2018-01-14 19:30 | 257 | 257
2018-01-14 20:00 | 247 | 247
2018-01-14 20:30 | 233 | 233
2018-01-14 21:00 | 221 | 221
2018-01-14 21:30 | 208 | 208
2018-01-14 22:00 | 204 | 204
2018-01-14 22:30 | 201 | 201
2018-01-14 23:00 | 182 | 182
2018-01-14 23:30 | 163 | 163
2018-01-15 | 149 | 148
2018-01-15 00:30 | 141 | 140
2018-01-15 01:00 | 135 | 134
2018-01-15 01:30 | 132 | 131
2018-01-15 02:00 | 130 | 130
2018-01-15 02:30 | 128 | 127
2018-01-15 03:00 | 128 | 127
2018-01-15 03:30 | 128 | 128
2018-01-15 04:00 | 132 | 132
2018-01-15 04:30 | 137 | 137
2018-01-15 05:00 | 153 | 153
2018-01-15 05:30 | 176 | 176
2018-01-15 06:00 | 193 | 193
2018-01-15 06:30 | 209 | 209
2018-01-15 07:00 | 222 | 222
2018-01-15 07:30 | 233 | 232
2018-01-15 08:00 | 235 | 235
2018-01-15 08:30 | 235 | 235
2018-01-15 09:00 | 236 | 236
2018-01-15 09:30 | 235 | 234
2018-01-15 10:00 | 235 | 235
2018-01-15 10:30 | 236 | 236
2018-01-15 11:00 | 239 | 239
2018-01-15 11:30 | 244 | 244
2018-01-15 12:00 | 245 | 245
2018-01-15 12:30 | 247 | 247
2018-01-15 13:00 | 249 | 249
2018-01-15 13:30 | 249 | 249
2018-01-15 14:00 | 254 | 254
2018-01-15 14:30 | 257 | 257
2018-01-15 15:00 | 259 | 259
2018-01-15 15:30 | 259 | 259
2018-01-15 16:00 | 264 | 264
2018-01-15 16:30 | 273 | 273
2018-01-15 17:00 | 271 | 271
2018-01-15 17:30 | 270 | 270
2018-01-15 18:00 | 270 | 268
2018-01-15 18:30 | 270 | 268
2018-01-15 19:00 | 270 | 269
2018-01-15 19:30 | 269 | 268
2018-01-15 20:00 | 257 | 257
2018-01-15 20:30 | 247 | 247
2018-01-15 21:00 | 238 | 238
2018-01-15 21:30 | 234 | 234
2018-01-15 22:00 | 227 | 227
2018-01-15 22:30 | 225 | 225
2018-01-15 23:00 | 208 | 207
2018-01-15 23:30 | 191 | 190
2018-01-16 | 182 | 181
2018-01-16 00:30 | 175 | 175
2018-01-16 01:00 | 171 | 170
2018-01-16 01:30 | 165 | 165
2018-01-16 02:00 | 167 | 167
2018-01-16 02:30 | 166 | 165
2018-01-16 03:00 | 168 | 167
2018-01-16 03:30 | 169 | 169
2018-01-16 04:00 | 172 | 172
2018-01-16 04:30 | 177 | 177
2018-01-16 05:00 | 177 | 177
2018-01-16 05:30 | 184 | 184
2018-01-16 06:00 | 200 | 200
2018-01-16 06:30 | 211 | 211
2018-01-16 07:00 | 227 | 227
2018-01-16 07:30 | 237 | 237
2018-01-16 08:00 | 240 | 240
2018-01-16 08:30 | 236 | 236
2018-01-16 09:00 | 235 | 235
2018-01-16 09:30 | 230 | 230
2018-01-16 10:00 | 236 | 236
2018-01-16 10:30 | 238 | 238
2018-01-16 11:00 | 234 | 234
2018-01-16 11:30 | 231 | 230
2018-01-16 12:00 | 236 | 235
2018-01-16 12:30 | 241 | 241
2018-01-16 13:00 | 243 | 243
2018-01-16 13:30 | 246 | 246
2018-01-16 14:00 | 245 | 245
2018-01-16 14:30 | 249 | 249
2018-01-16 15:00 | 251 | 250
2018-01-16 15:30 | 250 | 250
2018-01-16 16:00 | 255 | 255
2018-01-16 16:30 | 268 | 267
2018-01-16 17:00 | 293 | 292
2018-01-16 17:30 | 298 | 296
2018-01-16 18:00 | 278 | 275
2018-01-16 18:30 | 268 | 265
2018-01-16 19:00 | 268 | 266
2018-01-16 19:30 | 265 | 263
2018-01-16 20:00 | 254 | 253
2018-01-16 20:30 | 243 | 243
2018-01-16 21:00 | 229 | 229
2018-01-16 21:30 | 219 | 219
2018-01-16 22:00 | 213 | 213
2018-01-16 22:30 | 214 | 214
2018-01-16 23:00 | 197 | 196
2018-01-16 23:30 | 185 | 184
2018-01-17 | 178 | 178
2018-01-17 00:30 | 177 | 177
2018-01-17 01:00 | 174 | 174
2018-01-17 01:30 | 175 | 175
2018-01-17 02:00 | 176 | 176
2018-01-17 02:30 | 175 | 175
2018-01-17 03:00 | 178 | 178
2018-01-17 03:30 | 179 | 179
2018-01-17 04:00 | 180 | 180
2018-01-17 04:30 | 183 | 182
2018-01-17 05:00 | 185 | 185
2018-01-17 05:30 | 188 | 188
2018-01-17 06:00 | 201 | 201
2018-01-17 06:30 | 212 | 212
2018-01-17 07:00 | 229 | 229
2018-01-17 07:30 | 236 | 236
2018-01-17 08:00 | 243 | 242
2018-01-17 08:30 | 244 | 243
2018-01-17 09:00 | 246 | 245
2018-01-17 09:30 | 246 | 245
2018-01-17 10:00 | 248 | 247
2018-01-17 10:30 | 249 | 249
2018-01-17 11:00 | 249 | 249
2018-01-17 11:30 | 250 | 250
2018-01-17 12:00 | 251 | 251
2018-01-17 12:30 | 252 | 252
2018-01-17 13:00 | 254 | 254
2018-01-17 13:30 | 259 | 259
2018-01-17 14:00 | 263 | 263
2018-01-17 14:30 | 264 | 263
2018-01-17 15:00 | 265 | 265
2018-01-17 15:30 | 271 | 271
2018-01-17 16:00 | 280 | 280
2018-01-17 16:30 | 289 | 289
2018-01-17 17:00 | 288 | 288
2018-01-17 17:30 | 284 | 284
2018-01-17 18:00 | 283 | 282
2018-01-17 18:30 | 282 | 281
2018-01-17 19:00 | 281 | 280
2018-01-17 19:30 | 280 | 280
2018-01-17 20:00 | 271 | 270
2018-01-17 20:30 | 260 | 259
2018-01-17 21:00 | 255 | 254
2018-01-17 21:30 | 240 | 240
2018-01-17 22:00 | 235 | 235
2018-01-17 22:30 | 231 | 230
2018-01-17 23:00 | 215 | 214
2018-01-17 23:30 | 202 | 200
2018-01-18 | 190 | 187
2018-01-18 00:30 | 182 | 179
2018-01-18 01:00 | 174 | 172
2018-01-18 01:30 | 167 | 167
2018-01-18 02:00 | 179 | 179
2018-01-18 02:30 | 174 | 174
2018-01-18 03:00 | 172 | 172
2018-01-18 03:30 | 172 | 172
2018-01-18 04:00 | 181 | 181
2018-01-18 04:30 | 186 | 186
2018-01-18 05:00 | 193 | 193
2018-01-18 05:30 | 193 | 193
2018-01-18 06:00 | 199 | 199
2018-01-18 06:30 | 210 | 210
2018-01-18 07:00 | 224 | 224
2018-01-18 07:30 | 245 | 244
2018-01-18 08:00 | 248 | 248
2018-01-18 08:30 | 252 | 252
2018-01-18 09:00 | 247 | 247
2018-01-18 09:30 | 246 | 246
2018-01-18 10:00 | 247 | 247
2018-01-18 10:30 | 252 | 251
2018-01-18 11:00 | 253 | 253
2018-01-18 11:30 | 252 | 252
2018-01-18 12:00 | 259 | 259
2018-01-18 12:30 | 260 | 260
2018-01-18 13:00 | 263 | 262
2018-01-18 13:30 | 265 | 264
2018-01-18 14:00 | 267 | 267
2018-01-18 14:30 | 276 | 276
2018-01-18 15:00 | 247 | 247
2018-01-18 15:30 | 271 | 270
2018-01-18 16:00 | 304 | 304
2018-01-18 16:30 | 315 | 314
2018-01-18 17:00 | 309 | 308
2018-01-18 17:30 | 305 | 304
2018-01-18 18:00 | 285 | 283
2018-01-18 18:30 | 299 | 297
2018-01-18 19:00 | 304 | 302
2018-01-18 19:30 | 302 | 300
2018-01-18 20:00 | 292 | 289
2018-01-18 20:30 | 276 | 274
2018-01-18 21:00 | 261 | 259
2018-01-18 21:30 | 240 | 239
2018-01-18 22:00 | 234 | 234
2018-01-18 22:30 | 228 | 228
2018-01-18 23:00 | 208 | 207
2018-01-18 23:30 | 196 | 194
2018-01-19 | 189 | 188
2018-01-19 00:30 | 183 | 181
2018-01-19 01:00 | 178 | 176
2018-01-19 01:30 | 180 | 178
2018-01-19 02:00 | 177 | 176
2018-01-19 02:30 | 175 | 174
2018-01-19 03:00 | 175 | 173
2018-01-19 03:30 | 179 | 177
2018-01-19 04:00 | 186 | 184
2018-01-19 04:30 | 191 | 189
2018-01-19 05:00 | 190 | 188
2018-01-19 05:30 | 202 | 201
2018-01-19 06:00 | 210 | 210
2018-01-19 06:30 | 216 | 216
2018-01-19 07:00 | 228 | 228
2018-01-19 07:30 | 240 | 240
2018-01-19 08:00 | 251 | 251
2018-01-19 08:30 | 258 | 257
2018-01-19 09:00 | 261 | 260
2018-01-19 09:30 | 254 | 253
2018-01-19 10:00 | 253 | 253
2018-01-19 10:30 | 249 | 248
2018-01-19 11:00 | 234 | 233
2018-01-19 11:30 | 262 | 262
2018-01-19 12:00 | 253 | 253
2018-01-19 12:30 | 247 | 246
2018-01-19 13:00 | 297 | 297
2018-01-19 13:30 | 309 | 307
2018-01-19 14:00 | 315 | 313
2018-01-19 14:30 | 324 | 322
2018-01-19 15:00 | 332 | 330
2018-01-19 15:30 | 341 | 339
2018-01-19 16:00 | 350 | 348
2018-01-19 16:30 | 358 | 355
2018-01-19 17:00 | 357 | 355
2018-01-19 17:30 | 347 | 346
2018-01-19 18:00 | 349 | 347
2018-01-19 18:30 | 350 | 348
2018-01-19 19:00 | 353 | 350
2018-01-19 19:30 | 350 | 347
2018-01-19 20:00 | 287 | 283
2018-01-19 20:30 | 262 | 261
2018-01-19 21:00 | 255 | 255
2018-01-19 21:30 | 249 | 249
2018-01-19 22:00 | 245 | 245
2018-01-19 22:30 | 237 | 237
2018-01-19 23:00 | 220 | 220
2018-01-19 23:30 | 211 | 211
2018-01-20 | 205 | 204
2018-01-20 00:30 | 206 | 205
2018-01-20 01:00 | 209 | 208
2018-01-20 01:30 | 204 | 204
2018-01-20 02:00 | 201 | 200
2018-01-20 02:30 | 199 | 198
2018-01-20 03:00 | 197 | 197
2018-01-20 03:30 | 197 | 196
2018-01-20 04:00 | 198 | 197
2018-01-20 04:30 | 200 | 199
2018-01-20 05:00 | 203 | 201
2018-01-20 05:30 | 207 | 206
2018-01-20 06:00 | 216 | 215
2018-01-20 06:30 | 223 | 223
2018-01-20 07:00 | 235 | 235
2018-01-20 07:30 | 242 | 242
2018-01-20 08:00 | 251 | 251
2018-01-20 08:30 | 257 | 257
2018-01-20 09:00 | 237 | 237
2018-01-20 09:30 | 245 | 244
2018-01-20 10:00 | 252 | 252
2018-01-20 10:30 | 256 | 256
2018-01-20 11:00 | 252 | 252
2018-01-20 11:30 | 250 | 249
2018-01-20 12:00 | 250 | 250
2018-01-20 12:30 | 255 | 255
2018-01-20 13:00 | 258 | 258
2018-01-20 13:30 | 259 | 259
2018-01-20 14:00 | 264 | 264
2018-01-20 14:30 | 266 | 266
2018-01-20 15:00 | 273 | 273
2018-01-20 15:30 | 279 | 279
2018-01-20 16:00 | 285 | 284
2018-01-20 16:30 | 292 | 291
2018-01-20 17:00 | 294 | 292
2018-01-20 17:30 | 293 | 291
2018-01-20 18:00 | 291 | 289
2018-01-20 18:30 | 295 | 292
2018-01-20 19:00 | 295 | 293
2018-01-20 19:30 | 296 | 293
2018-01-20 20:00 | 287 | 284
2018-01-20 20:30 | 268 | 268
2018-01-20 21:00 | 260 | 260
2018-01-20 21:30 | 253 | 253
2018-01-20 22:00 | 248 | 248
2018-01-20 22:30 | 242 | 242
2018-01-20 23:00 | 224 | 223
2018-01-20 23:30 | 216 | 215
2018-01-21 | 209 | 208
2018-01-21 00:30 | 205 | 204
2018-01-21 01:00 | 200 | 199
2018-01-21 01:30 | 192 | 192
2018-01-21 02:00 | 190 | 189
2018-01-21 02:30 | 192 | 192
2018-01-21 03:00 | 190 | 189
2018-01-21 03:30 | 190 | 190
2018-01-21 04:00 | 188 | 187
2018-01-21 04:30 | 188 | 187
2018-01-21 05:00 | 190 | 188
2018-01-21 05:30 | 196 | 195
2018-01-21 06:00 | 202 | 201
2018-01-21 06:30 | 205 | 205
2018-01-21 07:00 | 215 | 215
2018-01-21 07:30 | 226 | 226
2018-01-21 08:00 | 234 | 234
2018-01-21 08:30 | 245 | 245
2018-01-21 09:00 | 250 | 250
2018-01-21 09:30 | 258 | 257
2018-01-21 10:00 | 260 | 259
2018-01-21 10:30 | 262 | 262
2018-01-21 11:00 | 256 | 256
2018-01-21 11:30 | 261 | 261
2018-01-21 12:00 | 264 | 263
2018-01-21 12:30 | 266 | 266
2018-01-21 13:00 | 264 | 264
2018-01-21 13:30 | 270 | 270
2018-01-21 14:00 | 286 | 285
2018-01-21 14:30 | 304 | 303
2018-01-21 15:00 | 306 | 304
2018-01-21 15:30 | 318 | 316
2018-01-21 16:00 | 320 | 319
2018-01-21 16:30 | 324 | 322
2018-01-21 17:00 | 325 | 323
2018-01-21 17:30 | 328 | 325
2018-01-21 18:00 | 320 | 317
2018-01-21 18:30 | 322 | 319
2018-01-21 19:00 | 316 | 313
2018-01-21 19:30 | 313 | 310
2018-01-21 20:00 | 298 | 294
2018-01-21 20:30 | 277 | 276
2018-01-21 21:00 | 270 | 268
2018-01-21 21:30 | 258 | 256
2018-01-21 22:00 | 244 | 244
2018-01-21 22:30 | 239 | 239
2018-01-21 23:00 | 223 | 223
2018-01-21 23:30 | 212 | 212
2018-01-22 | 204 | 203
2018-01-22 00:30 | 199 | 199
2018-01-22 01:00 | 194 | 193
2018-01-22 01:30 | 194 | 194
2018-01-22 02:00 | 196 | 196
2018-01-22 02:30 | 196 | 195
2018-01-22 03:00 | 195 | 194
2018-01-22 03:30 | 192 | 191
2018-01-22 04:00 | 196 | 196
2018-01-22 04:30 | 204 | 204
2018-01-22 05:00 | 209 | 209
2018-01-22 05:30 | 219 | 219
2018-01-22 06:00 | 233 | 233
2018-01-22 06:30 | 245 | 245
2018-01-22 07:00 | 270 | 270
2018-01-22 07:30 | 290 | 290
2018-01-22 08:00 | 306 | 306
2018-01-22 08:30 | 306 | 306
2018-01-22 09:00 | 314 | 313
2018-01-22 09:30 | 317 | 317
2018-01-22 10:00 | 321 | 321
2018-01-22 10:30 | 325 | 325
2018-01-22 11:00 | 325 | 325
2018-01-22 11:30 | 329 | 329
2018-01-22 12:00 | 333 | 333
2018-01-22 12:30 | 340 | 340
2018-01-22 13:00 | 346 | 346
2018-01-22 13:30 | 357 | 355
2018-01-22 14:00 | 361 | 359
2018-01-22 14:30 | 364 | 362
2018-01-22 15:00 | 370 | 368
2018-01-22 15:30 | 377 | 375
2018-01-22 16:00 | 379 | 377
2018-01-22 16:30 | 377 | 374
2018-01-22 17:00 | 369 | 364
2018-01-22 17:30 | 351 | 350
2018-01-22 18:00 | 346 | 345
2018-01-22 18:30 | 347 | 346
2018-01-22 19:00 | 346 | 345
2018-01-22 19:30 | 342 | 341
2018-01-22 20:00 | 332 | 330
2018-01-22 20:30 | 316 | 314
2018-01-22 21:00 | 300 | 299
2018-01-22 21:30 | 286 | 285
2018-01-22 22:00 | 272 | 270
2018-01-22 22:30 | 254 | 253
2018-01-22 23:00 | 233 | 232
2018-01-22 23:30 | 223 | 222
2018-01-23 | 215 | 214
2018-01-23 00:30 | 211 | 210
2018-01-23 01:00 | 205 | 205
2018-01-23 01:30 | 202 | 201
2018-01-23 02:00 | 200 | 200
2018-01-23 02:30 | 200 | 199
2018-01-23 03:00 | 200 | 199
2018-01-23 03:30 | 199 | 199
2018-01-23 04:00 | 202 | 201
2018-01-23 04:30 | 203 | 203
2018-01-23 05:00 | 208 | 208
2018-01-23 05:30 | 216 | 215
2018-01-23 06:00 | 217 | 217
2018-01-23 06:30 | 231 | 231
2018-01-23 07:00 | 253 | 253
2018-01-23 07:30 | 264 | 263
2018-01-23 08:00 | 272 | 271
2018-01-23 08:30 | 277 | 274
2018-01-23 09:00 | 286 | 286
2018-01-23 09:30 | 286 | 286
2018-01-23 10:00 | 311 | 311
2018-01-23 10:30 | 318 | 318
2018-01-23 11:00 | 317 | 317
2018-01-23 11:30 | 316 | 316
2018-01-23 12:00 | 317 | 317
2018-01-23 12:30 | 317 | 317
2018-01-23 13:00 | 321 | 321
2018-01-23 13:30 | 328 | 328
2018-01-23 14:00 | 334 | 334
2018-01-23 14:30 | 339 | 339
2018-01-23 15:00 | 344 | 344
2018-01-23 15:30 | 358 | 358
2018-01-23 16:00 | 365 | 365
2018-01-23 16:30 | 368 | 368
2018-01-23 17:00 | 366 | 365
2018-01-23 17:30 | 363 | 361
2018-01-23 18:00 | 355 | 353
2018-01-23 18:30 | 351 | 350
2018-01-23 19:00 | 352 | 352
2018-01-23 19:30 | 348 | 348
2018-01-23 20:00 | 335 | 334
2018-01-23 20:30 | 318 | 317
2018-01-23 21:00 | 302 | 302
2018-01-23 21:30 | 286 | 286
2018-01-23 22:00 | 269 | 269
2018-01-23 22:30 | 256 | 256
2018-01-23 23:00 | 236 | 236
2018-01-23 23:30 | 222 | 222
2018-01-24 | 214 | 214
2018-01-24 00:30 | 210 | 210
2018-01-24 01:00 | 208 | 208
2018-01-24 01:30 | 205 | 205
2018-01-24 02:00 | 203 | 203
2018-01-24 02:30 | 202 | 202
2018-01-24 03:00 | 204 | 204
2018-01-24 03:30 | 204 | 204
2018-01-24 04:00 | 204 | 204
2018-01-24 04:30 | 208 | 207
2018-01-24 05:00 | 213 | 213
2018-01-24 05:30 | 222 | 222
2018-01-24 06:00 | 239 | 239
2018-01-24 06:30 | 253 | 253
2018-01-24 07:00 | 278 | 278
2018-01-24 07:30 | 293 | 293
2018-01-24 08:00 | 303 | 303
2018-01-24 08:30 | 310 | 310
2018-01-24 09:00 | 322 | 321
2018-01-24 09:30 | 327 | 327
2018-01-24 10:00 | 334 | 333
2018-01-24 10:30 | 340 | 340
2018-01-24 11:00 | 336 | 336
2018-01-24 11:30 | 337 | 337
2018-01-24 12:00 | 343 | 343
2018-01-24 12:30 | 350 | 350
2018-01-24 13:00 | 355 | 355
2018-01-24 13:30 | 355 | 355
2018-01-24 14:00 | 358 | 357
2018-01-24 14:30 | 364 | 364
2018-01-24 15:00 | 365 | 365
2018-01-24 15:30 | 372 | 372
2018-01-24 16:00 | 371 | 371
2018-01-24 16:30 | 375 | 375
2018-01-24 17:00 | 370 | 370
2018-01-24 17:30 | 369 | 368
2018-01-24 18:00 | 362 | 360
2018-01-24 18:30 | 362 | 361
2018-01-24 19:00 | 356 | 355
2018-01-24 19:30 | 348 | 347
2018-01-24 20:00 | 332 | 331
2018-01-24 20:30 | 313 | 313
2018-01-24 21:00 | 304 | 303
2018-01-24 21:30 | 289 | 288
2018-01-24 22:00 | 270 | 270
2018-01-24 22:30 | 260 | 260
2018-01-24 23:00 | 238 | 238
2018-01-24 23:30 | 226 | 225
2018-01-25 | 215 | 214
2018-01-25 00:30 | 208 | 208
2018-01-25 01:00 | 202 | 202
2018-01-25 01:30 | 191 | 191
2018-01-25 02:00 | 195 | 195
2018-01-25 02:30 | 195 | 195
2018-01-25 03:00 | 198 | 198
2018-01-25 03:30 | 200 | 200
2018-01-25 04:00 | 201 | 201
2018-01-25 04:30 | 207 | 206
2018-01-25 05:00 | 209 | 209
2018-01-25 05:30 | 216 | 216
2018-01-25 06:00 | 236 | 236
2018-01-25 06:30 | 260 | 260
2018-01-25 07:00 | 290 | 290
2018-01-25 07:30 | 305 | 304
2018-01-25 08:00 | 307 | 307
2018-01-25 08:30 | 310 | 310
2018-01-25 09:00 | 317 | 317
2018-01-25 09:30 | 324 | 324
2018-01-25 10:00 | 329 | 329
2018-01-25 10:30 | 327 | 326
2018-01-25 11:00 | 337 | 336
2018-01-25 11:30 | 343 | 343
2018-01-25 12:00 | 346 | 346
2018-01-25 12:30 | 349 | 348
2018-01-25 13:00 | 354 | 354
2018-01-25 13:30 | 353 | 352
2018-01-25 14:00 | 366 | 366
2018-01-25 14:30 | 365 | 365
2018-01-25 15:00 | 360 | 360
2018-01-25 15:30 | 364 | 363
2018-01-25 16:00 | 353 | 352
2018-01-25 16:30 | 360 | 359
2018-01-25 17:00 | 359 | 357
2018-01-25 17:30 | 357 | 354
2018-01-25 18:00 | 350 | 348
2018-01-25 18:30 | 352 | 349
2018-01-25 19:00 | 351 | 349
2018-01-25 19:30 | 351 | 349
2018-01-25 20:00 | 335 | 334
2018-01-25 20:30 | 319 | 319
2018-01-25 21:00 | 309 | 308
2018-01-25 21:30 | 300 | 300
2018-01-25 22:00 | 287 | 287
2018-01-25 22:30 | 274 | 273
2018-01-25 23:00 | 254 | 252
2018-01-25 23:30 | 241 | 240
2018-01-26 | 225 | 225
2018-01-26 00:30 | 221 | 221
2018-01-26 01:00 | 215 | 215
2018-01-26 01:30 | 211 | 211
2018-01-26 02:00 | 208 | 208
2018-01-26 02:30 | 208 | 208
2018-01-26 03:00 | 207 | 207
2018-01-26 03:30 | 208 | 208
2018-01-26 04:00 | 209 | 209
2018-01-26 04:30 | 209 | 209
2018-01-26 05:00 | 209 | 209
2018-01-26 05:30 | 215 | 214
2018-01-26 06:00 | 224 | 224
2018-01-26 06:30 | 233 | 233
2018-01-26 07:00 | 254 | 254
2018-01-26 07:30 | 266 | 266
2018-01-26 08:00 | 276 | 276
2018-01-26 08:30 | 287 | 287
2018-01-26 09:00 | 295 | 295
2018-01-26 09:30 | 305 | 304
2018-01-26 10:00 | 311 | 310
2018-01-26 10:30 | 307 | 307
2018-01-26 11:00 | 306 | 305
2018-01-26 11:30 | 308 | 308
2018-01-26 12:00 | 309 | 309
2018-01-26 12:30 | 309 | 309
2018-01-26 13:00 | 315 | 315
2018-01-26 13:30 | 329 | 327
2018-01-26 14:00 | 337 | 336
2018-01-26 14:30 | 338 | 336
2018-01-26 15:00 | 334 | 332
2018-01-26 15:30 | 341 | 340
2018-01-26 16:00 | 347 | 346
2018-01-26 16:30 | 348 | 347
2018-01-26 17:00 | 345 | 343
2018-01-26 17:30 | 347 | 345
2018-01-26 18:00 | 347 | 344
2018-01-26 18:30 | 347 | 344
2018-01-26 19:00 | 347 | 345
2018-01-26 19:30 | 348 | 346
2018-01-26 20:00 | 340 | 337
2018-01-26 20:30 | 329 | 327
2018-01-26 21:00 | 320 | 319
2018-01-26 21:30 | 313 | 311
2018-01-26 22:00 | 304 | 302
2018-01-26 22:30 | 292 | 292
2018-01-26 23:00 | 272 | 272
2018-01-26 23:30 | 253 | 253
2018-01-27 | 235 | 235
2018-01-27 00:30 | 228 | 227
2018-01-27 01:00 | 222 | 222
2018-01-27 01:30 | 217 | 217
2018-01-27 02:00 | 216 | 216
2018-01-27 02:30 | 214 | 214
2018-01-27 03:00 | 210 | 210
2018-01-27 03:30 | 212 | 212
2018-01-27 04:00 | 210 | 210
2018-01-27 04:30 | 216 | 215
2018-01-27 05:00 | 218 | 217
2018-01-27 05:30 | 221 | 221
2018-01-27 06:00 | 234 | 233
2018-01-27 06:30 | 241 | 240
2018-01-27 07:00 | 257 | 257
2018-01-27 07:30 | 267 | 267
2018-01-27 08:00 | 279 | 279
2018-01-27 08:30 | 295 | 295
2018-01-27 09:00 | 315 | 315
2018-01-27 09:30 | 320 | 319
2018-01-27 10:00 | 325 | 324
2018-01-27 10:30 | 322 | 322
2018-01-27 11:00 | 320 | 320
2018-01-27 11:30 | 324 | 324
2018-01-27 12:00 | 326 | 326
2018-01-27 12:30 | 333 | 332
2018-01-27 13:00 | 339 | 339
2018-01-27 13:30 | 348 | 347
2018-01-27 14:00 | 349 | 348
2018-01-27 14:30 | 357 | 356
2018-01-27 15:00 | 363 | 363
2018-01-27 15:30 | 368 | 368
2018-01-27 16:00 | 374 | 373
2018-01-27 16:30 | 381 | 381
2018-01-27 17:00 | 383 | 382
2018-01-27 17:30 | 374 | 373
2018-01-27 18:00 | 360 | 358
2018-01-27 18:30 | 357 | 355
2018-01-27 19:00 | 353 | 352
2018-01-27 19:30 | 343 | 341
2018-01-27 20:00 | 329 | 326
2018-01-27 20:30 | 311 | 311
2018-01-27 21:00 | 297 | 297
2018-01-27 21:30 | 286 | 285
2018-01-27 22:00 | 284 | 284
2018-01-27 22:30 | 278 | 277
2018-01-27 23:00 | 256 | 254
2018-01-27 23:30 | 245 | 243
2018-01-28 | 230 | 230
2018-01-28 00:30 | 226 | 226
2018-01-28 01:00 | 223 | 223
2018-01-28 01:30 | 216 | 216
2018-01-28 02:00 | 209 | 209
2018-01-28 02:30 | 210 | 210
2018-01-28 03:00 | 210 | 209
2018-01-28 03:30 | 208 | 208
2018-01-28 04:00 | 208 | 208
2018-01-28 04:30 | 208 | 208
2018-01-28 05:00 | 209 | 209
2018-01-28 05:30 | 214 | 214
2018-01-28 06:00 | 221 | 221
2018-01-28 06:30 | 229 | 229
2018-01-28 07:00 | 239 | 239
2018-01-28 07:30 | 252 | 252
2018-01-28 08:00 | 267 | 267
2018-01-28 08:30 | 272 | 272
2018-01-28 09:00 | 277 | 277
2018-01-28 09:30 | 273 | 273
2018-01-28 10:00 | 271 | 271
2018-01-28 10:30 | 286 | 285
2018-01-28 11:00 | 297 | 297
2018-01-28 11:30 | 291 | 291
2018-01-28 12:00 | 302 | 301
2018-01-28 12:30 | 293 | 292
2018-01-28 13:00 | 304 | 303
2018-01-28 13:30 | 298 | 298
2018-01-28 14:00 | 299 | 298
2018-01-28 14:30 | 301 | 301
2018-01-28 15:00 | 306 | 305
2018-01-28 15:30 | 318 | 318
2018-01-28 16:00 | 332 | 329
2018-01-28 16:30 | 336 | 333
2018-01-28 17:00 | 333 | 329
2018-01-28 17:30 | 330 | 326
2018-01-28 18:00 | 332 | 328
2018-01-28 18:30 | 333 | 329
2018-01-28 19:00 | 330 | 326
2018-01-28 19:30 | 329 | 325
2018-01-28 20:00 | 315 | 314
2018-01-28 20:30 | 298 | 298
2018-01-28 21:00 | 288 | 288
2018-01-28 21:30 | 280 | 280
2018-01-28 22:00 | 268 | 268
2018-01-28 22:30 | 258 | 258
2018-01-28 23:00 | 239 | 239
2018-01-28 23:30 | 227 | 227
2018-01-29 | 217 | 216
2018-01-29 00:30 | 214 | 214
2018-01-29 01:00 | 211 | 211
2018-01-29 01:30 | 207 | 206
2018-01-29 02:00 | 205 | 205
2018-01-29 02:30 | 204 | 203
2018-01-29 03:00 | 203 | 203
2018-01-29 03:30 | 203 | 203
2018-01-29 04:00 | 207 | 207
2018-01-29 04:30 | 211 | 210
2018-01-29 05:00 | 217 | 217
2018-01-29 05:30 | 227 | 227
2018-01-29 06:00 | 238 | 238
2018-01-29 06:30 | 258 | 258
2018-01-29 07:00 | 285 | 285
2018-01-29 07:30 | 302 | 302
2018-01-29 08:00 | 313 | 313
2018-01-29 08:30 | 321 | 321
2018-01-29 09:00 | 316 | 316
2018-01-29 09:30 | 317 | 317
2018-01-29 10:00 | 320 | 320
2018-01-29 10:30 | 317 | 317
2018-01-29 11:00 | 324 | 324
2018-01-29 11:30 | 328 | 328
2018-01-29 12:00 | 327 | 327
2018-01-29 12:30 | 326 | 326
2018-01-29 13:00 | 338 | 338
2018-01-29 13:30 | 338 | 338
2018-01-29 14:00 | 335 | 335
2018-01-29 14:30 | 341 | 341
2018-01-29 15:00 | 342 | 342
2018-01-29 15:30 | 349 | 349
2018-01-29 16:00 | 347 | 347
2018-01-29 16:30 | 352 | 352
2018-01-29 17:00 | 348 | 347
2018-01-29 17:30 | 343 | 342
2018-01-29 18:00 | 339 | 338
2018-01-29 18:30 | 337 | 336
2018-01-29 19:00 | 332 | 330
2018-01-29 19:30 | 328 | 326
2018-01-29 20:00 | 312 | 310
2018-01-29 20:30 | 295 | 294
2018-01-29 21:00 | 281 | 280
2018-01-29 21:30 | 275 | 274
2018-01-29 22:00 | 262 | 259
2018-01-29 22:30 | 251 | 249
2018-01-29 23:00 | 232 | 231
2018-01-29 23:30 | 220 | 220
2018-01-30 | 209 | 208
2018-01-30 00:30 | 203 | 203
2018-01-30 01:00 | 198 | 197
2018-01-30 01:30 | 194 | 194
2018-01-30 02:00 | 192 | 191
2018-01-30 02:30 | 193 | 192
2018-01-30 03:00 | 194 | 194
2018-01-30 03:30 | 198 | 198
2018-01-30 04:00 | 203 | 202
2018-01-30 04:30 | 207 | 206
2018-01-30 05:00 | 213 | 213
2018-01-30 05:30 | 225 | 225
2018-01-30 06:00 | 241 | 241
2018-01-30 06:30 | 263 | 263
2018-01-30 07:00 | 290 | 290
2018-01-30 07:30 | 300 | 300
2018-01-30 08:00 | 309 | 309
2018-01-30 08:30 | 316 | 316
2018-01-30 09:00 | 320 | 320
2018-01-30 09:30 | 318 | 318
2018-01-30 10:00 | 315 | 315
2018-01-30 10:30 | 313 | 313
2018-01-30 11:00 | 324 | 324
2018-01-30 11:30 | 325 | 325
2018-01-30 12:00 | 327 | 327
2018-01-30 12:30 | 294 | 293
2018-01-30 13:00 | 304 | 304
2018-01-30 13:30 | 322 | 321
2018-01-30 14:00 | 334 | 332
2018-01-30 14:30 | 332 | 330
2018-01-30 15:00 | 334 | 333
2018-01-30 15:30 | 347 | 345
2018-01-30 16:00 | 355 | 353
2018-01-30 16:30 | 365 | 363
2018-01-30 17:00 | 364 | 361
2018-01-30 17:30 | 349 | 345
2018-01-30 18:00 | 348 | 347
2018-01-30 18:30 | 354 | 353
2018-01-30 19:00 | 356 | 355
2018-01-30 19:30 | 352 | 352
2018-01-30 20:00 | 338 | 337
2018-01-30 20:30 | 320 | 319
2018-01-30 21:00 | 308 | 305
2018-01-30 21:30 | 286 | 284
2018-01-30 22:00 | 270 | 268
2018-01-30 22:30 | 237 | 237
2018-01-30 23:00 | 215 | 214
2018-01-30 23:30 | 222 | 221
2018-01-31 | 207 | 207
2018-01-31 00:30 | 200 | 200
2018-01-31 01:00 | 177 | 177
2018-01-31 01:30 | 181 | 181
2018-01-31 02:00 | 177 | 177
2018-01-31 02:30 | 187 | 186
2018-01-31 03:00 | 184 | 183
2018-01-31 03:30 | 150 | 149
2018-01-31 04:00 | 154 | 153
2018-01-31 04:30 | 177 | 176
2018-01-31 05:00 | 160 | 160
2018-01-31 05:30 | 200 | 200
2018-01-31 06:00 | 236 | 236
2018-01-31 06:30 | 253 | 253
2018-01-31 07:00 | 280 | 280
2018-01-31 07:30 | 287 | 287
2018-01-31 08:00 | 293 | 293
2018-01-31 08:30 | 271 | 271
2018-01-31 09:00 | 291 | 291
2018-01-31 09:30 | 308 | 308
2018-01-31 10:00 | 296 | 295
2018-01-31 10:30 | 296 | 296
2018-01-31 11:00 | 312 | 311
2018-01-31 11:30 | 314 | 313
2018-01-31 12:00 | 311 | 310
2018-01-31 12:30 | 311 | 311
2018-01-31 13:00 | 314 | 313
2018-01-31 13:30 | 323 | 322
2018-01-31 14:00 | 329 | 329
2018-01-31 14:30 | 331 | 330
2018-01-31 15:00 | 341 | 340
2018-01-31 15:30 | 349 | 348
2018-01-31 16:00 | 351 | 350
2018-01-31 16:30 | 354 | 354
2018-01-31 17:00 | 343 | 341
2018-01-31 17:30 | 339 | 336
2018-01-31 18:00 | 329 | 328
2018-01-31 18:30 | 336 | 336
2018-01-31 19:00 | 322 | 322
2018-01-31 19:30 | 319 | 319
2018-01-31 20:00 | 301 | 300
2018-01-31 20:30 | 284 | 284
2018-01-31 21:00 | 271 | 271
2018-01-31 21:30 | 259 | 259
2018-01-31 22:00 | 245 | 245
2018-01-31 22:30 | 233 | 233
2018-01-31 23:00 | 217 | 217
2018-01-31 23:30 | 208 | 208
2018-02-01 | 197 | 197
2018-02-01 00:30 | 192 | 191
2018-02-01 01:00 | 187 | 187
2018-02-01 01:30 | 184 | 184
2018-02-01 02:00 | 183 | 183
2018-02-01 02:30 | 183 | 183
2018-02-01 03:00 | 185 | 185
2018-02-01 03:30 | 185 | 185
2018-02-01 04:00 | 186 | 186
2018-02-01 04:30 | 191 | 191
2018-02-01 05:00 | 203 | 203
2018-02-01 05:30 | 212 | 212
2018-02-01 06:00 | 231 | 231
2018-02-01 06:30 | 246 | 246
2018-02-01 07:00 | 267 | 267
2018-02-01 07:30 | 268 | 268
2018-02-01 08:00 | 270 | 269
2018-02-01 08:30 | 263 | 263
2018-02-01 09:00 | 258 | 258
2018-02-01 09:30 | 272 | 272
2018-02-01 10:00 | 292 | 292
2018-02-01 10:30 | 262 | 262
2018-02-01 11:00 | 266 | 266
2018-02-01 11:30 | 267 | 267
2018-02-01 12:00 | 254 | 254
2018-02-01 12:30 | 252 | 252
2018-02-01 13:00 | 265 | 265
2018-02-01 13:30 | 269 | 269
2018-02-01 14:00 | 268 | 268
2018-02-01 14:30 | 269 | 269
2018-02-01 15:00 | 269 | 269
2018-02-01 15:30 | 268 | 268
2018-02-01 16:00 | 269 | 269
2018-02-01 16:30 | 273 | 273
2018-02-01 17:00 | 280 | 280
2018-02-01 17:30 | 281 | 281
2018-02-01 18:00 | 279 | 278
2018-02-01 18:30 | 280 | 279
2018-02-01 19:00 | 280 | 279
2018-02-01 19:30 | 282 | 282
2018-02-01 20:00 | 272 | 272
2018-02-01 20:30 | 257 | 257
2018-02-01 21:00 | 241 | 241
2018-02-01 21:30 | 237 | 237
2018-02-01 22:00 | 231 | 231
2018-02-01 22:30 | 223 | 223
2018-02-01 23:00 | 211 | 210
2018-02-01 23:30 | 200 | 199
2018-02-02 | 195 | 194
2018-02-02 00:30 | 193 | 191
2018-02-02 01:00 | 187 | 185
2018-02-02 01:30 | 180 | 178
2018-02-02 02:00 | 179 | 176
2018-02-02 02:30 | 180 | 177
2018-02-02 03:00 | 182 | 180
2018-02-02 03:30 | 182 | 179
2018-02-02 04:00 | 183 | 181
2018-02-02 04:30 | 187 | 185
2018-02-02 05:00 | 195 | 193
2018-02-02 05:30 | 206 | 204
2018-02-02 06:00 | 228 | 228
2018-02-02 06:30 | 246 | 246
2018-02-02 07:00 | 267 | 266
2018-02-02 07:30 | 276 | 276
2018-02-02 08:00 | 274 | 274
2018-02-02 08:30 | 274 | 274
2018-02-02 09:00 | 281 | 281
2018-02-02 09:30 | 280 | 279
2018-02-02 10:00 | 274 | 274
2018-02-02 10:30 | 271 | 271
2018-02-02 11:00 | 265 | 265
2018-02-02 11:30 | 263 | 262
2018-02-02 12:00 | 260 | 260
2018-02-02 12:30 | 256 | 256
2018-02-02 13:00 | 259 | 259
2018-02-02 13:30 | 260 | 260
2018-02-02 14:00 | 261 | 261
2018-02-02 14:30 | 260 | 260
2018-02-02 15:00 | 257 | 257
2018-02-02 15:30 | 260 | 260
2018-02-02 16:00 | 264 | 264
2018-02-02 16:30 | 267 | 267
2018-02-02 17:00 | 263 | 263
2018-02-02 17:30 | 260 | 260
2018-02-02 18:00 | 256 | 256
2018-02-02 18:30 | 263 | 263
2018-02-02 19:00 | 264 | 263
2018-02-02 19:30 | 263 | 262
2018-02-02 20:00 | 256 | 255
2018-02-02 20:30 | 247 | 246
2018-02-02 21:00 | 247 | 245
2018-02-02 21:30 | 242 | 240
2018-02-02 22:00 | 238 | 236
2018-02-02 22:30 | 233 | 230
2018-02-02 23:00 | 218 | 215
2018-02-02 23:30 | 209 | 205
2018-02-03 | 195 | 190
2018-02-03 00:30 | 188 | 183
2018-02-03 01:00 | 184 | 178
2018-02-03 01:30 | 181 | 175
2018-02-03 02:00 | 179 | 173
2018-02-03 02:30 | 178 | 171
2018-02-03 03:00 | 178 | 171
2018-02-03 03:30 | 176 | 172
2018-02-03 04:00 | 180 | 177
2018-02-03 04:30 | 183 | 181
2018-02-03 05:00 | 187 | 184
2018-02-03 05:30 | 188 | 185
2018-02-03 06:00 | 195 | 192
2018-02-03 06:30 | 203 | 201
2018-02-03 07:00 | 211 | 210
2018-02-03 07:30 | 225 | 224
2018-02-03 08:00 | 234 | 233
2018-02-03 08:30 | 244 | 242
2018-02-03 09:00 | 250 | 249
2018-02-03 09:30 | 250 | 249
2018-02-03 10:00 | 249 | 247
2018-02-03 10:30 | 248 | 246
2018-02-03 11:00 | 245 | 243
2018-02-03 11:30 | 246 | 244
2018-02-03 12:00 | 243 | 241
2018-02-03 12:30 | 244 | 242
2018-02-03 13:00 | 242 | 240
2018-02-03 13:30 | 241 | 238
2018-02-03 14:00 | 240 | 238
2018-02-03 14:30 | 240 | 237
2018-02-03 15:00 | 238 | 235
2018-02-03 15:30 | 238 | 235
2018-02-03 16:00 | 241 | 239
2018-02-03 16:30 | 246 | 243
2018-02-03 17:00 | 246 | 243
2018-02-03 17:30 | 246 | 243
2018-02-03 18:00 | 248 | 245
2018-02-03 18:30 | 254 | 251
2018-02-03 19:00 | 255 | 252
2018-02-03 19:30 | 252 | 250
2018-02-03 20:00 | 246 | 244
2018-02-03 20:30 | 234 | 233
2018-02-03 21:00 | 226 | 225
2018-02-03 21:30 | 229 | 227
2018-02-03 22:00 | 232 | 230
2018-02-03 22:30 | 227 | 225
2018-02-03 23:00 | 215 | 213
2018-02-03 23:30 | 204 | 200
2018-02-04 | 194 | 192
2018-02-04 00:30 | 189 | 187
2018-02-04 01:00 | 184 | 182
2018-02-04 01:30 | 181 | 179
2018-02-04 02:00 | 180 | 178
2018-02-04 02:30 | 179 | 177
2018-02-04 03:00 | 179 | 176
2018-02-04 03:30 | 179 | 177
2018-02-04 04:00 | 180 | 178
2018-02-04 04:30 | 182 | 180
2018-02-04 05:00 | 187 | 185
2018-02-04 05:30 | 191 | 188
2018-02-04 06:00 | 192 | 190
2018-02-04 06:30 | 195 | 193
2018-02-04 07:00 | 204 | 203
2018-02-04 07:30 | 207 | 206
2018-02-04 08:00 | 211 | 210
2018-02-04 08:30 | 218 | 218
2018-02-04 09:00 | 219 | 219
2018-02-04 09:30 | 225 | 225
2018-02-04 10:00 | 224 | 224
2018-02-04 10:30 | 226 | 226
2018-02-04 11:00 | 225 | 225
2018-02-04 11:30 | 220 | 220
2018-02-04 12:00 | 221 | 221
2018-02-04 12:30 | 219 | 218
2018-02-04 13:00 | 213 | 213
2018-02-04 13:30 | 211 | 210
2018-02-04 14:00 | 216 | 216
2018-02-04 14:30 | 225 | 225
2018-02-04 15:00 | 233 | 233
2018-02-04 15:30 | 247 | 246
2018-02-04 16:00 | 256 | 255
2018-02-04 16:30 | 268 | 267
2018-02-04 17:00 | 271 | 270
2018-02-04 17:30 | 273 | 272
2018-02-04 18:00 | 273 | 272
2018-02-04 18:30 | 276 | 274
2018-02-04 19:00 | 273 | 272
2018-02-04 19:30 | 273 | 271
2018-02-04 20:00 | 268 | 266
2018-02-04 20:30 | 262 | 259
2018-02-04 21:00 | 255 | 252
2018-02-04 21:30 | 245 | 241
2018-02-04 22:00 | 232 | 232
2018-02-04 22:30 | 225 | 225
2018-02-04 23:00 | 212 | 211
2018-02-04 23:30 | 200 | 199
2018-02-05 | 194 | 193
2018-02-05 00:30 | 190 | 189
2018-02-05 01:00 | 189 | 188
2018-02-05 01:30 | 187 | 185
2018-02-05 02:00 | 183 | 181
2018-02-05 02:30 | 181 | 179
2018-02-05 03:00 | 182 | 181
2018-02-05 03:30 | 185 | 184
2018-02-05 04:00 | 192 | 191
2018-02-05 04:30 | 196 | 195
2018-02-05 05:00 | 205 | 204
2018-02-05 05:30 | 215 | 214
2018-02-05 06:00 | 223 | 223
2018-02-05 06:30 | 240 | 239
2018-02-05 07:00 | 259 | 259
2018-02-05 07:30 | 263 | 263
2018-02-05 08:00 | 265 | 265
2018-02-05 08:30 | 268 | 268
2018-02-05 09:00 | 275 | 274
2018-02-05 09:30 | 272 | 271
2018-02-05 10:00 | 271 | 270
2018-02-05 10:30 | 272 | 271
2018-02-05 11:00 | 271 | 270
2018-02-05 11:30 | 271 | 271
2018-02-05 12:00 | 273 | 272
2018-02-05 12:30 | 284 | 283
2018-02-05 13:00 | 294 | 294
2018-02-05 13:30 | 292 | 291
2018-02-05 14:00 | 289 | 288
2018-02-05 14:30 | 296 | 295
2018-02-05 15:00 | 306 | 305
2018-02-05 15:30 | 302 | 300
2018-02-05 16:00 | 307 | 305
2018-02-05 16:30 | 302 | 300
2018-02-05 17:00 | 297 | 294
2018-02-05 17:30 | 294 | 292
2018-02-05 18:00 | 292 | 288
2018-02-05 18:30 | 296 | 293
2018-02-05 19:00 | 295 | 293
2018-02-05 19:30 | 288 | 287
2018-02-05 20:00 | 278 | 277
2018-02-05 20:30 | 268 | 268
2018-02-05 21:00 | 257 | 257
2018-02-05 21:30 | 247 | 247
2018-02-05 22:00 | 241 | 240
2018-02-05 22:30 | 232 | 231
2018-02-05 23:00 | 219 | 217
2018-02-05 23:30 | 212 | 210
2018-02-06 | 206 | 203
2018-02-06 00:30 | 202 | 199
2018-02-06 01:00 | 199 | 196
2018-02-06 01:30 | 194 | 190
2018-02-06 02:00 | 191 | 189
2018-02-06 02:30 | 186 | 185
2018-02-06 03:00 | 182 | 180
2018-02-06 03:30 | 184 | 182
2018-02-06 04:00 | 187 | 186
2018-02-06 04:30 | 189 | 188
2018-02-06 05:00 | 194 | 193
2018-02-06 05:30 | 199 | 198
2018-02-06 06:00 | 214 | 214
2018-02-06 06:30 | 231 | 231
2018-02-06 07:00 | 249 | 249
2018-02-06 07:30 | 256 | 256
2018-02-06 08:00 | 258 | 258
2018-02-06 08:30 | 260 | 260
2018-02-06 09:00 | 262 | 262
2018-02-06 09:30 | 263 | 263
2018-02-06 10:00 | 258 | 258
2018-02-06 10:30 | 262 | 262
2018-02-06 11:00 | 265 | 265
2018-02-06 11:30 | 261 | 261
2018-02-06 12:00 | 267 | 267
2018-02-06 12:30 | 275 | 275
2018-02-06 13:00 | 285 | 285
2018-02-06 13:30 | 284 | 284
2018-02-06 14:00 | 287 | 287
2018-02-06 14:30 | 292 | 292
2018-02-06 15:00 | 291 | 291
2018-02-06 15:30 | 291 | 291
2018-02-06 16:00 | 294 | 294
2018-02-06 16:30 | 295 | 295
2018-02-06 17:00 | 297 | 297
2018-02-06 17:30 | 289 | 288
2018-02-06 18:00 | 283 | 282
2018-02-06 18:30 | 286 | 286
2018-02-06 19:00 | 287 | 286
2018-02-06 19:30 | 283 | 282
2018-02-06 20:00 | 274 | 272
2018-02-06 20:30 | 266 | 264
2018-02-06 21:00 | 256 | 254
2018-02-06 21:30 | 248 | 246
2018-02-06 22:00 | 241 | 238
2018-02-06 22:30 | 233 | 231
2018-02-06 23:00 | 219 | 217
2018-02-06 23:30 | 209 | 209
2018-02-07 | 202 | 202
2018-02-07 00:30 | 198 | 197
2018-02-07 01:00 | 194 | 194
2018-02-07 01:30 | 190 | 189
2018-02-07 02:00 | 187 | 186
2018-02-07 02:30 | 186 | 185
2018-02-07 03:00 | 186 | 185
2018-02-07 03:30 | 187 | 187
2018-02-07 04:00 | 194 | 194
2018-02-07 04:30 | 198 | 198
2018-02-07 05:00 | 204 | 203
2018-02-07 05:30 | 212 | 212
2018-02-07 06:00 | 223 | 223
2018-02-07 06:30 | 233 | 233
2018-02-07 07:00 | 246 | 246
2018-02-07 07:30 | 251 | 251
2018-02-07 08:00 | 255 | 255
2018-02-07 08:30 | 257 | 257
2018-02-07 09:00 | 255 | 254
2018-02-07 09:30 | 257 | 257
2018-02-07 10:00 | 259 | 259
2018-02-07 10:30 | 257 | 257
2018-02-07 11:00 | 256 | 256
2018-02-07 11:30 | 256 | 256
2018-02-07 12:00 | 256 | 256
2018-02-07 12:30 | 266 | 266
2018-02-07 13:00 | 247 | 246
2018-02-07 13:30 | 228 | 227
2018-02-07 14:00 | 244 | 244
2018-02-07 14:30 | 246 | 246
2018-02-07 15:00 | 238 | 238
2018-02-07 15:30 | 256 | 255
2018-02-07 16:00 | 281 | 280
2018-02-07 16:30 | 281 | 281
2018-02-07 17:00 | 286 | 285
2018-02-07 17:30 | 267 | 265
2018-02-07 18:00 | 284 | 281
2018-02-07 18:30 | 292 | 290
2018-02-07 19:00 | 296 | 294
2018-02-07 19:30 | 289 | 288
2018-02-07 20:00 | 280 | 279
2018-02-07 20:30 | 266 | 266
2018-02-07 21:00 | 254 | 253
2018-02-07 21:30 | 240 | 239
2018-02-07 22:00 | 235 | 233
2018-02-07 22:30 | 227 | 225
2018-02-07 23:00 | 212 | 210
2018-02-07 23:30 | 190 | 187
2018-02-08 | 177 | 173
2018-02-08 00:30 | 165 | 162
2018-02-08 01:00 | 157 | 155
2018-02-08 01:30 | 153 | 151
2018-02-08 02:00 | 152 | 149
2018-02-08 02:30 | 151 | 148
2018-02-08 03:00 | 152 | 149
2018-02-08 03:30 | 153 | 150
2018-02-08 04:00 | 156 | 154
2018-02-08 04:30 | 190 | 189
2018-02-08 05:00 | 197 | 196
2018-02-08 05:30 | 206 | 205
2018-02-08 06:00 | 218 | 218
2018-02-08 06:30 | 229 | 229
2018-02-08 07:00 | 246 | 246
2018-02-08 07:30 | 253 | 253
2018-02-08 08:00 | 255 | 254
2018-02-08 08:30 | 261 | 261
2018-02-08 09:00 | 270 | 269
2018-02-08 09:30 | 277 | 277
2018-02-08 10:00 | 270 | 270
2018-02-08 10:30 | 260 | 260
2018-02-08 11:00 | 255 | 255
2018-02-08 11:30 | 257 | 256
2018-02-08 12:00 | 249 | 249
2018-02-08 12:30 | 262 | 262
2018-02-08 13:00 | 269 | 269
2018-02-08 13:30 | 274 | 273
2018-02-08 14:00 | 278 | 276
2018-02-08 14:30 | 284 | 282
2018-02-08 15:00 | 292 | 290
2018-02-08 15:30 | 301 | 299
2018-02-08 16:00 | 307 | 305
2018-02-08 16:30 | 320 | 317
2018-02-08 17:00 | 320 | 317
2018-02-08 17:30 | 320 | 317
2018-02-08 18:00 | 319 | 314
2018-02-08 18:30 | 317 | 313
2018-02-08 19:00 | 313 | 309
2018-02-08 19:30 | 313 | 308
2018-02-08 20:00 | 310 | 304
2018-02-08 20:30 | 288 | 286
2018-02-08 21:00 | 274 | 270
2018-02-08 21:30 | 251 | 249
2018-02-08 22:00 | 242 | 240
2018-02-08 22:30 | 235 | 233
2018-02-08 23:00 | 220 | 216
2018-02-08 23:30 | 207 | 203
2018-02-09 | 198 | 197
2018-02-09 00:30 | 195 | 194
2018-02-09 01:00 | 191 | 190
2018-02-09 01:30 | 191 | 190
2018-02-09 02:00 | 187 | 186
2018-02-09 02:30 | 190 | 188
2018-02-09 03:00 | 190 | 188
2018-02-09 03:30 | 189 | 187
2018-02-09 04:00 | 189 | 187
2018-02-09 04:30 | 189 | 187
2018-02-09 05:00 | 196 | 195
2018-02-09 05:30 | 207 | 206
2018-02-09 06:00 | 223 | 223
2018-02-09 06:30 | 221 | 221
2018-02-09 07:00 | 229 | 229
2018-02-09 07:30 | 233 | 233
2018-02-09 08:00 | 237 | 236
2018-02-09 08:30 | 242 | 242
2018-02-09 09:00 | 247 | 247
2018-02-09 09:30 | 245 | 245
2018-02-09 10:00 | 244 | 243
2018-02-09 10:30 | 240 | 240
2018-02-09 11:00 | 235 | 235
2018-02-09 11:30 | 233 | 233
2018-02-09 12:00 | 233 | 233
2018-02-09 12:30 | 235 | 235
2018-02-09 13:00 | 238 | 238
2018-02-09 13:30 | 244 | 244
2018-02-09 14:00 | 251 | 251
2018-02-09 14:30 | 256 | 256
2018-02-09 15:00 | 276 | 275
2018-02-09 15:30 | 304 | 304
2018-02-09 16:00 | 311 | 310
2018-02-09 16:30 | 318 | 318
2018-02-09 17:00 | 317 | 316
2018-02-09 17:30 | 307 | 305
2018-02-09 18:00 | 304 | 302
2018-02-09 18:30 | 309 | 302
2018-02-09 19:00 | 315 | 308
2018-02-09 19:30 | 306 | 300
2018-02-09 20:00 | 295 | 288
2018-02-09 20:30 | 282 | 272
2018-02-09 21:00 | 272 | 261
2018-02-09 21:30 | 265 | 255
2018-02-09 22:00 | 259 | 248
2018-02-09 22:30 | 247 | 238
2018-02-09 23:00 | 227 | 219
2018-02-09 23:30 | 218 | 209
2018-02-10 | 214 | 203
2018-02-10 00:30 | 210 | 199
2018-02-10 01:00 | 206 | 193
2018-02-10 01:30 | 205 | 192
2018-02-10 02:00 | 204 | 191
2018-02-10 02:30 | 205 | 192
2018-02-10 03:00 | 205 | 193
2018-02-10 03:30 | 203 | 190
2018-02-10 04:00 | 203 | 190
2018-02-10 04:30 | 204 | 191
2018-02-10 05:00 | 207 | 194
2018-02-10 05:30 | 213 | 200
2018-02-10 06:00 | 217 | 206
2018-02-10 06:30 | 225 | 217
2018-02-10 07:00 | 241 | 235
2018-02-10 07:30 | 242 | 242
2018-02-10 08:00 | 251 | 250
2018-02-10 08:30 | 244 | 243
2018-02-10 09:00 | 245 | 244
2018-02-10 09:30 | 245 | 245
2018-02-10 10:00 | 245 | 245
2018-02-10 10:30 | 249 | 249
2018-02-10 11:00 | 253 | 253
2018-02-10 11:30 | 255 | 255
2018-02-10 12:00 | 256 | 256
2018-02-10 12:30 | 261 | 261
2018-02-10 13:00 | 258 | 258
2018-02-10 13:30 | 264 | 264
2018-02-10 14:00 | 275 | 275
2018-02-10 14:30 | 284 | 284
2018-02-10 15:00 | 289 | 289
2018-02-10 15:30 | 308 | 308
2018-02-10 16:00 | 322 | 321
2018-02-10 16:30 | 321 | 319
2018-02-10 17:00 | 322 | 320
2018-02-10 17:30 | 312 | 310
2018-02-10 18:00 | 304 | 302
2018-02-10 18:30 | 305 | 304
2018-02-10 19:00 | 304 | 302
2018-02-10 19:30 | 298 | 296
2018-02-10 20:00 | 288 | 287
2018-02-10 20:30 | 275 | 273
2018-02-10 21:00 | 262 | 261
2018-02-10 21:30 | 249 | 248
2018-02-10 22:00 | 246 | 245
2018-02-10 22:30 | 243 | 242
2018-02-10 23:00 | 224 | 222
2018-02-10 23:30 | 201 | 200
2018-02-11 | 184 | 184
2018-02-11 00:30 | 174 | 174
2018-02-11 01:00 | 166 | 166
2018-02-11 01:30 | 162 | 161
2018-02-11 02:00 | 159 | 158
2018-02-11 02:30 | 157 | 156
2018-02-11 03:00 | 155 | 154
2018-02-11 03:30 | 154 | 153
2018-02-11 04:00 | 154 | 153
2018-02-11 04:30 | 155 | 154
2018-02-11 05:00 | 158 | 156
2018-02-11 05:30 | 160 | 158
2018-02-11 06:00 | 167 | 165
2018-02-11 06:30 | 174 | 173
2018-02-11 07:00 | 186 | 186
2018-02-11 07:30 | 195 | 195
2018-02-11 08:00 | 208 | 207
2018-02-11 08:30 | 216 | 216
2018-02-11 09:00 | 226 | 226
2018-02-11 09:30 | 234 | 234
2018-02-11 10:00 | 245 | 245
2018-02-11 10:30 | 255 | 255
2018-02-11 11:00 | 264 | 264
2018-02-11 11:30 | 274 | 274
2018-02-11 12:00 | 286 | 285
2018-02-11 12:30 | 297 | 297
2018-02-11 13:00 | 315 | 314
2018-02-11 13:30 | 325 | 323
2018-02-11 14:00 | 336 | 335
2018-02-11 14:30 | 346 | 345
2018-02-11 15:00 | 357 | 356
2018-02-11 15:30 | 369 | 368
2018-02-11 16:00 | 392 | 391
2018-02-11 16:30 | 397 | 395
2018-02-11 17:00 | 394 | 390
2018-02-11 17:30 | 395 | 392
2018-02-11 18:00 | 373 | 371
2018-02-11 18:30 | 360 | 359
2018-02-11 19:00 | 345 | 345
2018-02-11 19:30 | 335 | 335
2018-02-11 20:00 | 321 | 321
2018-02-11 20:30 | 300 | 300
2018-02-11 21:00 | 284 | 284
2018-02-11 21:30 | 263 | 263
2018-02-11 22:00 | 254 | 254
2018-02-11 22:30 | 247 | 246
2018-02-11 23:00 | 225 | 224
2018-02-11 23:30 | 204 | 202
2018-02-12 | 191 | 188
2018-02-12 00:30 | 182 | 180
2018-02-12 01:00 | 175 | 173
2018-02-12 01:30 | 170 | 169
2018-02-12 02:00 | 168 | 167
2018-02-12 02:30 | 166 | 165
2018-02-12 03:00 | 166 | 165
2018-02-12 03:30 | 166 | 165
2018-02-12 04:00 | 169 | 168
2018-02-12 04:30 | 174 | 172
2018-02-12 05:00 | 184 | 182
2018-02-12 05:30 | 195 | 194
2018-02-12 06:00 | 220 | 219
2018-02-12 06:30 | 243 | 243
2018-02-12 07:00 | 267 | 267
2018-02-12 07:30 | 283 | 283
2018-02-12 08:00 | 294 | 294
2018-02-12 08:30 | 303 | 303
2018-02-12 09:00 | 313 | 313
2018-02-12 09:30 | 318 | 318
2018-02-12 10:00 | 325 | 324
2018-02-12 10:30 | 330 | 330
2018-02-12 11:00 | 336 | 336
2018-02-12 11:30 | 341 | 341
2018-02-12 12:00 | 347 | 346
2018-02-12 12:30 | 354 | 354
2018-02-12 13:00 | 363 | 363
2018-02-12 13:30 | 371 | 371
2018-02-12 14:00 | 376 | 376
2018-02-12 14:30 | 381 | 381
2018-02-12 15:00 | 390 | 390
2018-02-12 15:30 | 397 | 397
2018-02-12 16:00 | 404 | 404
2018-02-12 16:30 | 415 | 415
2018-02-12 17:00 | 418 | 418
2018-02-12 17:30 | 410 | 409
2018-02-12 18:00 | 403 | 402
2018-02-12 18:30 | 411 | 411
2018-02-12 19:00 | 410 | 410
2018-02-12 19:30 | 404 | 404
2018-02-12 20:00 | 385 | 384
2018-02-12 20:30 | 366 | 365
2018-02-12 21:00 | 348 | 346
2018-02-12 21:30 | 325 | 325
2018-02-12 22:00 | 309 | 308
2018-02-12 22:30 | 293 | 293
2018-02-12 23:00 | 270 | 270
2018-02-12 23:30 | 254 | 254
2018-02-13 | 239 | 239
2018-02-13 00:30 | 235 | 235
2018-02-13 01:00 | 228 | 228
2018-02-13 01:30 | 223 | 222
2018-02-13 02:00 | 221 | 221
2018-02-13 02:30 | 221 | 220
2018-02-13 03:00 | 221 | 220
2018-02-13 03:30 | 221 | 221
2018-02-13 04:00 | 223 | 222
2018-02-13 04:30 | 225 | 225
2018-02-13 05:00 | 230 | 229
2018-02-13 05:30 | 241 | 240
2018-02-13 06:00 | 263 | 263
2018-02-13 06:30 | 283 | 282
2018-02-13 07:00 | 309 | 308
2018-02-13 07:30 | 323 | 323
2018-02-13 08:00 | 334 | 334
2018-02-13 08:30 | 347 | 347
2018-02-13 09:00 | 337 | 337
2018-02-13 09:30 | 338 | 338
2018-02-13 10:00 | 349 | 349
2018-02-13 10:30 | 351 | 351
2018-02-13 11:00 | 352 | 352
2018-02-13 11:30 | 360 | 360
2018-02-13 12:00 | 366 | 365
2018-02-13 12:30 | 370 | 369
2018-02-13 13:00 | 375 | 374
2018-02-13 13:30 | 377 | 376
2018-02-13 14:00 | 382 | 382
2018-02-13 14:30 | 390 | 389
2018-02-13 15:00 | 396 | 396
2018-02-13 15:30 | 408 | 408
2018-02-13 16:00 | 420 | 420
2018-02-13 16:30 | 429 | 429
2018-02-13 17:00 | 424 | 424
2018-02-13 17:30 | 416 | 416
2018-02-13 18:00 | 413 | 413
2018-02-13 18:30 | 417 | 417
2018-02-13 19:00 | 388 | 387
2018-02-13 19:30 | 368 | 366
2018-02-13 20:00 | 353 | 350
2018-02-13 20:30 | 324 | 322
2018-02-13 21:00 | 307 | 305
2018-02-13 21:30 | 296 | 292
2018-02-13 22:00 | 276 | 275
2018-02-13 22:30 | 265 | 264
2018-02-13 23:00 | 250 | 248
2018-02-13 23:30 | 235 | 234
2018-02-14 | 222 | 220
2018-02-14 00:30 | 217 | 215
2018-02-14 01:00 | 211 | 209
2018-02-14 01:30 | 206 | 204
2018-02-14 02:00 | 205 | 202
2018-02-14 02:30 | 203 | 200
2018-02-14 03:00 | 200 | 197
2018-02-14 03:30 | 197 | 194
2018-02-14 04:00 | 205 | 202
2018-02-14 04:30 | 209 | 207
2018-02-14 05:00 | 218 | 216
2018-02-14 05:30 | 233 | 231
2018-02-14 06:00 | 250 | 247
2018-02-14 06:30 | 263 | 261
2018-02-14 07:00 | 285 | 284
2018-02-14 07:30 | 306 | 303
2018-02-14 08:00 | 312 | 310
2018-02-14 08:30 | 317 | 316
2018-02-14 09:00 | 325 | 325
2018-02-14 09:30 | 327 | 327
2018-02-14 10:00 | 336 | 336
2018-02-14 10:30 | 340 | 339
2018-02-14 11:00 | 346 | 345
2018-02-14 11:30 | 352 | 352
2018-02-14 12:00 | 358 | 358
2018-02-14 12:30 | 360 | 360
2018-02-14 13:00 | 368 | 368
2018-02-14 13:30 | 376 | 376
2018-02-14 14:00 | 388 | 386
2018-02-14 14:30 | 397 | 393
2018-02-14 15:00 | 407 | 404
2018-02-14 15:30 | 425 | 423
2018-02-14 16:00 | 441 | 439
2018-02-14 16:30 | 447 | 445
2018-02-14 17:00 | 446 | 443
2018-02-14 17:30 | 441 | 436
2018-02-14 18:00 | 432 | 426
2018-02-14 18:30 | 430 | 425
2018-02-14 19:00 | 424 | 417
2018-02-14 19:30 | 412 | 403
2018-02-14 20:00 | 402 | 394
2018-02-14 20:30 | 382 | 379
2018-02-14 21:00 | 356 | 352
2018-02-14 21:30 | 333 | 328
2018-02-14 22:00 | 302 | 300
2018-02-14 22:30 | 293 | 291
2018-02-14 23:00 | 278 | 275
2018-02-14 23:30 | 265 | 264
2018-02-15 | 254 | 253
2018-02-15 00:30 | 243 | 242
2018-02-15 01:00 | 236 | 236
2018-02-15 01:30 | 247 | 247
2018-02-15 02:00 | 238 | 238
2018-02-15 02:30 | 232 | 232
2018-02-15 03:00 | 229 | 229
2018-02-15 03:30 | 229 | 229
2018-02-15 04:00 | 231 | 231
2018-02-15 04:30 | 233 | 233
2018-02-15 05:00 | 246 | 246
2018-02-15 05:30 | 259 | 258
2018-02-15 06:00 | 275 | 274
2018-02-15 06:30 | 290 | 290
2018-02-15 07:00 | 319 | 319
2018-02-15 07:30 | 335 | 334
2018-02-15 08:00 | 340 | 340
2018-02-15 08:30 | 343 | 343
2018-02-15 09:00 | 356 | 356
2018-02-15 09:30 | 367 | 365
2018-02-15 10:00 | 366 | 365
2018-02-15 10:30 | 367 | 366
2018-02-15 11:00 | 369 | 368
2018-02-15 11:30 | 368 | 368
2018-02-15 12:00 | 372 | 371
2018-02-15 12:30 | 376 | 375
2018-02-15 13:00 | 384 | 383
2018-02-15 13:30 | 387 | 387
2018-02-15 14:00 | 392 | 391
2018-02-15 14:30 | 397 | 396
2018-02-15 15:00 | 405 | 404
2018-02-15 15:30 | 429 | 429
2018-02-15 16:00 | 431 | 431
2018-02-15 16:30 | 428 | 428
2018-02-15 17:00 | 422 | 422
2018-02-15 17:30 | 418 | 418
2018-02-15 18:00 | 412 | 411
2018-02-15 18:30 | 415 | 414
2018-02-15 19:00 | 409 | 409
2018-02-15 19:30 | 396 | 396
2018-02-15 20:00 | 394 | 393
2018-02-15 20:30 | 380 | 379
2018-02-15 21:00 | 346 | 346
2018-02-15 21:30 | 321 | 321
2018-02-15 22:00 | 291 | 291
2018-02-15 22:30 | 285 | 284
2018-02-15 23:00 | 265 | 265
2018-02-15 23:30 | 243 | 243
2018-02-16 | 225 | 225
2018-02-16 00:30 | 214 | 211
2018-02-16 01:00 | 204 | 202
2018-02-16 01:30 | 214 | 212
2018-02-16 02:00 | 209 | 206
2018-02-16 02:30 | 197 | 195
2018-02-16 03:00 | 192 | 190
2018-02-16 03:30 | 190 | 188
2018-02-16 04:00 | 192 | 190
2018-02-16 04:30 | 199 | 196
2018-02-16 05:00 | 210 | 209
2018-02-16 05:30 | 220 | 220
2018-02-16 06:00 | 246 | 246
2018-02-16 06:30 | 271 | 271
2018-02-16 07:00 | 296 | 295
2018-02-16 07:30 | 309 | 309
2018-02-16 08:00 | 322 | 322
2018-02-16 08:30 | 334 | 332
2018-02-16 09:00 | 343 | 341
2018-02-16 09:30 | 341 | 340
2018-02-16 10:00 | 344 | 344
2018-02-16 10:30 | 350 | 350
2018-02-16 11:00 | 354 | 354
2018-02-16 11:30 | 355 | 355
2018-02-16 12:00 | 356 | 356
2018-02-16 12:30 | 359 | 359
2018-02-16 13:00 | 365 | 365
2018-02-16 13:30 | 373 | 373
2018-02-16 14:00 | 380 | 380
2018-02-16 14:30 | 390 | 390
2018-02-16 15:00 | 416 | 416
2018-02-16 15:30 | 421 | 421
2018-02-16 16:00 | 420 | 419
2018-02-16 16:30 | 419 | 418
2018-02-16 17:00 | 403 | 401
2018-02-16 17:30 | 385 | 382
2018-02-16 18:00 | 369 | 364
2018-02-16 18:30 | 364 | 362
2018-02-16 19:00 | 361 | 358
2018-02-16 19:30 | 357 | 355
2018-02-16 20:00 | 344 | 343
2018-02-16 20:30 | 330 | 330
2018-02-16 21:00 | 324 | 323
2018-02-16 21:30 | 318 | 317
2018-02-16 22:00 | 300 | 299
2018-02-16 22:30 | 276 | 275
2018-02-16 23:00 | 265 | 265
2018-02-16 23:30 | 254 | 254
2018-02-17 | 242 | 242
2018-02-17 00:30 | 234 | 233
2018-02-17 01:00 | 228 | 227
2018-02-17 01:30 | 225 | 225
2018-02-17 02:00 | 224 | 224
2018-02-17 02:30 | 222 | 221
2018-02-17 03:00 | 219 | 219
2018-02-17 03:30 | 218 | 217
2018-02-17 04:00 | 216 | 216
2018-02-17 04:30 | 219 | 219
2018-02-17 05:00 | 224 | 224
2018-02-17 05:30 | 229 | 229
2018-02-17 06:00 | 237 | 237
2018-02-17 06:30 | 246 | 245
2018-02-17 07:00 | 262 | 262
2018-02-17 07:30 | 276 | 276
2018-02-17 08:00 | 291 | 291
2018-02-17 08:30 | 298 | 297
2018-02-17 09:00 | 302 | 301
2018-02-17 09:30 | 305 | 305
2018-02-17 10:00 | 306 | 305
2018-02-17 10:30 | 305 | 305
2018-02-17 11:00 | 304 | 304
2018-02-17 11:30 | 304 | 304
2018-02-17 12:00 | 307 | 307
2018-02-17 12:30 | 310 | 309
2018-02-17 13:00 | 312 | 312
2018-02-17 13:30 | 314 | 314
2018-02-17 14:00 | 317 | 317
2018-02-17 14:30 | 324 | 324
2018-02-17 15:00 | 331 | 331
2018-02-17 15:30 | 342 | 341
2018-02-17 16:00 | 348 | 346
2018-02-17 16:30 | 355 | 353
2018-02-17 17:00 | 348 | 345
2018-02-17 17:30 | 346 | 343
2018-02-17 18:00 | 342 | 337
2018-02-17 18:30 | 340 | 336
2018-02-17 19:00 | 336 | 332
2018-02-17 19:30 | 336 | 332
2018-02-17 20:00 | 321 | 319
2018-02-17 20:30 | 313 | 313
2018-02-17 21:00 | 307 | 306
2018-02-17 21:30 | 299 | 298
2018-02-17 22:00 | 281 | 281
2018-02-17 22:30 | 270 | 270
2018-02-17 23:00 | 261 | 260
2018-02-17 23:30 | 252 | 251
2018-02-18 | 238 | 236
2018-02-18 00:30 | 227 | 226
2018-02-18 01:00 | 220 | 219
2018-02-18 01:30 | 215 | 214
2018-02-18 02:00 | 210 | 210
2018-02-18 02:30 | 207 | 206
2018-02-18 03:00 | 204 | 203
2018-02-18 03:30 | 202 | 201
2018-02-18 04:00 | 201 | 200
2018-02-18 04:30 | 201 | 200
2018-02-18 05:00 | 203 | 202
2018-02-18 05:30 | 204 | 202
2018-02-18 06:00 | 211 | 210
2018-02-18 06:30 | 221 | 220
2018-02-18 07:00 | 232 | 232
2018-02-18 07:30 | 241 | 241
2018-02-18 08:00 | 255 | 255
2018-02-18 08:30 | 265 | 265
2018-02-18 09:00 | 274 | 274
2018-02-18 09:30 | 280 | 280
2018-02-18 10:00 | 286 | 286
2018-02-18 10:30 | 292 | 291
2018-02-18 11:00 | 296 | 295
2018-02-18 11:30 | 298 | 297
2018-02-18 12:00 | 299 | 298
2018-02-18 12:30 | 300 | 300
2018-02-18 13:00 | 301 | 300
2018-02-18 13:30 | 301 | 300
2018-02-18 14:00 | 307 | 306
2018-02-18 14:30 | 320 | 319
2018-02-18 15:00 | 333 | 333
2018-02-18 15:30 | 338 | 338
2018-02-18 16:00 | 337 | 336
2018-02-18 16:30 | 337 | 337
2018-02-18 17:00 | 333 | 333
2018-02-18 17:30 | 333 | 332
2018-02-18 18:00 | 329 | 328
2018-02-18 18:30 | 332 | 331
2018-02-18 19:00 | 326 | 325
2018-02-18 19:30 | 321 | 319
2018-02-18 20:00 | 306 | 304
2018-02-18 20:30 | 295 | 293
2018-02-18 21:00 | 289 | 286
2018-02-18 21:30 | 278 | 275
2018-02-18 22:00 | 268 | 266
2018-02-18 22:30 | 252 | 252
2018-02-18 23:00 | 240 | 239
2018-02-18 23:30 | 230 | 230
2018-02-19 | 216 | 216
2018-02-19 00:30 | 205 | 205
2018-02-19 01:00 | 198 | 198
2018-02-19 01:30 | 194 | 194
2018-02-19 02:00 | 191 | 191
2018-02-19 02:30 | 189 | 189
2018-02-19 03:00 | 189 | 188
2018-02-19 03:30 | 189 | 188
2018-02-19 04:00 | 192 | 192
2018-02-19 04:30 | 197 | 197
2018-02-19 05:00 | 208 | 208
2018-02-19 05:30 | 217 | 217
2018-02-19 06:00 | 234 | 234
2018-02-19 06:30 | 245 | 245
2018-02-19 07:00 | 270 | 270
2018-02-19 07:30 | 283 | 283
2018-02-19 08:00 | 286 | 286
2018-02-19 08:30 | 292 | 292
2018-02-19 09:00 | 296 | 296
2018-02-19 09:30 | 299 | 299
2018-02-19 10:00 | 302 | 302
2018-02-19 10:30 | 304 | 304
2018-02-19 11:00 | 307 | 307
2018-02-19 11:30 | 301 | 301
2018-02-19 12:00 | 301 | 300
2018-02-19 12:30 | 307 | 307
2018-02-19 13:00 | 312 | 311
2018-02-19 13:30 | 319 | 319
2018-02-19 14:00 | 328 | 327
2018-02-19 14:30 | 329 | 329
2018-02-19 15:00 | 338 | 337
2018-02-19 15:30 | 348 | 347
2018-02-19 16:00 | 351 | 350
2018-02-19 16:30 | 360 | 359
2018-02-19 17:00 | 358 | 356
2018-02-19 17:30 | 347 | 345
2018-02-19 18:00 | 339 | 339
2018-02-19 18:30 | 346 | 346
2018-02-19 19:00 | 342 | 341
2018-02-19 19:30 | 341 | 340
2018-02-19 20:00 | 323 | 321
2018-02-19 20:30 | 299 | 297
2018-02-19 21:00 | 284 | 283
2018-02-19 21:30 | 270 | 268
2018-02-19 22:00 | 259 | 256
2018-02-19 22:30 | 253 | 249
2018-02-19 23:00 | 237 | 232
2018-02-19 23:30 | 231 | 225
2018-02-20 | 217 | 213
2018-02-20 00:30 | 211 | 209
2018-02-20 01:00 | 207 | 205
2018-02-20 01:30 | 207 | 204
2018-02-20 02:00 | 204 | 201
2018-02-20 02:30 | 203 | 199
2018-02-20 03:00 | 203 | 200
2018-02-20 03:30 | 203 | 200
2018-02-20 04:00 | 206 | 203
2018-02-20 04:30 | 211 | 208
2018-02-20 05:00 | 218 | 215
2018-02-20 05:30 | 215 | 210
2018-02-20 06:00 | 233 | 230
2018-02-20 06:30 | 244 | 243
2018-02-20 07:00 | 266 | 266
2018-02-20 07:30 | 274 | 274
2018-02-20 08:00 | 280 | 280
2018-02-20 08:30 | 284 | 284
2018-02-20 09:00 | 279 | 279
2018-02-20 09:30 | 278 | 278
2018-02-20 10:00 | 286 | 286
2018-02-20 10:30 | 283 | 283
2018-02-20 11:00 | 273 | 273
2018-02-20 11:30 | 274 | 274
2018-02-20 12:00 | 277 | 277
2018-02-20 12:30 | 278 | 278
2018-02-20 13:00 | 285 | 285
2018-02-20 13:30 | 296 | 296
2018-02-20 14:00 | 295 | 295
2018-02-20 14:30 | 307 | 307
2018-02-20 15:00 | 311 | 311
2018-02-20 15:30 | 315 | 315
2018-02-20 16:00 | 319 | 319
2018-02-20 16:30 | 325 | 325
2018-02-20 17:00 | 325 | 325
2018-02-20 17:30 | 322 | 322
2018-02-20 18:00 | 319 | 319
2018-02-20 18:30 | 318 | 318
2018-02-20 19:00 | 315 | 315
2018-02-20 19:30 | 311 | 311
2018-02-20 20:00 | 303 | 302
2018-02-20 20:30 | 292 | 292
2018-02-20 21:00 | 283 | 283
2018-02-20 21:30 | 269 | 269
2018-02-20 22:00 | 259 | 259
2018-02-20 22:30 | 250 | 250
2018-02-20 23:00 | 231 | 231
2018-02-20 23:30 | 223 | 222
2018-02-21 | 215 | 214
2018-02-21 00:30 | 210 | 209
2018-02-21 01:00 | 203 | 203
2018-02-21 01:30 | 200 | 199
2018-02-21 02:00 | 197 | 197
2018-02-21 02:30 | 196 | 195
2018-02-21 03:00 | 197 | 196
2018-02-21 03:30 | 199 | 198
2018-02-21 04:00 | 202 | 201
2018-02-21 04:30 | 209 | 208
2018-02-21 05:00 | 216 | 216
2018-02-21 05:30 | 221 | 220
2018-02-21 06:00 | 236 | 235
2018-02-21 06:30 | 253 | 253
2018-02-21 07:00 | 274 | 274
2018-02-21 07:30 | 281 | 281
2018-02-21 08:00 | 283 | 282
2018-02-21 08:30 | 294 | 293
2018-02-21 09:00 | 295 | 295
2018-02-21 09:30 | 292 | 292
2018-02-21 10:00 | 284 | 284
2018-02-21 10:30 | 280 | 279
2018-02-21 11:00 | 275 | 274
2018-02-21 11:30 | 277 | 276
2018-02-21 12:00 | 274 | 273
2018-02-21 12:30 | 268 | 268
2018-02-21 13:00 | 262 | 262
2018-02-21 13:30 | 266 | 266
2018-02-21 14:00 | 282 | 281
2018-02-21 14:30 | 291 | 291
2018-02-21 15:00 | 295 | 295
2018-02-21 15:30 | 295 | 294
2018-02-21 16:00 | 294 | 294
2018-02-21 16:30 | 297 | 297
2018-02-21 17:00 | 297 | 297
2018-02-21 17:30 | 292 | 292
2018-02-21 18:00 | 287 | 287
2018-02-21 18:30 | 293 | 292
2018-02-21 19:00 | 288 | 287
2018-02-21 19:30 | 283 | 283
2018-02-21 20:00 | 273 | 272
2018-02-21 20:30 | 266 | 264
2018-02-21 21:00 | 259 | 258
2018-02-21 21:30 | 250 | 249
2018-02-21 22:00 | 245 | 243
2018-02-21 22:30 | 240 | 239
2018-02-21 23:00 | 226 | 225
2018-02-21 23:30 | 215 | 214
2018-02-22 | 200 | 200
2018-02-22 00:30 | 191 | 191
2018-02-22 01:00 | 186 | 186
2018-02-22 01:30 | 183 | 183
2018-02-22 02:00 | 181 | 181
2018-02-22 02:30 | 181 | 181
2018-02-22 03:00 | 181 | 180
2018-02-22 03:30 | 182 | 181
2018-02-22 04:00 | 185 | 184
2018-02-22 04:30 | 191 | 190
2018-02-22 05:00 | 201 | 201
2018-02-22 05:30 | 208 | 208
2018-02-22 06:00 | 222 | 222
2018-02-22 06:30 | 236 | 235
2018-02-22 07:00 | 259 | 259
2018-02-22 07:30 | 270 | 270
2018-02-22 08:00 | 277 | 276
2018-02-22 08:30 | 276 | 276
2018-02-22 09:00 | 277 | 277
2018-02-22 09:30 | 274 | 273
2018-02-22 10:00 | 275 | 274
2018-02-22 10:30 | 276 | 275
2018-02-22 11:00 | 270 | 270
2018-02-22 11:30 | 271 | 270
2018-02-22 12:00 | 281 | 281
2018-02-22 12:30 | 286 | 286
2018-02-22 13:00 | 289 | 288
2018-02-22 13:30 | 288 | 287
2018-02-22 14:00 | 289 | 288
2018-02-22 14:30 | 293 | 292
2018-02-22 15:00 | 290 | 288
2018-02-22 15:30 | 291 | 289
2018-02-22 16:00 | 294 | 292
2018-02-22 16:30 | 299 | 297
2018-02-22 17:00 | 300 | 298
2018-02-22 17:30 | 302 | 299
2018-02-22 18:00 | 298 | 295
2018-02-22 18:30 | 301 | 298
2018-02-22 19:00 | 296 | 293
2018-02-22 19:30 | 284 | 284
2018-02-22 20:00 | 272 | 272
2018-02-22 20:30 | 265 | 264
2018-02-22 21:00 | 257 | 256
2018-02-22 21:30 | 246 | 246
2018-02-22 22:00 | 243 | 242
2018-02-22 22:30 | 237 | 236
2018-02-22 23:00 | 224 | 223
2018-02-22 23:30 | 210 | 210
2018-02-23 | 197 | 196
2018-02-23 00:30 | 189 | 188
2018-02-23 01:00 | 186 | 185
2018-02-23 01:30 | 183 | 182
2018-02-23 02:00 | 182 | 182
2018-02-23 02:30 | 182 | 181
2018-02-23 03:00 | 183 | 182
2018-02-23 03:30 | 184 | 184
2018-02-23 04:00 | 188 | 187
2018-02-23 04:30 | 192 | 192
2018-02-23 05:00 | 201 | 201
2018-02-23 05:30 | 212 | 212
2018-02-23 06:00 | 231 | 231
2018-02-23 06:30 | 251 | 251
2018-02-23 07:00 | 271 | 271
2018-02-23 07:30 | 282 | 282
2018-02-23 08:00 | 292 | 292
2018-02-23 08:30 | 299 | 299
2018-02-23 09:00 | 302 | 302
2018-02-23 09:30 | 310 | 310
2018-02-23 10:00 | 312 | 311
2018-02-23 10:30 | 310 | 308
2018-02-23 11:00 | 305 | 303
2018-02-23 11:30 | 306 | 304
2018-02-23 12:00 | 303 | 301
2018-02-23 12:30 | 301 | 299
2018-02-23 13:00 | 298 | 295
2018-02-23 13:30 | 297 | 294
2018-02-23 14:00 | 294 | 292
2018-02-23 14:30 | 289 | 287
2018-02-23 15:00 | 291 | 289
2018-02-23 15:30 | 291 | 289
2018-02-23 16:00 | 295 | 293
2018-02-23 16:30 | 295 | 293
2018-02-23 17:00 | 291 | 288
2018-02-23 17:30 | 286 | 283
2018-02-23 18:00 | 279 | 279
2018-02-23 18:30 | 286 | 286
2018-02-23 19:00 | 284 | 284
2018-02-23 19:30 | 284 | 284
2018-02-23 20:00 | 276 | 276
2018-02-23 20:30 | 269 | 269
2018-02-23 21:00 | 265 | 265
2018-02-23 21:30 | 260 | 259
2018-02-23 22:00 | 251 | 251
2018-02-23 22:30 | 247 | 246
2018-02-23 23:00 | 231 | 230
2018-02-23 23:30 | 220 | 219
2018-02-24 | 205 | 204
2018-02-24 00:30 | 199 | 199
2018-02-24 01:00 | 193 | 193
2018-02-24 01:30 | 188 | 188
2018-02-24 02:00 | 187 | 186
2018-02-24 02:30 | 185 | 185
2018-02-24 03:00 | 183 | 182
2018-02-24 03:30 | 180 | 179
2018-02-24 04:00 | 183 | 182
2018-02-24 04:30 | 183 | 183
2018-02-24 05:00 | 191 | 190
2018-02-24 05:30 | 197 | 197
2018-02-24 06:00 | 204 | 204
2018-02-24 06:30 | 217 | 216
2018-02-24 07:00 | 240 | 240
2018-02-24 07:30 | 255 | 255
2018-02-24 08:00 | 258 | 258
2018-02-24 08:30 | 265 | 263
2018-02-24 09:00 | 274 | 273
2018-02-24 09:30 | 276 | 275
2018-02-24 10:00 | 275 | 275
2018-02-24 10:30 | 279 | 279
2018-02-24 11:00 | 276 | 276
2018-02-24 11:30 | 278 | 278
2018-02-24 12:00 | 268 | 268
2018-02-24 12:30 | 272 | 272
2018-02-24 13:00 | 272 | 272
2018-02-24 13:30 | 274 | 274
2018-02-24 14:00 | 277 | 276
2018-02-24 14:30 | 278 | 277
2018-02-24 15:00 | 278 | 277
2018-02-24 15:30 | 277 | 276
2018-02-24 16:00 | 283 | 282
2018-02-24 16:30 | 288 | 287
2018-02-24 17:00 | 292 | 290
2018-02-24 17:30 | 293 | 290
2018-02-24 18:00 | 290 | 288
2018-02-24 18:30 | 298 | 297
2018-02-24 19:00 | 294 | 292
2018-02-24 19:30 | 291 | 289
2018-02-24 20:00 | 289 | 286
2018-02-24 20:30 | 275 | 275
2018-02-24 21:00 | 264 | 264
2018-02-24 21:30 | 255 | 255
2018-02-24 22:00 | 250 | 250
2018-02-24 22:30 | 246 | 245
2018-02-24 23:00 | 232 | 230
2018-02-24 23:30 | 224 | 223
2018-02-25 | 214 | 212
2018-02-25 00:30 | 207 | 206
2018-02-25 01:00 | 201 | 200
2018-02-25 01:30 | 197 | 195
2018-02-25 02:00 | 193 | 192
2018-02-25 02:30 | 191 | 189
2018-02-25 03:00 | 190 | 188
2018-02-25 03:30 | 188 | 186
2018-02-25 04:00 | 189 | 186
2018-02-25 04:30 | 190 | 188
2018-02-25 05:00 | 194 | 192
2018-02-25 05:30 | 197 | 194
2018-02-25 06:00 | 202 | 200
2018-02-25 06:30 | 209 | 207
2018-02-25 07:00 | 222 | 222
2018-02-25 07:30 | 232 | 232
2018-02-25 08:00 | 240 | 240
2018-02-25 08:30 | 248 | 247
2018-02-25 09:00 | 260 | 260
2018-02-25 09:30 | 263 | 263
2018-02-25 10:00 | 271 | 271
2018-02-25 10:30 | 274 | 274
2018-02-25 11:00 | 273 | 273
2018-02-25 11:30 | 281 | 280
2018-02-25 12:00 | 286 | 284
2018-02-25 12:30 | 288 | 287
2018-02-25 13:00 | 287 | 286
2018-02-25 13:30 | 281 | 280
2018-02-25 14:00 | 285 | 284
2018-02-25 14:30 | 298 | 297
2018-02-25 15:00 | 301 | 301
2018-02-25 15:30 | 329 | 329
2018-02-25 16:00 | 337 | 337
2018-02-25 16:30 | 339 | 339
2018-02-25 17:00 | 333 | 333
2018-02-25 17:30 | 321 | 320
2018-02-25 18:00 | 314 | 314
2018-02-25 18:30 | 322 | 321
2018-02-25 19:00 | 315 | 315
2018-02-25 19:30 | 310 | 309
2018-02-25 20:00 | 300 | 299
2018-02-25 20:30 | 289 | 287
2018-02-25 21:00 | 275 | 274
2018-02-25 21:30 | 264 | 263
2018-02-25 22:00 | 255 | 254
2018-02-25 22:30 | 246 | 244
2018-02-25 23:00 | 230 | 230
2018-02-25 23:30 | 224 | 224
2018-02-26 | 213 | 213
2018-02-26 00:30 | 207 | 207
2018-02-26 01:00 | 200 | 200
2018-02-26 01:30 | 195 | 195
2018-02-26 02:00 | 194 | 194
2018-02-26 02:30 | 193 | 193
2018-02-26 03:00 | 189 | 189
2018-02-26 03:30 | 190 | 190
2018-02-26 04:00 | 198 | 198
2018-02-26 04:30 | 202 | 202
2018-02-26 05:00 | 209 | 209
2018-02-26 05:30 | 219 | 219
2018-02-26 06:00 | 237 | 237
2018-02-26 06:30 | 254 | 253
2018-02-26 07:00 | 278 | 277
2018-02-26 07:30 | 292 | 292
2018-02-26 08:00 | 299 | 299
2018-02-26 08:30 | 303 | 303
2018-02-26 09:00 | 312 | 312
2018-02-26 09:30 | 312 | 312
2018-02-26 10:00 | 311 | 311
2018-02-26 10:30 | 316 | 315
2018-02-26 11:00 | 319 | 318
2018-02-26 11:30 | 322 | 322
2018-02-26 12:00 | 323 | 323
2018-02-26 12:30 | 333 | 332
2018-02-26 13:00 | 343 | 342
2018-02-26 13:30 | 351 | 350
2018-02-26 14:00 | 357 | 356
2018-02-26 14:30 | 372 | 371
2018-02-26 15:00 | 376 | 376
2018-02-26 15:30 | 384 | 384
2018-02-26 16:00 | 402 | 401
2018-02-26 16:30 | 410 | 410
2018-02-26 17:00 | 408 | 408
2018-02-26 17:30 | 400 | 400
2018-02-26 18:00 | 388 | 387
2018-02-26 18:30 | 368 | 367
2018-02-26 19:00 | 344 | 343
2018-02-26 19:30 | 328 | 328
2018-02-26 20:00 | 310 | 309
2018-02-26 20:30 | 292 | 291
2018-02-26 21:00 | 277 | 276
2018-02-26 21:30 | 261 | 261
2018-02-26 22:00 | 252 | 251
2018-02-26 22:30 | 242 | 242
2018-02-26 23:00 | 228 | 226
2018-02-26 23:30 | 219 | 217
2018-02-27 | 208 | 206
2018-02-27 00:30 | 202 | 201
2018-02-27 01:00 | 196 | 195
2018-02-27 01:30 | 192 | 192
2018-02-27 02:00 | 191 | 190
2018-02-27 02:30 | 189 | 189
2018-02-27 03:00 | 189 | 189
2018-02-27 03:30 | 190 | 189
2018-02-27 04:00 | 193 | 193
2018-02-27 04:30 | 199 | 198
2018-02-27 05:00 | 209 | 209
2018-02-27 05:30 | 216 | 216
2018-02-27 06:00 | 234 | 234
2018-02-27 06:30 | 248 | 248
2018-02-27 07:00 | 270 | 270
2018-02-27 07:30 | 277 | 277
2018-02-27 08:00 | 279 | 279
2018-02-27 08:30 | 282 | 281
2018-02-27 09:00 | 283 | 283
2018-02-27 09:30 | 280 | 279
2018-02-27 10:00 | 273 | 273
2018-02-27 10:30 | 270 | 269
2018-02-27 11:00 | 269 | 269
2018-02-27 11:30 | 266 | 266
2018-02-27 12:00 | 266 | 266
2018-02-27 12:30 | 272 | 271
2018-02-27 13:00 | 277 | 276
2018-02-27 13:30 | 275 | 274
2018-02-27 14:00 | 276 | 275
2018-02-27 14:30 | 283 | 282
2018-02-27 15:00 | 279 | 279
2018-02-27 15:30 | 294 | 293
2018-02-27 16:00 | 298 | 298
2018-02-27 16:30 | 301 | 301
2018-02-27 17:00 | 302 | 301
2018-02-27 17:30 | 302 | 302
2018-02-27 18:00 | 298 | 298
2018-02-27 18:30 | 305 | 305
2018-02-27 19:00 | 297 | 297
2018-02-27 19:30 | 293 | 293
2018-02-27 20:00 | 281 | 281
2018-02-27 20:30 | 270 | 270
2018-02-27 21:00 | 262 | 261
2018-02-27 21:30 | 251 | 251
2018-02-27 22:00 | 245 | 244
2018-02-27 22:30 | 239 | 238
2018-02-27 23:00 | 222 | 222
2018-02-27 23:30 | 211 | 211
2018-02-28 | 200 | 200
2018-02-28 00:30 | 191 | 191
2018-02-28 01:00 | 185 | 185
2018-02-28 01:30 | 181 | 181
2018-02-28 02:00 | 179 | 179
2018-02-28 02:30 | 177 | 177
2018-02-28 03:00 | 178 | 178
2018-02-28 03:30 | 179 | 179
2018-02-28 04:00 | 183 | 183
2018-02-28 04:30 | 189 | 189
2018-02-28 05:00 | 201 | 201
2018-02-28 05:30 | 213 | 213
2018-02-28 06:00 | 232 | 232
2018-02-28 06:30 | 250 | 249
2018-02-28 07:00 | 258 | 257
2018-02-28 07:30 | 267 | 267
2018-02-28 08:00 | 269 | 269
2018-02-28 08:30 | 267 | 265
2018-02-28 09:00 | 269 | 268
2018-02-28 09:30 | 270 | 270
2018-02-28 10:00 | 276 | 275
2018-02-28 10:30 | 278 | 277
2018-02-28 11:00 | 277 | 277
2018-02-28 11:30 | 278 | 277
2018-02-28 12:00 | 275 | 274
2018-02-28 12:30 | 272 | 271
2018-02-28 13:00 | 273 | 272
2018-02-28 13:30 | 277 | 276
2018-02-28 14:00 | 287 | 286
2018-02-28 14:30 | 290 | 290
2018-02-28 15:00 | 297 | 297
2018-02-28 15:30 | 303 | 302
2018-02-28 16:00 | 313 | 311
2018-02-28 16:30 | 321 | 318
2018-02-28 17:00 | 319 | 315
2018-02-28 17:30 | 314 | 310
2018-02-28 18:00 | 308 | 305
2018-02-28 18:30 | 310 | 309
2018-02-28 19:00 | 308 | 305
2018-02-28 19:30 | 306 | 303
2018-02-28 20:00 | 297 | 294
2018-02-28 20:30 | 284 | 283
2018-02-28 21:00 | 274 | 273
2018-02-28 21:30 | 264 | 262
2018-02-28 22:00 | 253 | 253
2018-02-28 22:30 | 244 | 244
2018-02-28 23:00 | 229 | 229
2018-02-28 23:30 | 217 | 217
2018-03-01 | 203 | 203
2018-03-01 00:30 | 193 | 192
2018-03-01 01:00 | 186 | 186
2018-03-01 01:30 | 187 | 186
2018-03-01 02:00 | 191 | 190
2018-03-01 02:30 | 189 | 189
2018-03-01 03:00 | 190 | 189
2018-03-01 03:30 | 191 | 190
2018-03-01 04:00 | 194 | 194
2018-03-01 04:30 | 199 | 199
2018-03-01 05:00 | 204 | 203
2018-03-01 05:30 | 203 | 203
2018-03-01 06:00 | 222 | 222
2018-03-01 06:30 | 242 | 241
2018-03-01 07:00 | 258 | 258
2018-03-01 07:30 | 264 | 264
2018-03-01 08:00 | 269 | 269
2018-03-01 08:30 | 274 | 272
2018-03-01 09:00 | 280 | 280
2018-03-01 09:30 | 287 | 287
2018-03-01 10:00 | 295 | 294
2018-03-01 10:30 | 304 | 304
2018-03-01 11:00 | 313 | 313
2018-03-01 11:30 | 330 | 328
2018-03-01 12:00 | 339 | 338
2018-03-01 12:30 | 348 | 348
2018-03-01 13:00 | 360 | 360
2018-03-01 13:30 | 375 | 375
2018-03-01 14:00 | 390 | 390
2018-03-01 14:30 | 397 | 396
2018-03-01 15:00 | 412 | 411
2018-03-01 15:30 | 423 | 422
2018-03-01 16:00 | 434 | 433
2018-03-01 16:30 | 438 | 436
2018-03-01 17:00 | 422 | 420
2018-03-01 17:30 | 420 | 417
2018-03-01 18:00 | 414 | 410
2018-03-01 18:30 | 420 | 417
2018-03-01 19:00 | 412 | 409
2018-03-01 19:30 | 401 | 397
2018-03-01 20:00 | 383 | 379
2018-03-01 20:30 | 353 | 351
2018-03-01 21:00 | 326 | 324
2018-03-01 21:30 | 296 | 295
2018-03-01 22:00 | 284 | 283
2018-03-01 22:30 | 272 | 271
2018-03-01 23:00 | 246 | 245
2018-03-01 23:30 | 233 | 233
2018-03-02 | 221 | 221
2018-03-02 00:30 | 216 | 216
2018-03-02 01:00 | 213 | 213
2018-03-02 01:30 | 210 | 209
2018-03-02 02:00 | 204 | 204
2018-03-02 02:30 | 210 | 209
2018-03-02 03:00 | 205 | 204
2018-03-02 03:30 | 208 | 208
2018-03-02 04:00 | 206 | 205
2018-03-02 04:30 | 208 | 207
2018-03-02 05:00 | 214 | 214
2018-03-02 05:30 | 219 | 219
2018-03-02 06:00 | 238 | 238
2018-03-02 06:30 | 258 | 257
2018-03-02 07:00 | 281 | 280
2018-03-02 07:30 | 291 | 291
2018-03-02 08:00 | 297 | 297
2018-03-02 08:30 | 300 | 300
2018-03-02 09:00 | 303 | 303
2018-03-02 09:30 | 302 | 302
2018-03-02 10:00 | 312 | 312
2018-03-02 10:30 | 325 | 324
2018-03-02 11:00 | 330 | 330
2018-03-02 11:30 | 326 | 326
2018-03-02 12:00 | 324 | 323
2018-03-02 12:30 | 321 | 320
2018-03-02 13:00 | 322 | 320
2018-03-02 13:30 | 318 | 315
2018-03-02 14:00 | 320 | 317
2018-03-02 14:30 | 319 | 316
2018-03-02 15:00 | 322 | 319
2018-03-02 15:30 | 323 | 319
2018-03-02 16:00 | 326 | 322
2018-03-02 16:30 | 323 | 320
2018-03-02 17:00 | 322 | 319
2018-03-02 17:30 | 315 | 311
2018-03-02 18:00 | 313 | 309
2018-03-02 18:30 | 313 | 310
2018-03-02 19:00 | 308 | 304
2018-03-02 19:30 | 303 | 299
2018-03-02 20:00 | 292 | 288
2018-03-02 20:30 | 282 | 280
2018-03-02 21:00 | 279 | 277
2018-03-02 21:30 | 273 | 270
2018-03-02 22:00 | 269 | 266
2018-03-02 22:30 | 260 | 256
2018-03-02 23:00 | 234 | 234
2018-03-02 23:30 | 224 | 224
2018-03-03 | 214 | 213
2018-03-03 00:30 | 210 | 210
2018-03-03 01:00 | 209 | 209
2018-03-03 01:30 | 205 | 204
2018-03-03 02:00 | 202 | 202
2018-03-03 02:30 | 202 | 201
2018-03-03 03:00 | 201 | 200
2018-03-03 03:30 | 200 | 199
2018-03-03 04:00 | 199 | 198
2018-03-03 04:30 | 195 | 194
2018-03-03 05:00 | 201 | 201
2018-03-03 05:30 | 207 | 206
2018-03-03 06:00 | 216 | 216
2018-03-03 06:30 | 225 | 225
2018-03-03 07:00 | 244 | 244
2018-03-03 07:30 | 263 | 263
2018-03-03 08:00 | 277 | 275
2018-03-03 08:30 | 282 | 281
2018-03-03 09:00 | 283 | 282
2018-03-03 09:30 | 284 | 283
2018-03-03 10:00 | 292 | 291
2018-03-03 10:30 | 283 | 282
2018-03-03 11:00 | 275 | 274
2018-03-03 11:30 | 279 | 278
2018-03-03 12:00 | 287 | 286
2018-03-03 12:30 | 291 | 291
2018-03-03 13:00 | 309 | 309
2018-03-03 13:30 | 312 | 311
2018-03-03 14:00 | 326 | 325
2018-03-03 14:30 | 319 | 318
2018-03-03 15:00 | 318 | 317
2018-03-03 15:30 | 324 | 323
2018-03-03 16:00 | 328 | 326
2018-03-03 16:30 | 335 | 334
2018-03-03 17:00 | 332 | 331
2018-03-03 17:30 | 324 | 323
2018-03-03 18:00 | 320 | 318
2018-03-03 18:30 | 319 | 317
2018-03-03 19:00 | 316 | 314
2018-03-03 19:30 | 312 | 309
2018-03-03 20:00 | 306 | 302
2018-03-03 20:30 | 301 | 297
2018-03-03 21:00 | 291 | 288
2018-03-03 21:30 | 286 | 282
2018-03-03 22:00 | 269 | 267
2018-03-03 22:30 | 264 | 263
2018-03-03 23:00 | 250 | 248
2018-03-03 23:30 | 241 | 239
2018-03-04 | 229 | 228
2018-03-04 00:30 | 223 | 223
2018-03-04 01:00 | 217 | 217
2018-03-04 01:30 | 213 | 212
2018-03-04 02:00 | 209 | 209
2018-03-04 02:30 | 208 | 208
2018-03-04 03:00 | 208 | 207
2018-03-04 03:30 | 205 | 205
2018-03-04 04:00 | 203 | 203
2018-03-04 04:30 | 203 | 203
2018-03-04 05:00 | 206 | 206
2018-03-04 05:30 | 208 | 208
2018-03-04 06:00 | 215 | 214
2018-03-04 06:30 | 223 | 223
2018-03-04 07:00 | 239 | 239
2018-03-04 07:30 | 250 | 250
2018-03-04 08:00 | 262 | 261
2018-03-04 08:30 | 271 | 270
2018-03-04 09:00 | 281 | 281
2018-03-04 09:30 | 288 | 288
2018-03-04 10:00 | 299 | 299
2018-03-04 10:30 | 302 | 302
2018-03-04 11:00 | 308 | 308
2018-03-04 11:30 | 315 | 315
2018-03-04 12:00 | 317 | 317
2018-03-04 12:30 | 329 | 328
2018-03-04 13:00 | 349 | 348
2018-03-04 13:30 | 345 | 341
2018-03-04 14:00 | 359 | 357
2018-03-04 14:30 | 371 | 369
2018-03-04 15:00 | 372 | 370
2018-03-04 15:30 | 372 | 370
2018-03-04 16:00 | 373 | 370
2018-03-04 16:30 | 377 | 375
2018-03-04 17:00 | 376 | 373
2018-03-04 17:30 | 378 | 375
2018-03-04 18:00 | 375 | 373
2018-03-04 18:30 | 381 | 380
2018-03-04 19:00 | 371 | 370
2018-03-04 19:30 | 365 | 362
2018-03-04 20:00 | 349 | 349
2018-03-04 20:30 | 327 | 327
2018-03-04 21:00 | 311 | 310
2018-03-04 21:30 | 295 | 293
2018-03-04 22:00 | 278 | 277
2018-03-04 22:30 | 273 | 272
2018-03-04 23:00 | 259 | 258
2018-03-04 23:30 | 246 | 246
2018-03-05 | 234 | 234
2018-03-05 00:30 | 226 | 225
2018-03-05 01:00 | 220 | 219
2018-03-05 01:30 | 215 | 214
2018-03-05 02:00 | 210 | 210
2018-03-05 02:30 | 209 | 209
2018-03-05 03:00 | 208 | 207
2018-03-05 03:30 | 206 | 205
2018-03-05 04:00 | 206 | 206
2018-03-05 04:30 | 211 | 211
2018-03-05 05:00 | 218 | 218
2018-03-05 05:30 | 229 | 228
2018-03-05 06:00 | 247 | 247
2018-03-05 06:30 | 265 | 265
2018-03-05 07:00 | 283 | 283
2018-03-05 07:30 | 286 | 286
2018-03-05 08:00 | 290 | 289
2018-03-05 08:30 | 286 | 286
2018-03-05 09:00 | 299 | 299
2018-03-05 09:30 | 308 | 308
2018-03-05 10:00 | 309 | 308
2018-03-05 10:30 | 312 | 311
2018-03-05 11:00 | 313 | 313
2018-03-05 11:30 | 317 | 316
2018-03-05 12:00 | 316 | 315
2018-03-05 12:30 | 302 | 300
2018-03-05 13:00 | 302 | 300
2018-03-05 13:30 | 306 | 305
2018-03-05 14:00 | 307 | 306
2018-03-05 14:30 | 306 | 305
2018-03-05 15:00 | 311 | 310
2018-03-05 15:30 | 319 | 318
2018-03-05 16:00 | 319 | 318
2018-03-05 16:30 | 330 | 329
2018-03-05 17:00 | 329 | 327
2018-03-05 17:30 | 325 | 323
2018-03-05 18:00 | 327 | 325
2018-03-05 18:30 | 331 | 329
2018-03-05 19:00 | 320 | 318
2018-03-05 19:30 | 316 | 313
2018-03-05 20:00 | 307 | 304
2018-03-05 20:30 | 290 | 290
2018-03-05 21:00 | 281 | 280
2018-03-05 21:30 | 270 | 269
2018-03-05 22:00 | 264 | 262
2018-03-05 22:30 | 256 | 255
2018-03-05 23:00 | 239 | 237
2018-03-05 23:30 | 226 | 223
2018-03-06 | 209 | 208
2018-03-06 00:30 | 201 | 201
2018-03-06 01:00 | 198 | 197
2018-03-06 01:30 | 192 | 191
2018-03-06 02:00 | 185 | 184
2018-03-06 02:30 | 180 | 179
2018-03-06 03:00 | 181 | 180
2018-03-06 03:30 | 182 | 181
2018-03-06 04:00 | 191 | 190
2018-03-06 04:30 | 196 | 196
2018-03-06 05:00 | 205 | 205
2018-03-06 05:30 | 212 | 212
2018-03-06 06:00 | 233 | 232
2018-03-06 06:30 | 247 | 246
2018-03-06 07:00 | 269 | 268
2018-03-06 07:30 | 274 | 274
2018-03-06 08:00 | 281 | 281
2018-03-06 08:30 | 281 | 281
2018-03-06 09:00 | 278 | 278
2018-03-06 09:30 | 281 | 281
2018-03-06 10:00 | 280 | 280
2018-03-06 10:30 | 280 | 280
2018-03-06 11:00 | 274 | 274
2018-03-06 11:30 | 274 | 274
2018-03-06 12:00 | 270 | 269
2018-03-06 12:30 | 264 | 264
2018-03-06 13:00 | 265 | 265
2018-03-06 13:30 | 268 | 268
2018-03-06 14:00 | 277 | 277
2018-03-06 14:30 | 277 | 277
2018-03-06 15:00 | 278 | 277
2018-03-06 15:30 | 280 | 279
2018-03-06 16:00 | 286 | 285
2018-03-06 16:30 | 288 | 287
2018-03-06 17:00 | 285 | 283
2018-03-06 17:30 | 284 | 282
2018-03-06 18:00 | 285 | 283
2018-03-06 18:30 | 289 | 287
2018-03-06 19:00 | 281 | 279
2018-03-06 19:30 | 276 | 275
2018-03-06 20:00 | 266 | 266
2018-03-06 20:30 | 260 | 260
2018-03-06 21:00 | 252 | 252
2018-03-06 21:30 | 243 | 243
2018-03-06 22:00 | 232 | 232
2018-03-06 22:30 | 229 | 228
2018-03-06 23:00 | 219 | 219
2018-03-06 23:30 | 211 | 211
2018-03-07 | 202 | 201
2018-03-07 00:30 | 195 | 193
2018-03-07 01:00 | 192 | 190
2018-03-07 01:30 | 190 | 189
2018-03-07 02:00 | 187 | 185
2018-03-07 02:30 | 183 | 181
2018-03-07 03:00 | 186 | 184
2018-03-07 03:30 | 189 | 188
2018-03-07 04:00 | 194 | 193
2018-03-07 04:30 | 198 | 197
2018-03-07 05:00 | 205 | 204
2018-03-07 05:30 | 217 | 216
2018-03-07 06:00 | 245 | 245
2018-03-07 06:30 | 262 | 262
2018-03-07 07:00 | 288 | 288
2018-03-07 07:30 | 288 | 287
2018-03-07 08:00 | 276 | 275
2018-03-07 08:30 | 281 | 281
2018-03-07 09:00 | 279 | 279
2018-03-07 09:30 | 274 | 274
2018-03-07 10:00 | 274 | 274
2018-03-07 10:30 | 280 | 280
2018-03-07 11:00 | 284 | 284
2018-03-07 11:30 | 269 | 269
2018-03-07 12:00 | 256 | 256
2018-03-07 12:30 | 254 | 254
2018-03-07 13:00 | 256 | 256
2018-03-07 13:30 | 263 | 263
2018-03-07 14:00 | 256 | 256
2018-03-07 14:30 | 262 | 262
2018-03-07 15:00 | 265 | 265
2018-03-07 15:30 | 265 | 265
2018-03-07 16:00 | 270 | 270
2018-03-07 16:30 | 277 | 277
2018-03-07 17:00 | 279 | 278
2018-03-07 17:30 | 282 | 281
2018-03-07 18:00 | 285 | 285
2018-03-07 18:30 | 287 | 287
2018-03-07 19:00 | 282 | 281
2018-03-07 19:30 | 280 | 279
2018-03-07 20:00 | 267 | 266
2018-03-07 20:30 | 257 | 257
2018-03-07 21:00 | 250 | 249
2018-03-07 21:30 | 241 | 240
2018-03-07 22:00 | 237 | 236
2018-03-07 22:30 | 232 | 231
2018-03-07 23:00 | 219 | 217
2018-03-07 23:30 | 210 | 208
2018-03-08 | 202 | 199
2018-03-08 00:30 | 197 | 193
2018-03-08 01:00 | 194 | 190
2018-03-08 01:30 | 193 | 188
2018-03-08 02:00 | 188 | 183
2018-03-08 02:30 | 189 | 185
2018-03-08 03:00 | 190 | 185
2018-03-08 03:30 | 192 | 187
2018-03-08 04:00 | 191 | 187
2018-03-08 04:30 | 197 | 193
2018-03-08 05:00 | 204 | 201
2018-03-08 05:30 | 212 | 210
2018-03-08 06:00 | 224 | 223
2018-03-08 06:30 | 236 | 235
2018-03-08 07:00 | 245 | 245
2018-03-08 07:30 | 253 | 253
2018-03-08 08:00 | 256 | 256
2018-03-08 08:30 | 264 | 264
2018-03-08 09:00 | 248 | 248
2018-03-08 09:30 | 245 | 245
2018-03-08 10:00 | 250 | 250
2018-03-08 10:30 | 255 | 254
2018-03-08 11:00 | 253 | 253
2018-03-08 11:30 | 269 | 268
2018-03-08 12:00 | 266 | 265
2018-03-08 12:30 | 265 | 264
2018-03-08 13:00 | 270 | 269
2018-03-08 13:30 | 269 | 269
2018-03-08 14:00 | 259 | 258
2018-03-08 14:30 | 259 | 258
2018-03-08 15:00 | 259 | 258
2018-03-08 15:30 | 272 | 271
2018-03-08 16:00 | 280 | 279
2018-03-08 16:30 | 278 | 277
2018-03-08 17:00 | 274 | 273
2018-03-08 17:30 | 286 | 284
2018-03-08 18:00 | 298 | 296
2018-03-08 18:30 | 299 | 298
2018-03-08 19:00 | 293 | 291
2018-03-08 19:30 | 290 | 288
2018-03-08 20:00 | 278 | 275
2018-03-08 20:30 | 268 | 264
2018-03-08 21:00 | 258 | 256
2018-03-08 21:30 | 252 | 250
2018-03-08 22:00 | 247 | 244
2018-03-08 22:30 | 240 | 238
2018-03-08 23:00 | 224 | 221
2018-03-08 23:30 | 215 | 212
2018-03-09 | 205 | 202
2018-03-09 00:30 | 201 | 198
2018-03-09 01:00 | 199 | 195
2018-03-09 01:30 | 196 | 192
2018-03-09 02:00 | 194 | 190
2018-03-09 02:30 | 195 | 190
2018-03-09 03:00 | 196 | 192
2018-03-09 03:30 | 197 | 193
2018-03-09 04:00 | 197 | 194
2018-03-09 04:30 | 200 | 196
2018-03-09 05:00 | 206 | 204
2018-03-09 05:30 | 215 | 212
2018-03-09 06:00 | 224 | 222
2018-03-09 06:30 | 238 | 237
2018-03-09 07:00 | 252 | 252
2018-03-09 07:30 | 255 | 254
2018-03-09 08:00 | 258 | 257
2018-03-09 08:30 | 263 | 263
2018-03-09 09:00 | 266 | 266
2018-03-09 09:30 | 266 | 265
2018-03-09 10:00 | 269 | 269
2018-03-09 10:30 | 286 | 286
2018-03-09 11:00 | 284 | 284
2018-03-09 11:30 | 274 | 274
2018-03-09 12:00 | 266 | 266
2018-03-09 12:30 | 278 | 278
2018-03-09 13:00 | 277 | 277
2018-03-09 13:30 | 266 | 266
2018-03-09 14:00 | 269 | 269
2018-03-09 14:30 | 273 | 273
2018-03-09 15:00 | 280 | 280
2018-03-09 15:30 | 279 | 279
2018-03-09 16:00 | 286 | 286
2018-03-09 16:30 | 289 | 289
2018-03-09 17:00 | 288 | 288
2018-03-09 17:30 | 287 | 286
2018-03-09 18:00 | 290 | 289
2018-03-09 18:30 | 294 | 293
2018-03-09 19:00 | 285 | 283
2018-03-09 19:30 | 282 | 281
2018-03-09 20:00 | 279 | 278
2018-03-09 20:30 | 274 | 272
2018-03-09 21:00 | 266 | 264
2018-03-09 21:30 | 258 | 256
2018-03-09 22:00 | 252 | 250
2018-03-09 22:30 | 250 | 248
2018-03-09 23:00 | 236 | 233
2018-03-09 23:30 | 221 | 216
2018-03-10 | 207 | 204
2018-03-10 00:30 | 205 | 201
2018-03-10 01:00 | 203 | 200
2018-03-10 01:30 | 198 | 194
2018-03-10 02:00 | 196 | 192
2018-03-10 02:30 | 197 | 193
2018-03-10 03:00 | 194 | 190
2018-03-10 03:30 | 192 | 187
2018-03-10 04:00 | 193 | 189
2018-03-10 04:30 | 195 | 191
2018-03-10 05:00 | 198 | 195
2018-03-10 05:30 | 204 | 200
2018-03-10 06:00 | 212 | 209
2018-03-10 06:30 | 219 | 216
2018-03-10 07:00 | 225 | 223
2018-03-10 07:30 | 234 | 233
2018-03-10 08:00 | 244 | 244
2018-03-10 08:30 | 258 | 257
2018-03-10 09:00 | 259 | 258
2018-03-10 09:30 | 246 | 245
2018-03-10 10:00 | 236 | 235
2018-03-10 10:30 | 240 | 239
2018-03-10 11:00 | 239 | 238
2018-03-10 11:30 | 228 | 228
2018-03-10 12:00 | 236 | 235
2018-03-10 12:30 | 250 | 250
2018-03-10 13:00 | 243 | 242
2018-03-10 13:30 | 233 | 232
2018-03-10 14:00 | 236 | 236
2018-03-10 14:30 | 250 | 250
2018-03-10 15:00 | 249 | 249
2018-03-10 15:30 | 249 | 248
2018-03-10 16:00 | 245 | 245
2018-03-10 16:30 | 255 | 255
2018-03-10 17:00 | 258 | 258
2018-03-10 17:30 | 259 | 258
2018-03-10 18:00 | 259 | 259
2018-03-10 18:30 | 266 | 265
2018-03-10 19:00 | 261 | 260
2018-03-10 19:30 | 255 | 253
2018-03-10 20:00 | 246 | 244
2018-03-10 20:30 | 238 | 236
2018-03-10 21:00 | 236 | 233
2018-03-10 21:30 | 234 | 231
2018-03-10 22:00 | 237 | 234
2018-03-10 22:30 | 237 | 233
2018-03-10 23:00 | 224 | 219
2018-03-10 23:30 | 213 | 208
2018-03-11 | 203 | 199
2018-03-11 00:30 | 199 | 195
2018-03-11 01:00 | 195 | 191
2018-03-11 01:30 | 191 | 187
2018-03-11 02:00 | 191 | 185
2018-03-11 02:30 | 189 | 183
2018-03-11 03:00 | 189 | 183
2018-03-11 03:30 | 189 | 183
2018-03-11 04:00 | 188 | 181
2018-03-11 04:30 | 189 | 183
2018-03-11 05:00 | 192 | 186
2018-03-11 05:30 | 195 | 189
2018-03-11 06:00 | 202 | 196
2018-03-11 06:30 | 203 | 198
2018-03-11 07:00 | 211 | 207
2018-03-11 07:30 | 218 | 215
2018-03-11 08:00 | 229 | 226
2018-03-11 08:30 | 251 | 245
2018-03-11 09:00 | 252 | 246
2018-03-11 09:30 | 256 | 250
2018-03-11 10:00 | 250 | 244
2018-03-11 10:30 | 239 | 233
2018-03-11 11:00 | 239 | 232
2018-03-11 11:30 | 243 | 237
2018-03-11 12:00 | 239 | 233
2018-03-11 12:30 | 258 | 254
2018-03-11 13:00 | 254 | 249
2018-03-11 13:30 | 244 | 237
2018-03-11 14:00 | 244 | 237
2018-03-11 14:30 | 252 | 246
2018-03-11 15:00 | 260 | 254
2018-03-11 15:30 | 254 | 247
2018-03-11 16:00 | 256 | 250
2018-03-11 16:30 | 261 | 255
2018-03-11 17:00 | 266 | 260
2018-03-11 17:30 | 269 | 263
2018-03-11 18:00 | 274 | 269
2018-03-11 18:30 | 280 | 277
2018-03-11 19:00 | 271 | 266
2018-03-11 19:30 | 267 | 261
2018-03-11 20:00 | 261 | 254
2018-03-11 20:30 | 251 | 248
2018-03-11 21:00 | 244 | 240
2018-03-11 21:30 | 236 | 231
2018-03-11 22:00 | 231 | 226
2018-03-11 22:30 | 226 | 220
2018-03-11 23:00 | 216 | 209
2018-03-11 23:30 | 208 | 199
2018-03-12 | 200 | 190
2018-03-12 00:30 | 196 | 185
2018-03-12 01:00 | 193 | 181
2018-03-12 01:30 | 189 | 177
2018-03-12 02:00 | 187 | 175
2018-03-12 02:30 | 188 | 176
2018-03-12 03:00 | 188 | 176
2018-03-12 03:30 | 188 | 176
2018-03-12 04:00 | 190 | 178
2018-03-12 04:30 | 193 | 183
2018-03-12 05:00 | 204 | 196
2018-03-12 05:30 | 200 | 191
2018-03-12 06:00 | 215 | 210
2018-03-12 06:30 | 231 | 230
2018-03-12 07:00 | 243 | 243
2018-03-12 07:30 | 249 | 249
2018-03-12 08:00 | 251 | 250
2018-03-12 08:30 | 243 | 243
2018-03-12 09:00 | 247 | 247
2018-03-12 09:30 | 253 | 253
2018-03-12 10:00 | 242 | 242
2018-03-12 10:30 | 229 | 229
2018-03-12 11:00 | 229 | 229
2018-03-12 11:30 | 233 | 233
2018-03-12 12:00 | 239 | 239
2018-03-12 12:30 | 239 | 239
2018-03-12 13:00 | 239 | 239
2018-03-12 13:30 | 244 | 244
2018-03-12 14:00 | 251 | 251
2018-03-12 14:30 | 250 | 250
2018-03-12 15:00 | 257 | 257
2018-03-12 15:30 | 273 | 273
2018-03-12 16:00 | 282 | 282
2018-03-12 16:30 | 289 | 289
2018-03-12 17:00 | 289 | 289
2018-03-12 17:30 | 288 | 287
2018-03-12 18:00 | 288 | 288
2018-03-12 18:30 | 290 | 290
2018-03-12 19:00 | 285 | 285
2018-03-12 19:30 | 282 | 282
2018-03-12 20:00 | 274 | 273
2018-03-12 20:30 | 267 | 266
2018-03-12 21:00 | 263 | 261
2018-03-12 21:30 | 256 | 254
2018-03-12 22:00 | 243 | 241
2018-03-12 22:30 | 233 | 231
2018-03-12 23:00 | 219 | 218
2018-03-12 23:30 | 211 | 208
2018-03-13 | 199 | 196
2018-03-13 00:30 | 195 | 191
2018-03-13 01:00 | 193 | 189
2018-03-13 01:30 | 190 | 186
2018-03-13 02:00 | 188 | 184
2018-03-13 02:30 | 188 | 184
2018-03-13 03:00 | 189 | 185
2018-03-13 03:30 | 189 | 185
2018-03-13 04:00 | 189 | 187
2018-03-13 04:30 | 190 | 188
2018-03-13 05:00 | 199 | 198
2018-03-13 05:30 | 212 | 212
2018-03-13 06:00 | 227 | 226
2018-03-13 06:30 | 240 | 240
2018-03-13 07:00 | 255 | 255
2018-03-13 07:30 | 265 | 264
2018-03-13 08:00 | 261 | 261
2018-03-13 08:30 | 263 | 263
2018-03-13 09:00 | 265 | 265
2018-03-13 09:30 | 269 | 269
2018-03-13 10:00 | 269 | 269
2018-03-13 10:30 | 267 | 267
2018-03-13 11:00 | 270 | 270
2018-03-13 11:30 | 270 | 270
2018-03-13 12:00 | 274 | 274
2018-03-13 12:30 | 284 | 284
2018-03-13 13:00 | 285 | 285
2018-03-13 13:30 | 286 | 286
2018-03-13 14:00 | 287 | 286
2018-03-13 14:30 | 286 | 286
2018-03-13 15:00 | 284 | 284
2018-03-13 15:30 | 289 | 289
2018-03-13 16:00 | 294 | 294
2018-03-13 16:30 | 296 | 296
2018-03-13 17:00 | 299 | 298
2018-03-13 17:30 | 301 | 300
2018-03-13 18:00 | 301 | 300
2018-03-13 18:30 | 302 | 301
2018-03-13 19:00 | 294 | 292
2018-03-13 19:30 | 286 | 284
2018-03-13 20:00 | 278 | 276
2018-03-13 20:30 | 262 | 261
2018-03-13 21:00 | 256 | 256
2018-03-13 21:30 | 247 | 247
2018-03-13 22:00 | 241 | 241
2018-03-13 22:30 | 235 | 235
2018-03-13 23:00 | 222 | 221
2018-03-13 23:30 | 213 | 211
2018-03-14 | 203 | 201
2018-03-14 00:30 | 201 | 199
2018-03-14 01:00 | 197 | 195
2018-03-14 01:30 | 194 | 192
2018-03-14 02:00 | 189 | 187
2018-03-14 02:30 | 186 | 184
2018-03-14 03:00 | 187 | 184
2018-03-14 03:30 | 185 | 183
2018-03-14 04:00 | 191 | 189
2018-03-14 04:30 | 190 | 189
2018-03-14 05:00 | 198 | 197
2018-03-14 05:30 | 209 | 208
2018-03-14 06:00 | 224 | 224
2018-03-14 06:30 | 240 | 240
2018-03-14 07:00 | 257 | 257
2018-03-14 07:30 | 261 | 260
2018-03-14 08:00 | 258 | 257
2018-03-14 08:30 | 256 | 256
2018-03-14 09:00 | 260 | 260
2018-03-14 09:30 | 260 | 260
2018-03-14 10:00 | 268 | 268
2018-03-14 10:30 | 261 | 261
2018-03-14 11:00 | 247 | 247
2018-03-14 11:30 | 253 | 253
2018-03-14 12:00 | 262 | 262
2018-03-14 12:30 | 263 | 263
2018-03-14 13:00 | 264 | 264
2018-03-14 13:30 | 269 | 269
2018-03-14 14:00 | 272 | 272
2018-03-14 14:30 | 275 | 275
2018-03-14 15:00 | 280 | 280
2018-03-14 15:30 | 289 | 289
2018-03-14 16:00 | 297 | 297
2018-03-14 16:30 | 300 | 300
2018-03-14 17:00 | 298 | 297
2018-03-14 17:30 | 296 | 296
2018-03-14 18:00 | 295 | 295
2018-03-14 18:30 | 303 | 302
2018-03-14 19:00 | 295 | 294
2018-03-14 19:30 | 287 | 286
2018-03-14 20:00 | 278 | 276
2018-03-14 20:30 | 266 | 266
2018-03-14 21:00 | 258 | 258
2018-03-14 21:30 | 248 | 248
2018-03-14 22:00 | 241 | 240
2018-03-14 22:30 | 235 | 234
2018-03-14 23:00 | 223 | 221
2018-03-14 23:30 | 211 | 209
2018-03-15 | 203 | 200
2018-03-15 00:30 | 198 | 194
2018-03-15 01:00 | 192 | 188
2018-03-15 01:30 | 189 | 185
2018-03-15 02:00 | 181 | 176
2018-03-15 02:30 | 178 | 175
2018-03-15 03:00 | 176 | 174
2018-03-15 03:30 | 178 | 176
2018-03-15 04:00 | 180 | 178
2018-03-15 04:30 | 185 | 184
2018-03-15 05:00 | 194 | 193
2018-03-15 05:30 | 204 | 204
2018-03-15 06:00 | 223 | 223
2018-03-15 06:30 | 239 | 239
2018-03-15 07:00 | 262 | 261
2018-03-15 07:30 | 271 | 271
2018-03-15 08:00 | 273 | 273
2018-03-15 08:30 | 270 | 268
2018-03-15 09:00 | 259 | 258
2018-03-15 09:30 | 255 | 255
2018-03-15 10:00 | 259 | 259
2018-03-15 10:30 | 273 | 272
2018-03-15 11:00 | 277 | 273
2018-03-15 11:30 | 280 | 276
2018-03-15 12:00 | 277 | 274
2018-03-15 12:30 | 283 | 280
2018-03-15 13:00 | 285 | 283
2018-03-15 13:30 | 292 | 290
2018-03-15 14:00 | 305 | 302
2018-03-15 14:30 | 317 | 314
2018-03-15 15:00 | 307 | 303
2018-03-15 15:30 | 316 | 312
2018-03-15 16:00 | 317 | 315
2018-03-15 16:30 | 322 | 320
2018-03-15 17:00 | 316 | 315
2018-03-15 17:30 | 314 | 313
2018-03-15 18:00 | 318 | 317
2018-03-15 18:30 | 325 | 324
2018-03-15 19:00 | 316 | 315
2018-03-15 19:30 | 309 | 308
2018-03-15 20:00 | 298 | 297
2018-03-15 20:30 | 282 | 281
2018-03-15 21:00 | 265 | 264
2018-03-15 21:30 | 252 | 250
2018-03-15 22:00 | 242 | 241
2018-03-15 22:30 | 232 | 232
2018-03-15 23:00 | 217 | 217
2018-03-15 23:30 | 207 | 206
2018-03-16 | 199 | 198
2018-03-16 00:30 | 194 | 193
2018-03-16 01:00 | 188 | 186
2018-03-16 01:30 | 186 | 184
2018-03-16 02:00 | 184 | 182
2018-03-16 02:30 | 185 | 183
2018-03-16 03:00 | 185 | 183
2018-03-16 03:30 | 184 | 182
2018-03-16 04:00 | 187 | 185
2018-03-16 04:30 | 189 | 187
2018-03-16 05:00 | 194 | 193
2018-03-16 05:30 | 204 | 203
2018-03-16 06:00 | 219 | 219
2018-03-16 06:30 | 235 | 235
2018-03-16 07:00 | 254 | 254
2018-03-16 07:30 | 261 | 261
2018-03-16 08:00 | 267 | 267
2018-03-16 08:30 | 268 | 267
2018-03-16 09:00 | 270 | 270
2018-03-16 09:30 | 273 | 273
2018-03-16 10:00 | 275 | 275
2018-03-16 10:30 | 270 | 270
2018-03-16 11:00 | 267 | 267
2018-03-16 11:30 | 265 | 265
2018-03-16 12:00 | 271 | 271
2018-03-16 12:30 | 278 | 278
2018-03-16 13:00 | 284 | 283
2018-03-16 13:30 | 282 | 281
2018-03-16 14:00 | 285 | 285
2018-03-16 14:30 | 288 | 287
2018-03-16 15:00 | 294 | 293
2018-03-16 15:30 | 302 | 302
2018-03-16 16:00 | 309 | 309
2018-03-16 16:30 | 313 | 312
2018-03-16 17:00 | 310 | 309
2018-03-16 17:30 | 306 | 304
2018-03-16 18:00 | 303 | 301
2018-03-16 18:30 | 306 | 304
2018-03-16 19:00 | 301 | 298
2018-03-16 19:30 | 297 | 295
2018-03-16 20:00 | 289 | 288
2018-03-16 20:30 | 281 | 279
2018-03-16 21:00 | 274 | 271
2018-03-16 21:30 | 264 | 262
2018-03-16 22:00 | 248 | 245
2018-03-16 22:30 | 245 | 243
2018-03-16 23:00 | 231 | 228
2018-03-16 23:30 | 217 | 214
2018-03-17 | 204 | 202
2018-03-17 00:30 | 202 | 199
2018-03-17 01:00 | 199 | 196
2018-03-17 01:30 | 194 | 191
2018-03-17 02:00 | 190 | 186
2018-03-17 02:30 | 188 | 184
2018-03-17 03:00 | 188 | 183
2018-03-17 03:30 | 186 | 183
2018-03-17 04:00 | 185 | 183
2018-03-17 04:30 | 187 | 186
2018-03-17 05:00 | 192 | 191
2018-03-17 05:30 | 197 | 195
2018-03-17 06:00 | 201 | 200
2018-03-17 06:30 | 206 | 206
2018-03-17 07:00 | 217 | 217
2018-03-17 07:30 | 232 | 232
2018-03-17 08:00 | 245 | 245
2018-03-17 08:30 | 248 | 248
2018-03-17 09:00 | 252 | 251
2018-03-17 09:30 | 250 | 250
2018-03-17 10:00 | 250 | 250
2018-03-17 10:30 | 250 | 250
2018-03-17 11:00 | 249 | 249
2018-03-17 11:30 | 249 | 249
2018-03-17 12:00 | 251 | 251
2018-03-17 12:30 | 255 | 255
2018-03-17 13:00 | 265 | 265
2018-03-17 13:30 | 266 | 266
2018-03-17 14:00 | 275 | 274
2018-03-17 14:30 | 278 | 278
2018-03-17 15:00 | 287 | 287
2018-03-17 15:30 | 295 | 293
2018-03-17 16:00 | 294 | 293
2018-03-17 16:30 | 300 | 299
2018-03-17 17:00 | 297 | 295
2018-03-17 17:30 | 291 | 288
2018-03-17 18:00 | 288 | 286
2018-03-17 18:30 | 295 | 293
2018-03-17 19:00 | 288 | 286
2018-03-17 19:30 | 286 | 283
2018-03-17 20:00 | 277 | 275
2018-03-17 20:30 | 267 | 266
2018-03-17 21:00 | 260 | 259
2018-03-17 21:30 | 250 | 247
2018-03-17 22:00 | 247 | 245
2018-03-17 22:30 | 246 | 243
2018-03-17 23:00 | 223 | 222
2018-03-17 23:30 | 210 | 209
2018-03-18 | 196 | 196
2018-03-18 00:30 | 193 | 192
2018-03-18 01:00 | 189 | 188
2018-03-18 01:30 | 183 | 181
2018-03-18 02:00 | 180 | 178
2018-03-18 02:30 | 179 | 177
2018-03-18 03:00 | 180 | 178
2018-03-18 03:30 | 180 | 178
2018-03-18 04:00 | 179 | 177
2018-03-18 04:30 | 181 | 179
2018-03-18 05:00 | 178 | 177
2018-03-18 05:30 | 182 | 180
2018-03-18 06:00 | 190 | 188
2018-03-18 06:30 | 194 | 193
2018-03-18 07:00 | 193 | 192
2018-03-18 07:30 | 196 | 195
2018-03-18 08:00 | 206 | 206
2018-03-18 08:30 | 218 | 218
2018-03-18 09:00 | 227 | 227
2018-03-18 09:30 | 233 | 233
2018-03-18 10:00 | 227 | 227
2018-03-18 10:30 | 223 | 222
2018-03-18 11:00 | 209 | 208
2018-03-18 11:30 | 236 | 235
2018-03-18 12:00 | 241 | 240
2018-03-18 12:30 | 245 | 244
2018-03-18 13:00 | 251 | 250
2018-03-18 13:30 | 260 | 259
2018-03-18 14:00 | 269 | 268
2018-03-18 14:30 | 278 | 277
2018-03-18 15:00 | 287 | 286
2018-03-18 15:30 | 306 | 303
2018-03-18 16:00 | 311 | 309
2018-03-18 16:30 | 318 | 316
2018-03-18 17:00 | 319 | 316
2018-03-18 17:30 | 318 | 315
2018-03-18 18:00 | 322 | 320
2018-03-18 18:30 | 323 | 321
2018-03-18 19:00 | 317 | 314
2018-03-18 19:30 | 313 | 310
2018-03-18 20:00 | 302 | 298
2018-03-18 20:30 | 283 | 282
2018-03-18 21:00 | 266 | 265
2018-03-18 21:30 | 251 | 250
2018-03-18 22:00 | 243 | 241
2018-03-18 22:30 | 239 | 237
2018-03-18 23:00 | 229 | 227
2018-03-18 23:30 | 212 | 212
2018-03-19 | 200 | 200
2018-03-19 00:30 | 193 | 192
2018-03-19 01:00 | 189 | 188
2018-03-19 01:30 | 185 | 184
2018-03-19 02:00 | 185 | 184
2018-03-19 02:30 | 185 | 184
2018-03-19 03:00 | 185 | 184
2018-03-19 03:30 | 187 | 186
2018-03-19 04:00 | 193 | 192
2018-03-19 04:30 | 197 | 196
2018-03-19 05:00 | 204 | 204
2018-03-19 05:30 | 211 | 211
2018-03-19 06:00 | 227 | 227
2018-03-19 06:30 | 239 | 239
2018-03-19 07:00 | 263 | 262
2018-03-19 07:30 | 271 | 271
2018-03-19 08:00 | 280 | 280
2018-03-19 08:30 | 289 | 289
2018-03-19 09:00 | 290 | 289
2018-03-19 09:30 | 290 | 290
2018-03-19 10:00 | 290 | 290
2018-03-19 10:30 | 293 | 293
2018-03-19 11:00 | 293 | 293
2018-03-19 11:30 | 298 | 298
2018-03-19 12:00 | 302 | 302
2018-03-19 12:30 | 308 | 308
2018-03-19 13:00 | 311 | 311
2018-03-19 13:30 | 314 | 314
2018-03-19 14:00 | 320 | 320
2018-03-19 14:30 | 327 | 326
2018-03-19 15:00 | 333 | 332
2018-03-19 15:30 | 346 | 345
2018-03-19 16:00 | 357 | 356
2018-03-19 16:30 | 363 | 362
2018-03-19 17:00 | 360 | 359
2018-03-19 17:30 | 357 | 354
2018-03-19 18:00 | 358 | 356
2018-03-19 18:30 | 355 | 353
2018-03-19 19:00 | 343 | 340
2018-03-19 19:30 | 336 | 332
2018-03-19 20:00 | 323 | 320
2018-03-19 20:30 | 310 | 308
2018-03-19 21:00 | 301 | 298
2018-03-19 21:30 | 279 | 277
2018-03-19 22:00 | 264 | 264
2018-03-19 22:30 | 256 | 255
2018-03-19 23:00 | 240 | 240
2018-03-19 23:30 | 228 | 227
2018-03-20 | 216 | 216
2018-03-20 00:30 | 207 | 206
2018-03-20 01:00 | 203 | 203
2018-03-20 01:30 | 200 | 200
2018-03-20 02:00 | 200 | 199
2018-03-20 02:30 | 197 | 197
2018-03-20 03:00 | 196 | 196
2018-03-20 03:30 | 199 | 199
2018-03-20 04:00 | 201 | 200
2018-03-20 04:30 | 207 | 207
2018-03-20 05:00 | 208 | 208
2018-03-20 05:30 | 219 | 219
2018-03-20 06:00 | 241 | 240
2018-03-20 06:30 | 258 | 257
2018-03-20 07:00 | 277 | 276
2018-03-20 07:30 | 291 | 290
2018-03-20 08:00 | 296 | 295
2018-03-20 08:30 | 292 | 290
2018-03-20 09:00 | 290 | 288
2018-03-20 09:30 | 286 | 285
2018-03-20 10:00 | 291 | 290
2018-03-20 10:30 | 293 | 292
2018-03-20 11:00 | 290 | 288
2018-03-20 11:30 | 294 | 293
2018-03-20 12:00 | 304 | 299
2018-03-20 12:30 | 304 | 299
2018-03-20 13:00 | 305 | 300
2018-03-20 13:30 | 305 | 300
2018-03-20 14:00 | 309 | 304
2018-03-20 14:30 | 308 | 303
2018-03-20 15:00 | 311 | 306
2018-03-20 15:30 | 317 | 312
2018-03-20 16:00 | 322 | 317
2018-03-20 16:30 | 323 | 317
2018-03-20 17:00 | 317 | 313
2018-03-20 17:30 | 316 | 310
2018-03-20 18:00 | 321 | 316
2018-03-20 18:30 | 323 | 318
2018-03-20 19:00 | 314 | 308
2018-03-20 19:30 | 303 | 299
2018-03-20 20:00 | 296 | 290
2018-03-20 20:30 | 286 | 282
2018-03-20 21:00 | 274 | 271
2018-03-20 21:30 | 263 | 259
2018-03-20 22:00 | 253 | 249
2018-03-20 22:30 | 243 | 238
2018-03-20 23:00 | 230 | 224
2018-03-20 23:30 | 215 | 210
2018-03-21 | 203 | 196
2018-03-21 00:30 | 199 | 192
2018-03-21 01:00 | 193 | 185
2018-03-21 01:30 | 186 | 178
2018-03-21 02:00 | 186 | 181
2018-03-21 02:30 | 186 | 181
2018-03-21 03:00 | 186 | 181
2018-03-21 03:30 | 186 | 181
2018-03-21 04:00 | 189 | 184
2018-03-21 04:30 | 197 | 193
2018-03-21 05:00 | 204 | 201
2018-03-21 05:30 | 216 | 214
2018-03-21 06:00 | 233 | 231
2018-03-21 06:30 | 259 | 255
2018-03-21 07:00 | 273 | 271
2018-03-21 07:30 | 282 | 281
2018-03-21 08:00 | 285 | 284
2018-03-21 08:30 | 289 | 288
2018-03-21 09:00 | 302 | 301
2018-03-21 09:30 | 298 | 298
2018-03-21 10:00 | 284 | 284
2018-03-21 10:30 | 293 | 293
2018-03-21 11:00 | 287 | 287
2018-03-21 11:30 | 273 | 273
2018-03-21 12:00 | 280 | 280
2018-03-21 12:30 | 271 | 271
2018-03-21 13:00 | 266 | 265
2018-03-21 13:30 | 270 | 269
2018-03-21 14:00 | 276 | 276
2018-03-21 14:30 | 274 | 274
2018-03-21 15:00 | 281 | 280
2018-03-21 15:30 | 295 | 295
2018-03-21 16:00 | 297 | 297
2018-03-21 16:30 | 298 | 297
2018-03-21 17:00 | 297 | 296
2018-03-21 17:30 | 297 | 297
2018-03-21 18:00 | 300 | 300
2018-03-21 18:30 | 296 | 296
2018-03-21 19:00 | 289 | 289
2018-03-21 19:30 | 283 | 283
2018-03-21 20:00 | 278 | 278
2018-03-21 20:30 | 269 | 269
2018-03-21 21:00 | 260 | 259
2018-03-21 21:30 | 252 | 252
2018-03-21 22:00 | 246 | 245
2018-03-21 22:30 | 242 | 241
2018-03-21 23:00 | 226 | 225
2018-03-21 23:30 | 216 | 215
2018-03-22 | 205 | 204
2018-03-22 00:30 | 201 | 201
2018-03-22 01:00 | 190 | 190
2018-03-22 01:30 | 186 | 186
2018-03-22 02:00 | 188 | 188
2018-03-22 02:30 | 195 | 194
2018-03-22 03:00 | 197 | 197
2018-03-22 03:30 | 195 | 195
2018-03-22 04:00 | 193 | 193
2018-03-22 04:30 | 193 | 192
2018-03-22 05:00 | 200 | 199
2018-03-22 05:30 | 202 | 201
2018-03-22 06:00 | 219 | 218
2018-03-22 06:30 | 239 | 238
2018-03-22 07:00 | 260 | 260
2018-03-22 07:30 | 268 | 268
2018-03-22 08:00 | 270 | 270
2018-03-22 08:30 | 260 | 260
2018-03-22 09:00 | 262 | 261
2018-03-22 09:30 | 266 | 264
2018-03-22 10:00 | 278 | 276
2018-03-22 10:30 | 277 | 275
2018-03-22 11:00 | 265 | 263
2018-03-22 11:30 | 249 | 248
2018-03-22 12:00 | 243 | 242
2018-03-22 12:30 | 251 | 250
2018-03-22 13:00 | 250 | 249
2018-03-22 13:30 | 262 | 262
2018-03-22 14:00 | 269 | 268
2018-03-22 14:30 | 276 | 275
2018-03-22 15:00 | 288 | 287
2018-03-22 15:30 | 298 | 297
2018-03-22 16:00 | 296 | 294
2018-03-22 16:30 | 300 | 298
2018-03-22 17:00 | 303 | 300
2018-03-22 17:30 | 306 | 303
2018-03-22 18:00 | 309 | 307
2018-03-22 18:30 | 306 | 304
2018-03-22 19:00 | 300 | 297
2018-03-22 19:30 | 292 | 291
2018-03-22 20:00 | 287 | 286
2018-03-22 20:30 | 276 | 275
2018-03-22 21:00 | 263 | 263
2018-03-22 21:30 | 251 | 251
2018-03-22 22:00 | 245 | 244
2018-03-22 22:30 | 241 | 240
2018-03-22 23:00 | 229 | 228
2018-03-22 23:30 | 218 | 216
2018-03-23 | 208 | 205
2018-03-23 00:30 | 203 | 201
2018-03-23 01:00 | 195 | 194
2018-03-23 01:30 | 190 | 189
2018-03-23 02:00 | 189 | 188
2018-03-23 02:30 | 189 | 188
2018-03-23 03:00 | 192 | 191
2018-03-23 03:30 | 189 | 188
2018-03-23 04:00 | 190 | 189
2018-03-23 04:30 | 192 | 191
2018-03-23 05:00 | 204 | 203
2018-03-23 05:30 | 214 | 213
2018-03-23 06:00 | 228 | 228
2018-03-23 06:30 | 246 | 246
2018-03-23 07:00 | 262 | 262
2018-03-23 07:30 | 270 | 270
2018-03-23 08:00 | 274 | 274
2018-03-23 08:30 | 271 | 271
2018-03-23 09:00 | 277 | 277
2018-03-23 09:30 | 279 | 278
2018-03-23 10:00 | 272 | 272
2018-03-23 10:30 | 274 | 273
2018-03-23 11:00 | 276 | 276
2018-03-23 11:30 | 279 | 279
2018-03-23 12:00 | 278 | 277
2018-03-23 12:30 | 271 | 271
2018-03-23 13:00 | 279 | 278
2018-03-23 13:30 | 286 | 286
2018-03-23 14:00 | 293 | 293
2018-03-23 14:30 | 300 | 300
2018-03-23 15:00 | 299 | 299
2018-03-23 15:30 | 295 | 295
2018-03-23 16:00 | 300 | 300
2018-03-23 16:30 | 300 | 300
2018-03-23 17:00 | 297 | 296
2018-03-23 17:30 | 296 | 295
2018-03-23 18:00 | 297 | 296
2018-03-23 18:30 | 298 | 297
2018-03-23 19:00 | 293 | 291
2018-03-23 19:30 | 291 | 288
2018-03-23 20:00 | 286 | 283
2018-03-23 20:30 | 279 | 275
2018-03-23 21:00 | 268 | 267
2018-03-23 21:30 | 259 | 258
2018-03-23 22:00 | 249 | 249
2018-03-23 22:30 | 242 | 242
2018-03-23 23:00 | 225 | 225
2018-03-23 23:30 | 212 | 212
2018-03-24 | 203 | 203
2018-03-24 00:30 | 199 | 198
2018-03-24 01:00 | 194 | 193
2018-03-24 01:30 | 190 | 189
2018-03-24 02:00 | 188 | 187
2018-03-24 02:30 | 186 | 185
2018-03-24 03:00 | 186 | 185
2018-03-24 03:30 | 186 | 185
2018-03-24 04:00 | 189 | 188
2018-03-24 04:30 | 189 | 188
2018-03-24 05:00 | 196 | 195
2018-03-24 05:30 | 200 | 200
2018-03-24 06:00 | 209 | 209
2018-03-24 06:30 | 217 | 217
2018-03-24 07:00 | 227 | 227
2018-03-24 07:30 | 238 | 238
2018-03-24 08:00 | 250 | 250
2018-03-24 08:30 | 250 | 250
2018-03-24 09:00 | 256 | 256
2018-03-24 09:30 | 255 | 255
2018-03-24 10:00 | 255 | 254
2018-03-24 10:30 | 253 | 253
2018-03-24 11:00 | 252 | 252
2018-03-24 11:30 | 257 | 256
2018-03-24 12:00 | 255 | 255
2018-03-24 12:30 | 254 | 254
2018-03-24 13:00 | 256 | 256
2018-03-24 13:30 | 264 | 263
2018-03-24 14:00 | 265 | 265
2018-03-24 14:30 | 267 | 267
2018-03-24 15:00 | 272 | 272
2018-03-24 15:30 | 282 | 282
2018-03-24 16:00 | 282 | 282
2018-03-24 16:30 | 283 | 283
2018-03-24 17:00 | 279 | 279
2018-03-24 17:30 | 277 | 277
2018-03-24 18:00 | 282 | 282
2018-03-24 18:30 | 281 | 281
2018-03-24 19:00 | 273 | 272
2018-03-24 19:30 | 268 | 267
2018-03-24 20:00 | 258 | 258
2018-03-24 20:30 | 253 | 253
2018-03-24 21:00 | 245 | 245
2018-03-24 21:30 | 238 | 238
2018-03-24 22:00 | 237 | 237
2018-03-24 22:30 | 233 | 233
2018-03-24 23:00 | 218 | 218
2018-03-24 23:30 | 207 | 206
2018-03-25 | 194 | 193
2018-03-25 00:30 | 187 | 185
2018-03-25 01:00 | 183 | 182
2018-03-25 01:30 | 180 | 178
2018-03-25 02:00 | 180 | 179
2018-03-25 02:30 | 181 | 179
2018-03-25 03:00 | 177 | 175
2018-03-25 03:30 | 167 | 165
2018-03-25 04:00 | 172 | 169
2018-03-25 04:30 | 174 | 172
2018-03-25 05:00 | 186 | 185
2018-03-25 05:30 | 193 | 191
2018-03-25 06:00 | 195 | 193
2018-03-25 06:30 | 201 | 200
2018-03-25 07:00 | 212 | 212
2018-03-25 07:30 | 216 | 216
2018-03-25 08:00 | 223 | 223
2018-03-25 08:30 | 230 | 230
2018-03-25 09:00 | 231 | 230
2018-03-25 09:30 | 238 | 237
2018-03-25 10:00 | 238 | 238
2018-03-25 10:30 | 232 | 232
2018-03-25 11:00 | 228 | 228
2018-03-25 11:30 | 227 | 227
2018-03-25 12:00 | 240 | 240
2018-03-25 12:30 | 231 | 230
2018-03-25 13:00 | 222 | 222
2018-03-25 13:30 | 220 | 220
2018-03-25 14:00 | 248 | 247
2018-03-25 14:30 | 256 | 252
2018-03-25 15:00 | 267 | 264
2018-03-25 15:30 | 278 | 275
2018-03-25 16:00 | 286 | 283
2018-03-25 16:30 | 288 | 285
2018-03-25 17:00 | 287 | 283
2018-03-25 17:30 | 283 | 280
2018-03-25 18:00 | 293 | 289
2018-03-25 18:30 | 294 | 289
2018-03-25 19:00 | 284 | 279
2018-03-25 19:30 | 270 | 268
2018-03-25 20:00 | 262 | 261
2018-03-25 20:30 | 251 | 250
2018-03-25 21:00 | 231 | 230
2018-03-25 21:30 | 226 | 225
2018-03-25 22:00 | 224 | 223
2018-03-25 22:30 | 225 | 224
2018-03-25 23:00 | 214 | 213
2018-03-25 23:30 | 205 | 203
2018-03-26 | 198 | 195
2018-03-26 00:30 | 192 | 189
2018-03-26 01:00 | 185 | 182
2018-03-26 01:30 | 185 | 181
2018-03-26 02:00 | 182 | 180
2018-03-26 02:30 | 175 | 174
2018-03-26 03:00 | 177 | 175
2018-03-26 03:30 | 183 | 182
2018-03-26 04:00 | 192 | 191
2018-03-26 04:30 | 197 | 196
2018-03-26 05:00 | 211 | 210
2018-03-26 05:30 | 228 | 227
2018-03-26 06:00 | 242 | 242
2018-03-26 06:30 | 261 | 260
2018-03-26 07:00 | 285 | 282
2018-03-26 07:30 | 293 | 291
2018-03-26 08:00 | 300 | 299
2018-03-26 08:30 | 303 | 302
2018-03-26 09:00 | 307 | 307
2018-03-26 09:30 | 310 | 310
2018-03-26 10:00 | 309 | 308
2018-03-26 10:30 | 314 | 314
2018-03-26 11:00 | 309 | 309
2018-03-26 11:30 | 306 | 306
2018-03-26 12:00 | 307 | 307
2018-03-26 12:30 | 305 | 304
2018-03-26 13:00 | 302 | 302
2018-03-26 13:30 | 305 | 305
2018-03-26 14:00 | 304 | 304
2018-03-26 14:30 | 311 | 311
2018-03-26 15:00 | 319 | 319
2018-03-26 15:30 | 327 | 327
2018-03-26 16:00 | 328 | 328
2018-03-26 16:30 | 333 | 333
2018-03-26 17:00 | 333 | 333
2018-03-26 17:30 | 334 | 333
2018-03-26 18:00 | 340 | 340
2018-03-26 18:30 | 338 | 338
2018-03-26 19:00 | 330 | 330
2018-03-26 19:30 | 327 | 326
2018-03-26 20:00 | 315 | 315
2018-03-26 20:30 | 300 | 300
2018-03-26 21:00 | 291 | 291
2018-03-26 21:30 | 272 | 272
2018-03-26 22:00 | 266 | 266
2018-03-26 22:30 | 260 | 260
2018-03-26 23:00 | 241 | 240
2018-03-26 23:30 | 231 | 231
2018-03-27 | 221 | 221
2018-03-27 00:30 | 217 | 216
2018-03-27 01:00 | 211 | 211
2018-03-27 01:30 | 205 | 204
2018-03-27 02:00 | 203 | 202
2018-03-27 02:30 | 203 | 202
2018-03-27 03:00 | 204 | 203
2018-03-27 03:30 | 204 | 203
2018-03-27 04:00 | 207 | 206
2018-03-27 04:30 | 210 | 210
2018-03-27 05:00 | 222 | 222
2018-03-27 05:30 | 233 | 233
2018-03-27 06:00 | 245 | 245
2018-03-27 06:30 | 258 | 258
2018-03-27 07:00 | 279 | 279
2018-03-27 07:30 | 292 | 292
2018-03-27 08:00 | 293 | 293
2018-03-27 08:30 | 299 | 298
2018-03-27 09:00 | 297 | 296
2018-03-27 09:30 | 305 | 305
2018-03-27 10:00 | 318 | 318
2018-03-27 10:30 | 315 | 315
2018-03-27 11:00 | 320 | 320
2018-03-27 11:30 | 324 | 324
2018-03-27 12:00 | 322 | 322
2018-03-27 12:30 | 312 | 312
2018-03-27 13:00 | 298 | 298
2018-03-27 13:30 | 282 | 282
2018-03-27 14:00 | 300 | 300
2018-03-27 14:30 | 312 | 312
2018-03-27 15:00 | 318 | 318
2018-03-27 15:30 | 319 | 319
2018-03-27 16:00 | 315 | 314
2018-03-27 16:30 | 316 | 315
2018-03-27 17:00 | 313 | 311
2018-03-27 17:30 | 313 | 310
2018-03-27 18:00 | 311 | 308
2018-03-27 18:30 | 310 | 307
2018-03-27 19:00 | 302 | 299
2018-03-27 19:30 | 295 | 295
2018-03-27 20:00 | 288 | 288
2018-03-27 20:30 | 274 | 273
2018-03-27 21:00 | 266 | 266
2018-03-27 21:30 | 258 | 258
2018-03-27 22:00 | 242 | 242
2018-03-27 22:30 | 235 | 235
2018-03-27 23:00 | 219 | 218
2018-03-27 23:30 | 203 | 203
2018-03-28 | 193 | 193
2018-03-28 00:30 | 190 | 190
2018-03-28 01:00 | 187 | 187
2018-03-28 01:30 | 182 | 182
2018-03-28 02:00 | 177 | 177
2018-03-28 02:30 | 174 | 174
2018-03-28 03:00 | 176 | 176
2018-03-28 03:30 | 176 | 176
2018-03-28 04:00 | 184 | 184
2018-03-28 04:30 | 206 | 206
2018-03-28 05:00 | 201 | 201
2018-03-28 05:30 | 211 | 210
2018-03-28 06:00 | 230 | 230
2018-03-28 06:30 | 242 | 242
2018-03-28 07:00 | 259 | 259
2018-03-28 07:30 | 269 | 269
2018-03-28 08:00 | 273 | 273
2018-03-28 08:30 | 274 | 274
2018-03-28 09:00 | 275 | 275
2018-03-28 09:30 | 278 | 278
2018-03-28 10:00 | 282 | 282
2018-03-28 10:30 | 283 | 283
2018-03-28 11:00 | 283 | 283
2018-03-28 11:30 | 282 | 282
2018-03-28 12:00 | 279 | 279
2018-03-28 12:30 | 281 | 281
2018-03-28 13:00 | 288 | 287
2018-03-28 13:30 | 292 | 292
2018-03-28 14:00 | 299 | 299
2018-03-28 14:30 | 305 | 305
2018-03-28 15:00 | 311 | 311
2018-03-28 15:30 | 313 | 312
2018-03-28 16:00 | 320 | 320
2018-03-28 16:30 | 325 | 324
2018-03-28 17:00 | 325 | 324
2018-03-28 17:30 | 321 | 320
2018-03-28 18:00 | 322 | 321
2018-03-28 18:30 | 320 | 320
2018-03-28 19:00 | 310 | 309
2018-03-28 19:30 | 305 | 303
2018-03-28 20:00 | 298 | 295
2018-03-28 20:30 | 287 | 284
2018-03-28 21:00 | 277 | 275
2018-03-28 21:30 | 267 | 265
2018-03-28 22:00 | 260 | 259
2018-03-28 22:30 | 249 | 248
2018-03-28 23:00 | 234 | 234
2018-03-28 23:30 | 226 | 224
2018-03-29 | 217 | 216
2018-03-29 00:30 | 212 | 210
2018-03-29 01:00 | 208 | 206
2018-03-29 01:30 | 200 | 199
2018-03-29 02:00 | 198 | 197
2018-03-29 02:30 | 199 | 199
2018-03-29 03:00 | 200 | 199
2018-03-29 03:30 | 204 | 203
2018-03-29 04:00 | 207 | 206
2018-03-29 04:30 | 211 | 211
2018-03-29 05:00 | 220 | 220
2018-03-29 05:30 | 233 | 232
2018-03-29 06:00 | 244 | 243
2018-03-29 06:30 | 262 | 261
2018-03-29 07:00 | 288 | 288
2018-03-29 07:30 | 290 | 290
2018-03-29 08:00 | 298 | 298
2018-03-29 08:30 | 302 | 302
2018-03-29 09:00 | 308 | 307
2018-03-29 09:30 | 303 | 302
2018-03-29 10:00 | 303 | 302
2018-03-29 10:30 | 309 | 307
2018-03-29 11:00 | 307 | 306
2018-03-29 11:30 | 303 | 302
2018-03-29 12:00 | 298 | 297
2018-03-29 12:30 | 301 | 300
2018-03-29 13:00 | 298 | 297
2018-03-29 13:30 | 305 | 303
2018-03-29 14:00 | 306 | 304
2018-03-29 14:30 | 310 | 309
2018-03-29 15:00 | 311 | 310
2018-03-29 15:30 | 314 | 313
2018-03-29 16:00 | 317 | 316
2018-03-29 16:30 | 319 | 318
2018-03-29 17:00 | 312 | 312
2018-03-29 17:30 | 316 | 316
2018-03-29 18:00 | 316 | 316
2018-03-29 18:30 | 318 | 318
2018-03-29 19:00 | 312 | 312
2018-03-29 19:30 | 305 | 305
2018-03-29 20:00 | 292 | 292
2018-03-29 20:30 | 282 | 282
2018-03-29 21:00 | 275 | 275
2018-03-29 21:30 | 260 | 260
2018-03-29 22:00 | 251 | 251
2018-03-29 22:30 | 243 | 243
2018-03-29 23:00 | 227 | 226
2018-03-29 23:30 | 217 | 216
2018-03-30 | 209 | 208
2018-03-30 00:30 | 203 | 202
2018-03-30 01:00 | 199 | 199
2018-03-30 01:30 | 197 | 196
2018-03-30 02:00 | 197 | 196
2018-03-30 02:30 | 194 | 194
2018-03-30 03:00 | 194 | 193
2018-03-30 03:30 | 192 | 191
2018-03-30 04:00 | 192 | 192
2018-03-30 04:30 | 193 | 193
2018-03-30 05:00 | 197 | 197
2018-03-30 05:30 | 201 | 200
2018-03-30 06:00 | 209 | 209
2018-03-30 06:30 | 218 | 217
2018-03-30 07:00 | 231 | 230
2018-03-30 07:30 | 240 | 239
2018-03-30 08:00 | 250 | 247
2018-03-30 08:30 | 254 | 253
2018-03-30 09:00 | 256 | 255
2018-03-30 09:30 | 263 | 262
2018-03-30 10:00 | 271 | 271
2018-03-30 10:30 | 271 | 271
2018-03-30 11:00 | 261 | 261
2018-03-30 11:30 | 262 | 262
2018-03-30 12:00 | 260 | 260
2018-03-30 12:30 | 259 | 259
2018-03-30 13:00 | 259 | 259
2018-03-30 13:30 | 263 | 263
2018-03-30 14:00 | 268 | 268
2018-03-30 14:30 | 270 | 270
2018-03-30 15:00 | 271 | 270
2018-03-30 15:30 | 276 | 276
2018-03-30 16:00 | 284 | 283
2018-03-30 16:30 | 288 | 287
2018-03-30 17:00 | 291 | 291
2018-03-30 17:30 | 296 | 296
2018-03-30 18:00 | 302 | 302
2018-03-30 18:30 | 303 | 303
2018-03-30 19:00 | 293 | 292
2018-03-30 19:30 | 292 | 292
2018-03-30 20:00 | 281 | 281
2018-03-30 20:30 | 266 | 266
2018-03-30 21:00 | 261 | 261
2018-03-30 21:30 | 254 | 254
2018-03-30 22:00 | 250 | 249
2018-03-30 22:30 | 245 | 245
2018-03-30 23:00 | 232 | 230
2018-03-30 23:30 | 222 | 221
2018-03-31 | 215 | 213
2018-03-31 00:30 | 208 | 205
2018-03-31 01:00 | 202 | 199
2018-03-31 01:30 | 199 | 196
2018-03-31 02:00 | 194 | 192
2018-03-31 02:30 | 192 | 191
2018-03-31 03:00 | 194 | 193
2018-03-31 03:30 | 193 | 192
2018-03-31 04:00 | 193 | 191
2018-03-31 04:30 | 193 | 191
2018-03-31 05:00 | 196 | 194
2018-03-31 05:30 | 202 | 201
2018-03-31 06:00 | 209 | 208
2018-03-31 06:30 | 221 | 220
2018-03-31 07:00 | 229 | 229
2018-03-31 07:30 | 238 | 238
2018-03-31 08:00 | 248 | 248
2018-03-31 08:30 | 258 | 258
2018-03-31 09:00 | 261 | 261
2018-03-31 09:30 | 258 | 258
2018-03-31 10:00 | 254 | 254
2018-03-31 10:30 | 248 | 248
2018-03-31 11:00 | 245 | 245
2018-03-31 11:30 | 246 | 246
2018-03-31 12:00 | 248 | 247
2018-03-31 12:30 | 249 | 249
2018-03-31 13:00 | 252 | 252
2018-03-31 13:30 | 254 | 254
2018-03-31 14:00 | 256 | 256
2018-03-31 14:30 | 258 | 258
2018-03-31 15:00 | 268 | 267
2018-03-31 15:30 | 278 | 277
2018-03-31 16:00 | 288 | 287
2018-03-31 16:30 | 296 | 295
2018-03-31 17:00 | 300 | 298
2018-03-31 17:30 | 300 | 297
2018-03-31 18:00 | 306 | 304
2018-03-31 18:30 | 308 | 306
2018-03-31 19:00 | 299 | 297
2018-03-31 19:30 | 293 | 291
2018-03-31 20:00 | 279 | 278
2018-03-31 20:30 | 268 | 268
2018-03-31 21:00 | 260 | 260
2018-03-31 21:30 | 254 | 254
2018-03-31 22:00 | 251 | 251
2018-03-31 22:30 | 253 | 252
2018-03-31 23:00 | 240 | 239
2018-03-31 23:30 | 227 | 225
2018-04-01 | 216 | 214
2018-04-01 00:30 | 206 | 203
2018-04-01 01:00 | 202 | 199
2018-04-01 01:30 | 198 | 195
2018-04-01 02:00 | 192 | 191
2018-04-01 02:30 | 189 | 188
2018-04-01 03:00 | 193 | 191
2018-04-01 03:30 | 190 | 189
2018-04-01 04:00 | 191 | 190
2018-04-01 04:30 | 190 | 189
2018-04-01 05:00 | 191 | 190
2018-04-01 05:30 | 197 | 195
2018-04-01 06:00 | 200 | 198
2018-04-01 06:30 | 205 | 203
2018-04-01 07:00 | 216 | 215
2018-04-01 07:30 | 224 | 224
2018-04-01 08:00 | 230 | 230
2018-04-01 08:30 | 235 | 235
2018-04-01 09:00 | 247 | 247
2018-04-01 09:30 | 239 | 239
2018-04-01 10:00 | 237 | 237
2018-04-01 10:30 | 240 | 240
2018-04-01 11:00 | 240 | 239
2018-04-01 11:30 | 240 | 240
2018-04-01 12:00 | 236 | 236
2018-04-01 12:30 | 235 | 235
2018-04-01 13:00 | 243 | 243
2018-04-01 13:30 | 248 | 248
2018-04-01 14:00 | 257 | 257
2018-04-01 14:30 | 262 | 261
2018-04-01 15:00 | 271 | 271
2018-04-01 15:30 | 277 | 277
2018-04-01 16:00 | 285 | 285
2018-04-01 16:30 | 296 | 296
2018-04-01 17:00 | 297 | 297
2018-04-01 17:30 | 296 | 296
2018-04-01 18:00 | 302 | 302
2018-04-01 18:30 | 303 | 303
2018-04-01 19:00 | 296 | 296
2018-04-01 19:30 | 290 | 289
2018-04-01 20:00 | 277 | 276
2018-04-01 20:30 | 266 | 265
2018-04-01 21:00 | 259 | 259
2018-04-01 21:30 | 248 | 248
2018-04-01 22:00 | 240 | 240
2018-04-01 22:30 | 236 | 236
2018-04-01 23:00 | 226 | 226
2018-04-01 23:30 | 217 | 216
2018-04-02 | 207 | 207
2018-04-02 00:30 | 200 | 200
2018-04-02 01:00 | 196 | 196
2018-04-02 01:30 | 194 | 193
2018-04-02 02:00 | 193 | 193
2018-04-02 02:30 | 190 | 190
2018-04-02 03:00 | 191 | 191
2018-04-02 03:30 | 191 | 191
2018-04-02 04:00 | 193 | 193
2018-04-02 04:30 | 192 | 192
2018-04-02 05:00 | 195 | 195
2018-04-02 05:30 | 199 | 199
2018-04-02 06:00 | 206 | 206
2018-04-02 06:30 | 211 | 211
2018-04-02 07:00 | 225 | 225
2018-04-02 07:30 | 237 | 237
2018-04-02 08:00 | 250 | 250
2018-04-02 08:30 | 258 | 258
2018-04-02 09:00 | 257 | 257
2018-04-02 09:30 | 262 | 262
2018-04-02 10:00 | 260 | 260
2018-04-02 10:30 | 257 | 257
2018-04-02 11:00 | 256 | 256
2018-04-02 11:30 | 257 | 257
2018-04-02 12:00 | 253 | 253
2018-04-02 12:30 | 249 | 249
2018-04-02 13:00 | 253 | 253
2018-04-02 13:30 | 262 | 262
2018-04-02 14:00 | 272 | 272
2018-04-02 14:30 | 279 | 279
2018-04-02 15:00 | 278 | 278
2018-04-02 15:30 | 286 | 286
2018-04-02 16:00 | 293 | 293
2018-04-02 16:30 | 300 | 300
2018-04-02 17:00 | 307 | 307
2018-04-02 17:30 | 313 | 313
2018-04-02 18:00 | 314 | 314
2018-04-02 18:30 | 309 | 309
2018-04-02 19:00 | 298 | 298
2018-04-02 19:30 | 292 | 291
2018-04-02 20:00 | 281 | 280
2018-04-02 20:30 | 268 | 268
2018-04-02 21:00 | 261 | 261
2018-04-02 21:30 | 250 | 250
2018-04-02 22:00 | 248 | 248
2018-04-02 22:30 | 246 | 245
2018-04-02 23:00 | 231 | 231
2018-04-02 23:30 | 216 | 216
2018-04-03 | 208 | 208
2018-04-03 00:30 | 202 | 202
2018-04-03 01:00 | 198 | 198
2018-04-03 01:30 | 197 | 197
2018-04-03 02:00 | 195 | 195
2018-04-03 02:30 | 193 | 193
2018-04-03 03:00 | 191 | 191
2018-04-03 03:30 | 189 | 189
2018-04-03 04:00 | 194 | 194
2018-04-03 04:30 | 196 | 196
2018-04-03 05:00 | 205 | 205
2018-04-03 05:30 | 211 | 211
2018-04-03 06:00 | 223 | 222
2018-04-03 06:30 | 237 | 237
2018-04-03 07:00 | 258 | 258
2018-04-03 07:30 | 277 | 277
2018-04-03 08:00 | 286 | 286
2018-04-03 08:30 | 291 | 291
2018-04-03 09:00 | 293 | 291
2018-04-03 09:30 | 291 | 289
2018-04-03 10:00 | 287 | 285
2018-04-03 10:30 | 285 | 284
2018-04-03 11:00 | 283 | 282
2018-04-03 11:30 | 281 | 280
2018-04-03 12:00 | 283 | 282
2018-04-03 12:30 | 286 | 285
2018-04-03 13:00 | 287 | 286
2018-04-03 13:30 | 287 | 287
2018-04-03 14:00 | 291 | 291
2018-04-03 14:30 | 297 | 296
2018-04-03 15:00 | 302 | 301
2018-04-03 15:30 | 307 | 306
2018-04-03 16:00 | 315 | 314
2018-04-03 16:30 | 321 | 319
2018-04-03 17:00 | 323 | 321
2018-04-03 17:30 | 325 | 323
2018-04-03 18:00 | 329 | 327
2018-04-03 18:30 | 327 | 324
2018-04-03 19:00 | 314 | 311
2018-04-03 19:30 | 302 | 301
2018-04-03 20:00 | 289 | 288
2018-04-03 20:30 | 279 | 279
2018-04-03 21:00 | 269 | 269
2018-04-03 21:30 | 257 | 256
2018-04-03 22:00 | 248 | 248
2018-04-03 22:30 | 245 | 245
2018-04-03 23:00 | 231 | 231
2018-04-03 23:30 | 220 | 220
2018-04-04 | 208 | 208
2018-04-04 00:30 | 200 | 200
2018-04-04 01:00 | 197 | 196
2018-04-04 01:30 | 194 | 193
2018-04-04 02:00 | 193 | 192
2018-04-04 02:30 | 193 | 192
2018-04-04 03:00 | 195 | 194
2018-04-04 03:30 | 199 | 198
2018-04-04 04:00 | 201 | 200
2018-04-04 04:30 | 200 | 200
2018-04-04 05:00 | 205 | 205
2018-04-04 05:30 | 230 | 230
2018-04-04 06:00 | 227 | 226
2018-04-04 06:30 | 241 | 241
2018-04-04 07:00 | 260 | 259
2018-04-04 07:30 | 268 | 268
2018-04-04 08:00 | 278 | 278
2018-04-04 08:30 | 278 | 278
2018-04-04 09:00 | 274 | 274
2018-04-04 09:30 | 270 | 269
2018-04-04 10:00 | 268 | 267
2018-04-04 10:30 | 270 | 270
2018-04-04 11:00 | 273 | 272
2018-04-04 11:30 | 277 | 276
2018-04-04 12:00 | 271 | 270
2018-04-04 12:30 | 269 | 268
2018-04-04 13:00 | 277 | 276
2018-04-04 13:30 | 285 | 285
2018-04-04 14:00 | 287 | 286
2018-04-04 14:30 | 291 | 290
2018-04-04 15:00 | 294 | 293
2018-04-04 15:30 | 297 | 296
2018-04-04 16:00 | 300 | 299
2018-04-04 16:30 | 310 | 309
2018-04-04 17:00 | 325 | 323
2018-04-04 17:30 | 330 | 329
2018-04-04 18:00 | 329 | 328
2018-04-04 18:30 | 328 | 326
2018-04-04 19:00 | 317 | 315
2018-04-04 19:30 | 312 | 309
2018-04-04 20:00 | 297 | 297
2018-04-04 20:30 | 286 | 286
2018-04-04 21:00 | 278 | 278
2018-04-04 21:30 | 265 | 265
2018-04-04 22:00 | 264 | 264
2018-04-04 22:30 | 266 | 266
2018-04-04 23:00 | 256 | 256
2018-04-04 23:30 | 241 | 241
2018-04-05 | 223 | 223
2018-04-05 00:30 | 212 | 212
2018-04-05 01:00 | 208 | 208
2018-04-05 01:30 | 200 | 200
2018-04-05 02:00 | 200 | 200
2018-04-05 02:30 | 200 | 199
2018-04-05 03:00 | 199 | 199
2018-04-05 03:30 | 200 | 200
2018-04-05 04:00 | 202 | 202
2018-04-05 04:30 | 205 | 205
2018-04-05 05:00 | 215 | 215
2018-04-05 05:30 | 218 | 218
2018-04-05 06:00 | 219 | 219
2018-04-05 06:30 | 233 | 233
2018-04-05 07:00 | 245 | 245
2018-04-05 07:30 | 252 | 252
2018-04-05 08:00 | 258 | 258
2018-04-05 08:30 | 257 | 257
2018-04-05 09:00 | 259 | 258
2018-04-05 09:30 | 263 | 263
2018-04-05 10:00 | 257 | 257
2018-04-05 10:30 | 261 | 261
2018-04-05 11:00 | 270 | 270
2018-04-05 11:30 | 266 | 265
2018-04-05 12:00 | 267 | 267
2018-04-05 12:30 | 280 | 280
2018-04-05 13:00 | 286 | 286
2018-04-05 13:30 | 277 | 277
2018-04-05 14:00 | 279 | 278
2018-04-05 14:30 | 274 | 274
2018-04-05 15:00 | 284 | 284
2018-04-05 15:30 | 292 | 292
2018-04-05 16:00 | 297 | 296
2018-04-05 16:30 | 303 | 302
2018-04-05 17:00 | 300 | 299
2018-04-05 17:30 | 302 | 302
2018-04-05 18:00 | 309 | 309
2018-04-05 18:30 | 310 | 310
2018-04-05 19:00 | 304 | 303
2018-04-05 19:30 | 304 | 303
2018-04-05 20:00 | 298 | 298
2018-04-05 20:30 | 289 | 289
2018-04-05 21:00 | 277 | 277
2018-04-05 21:30 | 262 | 262
2018-04-05 22:00 | 261 | 261
2018-04-05 22:30 | 258 | 258
2018-04-05 23:00 | 250 | 250
2018-04-05 23:30 | 236 | 236
2018-04-06 | 221 | 221
2018-04-06 00:30 | 207 | 206
2018-04-06 01:00 | 202 | 201
2018-04-06 01:30 | 200 | 199
2018-04-06 02:00 | 196 | 195
2018-04-06 02:30 | 195 | 194
2018-04-06 03:00 | 194 | 193
2018-04-06 03:30 | 195 | 194
2018-04-06 04:00 | 199 | 198
2018-04-06 04:30 | 201 | 200
2018-04-06 05:00 | 210 | 210
2018-04-06 05:30 | 209 | 209
2018-04-06 06:00 | 215 | 215
2018-04-06 06:30 | 228 | 228
2018-04-06 07:00 | 240 | 240
2018-04-06 07:30 | 250 | 250
2018-04-06 08:00 | 256 | 255
2018-04-06 08:30 | 258 | 257
2018-04-06 09:00 | 258 | 258
2018-04-06 09:30 | 264 | 263
2018-04-06 10:00 | 272 | 270
2018-04-06 10:30 | 264 | 262
2018-04-06 11:00 | 253 | 251
2018-04-06 11:30 | 252 | 250
2018-04-06 12:00 | 246 | 245
2018-04-06 12:30 | 243 | 243
2018-04-06 13:00 | 246 | 246
2018-04-06 13:30 | 256 | 256
2018-04-06 14:00 | 265 | 265
2018-04-06 14:30 | 275 | 275
2018-04-06 15:00 | 295 | 295
2018-04-06 15:30 | 307 | 307
2018-04-06 16:00 | 316 | 313
2018-04-06 16:30 | 319 | 316
2018-04-06 17:00 | 322 | 319
2018-04-06 17:30 | 321 | 318
2018-04-06 18:00 | 320 | 316
2018-04-06 18:30 | 322 | 318
2018-04-06 19:00 | 310 | 309
2018-04-06 19:30 | 303 | 303
2018-04-06 20:00 | 295 | 295
2018-04-06 20:30 | 286 | 286
2018-04-06 21:00 | 279 | 278
2018-04-06 21:30 | 272 | 270
2018-04-06 22:00 | 267 | 266
2018-04-06 22:30 | 261 | 261
2018-04-06 23:00 | 250 | 250
2018-04-06 23:30 | 235 | 235
2018-04-07 | 220 | 220
2018-04-07 00:30 | 211 | 210
2018-04-07 01:00 | 208 | 207
2018-04-07 01:30 | 202 | 201
2018-04-07 02:00 | 199 | 198
2018-04-07 02:30 | 199 | 198
2018-04-07 03:00 | 199 | 198
2018-04-07 03:30 | 195 | 194
2018-04-07 04:00 | 195 | 194
2018-04-07 04:30 | 196 | 195
2018-04-07 05:00 | 202 | 201
2018-04-07 05:30 | 206 | 205
2018-04-07 06:00 | 212 | 212
2018-04-07 06:30 | 217 | 217
2018-04-07 07:00 | 230 | 229
2018-04-07 07:30 | 239 | 239
2018-04-07 08:00 | 244 | 244
2018-04-07 08:30 | 249 | 248
2018-04-07 09:00 | 258 | 258
2018-04-07 09:30 | 256 | 255
2018-04-07 10:00 | 252 | 251
2018-04-07 10:30 | 254 | 254
2018-04-07 11:00 | 252 | 252
2018-04-07 11:30 | 253 | 252
2018-04-07 12:00 | 254 | 254
2018-04-07 12:30 | 263 | 263
2018-04-07 13:00 | 267 | 267
2018-04-07 13:30 | 263 | 263
2018-04-07 14:00 | 265 | 265
2018-04-07 14:30 | 269 | 269
2018-04-07 15:00 | 278 | 278
2018-04-07 15:30 | 288 | 287
2018-04-07 16:00 | 299 | 299
2018-04-07 16:30 | 310 | 310
2018-04-07 17:00 | 301 | 300
2018-04-07 17:30 | 309 | 308
2018-04-07 18:00 | 328 | 327
2018-04-07 18:30 | 325 | 322
2018-04-07 19:00 | 313 | 311
2018-04-07 19:30 | 299 | 298
2018-04-07 20:00 | 284 | 284
2018-04-07 20:30 | 277 | 277
2018-04-07 21:00 | 272 | 272
2018-04-07 21:30 | 264 | 264
2018-04-07 22:00 | 256 | 256
2018-04-07 22:30 | 255 | 255
2018-04-07 23:00 | 243 | 243
2018-04-07 23:30 | 228 | 228
2018-04-08 | 211 | 210
2018-04-08 00:30 | 200 | 200
2018-04-08 01:00 | 203 | 202
2018-04-08 01:30 | 194 | 193
2018-04-08 02:00 | 192 | 191
2018-04-08 02:30 | 189 | 187
2018-04-08 03:00 | 186 | 184
2018-04-08 03:30 | 185 | 184
2018-04-08 04:00 | 184 | 183
2018-04-08 04:30 | 186 | 185
2018-04-08 05:00 | 187 | 186
2018-04-08 05:30 | 188 | 187
2018-04-08 06:00 | 188 | 187
2018-04-08 06:30 | 194 | 193
2018-04-08 07:00 | 192 | 192
2018-04-08 07:30 | 197 | 196
2018-04-08 08:00 | 204 | 204
2018-04-08 08:30 | 216 | 216
2018-04-08 09:00 | 236 | 236
2018-04-08 09:30 | 240 | 240
2018-04-08 10:00 | 221 | 221
2018-04-08 10:30 | 224 | 223
2018-04-08 11:00 | 228 | 228
2018-04-08 11:30 | 219 | 219
2018-04-08 12:00 | 221 | 221
2018-04-08 12:30 | 233 | 233
2018-04-08 13:00 | 234 | 234
2018-04-08 13:30 | 237 | 237
2018-04-08 14:00 | 247 | 247
2018-04-08 14:30 | 259 | 259
2018-04-08 15:00 | 269 | 268
2018-04-08 15:30 | 279 | 279
2018-04-08 16:00 | 286 | 285
2018-04-08 16:30 | 292 | 291
2018-04-08 17:00 | 295 | 295
2018-04-08 17:30 | 299 | 298
2018-04-08 18:00 | 306 | 304
2018-04-08 18:30 | 304 | 302
2018-04-08 19:00 | 293 | 292
2018-04-08 19:30 | 286 | 286
2018-04-08 20:00 | 278 | 278
2018-04-08 20:30 | 271 | 271
2018-04-08 21:00 | 268 | 267
2018-04-08 21:30 | 258 | 257
2018-04-08 22:00 | 244 | 243
2018-04-08 22:30 | 243 | 242
2018-04-08 23:00 | 233 | 232
2018-04-08 23:30 | 218 | 217
2018-04-09 | 203 | 201
2018-04-09 00:30 | 196 | 194
2018-04-09 01:00 | 189 | 186
2018-04-09 01:30 | 183 | 180
2018-04-09 02:00 | 181 | 179
2018-04-09 02:30 | 181 | 179
2018-04-09 03:00 | 180 | 178
2018-04-09 03:30 | 184 | 182
2018-04-09 04:00 | 186 | 184
2018-04-09 04:30 | 190 | 187
2018-04-09 05:00 | 197 | 195
2018-04-09 05:30 | 205 | 203
2018-04-09 06:00 | 220 | 218
2018-04-09 06:30 | 232 | 231
2018-04-09 07:00 | 246 | 243
2018-04-09 07:30 | 253 | 251
2018-04-09 08:00 | 259 | 258
2018-04-09 08:30 | 262 | 260
2018-04-09 09:00 | 264 | 264
2018-04-09 09:30 | 262 | 262
2018-04-09 10:00 | 261 | 261
2018-04-09 10:30 | 259 | 259
2018-04-09 11:00 | 256 | 256
2018-04-09 11:30 | 256 | 256
2018-04-09 12:00 | 258 | 258
2018-04-09 12:30 | 262 | 262
2018-04-09 13:00 | 266 | 266
2018-04-09 13:30 | 272 | 272
2018-04-09 14:00 | 278 | 278
2018-04-09 14:30 | 287 | 287
2018-04-09 15:00 | 296 | 296
2018-04-09 15:30 | 304 | 304
2018-04-09 16:00 | 311 | 311
2018-04-09 16:30 | 322 | 322
2018-04-09 17:00 | 330 | 330
2018-04-09 17:30 | 332 | 332
2018-04-09 18:00 | 333 | 333
2018-04-09 18:30 | 325 | 325
2018-04-09 19:00 | 308 | 308
2018-04-09 19:30 | 298 | 297
2018-04-09 20:00 | 287 | 286
2018-04-09 20:30 | 276 | 276
2018-04-09 21:00 | 267 | 267
2018-04-09 21:30 | 257 | 257
2018-04-09 22:00 | 255 | 255
2018-04-09 22:30 | 255 | 255
2018-04-09 23:00 | 243 | 243
2018-04-09 23:30 | 232 | 231
2018-04-10 | 212 | 212
2018-04-10 00:30 | 199 | 199
2018-04-10 01:00 | 188 | 188
2018-04-10 01:30 | 180 | 180
2018-04-10 02:00 | 184 | 184
2018-04-10 02:30 | 185 | 184
2018-04-10 03:00 | 183 | 183
2018-04-10 03:30 | 183 | 182
2018-04-10 04:00 | 186 | 186
2018-04-10 04:30 | 190 | 190
2018-04-10 05:00 | 202 | 202
2018-04-10 05:30 | 204 | 204
2018-04-10 06:00 | 214 | 214
2018-04-10 06:30 | 225 | 225
2018-04-10 07:00 | 238 | 238
2018-04-10 07:30 | 246 | 244
2018-04-10 08:00 | 250 | 249
2018-04-10 08:30 | 252 | 252
2018-04-10 09:00 | 257 | 256
2018-04-10 09:30 | 261 | 260
2018-04-10 10:00 | 264 | 262
2018-04-10 10:30 | 259 | 258
2018-04-10 11:00 | 255 | 255
2018-04-10 11:30 | 258 | 258
2018-04-10 12:00 | 261 | 260
2018-04-10 12:30 | 266 | 265
2018-04-10 13:00 | 278 | 278
2018-04-10 13:30 | 292 | 292
2018-04-10 14:00 | 300 | 297
2018-04-10 14:30 | 296 | 294
2018-04-10 15:00 | 299 | 296
2018-04-10 15:30 | 304 | 301
2018-04-10 16:00 | 306 | 302
2018-04-10 16:30 | 312 | 308
2018-04-10 17:00 | 312 | 309
2018-04-10 17:30 | 313 | 310
2018-04-10 18:00 | 315 | 313
2018-04-10 18:30 | 311 | 309
2018-04-10 19:00 | 302 | 298
2018-04-10 19:30 | 296 | 292
2018-04-10 20:00 | 285 | 283
2018-04-10 20:30 | 272 | 272
2018-04-10 21:00 | 264 | 263
2018-04-10 21:30 | 258 | 257
2018-04-10 22:00 | 256 | 255
2018-04-10 22:30 | 255 | 255
2018-04-10 23:00 | 246 | 245
2018-04-10 23:30 | 235 | 234
2018-04-11 | 215 | 215
2018-04-11 00:30 | 211 | 211
2018-04-11 01:00 | 208 | 208
2018-04-11 01:30 | 200 | 200
2018-04-11 02:00 | 192 | 192
2018-04-11 02:30 | 190 | 190
2018-04-11 03:00 | 192 | 192
2018-04-11 03:30 | 190 | 190
2018-04-11 04:00 | 191 | 191
2018-04-11 04:30 | 193 | 193
2018-04-11 05:00 | 202 | 202
2018-04-11 05:30 | 209 | 209
2018-04-11 06:00 | 219 | 219
2018-04-11 06:30 | 235 | 235
2018-04-11 07:00 | 250 | 250
2018-04-11 07:30 | 265 | 265
2018-04-11 08:00 | 270 | 270
2018-04-11 08:30 | 273 | 272
2018-04-11 09:00 | 277 | 277
2018-04-11 09:30 | 279 | 278
2018-04-11 10:00 | 274 | 274
2018-04-11 10:30 | 275 | 274
2018-04-11 11:00 | 276 | 276
2018-04-11 11:30 | 268 | 268
2018-04-11 12:00 | 266 | 265
2018-04-11 12:30 | 264 | 264
2018-04-11 13:00 | 269 | 268
2018-04-11 13:30 | 282 | 282
2018-04-11 14:00 | 287 | 286
2018-04-11 14:30 | 299 | 299
2018-04-11 15:00 | 303 | 302
2018-04-11 15:30 | 310 | 309
2018-04-11 16:00 | 310 | 310
2018-04-11 16:30 | 310 | 309
2018-04-11 17:00 | 307 | 305
2018-04-11 17:30 | 309 | 308
2018-04-11 18:00 | 312 | 311
2018-04-11 18:30 | 308 | 307
2018-04-11 19:00 | 297 | 297
2018-04-11 19:30 | 290 | 290
2018-04-11 20:00 | 281 | 281
2018-04-11 20:30 | 268 | 268
2018-04-11 21:00 | 258 | 258
2018-04-11 21:30 | 248 | 248
2018-04-11 22:00 | 242 | 241
2018-04-11 22:30 | 248 | 247
2018-04-11 23:00 | 239 | 238
2018-04-11 23:30 | 226 | 225
2018-04-12 | 210 | 207
2018-04-12 00:30 | 196 | 195
2018-04-12 01:00 | 189 | 188
2018-04-12 01:30 | 195 | 193
2018-04-12 02:00 | 196 | 195
2018-04-12 02:30 | 192 | 190
2018-04-12 03:00 | 191 | 189
2018-04-12 03:30 | 191 | 190
2018-04-12 04:00 | 193 | 192
2018-04-12 04:30 | 194 | 193
2018-04-12 05:00 | 200 | 199
2018-04-12 05:30 | 205 | 205
2018-04-12 06:00 | 215 | 215
2018-04-12 06:30 | 230 | 230
2018-04-12 07:00 | 243 | 243
2018-04-12 07:30 | 249 | 249
2018-04-12 08:00 | 259 | 259
2018-04-12 08:30 | 262 | 262
2018-04-12 09:00 | 259 | 259
2018-04-12 09:30 | 252 | 252
2018-04-12 10:00 | 251 | 250
2018-04-12 10:30 | 254 | 253
2018-04-12 11:00 | 255 | 254
2018-04-12 11:30 | 253 | 253
2018-04-12 12:00 | 255 | 254
2018-04-12 12:30 | 260 | 259
2018-04-12 13:00 | 266 | 265
2018-04-12 13:30 | 268 | 268
2018-04-12 14:00 | 275 | 274
2018-04-12 14:30 | 275 | 274
2018-04-12 15:00 | 283 | 282
2018-04-12 15:30 | 291 | 290
2018-04-12 16:00 | 275 | 274
2018-04-12 16:30 | 301 | 300
2018-04-12 17:00 | 312 | 311
2018-04-12 17:30 | 322 | 321
2018-04-12 18:00 | 334 | 330
2018-04-12 18:30 | 326 | 322
2018-04-12 19:00 | 312 | 310
2018-04-12 19:30 | 308 | 307
2018-04-12 20:00 | 298 | 297
2018-04-12 20:30 | 287 | 287
2018-04-12 21:00 | 273 | 273
2018-04-12 21:30 | 263 | 262
2018-04-12 22:00 | 262 | 261
2018-04-12 22:30 | 253 | 252
2018-04-12 23:00 | 239 | 239
2018-04-12 23:30 | 224 | 224
2018-04-13 | 212 | 211
2018-04-13 00:30 | 204 | 203
2018-04-13 01:00 | 202 | 201
2018-04-13 01:30 | 199 | 198
2018-04-13 02:00 | 197 | 196
2018-04-13 02:30 | 193 | 192
2018-04-13 03:00 | 192 | 191
2018-04-13 03:30 | 192 | 191
2018-04-13 04:00 | 193 | 191
2018-04-13 04:30 | 196 | 195
2018-04-13 05:00 | 205 | 205
2018-04-13 05:30 | 212 | 211
2018-04-13 06:00 | 216 | 216
2018-04-13 06:30 | 229 | 229
2018-04-13 07:00 | 243 | 242
2018-04-13 07:30 | 256 | 256
2018-04-13 08:00 | 262 | 262
2018-04-13 08:30 | 267 | 267
2018-04-13 09:00 | 271 | 271
2018-04-13 09:30 | 267 | 267
2018-04-13 10:00 | 267 | 267
2018-04-13 10:30 | 261 | 261
2018-04-13 11:00 | 252 | 252
2018-04-13 11:30 | 240 | 240
2018-04-13 12:00 | 227 | 227
2018-04-13 12:30 | 231 | 231
2018-04-13 13:00 | 263 | 263
2018-04-13 13:30 | 263 | 263
2018-04-13 14:00 | 267 | 267
2018-04-13 14:30 | 274 | 274
2018-04-13 15:00 | 281 | 281
2018-04-13 15:30 | 283 | 283
2018-04-13 16:00 | 296 | 296
2018-04-13 16:30 | 292 | 292
2018-04-13 17:00 | 297 | 297
2018-04-13 17:30 | 301 | 300
2018-04-13 18:00 | 297 | 297
2018-04-13 18:30 | 302 | 302
2018-04-13 19:00 | 295 | 295
2018-04-13 19:30 | 294 | 294
2018-04-13 20:00 | 290 | 289
2018-04-13 20:30 | 281 | 280
2018-04-13 21:00 | 273 | 273
2018-04-13 21:30 | 265 | 265
2018-04-13 22:00 | 263 | 263
2018-04-13 22:30 | 261 | 261
2018-04-13 23:00 | 243 | 243
2018-04-13 23:30 | 229 | 228
2018-04-14 | 215 | 214
2018-04-14 00:30 | 209 | 208
2018-04-14 01:00 | 204 | 202
2018-04-14 01:30 | 198 | 195
2018-04-14 02:00 | 190 | 187
2018-04-14 02:30 | 183 | 180
2018-04-14 03:00 | 178 | 175
2018-04-14 03:30 | 148 | 146
2018-04-14 04:00 | 150 | 148
2018-04-14 04:30 | 141 | 139
2018-04-14 05:00 | 146 | 144
2018-04-14 05:30 | 164 | 163
2018-04-14 06:00 | 197 | 196
2018-04-14 06:30 | 199 | 198
2018-04-14 07:00 | 217 | 216
2018-04-14 07:30 | 214 | 214
2018-04-14 08:00 | 218 | 218
2018-04-14 08:30 | 230 | 230
2018-04-14 09:00 | 252 | 252
2018-04-14 09:30 | 269 | 269
2018-04-14 10:00 | 273 | 272
2018-04-14 10:30 | 276 | 276
2018-04-14 11:00 | 274 | 273
2018-04-14 11:30 | 269 | 268
2018-04-14 12:00 | 264 | 264
2018-04-14 12:30 | 263 | 262
2018-04-14 13:00 | 255 | 254
2018-04-14 13:30 | 263 | 262
2018-04-14 14:00 | 249 | 248
2018-04-14 14:30 | 245 | 243
2018-04-14 15:00 | 256 | 255
2018-04-14 15:30 | 272 | 271
2018-04-14 16:00 | 276 | 275
2018-04-14 16:30 | 278 | 277
2018-04-14 17:00 | 280 | 279
2018-04-14 17:30 | 285 | 285
2018-04-14 18:00 | 281 | 281
2018-04-14 18:30 | 274 | 273
2018-04-14 19:00 | 249 | 249
2018-04-14 19:30 | 262 | 262
2018-04-14 20:00 | 274 | 274
2018-04-14 20:30 | 270 | 269
2018-04-14 21:00 | 263 | 263
2018-04-14 21:30 | 254 | 253
2018-04-14 22:00 | 251 | 251
2018-04-14 22:30 | 249 | 249
2018-04-14 23:00 | 231 | 230
2018-04-14 23:30 | 223 | 222
2018-04-15 | 202 | 199
2018-04-15 00:30 | 201 | 198
2018-04-15 01:00 | 189 | 186
2018-04-15 01:30 | 165 | 164
2018-04-15 02:00 | 173 | 172
2018-04-15 02:30 | 142 | 140
2018-04-15 03:00 | 124 | 123
2018-04-15 03:30 | 141 | 139
2018-04-15 04:00 | 132 | 130
2018-04-15 04:30 | 133 | 131
2018-04-15 05:00 | 147 | 145
2018-04-15 05:30 | 153 | 152
2018-04-15 06:00 | 191 | 189
2018-04-15 06:30 | 197 | 195
2018-04-15 07:00 | 205 | 204
2018-04-15 07:30 | 210 | 209
2018-04-15 08:00 | 217 | 217
2018-04-15 08:30 | 222 | 222
2018-04-15 09:00 | 225 | 225
2018-04-15 09:30 | 227 | 227
2018-04-15 10:00 | 228 | 228
2018-04-15 10:30 | 228 | 228
2018-04-15 11:00 | 233 | 232
2018-04-15 11:30 | 235 | 235
2018-04-15 12:00 | 240 | 240
2018-04-15 12:30 | 247 | 247
2018-04-15 13:00 | 257 | 257
2018-04-15 13:30 | 273 | 273
2018-04-15 14:00 | 285 | 284
2018-04-15 14:30 | 289 | 289
2018-04-15 15:00 | 295 | 294
2018-04-15 15:30 | 303 | 303
2018-04-15 16:00 | 311 | 310
2018-04-15 16:30 | 317 | 317
2018-04-15 17:00 | 307 | 307
2018-04-15 17:30 | 315 | 314
2018-04-15 18:00 | 318 | 318
2018-04-15 18:30 | 315 | 315
2018-04-15 19:00 | 303 | 302
2018-04-15 19:30 | 295 | 294
2018-04-15 20:00 | 282 | 282
2018-04-15 20:30 | 273 | 273
2018-04-15 21:00 | 265 | 264
2018-04-15 21:30 | 233 | 232
2018-04-15 22:00 | 253 | 251
2018-04-15 22:30 | 258 | 256
2018-04-15 23:00 | 242 | 240
2018-04-15 23:30 | 226 | 224
2018-04-16 | 207 | 205
2018-04-16 00:30 | 197 | 195
2018-04-16 01:00 | 163 | 161
2018-04-16 01:30 | 156 | 155
2018-04-16 02:00 | 171 | 169
2018-04-16 02:30 | 179 | 177
2018-04-16 03:00 | 178 | 177
2018-04-16 03:30 | 178 | 176
2018-04-16 04:00 | 181 | 179
2018-04-16 04:30 | 185 | 184
2018-04-16 05:00 | 194 | 193
2018-04-16 05:30 | 205 | 204
2018-04-16 06:00 | 219 | 218
2018-04-16 06:30 | 230 | 230
2018-04-16 07:00 | 248 | 248
2018-04-16 07:30 | 258 | 258
2018-04-16 08:00 | 264 | 264
2018-04-16 08:30 | 270 | 270
2018-04-16 09:00 | 271 | 270
2018-04-16 09:30 | 271 | 271
2018-04-16 10:00 | 279 | 278
2018-04-16 10:30 | 278 | 278
2018-04-16 11:00 | 277 | 276
2018-04-16 11:30 | 280 | 278
2018-04-16 12:00 | 280 | 278
2018-04-16 12:30 | 283 | 282
2018-04-16 13:00 | 284 | 283
2018-04-16 13:30 | 289 | 288
2018-04-16 14:00 | 291 | 289
2018-04-16 14:30 | 299 | 298
2018-04-16 15:00 | 305 | 304
2018-04-16 15:30 | 314 | 312
2018-04-16 16:00 | 320 | 318
2018-04-16 16:30 | 326 | 324
2018-04-16 17:00 | 328 | 325
2018-04-16 17:30 | 337 | 335
2018-04-16 18:00 | 342 | 339
2018-04-16 18:30 | 334 | 331
2018-04-16 19:00 | 323 | 320
2018-04-16 19:30 | 316 | 315
2018-04-16 20:00 | 309 | 308
2018-04-16 20:30 | 294 | 293
2018-04-16 21:00 | 280 | 279
2018-04-16 21:30 | 272 | 271
2018-04-16 22:00 | 269 | 268
2018-04-16 22:30 | 260 | 258
2018-04-16 23:00 | 250 | 247
2018-04-16 23:30 | 235 | 231
2018-04-17 | 214 | 211
2018-04-17 00:30 | 205 | 202
2018-04-17 01:00 | 196 | 193
2018-04-17 01:30 | 194 | 192
2018-04-17 02:00 | 191 | 189
2018-04-17 02:30 | 191 | 190
2018-04-17 03:00 | 189 | 188
2018-04-17 03:30 | 188 | 187
2018-04-17 04:00 | 186 | 184
2018-04-17 04:30 | 190 | 189
2018-04-17 05:00 | 197 | 196
2018-04-17 05:30 | 202 | 201
2018-04-17 06:00 | 218 | 217
2018-04-17 06:30 | 220 | 220
2018-04-17 07:00 | 227 | 227
2018-04-17 07:30 | 229 | 229
2018-04-17 08:00 | 227 | 227
2018-04-17 08:30 | 226 | 226
2018-04-17 09:00 | 229 | 229
2018-04-17 09:30 | 230 | 230
2018-04-17 10:00 | 231 | 230
2018-04-17 10:30 | 231 | 230
2018-04-17 11:00 | 232 | 231
2018-04-17 11:30 | 237 | 236
2018-04-17 12:00 | 243 | 242
2018-04-17 12:30 | 248 | 247
2018-04-17 13:00 | 253 | 253
2018-04-17 13:30 | 261 | 261
2018-04-17 14:00 | 268 | 267
2018-04-17 14:30 | 272 | 272
2018-04-17 15:00 | 281 | 280
2018-04-17 15:30 | 297 | 296
2018-04-17 16:00 | 305 | 304
2018-04-17 16:30 | 309 | 307
2018-04-17 17:00 | 313 | 311
2018-04-17 17:30 | 327 | 325
2018-04-17 18:00 | 329 | 328
2018-04-17 18:30 | 325 | 323
2018-04-17 19:00 | 308 | 306
2018-04-17 19:30 | 304 | 302
2018-04-17 20:00 | 297 | 295
2018-04-17 20:30 | 287 | 285
2018-04-17 21:00 | 276 | 275
2018-04-17 21:30 | 265 | 265
2018-04-17 22:00 | 259 | 259
2018-04-17 22:30 | 251 | 250
2018-04-17 23:00 | 239 | 238
2018-04-17 23:30 | 226 | 225
2018-04-18 | 213 | 211
2018-04-18 00:30 | 205 | 203
2018-04-18 01:00 | 203 | 200
2018-04-18 01:30 | 200 | 197
2018-04-18 02:00 | 198 | 195
2018-04-18 02:30 | 195 | 192
2018-04-18 03:00 | 195 | 191
2018-04-18 03:30 | 195 | 191
2018-04-18 04:00 | 197 | 194
2018-04-18 04:30 | 202 | 199
2018-04-18 05:00 | 210 | 208
2018-04-18 05:30 | 228 | 226
2018-04-18 06:00 | 225 | 224
2018-04-18 06:30 | 235 | 235
2018-04-18 07:00 | 237 | 236
2018-04-18 07:30 | 249 | 249
2018-04-18 08:00 | 248 | 248
2018-04-18 08:30 | 253 | 253
2018-04-18 09:00 | 260 | 258
2018-04-18 09:30 | 246 | 244
2018-04-18 10:00 | 240 | 239
2018-04-18 10:30 | 246 | 245
2018-04-18 11:00 | 249 | 247
2018-04-18 11:30 | 245 | 244
2018-04-18 12:00 | 244 | 242
2018-04-18 12:30 | 238 | 236
2018-04-18 13:00 | 235 | 233
2018-04-18 13:30 | 235 | 234
2018-04-18 14:00 | 242 | 242
2018-04-18 14:30 | 242 | 242
2018-04-18 15:00 | 247 | 247
2018-04-18 15:30 | 268 | 268
2018-04-18 16:00 | 279 | 278
2018-04-18 16:30 | 294 | 294
2018-04-18 17:00 | 303 | 302
2018-04-18 17:30 | 314 | 313
2018-04-18 18:00 | 313 | 313
2018-04-18 18:30 | 307 | 307
2018-04-18 19:00 | 302 | 301
2018-04-18 19:30 | 301 | 300
2018-04-18 20:00 | 294 | 293
2018-04-18 20:30 | 265 | 265
2018-04-18 21:00 | 260 | 260
2018-04-18 21:30 | 252 | 252
2018-04-18 22:00 | 249 | 249
2018-04-18 22:30 | 244 | 243
2018-04-18 23:00 | 229 | 229
2018-04-18 23:30 | 218 | 218
2018-04-19 | 204 | 203
2018-04-19 00:30 | 194 | 193
2018-04-19 01:00 | 191 | 190
2018-04-19 01:30 | 184 | 183
2018-04-19 02:00 | 184 | 183
2018-04-19 02:30 | 184 | 182
2018-04-19 03:00 | 183 | 181
2018-04-19 03:30 | 182 | 181
2018-04-19 04:00 | 183 | 182
2018-04-19 04:30 | 186 | 184
2018-04-19 05:00 | 193 | 192
2018-04-19 05:30 | 204 | 204
2018-04-19 06:00 | 217 | 217
2018-04-19 06:30 | 230 | 230
2018-04-19 07:00 | 248 | 248
2018-04-19 07:30 | 255 | 255
2018-04-19 08:00 | 255 | 255
2018-04-19 08:30 | 248 | 248
2018-04-19 09:00 | 253 | 253
2018-04-19 09:30 | 249 | 249
2018-04-19 10:00 | 251 | 251
2018-04-19 10:30 | 251 | 251
2018-04-19 11:00 | 250 | 249
2018-04-19 11:30 | 241 | 240
2018-04-19 12:00 | 244 | 243
2018-04-19 12:30 | 246 | 246
2018-04-19 13:00 | 251 | 250
2018-04-19 13:30 | 256 | 256
2018-04-19 14:00 | 266 | 266
2018-04-19 14:30 | 272 | 272
2018-04-19 15:00 | 280 | 280
2018-04-19 15:30 | 291 | 291
2018-04-19 16:00 | 300 | 300
2018-04-19 16:30 | 311 | 311
2018-04-19 17:00 | 317 | 317
2018-04-19 17:30 | 322 | 322
2018-04-19 18:00 | 322 | 322
2018-04-19 18:30 | 313 | 313
2018-04-19 19:00 | 291 | 291
2018-04-19 19:30 | 293 | 292
2018-04-19 20:00 | 289 | 288
2018-04-19 20:30 | 282 | 282
2018-04-19 21:00 | 267 | 266
2018-04-19 21:30 | 261 | 258
2018-04-19 22:00 | 250 | 249
2018-04-19 22:30 | 242 | 241
2018-04-19 23:00 | 225 | 225
2018-04-19 23:30 | 211 | 210
2018-04-20 | 201 | 200
2018-04-20 00:30 | 191 | 190
2018-04-20 01:00 | 185 | 184
2018-04-20 01:30 | 180 | 178
2018-04-20 02:00 | 179 | 178
2018-04-20 02:30 | 181 | 179
2018-04-20 03:00 | 178 | 177
2018-04-20 03:30 | 177 | 175
2018-04-20 04:00 | 175 | 174
2018-04-20 04:30 | 177 | 175
2018-04-20 05:00 | 183 | 182
2018-04-20 05:30 | 196 | 195
2018-04-20 06:00 | 210 | 210
2018-04-20 06:30 | 228 | 228
2018-04-20 07:00 | 242 | 242
2018-04-20 07:30 | 253 | 253
2018-04-20 08:00 | 257 | 257
2018-04-20 08:30 | 257 | 257
2018-04-20 09:00 | 259 | 259
2018-04-20 09:30 | 262 | 262
2018-04-20 10:00 | 263 | 263
2018-04-20 10:30 | 257 | 257
2018-04-20 11:00 | 257 | 257
2018-04-20 11:30 | 267 | 267
2018-04-20 12:00 | 276 | 276
2018-04-20 12:30 | 280 | 280
2018-04-20 13:00 | 278 | 278
2018-04-20 13:30 | 274 | 274
2018-04-20 14:00 | 276 | 276
2018-04-20 14:30 | 278 | 278
2018-04-20 15:00 | 278 | 278
2018-04-20 15:30 | 285 | 285
2018-04-20 16:00 | 288 | 288
2018-04-20 16:30 | 295 | 295
2018-04-20 17:00 | 295 | 295
2018-04-20 17:30 | 298 | 298
2018-04-20 18:00 | 295 | 295
2018-04-20 18:30 | 287 | 287
2018-04-20 19:00 | 272 | 271
2018-04-20 19:30 | 269 | 269
2018-04-20 20:00 | 268 | 268
2018-04-20 20:30 | 260 | 260
2018-04-20 21:00 | 251 | 251
2018-04-20 21:30 | 242 | 242
2018-04-20 22:00 | 236 | 236
2018-04-20 22:30 | 231 | 231
2018-04-20 23:00 | 219 | 219
2018-04-20 23:30 | 207 | 207
2018-04-21 | 193 | 193
2018-04-21 00:30 | 189 | 189
2018-04-21 01:00 | 181 | 181
2018-04-21 01:30 | 173 | 173
2018-04-21 02:00 | 166 | 166
2018-04-21 02:30 | 163 | 163
2018-04-21 03:00 | 163 | 163
2018-04-21 03:30 | 163 | 163
2018-04-21 04:00 | 163 | 163
2018-04-21 04:30 | 169 | 169
2018-04-21 05:00 | 173 | 173
2018-04-21 05:30 | 180 | 180
2018-04-21 06:00 | 190 | 190
2018-04-21 06:30 | 202 | 202
2018-04-21 07:00 | 216 | 216
2018-04-21 07:30 | 226 | 226
2018-04-21 08:00 | 229 | 229
2018-04-21 08:30 | 233 | 233
2018-04-21 09:00 | 238 | 238
2018-04-21 09:30 | 238 | 237
2018-04-21 10:00 | 239 | 238
2018-04-21 10:30 | 237 | 236
2018-04-21 11:00 | 240 | 239
2018-04-21 11:30 | 244 | 243
2018-04-21 12:00 | 240 | 238
2018-04-21 12:30 | 234 | 233
2018-04-21 13:00 | 233 | 232
2018-04-21 13:30 | 244 | 244
2018-04-21 14:00 | 248 | 248
2018-04-21 14:30 | 242 | 242
2018-04-21 15:00 | 249 | 249
2018-04-21 15:30 | 249 | 249
2018-04-21 16:00 | 251 | 250
2018-04-21 16:30 | 258 | 257
2018-04-21 17:00 | 256 | 255
2018-04-21 17:30 | 263 | 263
2018-04-21 18:00 | 259 | 259
2018-04-21 18:30 | 256 | 256
2018-04-21 19:00 | 250 | 250
2018-04-21 19:30 | 250 | 249
2018-04-21 20:00 | 248 | 247
2018-04-21 20:30 | 239 | 239
2018-04-21 21:00 | 234 | 234
2018-04-21 21:30 | 230 | 230
2018-04-21 22:00 | 226 | 226
2018-04-21 22:30 | 224 | 224
2018-04-21 23:00 | 216 | 215
2018-04-21 23:30 | 205 | 204
2018-04-22 | 193 | 192
2018-04-22 00:30 | 186 | 185
2018-04-22 01:00 | 180 | 178
2018-04-22 01:30 | 174 | 172
2018-04-22 02:00 | 171 | 168
2018-04-22 02:30 | 172 | 169
2018-04-22 03:00 | 170 | 167
2018-04-22 03:30 | 171 | 168
2018-04-22 04:00 | 167 | 164
2018-04-22 04:30 | 169 | 166
2018-04-22 05:00 | 170 | 167
2018-04-22 05:30 | 177 | 174
2018-04-22 06:00 | 185 | 182
2018-04-22 06:30 | 195 | 193
2018-04-22 07:00 | 202 | 201
2018-04-22 07:30 | 212 | 211
2018-04-22 08:00 | 220 | 220
2018-04-22 08:30 | 223 | 223
2018-04-22 09:00 | 230 | 229
2018-04-22 09:30 | 231 | 231
2018-04-22 10:00 | 224 | 224
2018-04-22 10:30 | 223 | 223
2018-04-22 11:00 | 232 | 232
2018-04-22 11:30 | 215 | 215
2018-04-22 12:00 | 221 | 221
2018-04-22 12:30 | 220 | 220
2018-04-22 13:00 | 219 | 219
2018-04-22 13:30 | 221 | 221
2018-04-22 14:00 | 226 | 226
2018-04-22 14:30 | 235 | 235
2018-04-22 15:00 | 240 | 240
2018-04-22 15:30 | 251 | 249
2018-04-22 16:00 | 257 | 255
2018-04-22 16:30 | 264 | 261
2018-04-22 17:00 | 267 | 264
2018-04-22 17:30 | 280 | 279
2018-04-22 18:00 | 279 | 278
2018-04-22 18:30 | 269 | 269
2018-04-22 19:00 | 260 | 260
2018-04-22 19:30 | 257 | 257
2018-04-22 20:00 | 251 | 251
2018-04-22 20:30 | 243 | 243
2018-04-22 21:00 | 236 | 236
2018-04-22 21:30 | 230 | 230
2018-04-22 22:00 | 231 | 231
2018-04-22 22:30 | 233 | 233
2018-04-22 23:00 | 224 | 224
2018-04-22 23:30 | 218 | 218
2018-04-23 | 204 | 204
2018-04-23 00:30 | 177 | 177
2018-04-23 01:00 | 173 | 173
2018-04-23 01:30 | 168 | 168
2018-04-23 02:00 | 166 | 166
2018-04-23 02:30 | 167 | 166
2018-04-23 03:00 | 167 | 166
2018-04-23 03:30 | 165 | 165
2018-04-23 04:00 | 163 | 162
2018-04-23 04:30 | 165 | 165
2018-04-23 05:00 | 179 | 179
2018-04-23 05:30 | 192 | 192
2018-04-23 06:00 | 211 | 211
2018-04-23 06:30 | 227 | 227
2018-04-23 07:00 | 242 | 242
2018-04-23 07:30 | 247 | 247
2018-04-23 08:00 | 245 | 245
2018-04-23 08:30 | 244 | 244
2018-04-23 09:00 | 242 | 242
2018-04-23 09:30 | 241 | 241
2018-04-23 10:00 | 241 | 241
2018-04-23 10:30 | 240 | 240
2018-04-23 11:00 | 238 | 238
2018-04-23 11:30 | 240 | 240
2018-04-23 12:00 | 242 | 242
2018-04-23 12:30 | 250 | 250
2018-04-23 13:00 | 255 | 255
2018-04-23 13:30 | 250 | 249
2018-04-23 14:00 | 253 | 253
2018-04-23 14:30 | 251 | 251
2018-04-23 15:00 | 253 | 253
2018-04-23 15:30 | 255 | 255
2018-04-23 16:00 | 265 | 265
2018-04-23 16:30 | 274 | 273
2018-04-23 17:00 | 281 | 280
2018-04-23 17:30 | 294 | 294
2018-04-23 18:00 | 293 | 293
2018-04-23 18:30 | 287 | 286
2018-04-23 19:00 | 273 | 272
2018-04-23 19:30 | 267 | 267
2018-04-23 20:00 | 262 | 262
2018-04-23 20:30 | 252 | 252
2018-04-23 21:00 | 244 | 244
2018-04-23 21:30 | 234 | 233
2018-04-23 22:00 | 232 | 232
2018-04-23 22:30 | 227 | 227
2018-04-23 23:00 | 216 | 215
2018-04-23 23:30 | 203 | 202
2018-04-24 | 189 | 188
2018-04-24 00:30 | 178 | 176
2018-04-24 01:00 | 176 | 174
2018-04-24 01:30 | 172 | 170
2018-04-24 02:00 | 171 | 169
2018-04-24 02:30 | 171 | 169
2018-04-24 03:00 | 170 | 168
2018-04-24 03:30 | 169 | 167
2018-04-24 04:00 | 165 | 163
2018-04-24 04:30 | 167 | 165
2018-04-24 05:00 | 176 | 175
2018-04-24 05:30 | 191 | 191
2018-04-24 06:00 | 213 | 213
2018-04-24 06:30 | 228 | 228
2018-04-24 07:00 | 241 | 241
2018-04-24 07:30 | 246 | 246
2018-04-24 08:00 | 252 | 251
2018-04-24 08:30 | 247 | 247
2018-04-24 09:00 | 247 | 246
2018-04-24 09:30 | 246 | 246
2018-04-24 10:00 | 245 | 245
2018-04-24 10:30 | 241 | 241
2018-04-24 11:00 | 238 | 238
2018-04-24 11:30 | 240 | 240
2018-04-24 12:00 | 245 | 245
2018-04-24 12:30 | 256 | 256
2018-04-24 13:00 | 274 | 273
2018-04-24 13:30 | 275 | 274
2018-04-24 14:00 | 270 | 269
2018-04-24 14:30 | 266 | 264
2018-04-24 15:00 | 271 | 270
2018-04-24 15:30 | 276 | 274
2018-04-24 16:00 | 282 | 279
2018-04-24 16:30 | 286 | 283
2018-04-24 17:00 | 296 | 294
2018-04-24 17:30 | 308 | 306
2018-04-24 18:00 | 309 | 307
2018-04-24 18:30 | 308 | 306
2018-04-24 19:00 | 287 | 286
2018-04-24 19:30 | 278 | 278
2018-04-24 20:00 | 268 | 268
2018-04-24 20:30 | 256 | 256
2018-04-24 21:00 | 245 | 245
2018-04-24 21:30 | 241 | 240
2018-04-24 22:00 | 232 | 232
2018-04-24 22:30 | 230 | 229
2018-04-24 23:00 | 220 | 219
2018-04-24 23:30 | 214 | 213
2018-04-25 | 197 | 196
2018-04-25 00:30 | 191 | 189
2018-04-25 01:00 | 187 | 185
2018-04-25 01:30 | 184 | 182
2018-04-25 02:00 | 179 | 177
2018-04-25 02:30 | 178 | 176
2018-04-25 03:00 | 177 | 174
2018-04-25 03:30 | 178 | 176
2018-04-25 04:00 | 179 | 177
2018-04-25 04:30 | 178 | 176
2018-04-25 05:00 | 176 | 174
2018-04-25 05:30 | 184 | 182
2018-04-25 06:00 | 188 | 186
2018-04-25 06:30 | 194 | 192
2018-04-25 07:00 | 204 | 203
2018-04-25 07:30 | 209 | 209
2018-04-25 08:00 | 217 | 217
2018-04-25 08:30 | 221 | 221
2018-04-25 09:00 | 225 | 225
2018-04-25 09:30 | 229 | 229
2018-04-25 10:00 | 237 | 237
2018-04-25 10:30 | 247 | 247
2018-04-25 11:00 | 242 | 242
2018-04-25 11:30 | 234 | 234
2018-04-25 12:00 | 230 | 230
2018-04-25 12:30 | 230 | 230
2018-04-25 13:00 | 234 | 234
2018-04-25 13:30 | 236 | 236
2018-04-25 14:00 | 237 | 237
2018-04-25 14:30 | 236 | 236
2018-04-25 15:00 | 235 | 235
2018-04-25 15:30 | 240 | 240
2018-04-25 16:00 | 240 | 240
2018-04-25 16:30 | 245 | 245
2018-04-25 17:00 | 255 | 255
2018-04-25 17:30 | 269 | 269
2018-04-25 18:00 | 275 | 275
2018-04-25 18:30 | 269 | 269
2018-04-25 19:00 | 259 | 258
2018-04-25 19:30 | 258 | 258
2018-04-25 20:00 | 254 | 254
2018-04-25 20:30 | 245 | 244
2018-04-25 21:00 | 234 | 234
2018-04-25 21:30 | 227 | 226
2018-04-25 22:00 | 221 | 220
2018-04-25 22:30 | 218 | 218
2018-04-25 23:00 | 209 | 208
2018-04-25 23:30 | 203 | 201
2018-04-26 | 188 | 187
2018-04-26 00:30 | 183 | 181
2018-04-26 01:00 | 179 | 177
2018-04-26 01:30 | 178 | 176
2018-04-26 02:00 | 176 | 174
2018-04-26 02:30 | 175 | 173
2018-04-26 03:00 | 173 | 171
2018-04-26 03:30 | 174 | 172
2018-04-26 04:00 | 178 | 176
2018-04-26 04:30 | 180 | 178
2018-04-26 05:00 | 188 | 187
2018-04-26 05:30 | 201 | 200
2018-04-26 06:00 | 216 | 216
2018-04-26 06:30 | 236 | 236
2018-04-26 07:00 | 252 | 252
2018-04-26 07:30 | 259 | 259
2018-04-26 08:00 | 268 | 267
2018-04-26 08:30 | 264 | 261
2018-04-26 09:00 | 261 | 259
2018-04-26 09:30 | 257 | 255
2018-04-26 10:00 | 251 | 250
2018-04-26 10:30 | 250 | 248
2018-04-26 11:00 | 251 | 250
2018-04-26 11:30 | 247 | 246
2018-04-26 12:00 | 240 | 239
2018-04-26 12:30 | 249 | 248
2018-04-26 13:00 | 262 | 261
2018-04-26 13:30 | 263 | 262
2018-04-26 14:00 | 246 | 245
2018-04-26 14:30 | 249 | 248
2018-04-26 15:00 | 254 | 252
2018-04-26 15:30 | 274 | 272
2018-04-26 16:00 | 282 | 280
2018-04-26 16:30 | 292 | 290
2018-04-26 17:00 | 299 | 298
2018-04-26 17:30 | 318 | 317
2018-04-26 18:00 | 316 | 315
2018-04-26 18:30 | 312 | 310
2018-04-26 19:00 | 298 | 296
2018-04-26 19:30 | 296 | 293
2018-04-26 20:00 | 288 | 287
2018-04-26 20:30 | 274 | 274
2018-04-26 21:00 | 258 | 257
2018-04-26 21:30 | 246 | 246
2018-04-26 22:00 | 243 | 242
2018-04-26 22:30 | 235 | 234
2018-04-26 23:00 | 224 | 224
2018-04-26 23:30 | 213 | 213
2018-04-27 | 196 | 196
2018-04-27 00:30 | 186 | 186
2018-04-27 01:00 | 180 | 179
2018-04-27 01:30 | 176 | 175
2018-04-27 02:00 | 173 | 172
2018-04-27 02:30 | 173 | 172
2018-04-27 03:00 | 175 | 174
2018-04-27 03:30 | 175 | 175
2018-04-27 04:00 | 174 | 174
2018-04-27 04:30 | 176 | 175
2018-04-27 05:00 | 186 | 186
2018-04-27 05:30 | 199 | 199
2018-04-27 06:00 | 215 | 215
2018-04-27 06:30 | 227 | 227
2018-04-27 07:00 | 245 | 245
2018-04-27 07:30 | 253 | 253
2018-04-27 08:00 | 257 | 257
2018-04-27 08:30 | 258 | 258
2018-04-27 09:00 | 254 | 254
2018-04-27 09:30 | 253 | 253
2018-04-27 10:00 | 251 | 251
2018-04-27 10:30 | 247 | 247
2018-04-27 11:00 | 248 | 248
2018-04-27 11:30 | 247 | 246
2018-04-27 12:00 | 244 | 244
2018-04-27 12:30 | 242 | 242
2018-04-27 13:00 | 248 | 248
2018-04-27 13:30 | 256 | 256
2018-04-27 14:00 | 257 | 257
2018-04-27 14:30 | 260 | 260
2018-04-27 15:00 | 258 | 258
2018-04-27 15:30 | 266 | 266
2018-04-27 16:00 | 273 | 273
2018-04-27 16:30 | 275 | 274
2018-04-27 17:00 | 277 | 277
2018-04-27 17:30 | 290 | 289
2018-04-27 18:00 | 286 | 286
2018-04-27 18:30 | 280 | 279
2018-04-27 19:00 | 271 | 270
2018-04-27 19:30 | 268 | 267
2018-04-27 20:00 | 265 | 263
2018-04-27 20:30 | 253 | 253
2018-04-27 21:00 | 245 | 244
2018-04-27 21:30 | 239 | 239
2018-04-27 22:00 | 236 | 236
2018-04-27 22:30 | 226 | 225
2018-04-27 23:00 | 215 | 214
2018-04-27 23:30 | 205 | 203
2018-04-28 | 195 | 194
2018-04-28 00:30 | 187 | 186
2018-04-28 01:00 | 175 | 173
2018-04-28 01:30 | 171 | 168
2018-04-28 02:00 | 167 | 165
2018-04-28 02:30 | 166 | 163
2018-04-28 03:00 | 165 | 164
2018-04-28 03:30 | 162 | 162
2018-04-28 04:00 | 163 | 162
2018-04-28 04:30 | 163 | 163
2018-04-28 05:00 | 169 | 169
2018-04-28 05:30 | 176 | 176
2018-04-28 06:00 | 185 | 185
2018-04-28 06:30 | 194 | 193
2018-04-28 07:00 | 212 | 212
2018-04-28 07:30 | 227 | 227
2018-04-28 08:00 | 226 | 226
2018-04-28 08:30 | 241 | 241
2018-04-28 09:00 | 251 | 251
2018-04-28 09:30 | 245 | 245
2018-04-28 10:00 | 241 | 241
2018-04-28 10:30 | 223 | 223
2018-04-28 11:00 | 213 | 212
2018-04-28 11:30 | 221 | 221
2018-04-28 12:00 | 213 | 212
2018-04-28 12:30 | 209 | 209
2018-04-28 13:00 | 211 | 211
2018-04-28 13:30 | 235 | 235
2018-04-28 14:00 | 230 | 230
2018-04-28 14:30 | 224 | 224
2018-04-28 15:00 | 228 | 228
2018-04-28 15:30 | 234 | 234
2018-04-28 16:00 | 243 | 243
2018-04-28 16:30 | 254 | 254
2018-04-28 17:00 | 262 | 262
2018-04-28 17:30 | 269 | 269
2018-04-28 18:00 | 262 | 261
2018-04-28 18:30 | 261 | 260
2018-04-28 19:00 | 248 | 246
2018-04-28 19:30 | 246 | 244
2018-04-28 20:00 | 238 | 237
2018-04-28 20:30 | 230 | 230
2018-04-28 21:00 | 224 | 224
2018-04-28 21:30 | 220 | 220
2018-04-28 22:00 | 215 | 214
2018-04-28 22:30 | 216 | 216
2018-04-28 23:00 | 208 | 208
2018-04-28 23:30 | 198 | 197
2018-04-29 | 183 | 181
2018-04-29 00:30 | 178 | 176
2018-04-29 01:00 | 176 | 174
2018-04-29 01:30 | 173 | 172
2018-04-29 02:00 | 169 | 168
2018-04-29 02:30 | 163 | 162
2018-04-29 03:00 | 163 | 162
2018-04-29 03:30 | 163 | 162
2018-04-29 04:00 | 161 | 160
2018-04-29 04:30 | 160 | 160
2018-04-29 05:00 | 165 | 164
2018-04-29 05:30 | 170 | 169
2018-04-29 06:00 | 173 | 172
2018-04-29 06:30 | 179 | 179
2018-04-29 07:00 | 190 | 190
2018-04-29 07:30 | 200 | 200
2018-04-29 08:00 | 212 | 212
2018-04-29 08:30 | 217 | 217
2018-04-29 09:00 | 223 | 223
2018-04-29 09:30 | 218 | 218
2018-04-29 10:00 | 219 | 219
2018-04-29 10:30 | 228 | 227
2018-04-29 11:00 | 220 | 220
2018-04-29 11:30 | 211 | 211
2018-04-29 12:00 | 212 | 212
2018-04-29 12:30 | 215 | 215
2018-04-29 13:00 | 223 | 223
2018-04-29 13:30 | 227 | 227
2018-04-29 14:00 | 231 | 231
2018-04-29 14:30 | 228 | 228
2018-04-29 15:00 | 231 | 231
2018-04-29 15:30 | 237 | 237
2018-04-29 16:00 | 241 | 241
2018-04-29 16:30 | 249 | 249
2018-04-29 17:00 | 258 | 258
2018-04-29 17:30 | 273 | 273
2018-04-29 18:00 | 270 | 269
2018-04-29 18:30 | 265 | 264
2018-04-29 19:00 | 252 | 250
2018-04-29 19:30 | 246 | 246
2018-04-29 20:00 | 242 | 242
2018-04-29 20:30 | 233 | 233
2018-04-29 21:00 | 225 | 225
2018-04-29 21:30 | 212 | 211
2018-04-29 22:00 | 202 | 201
2018-04-29 22:30 | 198 | 197
2018-04-29 23:00 | 195 | 194
2018-04-29 23:30 | 189 | 187
2018-04-30 | 180 | 178
2018-04-30 00:30 | 172 | 171
2018-04-30 01:00 | 167 | 167
2018-04-30 01:30 | 165 | 164
2018-04-30 02:00 | 160 | 160
2018-04-30 02:30 | 155 | 154
2018-04-30 03:00 | 155 | 154
2018-04-30 03:30 | 155 | 154
2018-04-30 04:00 | 159 | 158
2018-04-30 04:30 | 163 | 163
2018-04-30 05:00 | 170 | 170
2018-04-30 05:30 | 181 | 181
2018-04-30 06:00 | 201 | 201
2018-04-30 06:30 | 219 | 219
2018-04-30 07:00 | 235 | 235
2018-04-30 07:30 | 242 | 242
2018-04-30 08:00 | 241 | 241
2018-04-30 08:30 | 244 | 244
2018-04-30 09:00 | 239 | 238
2018-04-30 09:30 | 234 | 234
2018-04-30 10:00 | 224 | 224
2018-04-30 10:30 | 225 | 225
2018-04-30 11:00 | 224 | 224
2018-04-30 11:30 | 220 | 220
2018-04-30 12:00 | 212 | 212
2018-04-30 12:30 | 215 | 215
2018-04-30 13:00 | 218 | 218
2018-04-30 13:30 | 225 | 225
2018-04-30 14:00 | 231 | 229
2018-04-30 14:30 | 227 | 227
2018-04-30 15:00 | 229 | 228
2018-04-30 15:30 | 232 | 232
2018-04-30 16:00 | 242 | 241
2018-04-30 16:30 | 253 | 252
2018-04-30 17:00 | 264 | 264
2018-04-30 17:30 | 282 | 282
2018-04-30 18:00 | 284 | 283
2018-04-30 18:30 | 280 | 280
2018-04-30 19:00 | 271 | 270
2018-04-30 19:30 | 265 | 265
2018-04-30 20:00 | 259 | 259
2018-04-30 20:30 | 247 | 247
2018-04-30 21:00 | 234 | 234
2018-04-30 21:30 | 230 | 229
2018-04-30 22:00 | 226 | 225
2018-04-30 22:30 | 222 | 221
2018-04-30 23:00 | 213 | 212
2018-04-30 23:30 | 204 | 202
2018-05-01 | 187 | 185
2018-05-01 00:30 | 178 | 176
2018-05-01 01:00 | 169 | 167
2018-05-01 01:30 | 168 | 166
2018-05-01 02:00 | 168 | 165
2018-05-01 02:30 | 165 | 162
2018-05-01 03:00 | 162 | 159
2018-05-01 03:30 | 161 | 158
2018-05-01 04:00 | 163 | 160
2018-05-01 04:30 | 166 | 163
2018-05-01 05:00 | 179 | 178
2018-05-01 05:30 | 191 | 190
2018-05-01 06:00 | 210 | 210
2018-05-01 06:30 | 230 | 230
2018-05-01 07:00 | 245 | 245
2018-05-01 07:30 | 253 | 253
2018-05-01 08:00 | 254 | 254
2018-05-01 08:30 | 246 | 246
2018-05-01 09:00 | 245 | 245
2018-05-01 09:30 | 250 | 250
2018-05-01 10:00 | 255 | 255
2018-05-01 10:30 | 242 | 242
2018-05-01 11:00 | 234 | 234
2018-05-01 11:30 | 235 | 235
2018-05-01 12:00 | 236 | 236
2018-05-01 12:30 | 244 | 244
2018-05-01 13:00 | 253 | 253
2018-05-01 13:30 | 251 | 250
2018-05-01 14:00 | 245 | 244
2018-05-01 14:30 | 240 | 240
2018-05-01 15:00 | 245 | 245
2018-05-01 15:30 | 256 | 255
2018-05-01 16:00 | 266 | 265
2018-05-01 16:30 | 275 | 275
2018-05-01 17:00 | 291 | 290
2018-05-01 17:30 | 309 | 308
2018-05-01 18:00 | 309 | 306
2018-05-01 18:30 | 291 | 288
2018-05-01 19:00 | 275 | 274
2018-05-01 19:30 | 269 | 268
2018-05-01 20:00 | 265 | 263
2018-05-01 20:30 | 256 | 256
2018-05-01 21:00 | 245 | 245
2018-05-01 21:30 | 235 | 234
2018-05-01 22:00 | 230 | 229
2018-05-01 22:30 | 229 | 228
2018-05-01 23:00 | 224 | 223
2018-05-01 23:30 | 214 | 213
2018-05-02 | 198 | 197
2018-05-02 00:30 | 186 | 184
2018-05-02 01:00 | 181 | 179
2018-05-02 01:30 | 178 | 176
2018-05-02 02:00 | 176 | 174
2018-05-02 02:30 | 176 | 174
2018-05-02 03:00 | 177 | 174
2018-05-02 03:30 | 178 | 175
2018-05-02 04:00 | 179 | 176
2018-05-02 04:30 | 182 | 180
2018-05-02 05:00 | 185 | 184
2018-05-02 05:30 | 203 | 203
2018-05-02 06:00 | 233 | 232
2018-05-02 06:30 | 264 | 260
2018-05-02 07:00 | 275 | 273
2018-05-02 07:30 | 286 | 282
2018-05-02 08:00 | 282 | 279
2018-05-02 08:30 | 279 | 277
2018-05-02 09:00 | 268 | 266
2018-05-02 09:30 | 263 | 261
2018-05-02 10:00 | 276 | 275
2018-05-02 10:30 | 282 | 281
2018-05-02 11:00 | 278 | 276
2018-05-02 11:30 | 265 | 263
2018-05-02 12:00 | 266 | 265
2018-05-02 12:30 | 256 | 254
2018-05-02 13:00 | 278 | 277
2018-05-02 13:30 | 263 | 261
2018-05-02 14:00 | 260 | 258
2018-05-02 14:30 | 270 | 269
2018-05-02 15:00 | 281 | 280
2018-05-02 15:30 | 295 | 293
2018-05-02 16:00 | 301 | 299
2018-05-02 16:30 | 317 | 315
2018-05-02 17:00 | 327 | 325
2018-05-02 17:30 | 337 | 336
2018-05-02 18:00 | 336 | 334
2018-05-02 18:30 | 328 | 327
2018-05-02 19:00 | 310 | 307
2018-05-02 19:30 | 282 | 282
2018-05-02 20:00 | 272 | 272
2018-05-02 20:30 | 259 | 259
2018-05-02 21:00 | 250 | 250
2018-05-02 21:30 | 252 | 252
2018-05-02 22:00 | 231 | 231
2018-05-02 22:30 | 227 | 226
2018-05-02 23:00 | 235 | 235
2018-05-02 23:30 | 230 | 229
2018-05-03 | 216 | 215
2018-05-03 00:30 | 208 | 207
2018-05-03 01:00 | 201 | 200
2018-05-03 01:30 | 197 | 195
2018-05-03 02:00 | 192 | 191
2018-05-03 02:30 | 191 | 190
2018-05-03 03:00 | 190 | 188
2018-05-03 03:30 | 192 | 190
2018-05-03 04:00 | 193 | 191
2018-05-03 04:30 | 200 | 198
2018-05-03 05:00 | 198 | 197
2018-05-03 05:30 | 205 | 204
2018-05-03 06:00 | 210 | 209
2018-05-03 06:30 | 227 | 227
2018-05-03 07:00 | 243 | 243
2018-05-03 07:30 | 252 | 252
2018-05-03 08:00 | 267 | 267
2018-05-03 08:30 | 268 | 267
2018-05-03 09:00 | 268 | 267
2018-05-03 09:30 | 274 | 273
2018-05-03 10:00 | 243 | 243
2018-05-03 10:30 | 232 | 231
2018-05-03 11:00 | 233 | 232
2018-05-03 11:30 | 248 | 248
2018-05-03 12:00 | 257 | 257
2018-05-03 12:30 | 254 | 254
2018-05-03 13:00 | 253 | 253
2018-05-03 13:30 | 259 | 258
2018-05-03 14:00 | 255 | 255
2018-05-03 14:30 | 259 | 259
2018-05-03 15:00 | 264 | 264
2018-05-03 15:30 | 273 | 273
2018-05-03 16:00 | 281 | 280
2018-05-03 16:30 | 293 | 292
2018-05-03 17:00 | 306 | 306
2018-05-03 17:30 | 324 | 322
2018-05-03 18:00 | 318 | 316
2018-05-03 18:30 | 314 | 312
2018-05-03 19:00 | 297 | 297
2018-05-03 19:30 | 296 | 296
2018-05-03 20:00 | 277 | 277
2018-05-03 20:30 | 245 | 245
2018-05-03 21:00 | 234 | 234
2018-05-03 21:30 | 222 | 221
2018-05-03 22:00 | 215 | 215
2018-05-03 22:30 | 209 | 209
2018-05-03 23:00 | 201 | 200
2018-05-03 23:30 | 189 | 188
2018-05-04 | 174 | 172
2018-05-04 00:30 | 169 | 167
2018-05-04 01:00 | 160 | 159
2018-05-04 01:30 | 156 | 155
2018-05-04 02:00 | 152 | 151
2018-05-04 02:30 | 149 | 149
2018-05-04 03:00 | 149 | 148
2018-05-04 03:30 | 150 | 149
2018-05-04 04:00 | 154 | 153
2018-05-04 04:30 | 160 | 159
2018-05-04 05:00 | 168 | 168
2018-05-04 05:30 | 173 | 173
2018-05-04 06:00 | 188 | 188
2018-05-04 06:30 | 221 | 221
2018-05-04 07:00 | 233 | 233
2018-05-04 07:30 | 238 | 237
2018-05-04 08:00 | 236 | 236
2018-05-04 08:30 | 228 | 228
2018-05-04 09:00 | 227 | 227
2018-05-04 09:30 | 221 | 221
2018-05-04 10:00 | 222 | 222
2018-05-04 10:30 | 219 | 219
2018-05-04 11:00 | 227 | 227
2018-05-04 11:30 | 234 | 234
2018-05-04 12:00 | 230 | 230
2018-05-04 12:30 | 224 | 224
2018-05-04 13:00 | 221 | 221
2018-05-04 13:30 | 229 | 229
2018-05-04 14:00 | 236 | 236
2018-05-04 14:30 | 241 | 241
2018-05-04 15:00 | 249 | 249
2018-05-04 15:30 | 264 | 262
2018-05-04 16:00 | 272 | 268
2018-05-04 16:30 | 280 | 277
2018-05-04 17:00 | 283 | 281
2018-05-04 17:30 | 282 | 280
2018-05-04 18:00 | 268 | 266
2018-05-04 18:30 | 263 | 262
2018-05-04 19:00 | 256 | 256
2018-05-04 19:30 | 255 | 254
2018-05-04 20:00 | 251 | 251
2018-05-04 20:30 | 243 | 243
2018-05-04 21:00 | 234 | 234
2018-05-04 21:30 | 225 | 225
2018-05-04 22:00 | 219 | 219
2018-05-04 22:30 | 216 | 216
2018-05-04 23:00 | 207 | 207
2018-05-04 23:30 | 192 | 192
2018-05-05 | 177 | 177
2018-05-05 00:30 | 171 | 170
2018-05-05 01:00 | 167 | 167
2018-05-05 01:30 | 166 | 165
2018-05-05 02:00 | 164 | 163
2018-05-05 02:30 | 159 | 159
2018-05-05 03:00 | 159 | 158
2018-05-05 03:30 | 160 | 159
2018-05-05 04:00 | 163 | 162
2018-05-05 04:30 | 163 | 162
2018-05-05 05:00 | 166 | 166
2018-05-05 05:30 | 172 | 172
2018-05-05 06:00 | 180 | 179
2018-05-05 06:30 | 187 | 187
2018-05-05 07:00 | 203 | 203
2018-05-05 07:30 | 215 | 215
2018-05-05 08:00 | 223 | 223
2018-05-05 08:30 | 227 | 227
2018-05-05 09:00 | 227 | 226
2018-05-05 09:30 | 222 | 222
2018-05-05 10:00 | 216 | 216
2018-05-05 10:30 | 215 | 215
2018-05-05 11:00 | 209 | 209
2018-05-05 11:30 | 202 | 202
2018-05-05 12:00 | 200 | 200
2018-05-05 12:30 | 199 | 199
2018-05-05 13:00 | 202 | 202
2018-05-05 13:30 | 203 | 203
2018-05-05 14:00 | 209 | 208
2018-05-05 14:30 | 213 | 213
2018-05-05 15:00 | 219 | 219
2018-05-05 15:30 | 230 | 230
2018-05-05 16:00 | 236 | 236
2018-05-05 16:30 | 246 | 246
2018-05-05 17:00 | 255 | 255
2018-05-05 17:30 | 264 | 264
2018-05-05 18:00 | 262 | 261
2018-05-05 18:30 | 257 | 255
2018-05-05 19:00 | 250 | 249
2018-05-05 19:30 | 247 | 247
2018-05-05 20:00 | 240 | 240
2018-05-05 20:30 | 232 | 232
2018-05-05 21:00 | 228 | 228
2018-05-05 21:30 | 223 | 223
2018-05-05 22:00 | 219 | 219
2018-05-05 22:30 | 219 | 219
2018-05-05 23:00 | 210 | 210
2018-05-05 23:30 | 194 | 193
2018-05-06 | 185 | 183
2018-05-06 00:30 | 174 | 172
2018-05-06 01:00 | 167 | 166
2018-05-06 01:30 | 160 | 159
2018-05-06 02:00 | 158 | 157
2018-05-06 02:30 | 159 | 158
2018-05-06 03:00 | 162 | 162
2018-05-06 03:30 | 164 | 163
2018-05-06 04:00 | 163 | 162
2018-05-06 04:30 | 162 | 161
2018-05-06 05:00 | 161 | 160
2018-05-06 05:30 | 165 | 165
2018-05-06 06:00 | 170 | 169
2018-05-06 06:30 | 178 | 177
2018-05-06 07:00 | 186 | 186
2018-05-06 07:30 | 199 | 199
2018-05-06 08:00 | 207 | 207
2018-05-06 08:30 | 210 | 210
2018-05-06 09:00 | 211 | 211
2018-05-06 09:30 | 213 | 213
2018-05-06 10:00 | 208 | 208
2018-05-06 10:30 | 202 | 202
2018-05-06 11:00 | 199 | 199
2018-05-06 11:30 | 203 | 203
2018-05-06 12:00 | 195 | 195
2018-05-06 12:30 | 199 | 199
2018-05-06 13:00 | 205 | 205
2018-05-06 13:30 | 214 | 214
2018-05-06 14:00 | 220 | 220
2018-05-06 14:30 | 219 | 219
2018-05-06 15:00 | 223 | 223
2018-05-06 15:30 | 226 | 226
2018-05-06 16:00 | 232 | 231
2018-05-06 16:30 | 243 | 243
2018-05-06 17:00 | 252 | 252
2018-05-06 17:30 | 267 | 267
2018-05-06 18:00 | 265 | 265
2018-05-06 18:30 | 258 | 258
2018-05-06 19:00 | 243 | 242
2018-05-06 19:30 | 240 | 239
2018-05-06 20:00 | 239 | 238
2018-05-06 20:30 | 230 | 229
2018-05-06 21:00 | 225 | 223
2018-05-06 21:30 | 217 | 215
2018-05-06 22:00 | 206 | 204
2018-05-06 22:30 | 203 | 202
2018-05-06 23:00 | 198 | 197
2018-05-06 23:30 | 189 | 187
2018-05-07 | 176 | 174
2018-05-07 00:30 | 166 | 166
2018-05-07 01:00 | 162 | 157
2018-05-07 01:30 | 153 | 148
2018-05-07 02:00 | 144 | 141
2018-05-07 02:30 | 141 | 140
2018-05-07 03:00 | 135 | 134
2018-05-07 03:30 | 133 | 132
2018-05-07 04:00 | 106 | 105
2018-05-07 04:30 | 138 | 137
2018-05-07 05:00 | 151 | 151
2018-05-07 05:30 | 166 | 166
2018-05-07 06:00 | 178 | 177
2018-05-07 06:30 | 184 | 184
2018-05-07 07:00 | 197 | 197
2018-05-07 07:30 | 211 | 211
2018-05-07 08:00 | 219 | 219
2018-05-07 08:30 | 219 | 219
2018-05-07 09:00 | 223 | 223
2018-05-07 09:30 | 231 | 231
2018-05-07 10:00 | 229 | 227
2018-05-07 10:30 | 220 | 217
2018-05-07 11:00 | 217 | 215
2018-05-07 11:30 | 227 | 225
2018-05-07 12:00 | 222 | 220
2018-05-07 12:30 | 225 | 222
2018-05-07 13:00 | 229 | 226
2018-05-07 13:30 | 239 | 237
2018-05-07 14:00 | 249 | 247
2018-05-07 14:30 | 253 | 251
2018-05-07 15:00 | 253 | 251
2018-05-07 15:30 | 259 | 257
2018-05-07 16:00 | 265 | 263
2018-05-07 16:30 | 276 | 275
2018-05-07 17:00 | 287 | 286
2018-05-07 17:30 | 286 | 286
2018-05-07 18:00 | 283 | 282
2018-05-07 18:30 | 278 | 277
2018-05-07 19:00 | 274 | 273
2018-05-07 19:30 | 270 | 268
2018-05-07 20:00 | 264 | 263
2018-05-07 20:30 | 253 | 253
2018-05-07 21:00 | 244 | 244
2018-05-07 21:30 | 240 | 239
2018-05-07 22:00 | 230 | 230
2018-05-07 22:30 | 222 | 221
2018-05-07 23:00 | 210 | 209
2018-05-07 23:30 | 202 | 201
2018-05-08 | 192 | 191
2018-05-08 00:30 | 189 | 188
2018-05-08 01:00 | 184 | 182
2018-05-08 01:30 | 179 | 177
2018-05-08 02:00 | 177 | 175
2018-05-08 02:30 | 177 | 175
2018-05-08 03:00 | 177 | 175
2018-05-08 03:30 | 180 | 178
2018-05-08 04:00 | 182 | 180
2018-05-08 04:30 | 185 | 183
2018-05-08 05:00 | 189 | 188
2018-05-08 05:30 | 198 | 198
2018-05-08 06:00 | 221 | 221
2018-05-08 06:30 | 242 | 242
2018-05-08 07:00 | 263 | 263
2018-05-08 07:30 | 275 | 274
2018-05-08 08:00 | 277 | 276
2018-05-08 08:30 | 279 | 278
2018-05-08 09:00 | 277 | 276
2018-05-08 09:30 | 272 | 271
2018-05-08 10:00 | 268 | 268
2018-05-08 10:30 | 268 | 267
2018-05-08 11:00 | 256 | 255
2018-05-08 11:30 | 260 | 259
2018-05-08 12:00 | 275 | 274
2018-05-08 12:30 | 268 | 267
2018-05-08 13:00 | 276 | 276
2018-05-08 13:30 | 279 | 278
2018-05-08 14:00 | 277 | 276
2018-05-08 14:30 | 274 | 273
2018-05-08 15:00 | 277 | 276
2018-05-08 15:30 | 285 | 284
2018-05-08 16:00 | 295 | 294
2018-05-08 16:30 | 306 | 305
2018-05-08 17:00 | 321 | 320
2018-05-08 17:30 | 334 | 332
2018-05-08 18:00 | 331 | 329
2018-05-08 18:30 | 328 | 327
2018-05-08 19:00 | 318 | 316
2018-05-08 19:30 | 313 | 311
2018-05-08 20:00 | 304 | 301
2018-05-08 20:30 | 265 | 265
2018-05-08 21:00 | 255 | 255
2018-05-08 21:30 | 250 | 250
2018-05-08 22:00 | 245 | 245
2018-05-08 22:30 | 238 | 238
2018-05-08 23:00 | 228 | 228
2018-05-08 23:30 | 213 | 213
2018-05-09 | 201 | 201
2018-05-09 00:30 | 197 | 197
2018-05-09 01:00 | 189 | 189
2018-05-09 01:30 | 180 | 180
2018-05-09 02:00 | 177 | 177
2018-05-09 02:30 | 176 | 175
2018-05-09 03:00 | 177 | 177
2018-05-09 03:30 | 181 | 181
2018-05-09 04:00 | 182 | 182
2018-05-09 04:30 | 184 | 184
2018-05-09 05:00 | 191 | 191
2018-05-09 05:30 | 202 | 202
2018-05-09 06:00 | 225 | 225
2018-05-09 06:30 | 243 | 243
2018-05-09 07:00 | 265 | 264
2018-05-09 07:30 | 271 | 270
2018-05-09 08:00 | 267 | 266
2018-05-09 08:30 | 252 | 251
2018-05-09 09:00 | 245 | 245
2018-05-09 09:30 | 239 | 239
2018-05-09 10:00 | 232 | 232
2018-05-09 10:30 | 231 | 230
2018-05-09 11:00 | 228 | 228
2018-05-09 11:30 | 232 | 232
2018-05-09 12:00 | 233 | 233
2018-05-09 12:30 | 234 | 234
2018-05-09 13:00 | 239 | 239
2018-05-09 13:30 | 241 | 241
2018-05-09 14:00 | 249 | 248
2018-05-09 14:30 | 253 | 252
2018-05-09 15:00 | 257 | 257
2018-05-09 15:30 | 266 | 266
2018-05-09 16:00 | 272 | 271
2018-05-09 16:30 | 279 | 278
2018-05-09 17:00 | 295 | 295
2018-05-09 17:30 | 308 | 308
2018-05-09 18:00 | 299 | 299
2018-05-09 18:30 | 296 | 296
2018-05-09 19:00 | 290 | 289
2018-05-09 19:30 | 288 | 287
2018-05-09 20:00 | 274 | 273
2018-05-09 20:30 | 258 | 258
2018-05-09 21:00 | 248 | 248
2018-05-09 21:30 | 237 | 237
2018-05-09 22:00 | 226 | 226
2018-05-09 22:30 | 222 | 222
2018-05-09 23:00 | 215 | 214
2018-05-09 23:30 | 201 | 201
2018-05-10 | 189 | 189
2018-05-10 00:30 | 179 | 179
2018-05-10 01:00 | 172 | 171
2018-05-10 01:30 | 168 | 167
2018-05-10 02:00 | 167 | 166
2018-05-10 02:30 | 166 | 165
2018-05-10 03:00 | 160 | 160
2018-05-10 03:30 | 160 | 160
2018-05-10 04:00 | 165 | 165
2018-05-10 04:30 | 171 | 171
2018-05-10 05:00 | 184 | 184
2018-05-10 05:30 | 196 | 196
2018-05-10 06:00 | 215 | 215
2018-05-10 06:30 | 238 | 238
2018-05-10 07:00 | 251 | 251
2018-05-10 07:30 | 262 | 262
2018-05-10 08:00 | 256 | 256
2018-05-10 08:30 | 250 | 249
2018-05-10 09:00 | 244 | 244
2018-05-10 09:30 | 241 | 240
2018-05-10 10:00 | 235 | 234
2018-05-10 10:30 | 227 | 226
2018-05-10 11:00 | 221 | 221
2018-05-10 11:30 | 220 | 219
2018-05-10 12:00 | 221 | 220
2018-05-10 12:30 | 225 | 224
2018-05-10 13:00 | 233 | 233
2018-05-10 13:30 | 240 | 239
2018-05-10 14:00 | 247 | 247
2018-05-10 14:30 | 241 | 241
2018-05-10 15:00 | 250 | 250
2018-05-10 15:30 | 258 | 258
2018-05-10 16:00 | 266 | 266
2018-05-10 16:30 | 273 | 272
2018-05-10 17:00 | 283 | 282
2018-05-10 17:30 | 303 | 302
2018-05-10 18:00 | 298 | 297
2018-05-10 18:30 | 295 | 294
2018-05-10 19:00 | 285 | 283
2018-05-10 19:30 | 278 | 276
2018-05-10 20:00 | 266 | 265
2018-05-10 20:30 | 258 | 258
2018-05-10 21:00 | 248 | 248
2018-05-10 21:30 | 237 | 237
2018-05-10 22:00 | 234 | 234
2018-05-10 22:30 | 229 | 229
2018-05-10 23:00 | 213 | 213
2018-05-10 23:30 | 198 | 198
2018-05-11 | 189 | 188
2018-05-11 00:30 | 183 | 183
2018-05-11 01:00 | 179 | 178
2018-05-11 01:30 | 174 | 173
2018-05-11 02:00 | 172 | 172
2018-05-11 02:30 | 169 | 168
2018-05-11 03:00 | 166 | 165
2018-05-11 03:30 | 167 | 166
2018-05-11 04:00 | 168 | 167
2018-05-11 04:30 | 170 | 170
2018-05-11 05:00 | 181 | 181
2018-05-11 05:30 | 200 | 200
2018-05-11 06:00 | 217 | 217
2018-05-11 06:30 | 236 | 236
2018-05-11 07:00 | 250 | 250
2018-05-11 07:30 | 259 | 258
2018-05-11 08:00 | 260 | 259
2018-05-11 08:30 | 252 | 252
2018-05-11 09:00 | 250 | 249
2018-05-11 09:30 | 244 | 243
2018-05-11 10:00 | 240 | 239
2018-05-11 10:30 | 236 | 235
2018-05-11 11:00 | 231 | 230
2018-05-11 11:30 | 228 | 227
2018-05-11 12:00 | 222 | 222
2018-05-11 12:30 | 220 | 220
2018-05-11 13:00 | 222 | 221
2018-05-11 13:30 | 228 | 227
2018-05-11 14:00 | 232 | 231
2018-05-11 14:30 | 234 | 234
2018-05-11 15:00 | 245 | 245
2018-05-11 15:30 | 255 | 255
2018-05-11 16:00 | 268 | 268
2018-05-11 16:30 | 281 | 281
2018-05-11 17:00 | 291 | 291
2018-05-11 17:30 | 299 | 299
2018-05-11 18:00 | 295 | 294
2018-05-11 18:30 | 292 | 290
2018-05-11 19:00 | 279 | 278
2018-05-11 19:30 | 280 | 278
2018-05-11 20:00 | 274 | 273
2018-05-11 20:30 | 263 | 263
2018-05-11 21:00 | 255 | 255
2018-05-11 21:30 | 247 | 247
2018-05-11 22:00 | 241 | 241
2018-05-11 22:30 | 235 | 235
2018-05-11 23:00 | 223 | 222
2018-05-11 23:30 | 207 | 206
2018-05-12 | 196 | 194
2018-05-12 00:30 | 188 | 186
2018-05-12 01:00 | 179 | 178
2018-05-12 01:30 | 172 | 171
2018-05-12 02:00 | 170 | 169
2018-05-12 02:30 | 168 | 167
2018-05-12 03:00 | 165 | 164
2018-05-12 03:30 | 163 | 162
2018-05-12 04:00 | 161 | 160
2018-05-12 04:30 | 162 | 161
2018-05-12 05:00 | 169 | 168
2018-05-12 05:30 | 178 | 177
2018-05-12 06:00 | 190 | 190
2018-05-12 06:30 | 205 | 205
2018-05-12 07:00 | 220 | 220
2018-05-12 07:30 | 228 | 228
2018-05-12 08:00 | 234 | 233
2018-05-12 08:30 | 233 | 233
2018-05-12 09:00 | 234 | 234
2018-05-12 09:30 | 230 | 230
2018-05-12 10:00 | 220 | 220
2018-05-12 10:30 | 214 | 214
2018-05-12 11:00 | 207 | 207
2018-05-12 11:30 | 202 | 202
2018-05-12 12:00 | 200 | 200
2018-05-12 12:30 | 200 | 200
2018-05-12 13:00 | 201 | 201
2018-05-12 13:30 | 206 | 206
2018-05-12 14:00 | 214 | 214
2018-05-12 14:30 | 222 | 222
2018-05-12 15:00 | 231 | 231
2018-05-12 15:30 | 243 | 243
2018-05-12 16:00 | 250 | 250
2018-05-12 16:30 | 261 | 261
2018-05-12 17:00 | 273 | 273
2018-05-12 17:30 | 287 | 287
2018-05-12 18:00 | 286 | 286
2018-05-12 18:30 | 279 | 279
2018-05-12 19:00 | 269 | 269
2018-05-12 19:30 | 263 | 263
2018-05-12 20:00 | 258 | 258
2018-05-12 20:30 | 247 | 247
2018-05-12 21:00 | 241 | 240
2018-05-12 21:30 | 235 | 234
2018-05-12 22:00 | 231 | 229
2018-05-12 22:30 | 235 | 233
2018-05-12 23:00 | 228 | 227
2018-05-12 23:30 | 217 | 216
2018-05-13 | 200 | 198
2018-05-13 00:30 | 189 | 187
2018-05-13 01:00 | 179 | 178
2018-05-13 01:30 | 173 | 172
2018-05-13 02:00 | 172 | 171
2018-05-13 02:30 | 170 | 169
2018-05-13 03:00 | 171 | 170
2018-05-13 03:30 | 168 | 167
2018-05-13 04:00 | 168 | 167
2018-05-13 04:30 | 168 | 168
2018-05-13 05:00 | 172 | 171
2018-05-13 05:30 | 177 | 177
2018-05-13 06:00 | 183 | 183
2018-05-13 06:30 | 189 | 188
2018-05-13 07:00 | 199 | 199
2018-05-13 07:30 | 212 | 212
2018-05-13 08:00 | 227 | 227
2018-05-13 08:30 | 227 | 227
2018-05-13 09:00 | 223 | 223
2018-05-13 09:30 | 219 | 219
2018-05-13 10:00 | 216 | 216
2018-05-13 10:30 | 210 | 210
2018-05-13 11:00 | 202 | 202
2018-05-13 11:30 | 199 | 198
2018-05-13 12:00 | 195 | 195
2018-05-13 12:30 | 193 | 193
2018-05-13 13:00 | 194 | 193
2018-05-13 13:30 | 200 | 200
2018-05-13 14:00 | 208 | 208
2018-05-13 14:30 | 213 | 213
2018-05-13 15:00 | 222 | 221
2018-05-13 15:30 | 230 | 230
2018-05-13 16:00 | 237 | 237
2018-05-13 16:30 | 255 | 255
2018-05-13 17:00 | 270 | 270
2018-05-13 17:30 | 290 | 289
2018-05-13 18:00 | 288 | 287
2018-05-13 18:30 | 285 | 284
2018-05-13 19:00 | 273 | 272
2018-05-13 19:30 | 276 | 274
2018-05-13 20:00 | 273 | 270
2018-05-13 20:30 | 255 | 255
2018-05-13 21:00 | 241 | 241
2018-05-13 21:30 | 232 | 231
2018-05-13 22:00 | 227 | 227
2018-05-13 22:30 | 225 | 224
2018-05-13 23:00 | 217 | 216
2018-05-13 23:30 | 203 | 201
2018-05-14 | 191 | 189
2018-05-14 00:30 | 183 | 180
2018-05-14 01:00 | 177 | 175
2018-05-14 01:30 | 173 | 172
2018-05-14 02:00 | 173 | 172
2018-05-14 02:30 | 172 | 171
2018-05-14 03:00 | 172 | 172
2018-05-14 03:30 | 173 | 173
2018-05-14 04:00 | 177 | 176
2018-05-14 04:30 | 181 | 180
2018-05-14 05:00 | 194 | 194
2018-05-14 05:30 | 203 | 203
2018-05-14 06:00 | 226 | 226
2018-05-14 06:30 | 253 | 253
2018-05-14 07:00 | 270 | 270
2018-05-14 07:30 | 275 | 273
2018-05-14 08:00 | 267 | 266
2018-05-14 08:30 | 260 | 259
2018-05-14 09:00 | 252 | 251
2018-05-14 09:30 | 247 | 246
2018-05-14 10:00 | 242 | 242
2018-05-14 10:30 | 240 | 240
2018-05-14 11:00 | 239 | 239
2018-05-14 11:30 | 230 | 230
2018-05-14 12:00 | 231 | 230
2018-05-14 12:30 | 236 | 236
2018-05-14 13:00 | 243 | 243
2018-05-14 13:30 | 248 | 248
2018-05-14 14:00 | 257 | 257
2018-05-14 14:30 | 262 | 261
2018-05-14 15:00 | 266 | 265
2018-05-14 15:30 | 268 | 267
2018-05-14 16:00 | 274 | 273
2018-05-14 16:30 | 285 | 284
2018-05-14 17:00 | 299 | 299
2018-05-14 17:30 | 316 | 315
2018-05-14 18:00 | 314 | 313
2018-05-14 18:30 | 314 | 314
2018-05-14 19:00 | 303 | 302
2018-05-14 19:30 | 293 | 292
2018-05-14 20:00 | 290 | 288
2018-05-14 20:30 | 275 | 275
2018-05-14 21:00 | 271 | 271
2018-05-14 21:30 | 257 | 257
2018-05-14 22:00 | 250 | 249
2018-05-14 22:30 | 247 | 246
2018-05-14 23:00 | 238 | 237
2018-05-14 23:30 | 221 | 221
2018-05-15 | 208 | 207
2018-05-15 00:30 | 196 | 194
2018-05-15 01:00 | 189 | 187
2018-05-15 01:30 | 184 | 182
2018-05-15 02:00 | 185 | 183
2018-05-15 02:30 | 184 | 182
2018-05-15 03:00 | 183 | 181
2018-05-15 03:30 | 183 | 181
2018-05-15 04:00 | 182 | 180
2018-05-15 04:30 | 183 | 181
2018-05-15 05:00 | 193 | 191
2018-05-15 05:30 | 207 | 206
2018-05-15 06:00 | 234 | 233
2018-05-15 06:30 | 261 | 260
2018-05-15 07:00 | 272 | 272
2018-05-15 07:30 | 272 | 272
2018-05-15 08:00 | 267 | 267
2018-05-15 08:30 | 254 | 254
2018-05-15 09:00 | 243 | 243
2018-05-15 09:30 | 236 | 236
2018-05-15 10:00 | 231 | 231
2018-05-15 10:30 | 227 | 227
2018-05-15 11:00 | 225 | 225
2018-05-15 11:30 | 221 | 221
2018-05-15 12:00 | 221 | 221
2018-05-15 12:30 | 220 | 220
2018-05-15 13:00 | 225 | 225
2018-05-15 13:30 | 230 | 230
2018-05-15 14:00 | 234 | 234
2018-05-15 14:30 | 246 | 246
2018-05-15 15:00 | 257 | 257
2018-05-15 15:30 | 264 | 263
2018-05-15 16:00 | 274 | 273
2018-05-15 16:30 | 284 | 283
2018-05-15 17:00 | 298 | 298
2018-05-15 17:30 | 311 | 311
2018-05-15 18:00 | 315 | 314
2018-05-15 18:30 | 310 | 309
2018-05-15 19:00 | 302 | 300
2018-05-15 19:30 | 295 | 294
2018-05-15 20:00 | 291 | 290
2018-05-15 20:30 | 274 | 274
2018-05-15 21:00 | 265 | 264
2018-05-15 21:30 | 261 | 261
2018-05-15 22:00 | 251 | 250
2018-05-15 22:30 | 248 | 246
2018-05-15 23:00 | 237 | 236
2018-05-15 23:30 | 226 | 223
2018-05-16 | 209 | 205
2018-05-16 00:30 | 200 | 196
2018-05-16 01:00 | 192 | 189
2018-05-16 01:30 | 185 | 182
2018-05-16 02:00 | 179 | 177
2018-05-16 02:30 | 175 | 172
2018-05-16 03:00 | 175 | 172
2018-05-16 03:30 | 177 | 174
2018-05-16 04:00 | 179 | 177
2018-05-16 04:30 | 182 | 180
2018-05-16 05:00 | 188 | 187
2018-05-16 05:30 | 205 | 204
2018-05-16 06:00 | 233 | 233
2018-05-16 06:30 | 247 | 247
2018-05-16 07:00 | 253 | 253
2018-05-16 07:30 | 250 | 250
2018-05-16 08:00 | 239 | 239
2018-05-16 08:30 | 228 | 228
2018-05-16 09:00 | 222 | 222
2018-05-16 09:30 | 217 | 216
2018-05-16 10:00 | 212 | 211
2018-05-16 10:30 | 209 | 209
2018-05-16 11:00 | 204 | 204
2018-05-16 11:30 | 203 | 202
2018-05-16 12:00 | 201 | 201
2018-05-16 12:30 | 204 | 203
2018-05-16 13:00 | 206 | 206
2018-05-16 13:30 | 213 | 213
2018-05-16 14:00 | 220 | 220
2018-05-16 14:30 | 224 | 224
2018-05-16 15:00 | 233 | 233
2018-05-16 15:30 | 242 | 242
2018-05-16 16:00 | 256 | 256
2018-05-16 16:30 | 272 | 271
2018-05-16 17:00 | 286 | 286
2018-05-16 17:30 | 302 | 300
2018-05-16 18:00 | 295 | 293
2018-05-16 18:30 | 290 | 288
2018-05-16 19:00 | 279 | 277
2018-05-16 19:30 | 272 | 272
2018-05-16 20:00 | 266 | 266
2018-05-16 20:30 | 256 | 253
2018-05-16 21:00 | 245 | 241
2018-05-16 21:30 | 234 | 229
2018-05-16 22:00 | 233 | 227
2018-05-16 22:30 | 231 | 225
2018-05-16 23:00 | 220 | 213
2018-05-16 23:30 | 205 | 195
2018-05-17 | 191 | 180
2018-05-17 00:30 | 184 | 171
2018-05-17 01:00 | 180 | 165
2018-05-17 01:30 | 170 | 159
2018-05-17 02:00 | 166 | 155
2018-05-17 02:30 | 164 | 153
2018-05-17 03:00 | 163 | 152
2018-05-17 03:30 | 164 | 153
2018-05-17 04:00 | 168 | 157
2018-05-17 04:30 | 173 | 164
2018-05-17 05:00 | 184 | 177
2018-05-17 05:30 | 200 | 195
2018-05-17 06:00 | 221 | 219
2018-05-17 06:30 | 240 | 240
2018-05-17 07:00 | 257 | 257
2018-05-17 07:30 | 254 | 254
2018-05-17 08:00 | 245 | 245
2018-05-17 08:30 | 235 | 235
2018-05-17 09:00 | 229 | 229
2018-05-17 09:30 | 221 | 221
2018-05-17 10:00 | 221 | 221
2018-05-17 10:30 | 224 | 223
2018-05-17 11:00 | 221 | 219
2018-05-17 11:30 | 221 | 219
2018-05-17 12:00 | 222 | 221
2018-05-17 12:30 | 227 | 225
2018-05-17 13:00 | 236 | 234
2018-05-17 13:30 | 242 | 238
2018-05-17 14:00 | 249 | 244
2018-05-17 14:30 | 251 | 246
2018-05-17 15:00 | 244 | 238
2018-05-17 15:30 | 248 | 242
2018-05-17 16:00 | 259 | 253
2018-05-17 16:30 | 274 | 269
2018-05-17 17:00 | 289 | 285
2018-05-17 17:30 | 300 | 299
2018-05-17 18:00 | 309 | 308
2018-05-17 18:30 | 304 | 303
2018-05-17 19:00 | 294 | 293
2018-05-17 19:30 | 294 | 293
2018-05-17 20:00 | 294 | 294
2018-05-17 20:30 | 279 | 277
2018-05-17 21:00 | 265 | 265
2018-05-17 21:30 | 255 | 254
2018-05-17 22:00 | 250 | 250
2018-05-17 22:30 | 244 | 243
2018-05-17 23:00 | 235 | 235
2018-05-17 23:30 | 225 | 224
2018-05-18 | 211 | 209
2018-05-18 00:30 | 199 | 197
2018-05-18 01:00 | 193 | 191
2018-05-18 01:30 | 185 | 184
2018-05-18 02:00 | 181 | 180
2018-05-18 02:30 | 178 | 177
2018-05-18 03:00 | 179 | 178
2018-05-18 03:30 | 179 | 178
2018-05-18 04:00 | 185 | 185
2018-05-18 04:30 | 193 | 193
2018-05-18 05:00 | 203 | 203
2018-05-18 05:30 | 215 | 215
2018-05-18 06:00 | 234 | 234
2018-05-18 06:30 | 264 | 264
2018-05-18 07:00 | 270 | 270
2018-05-18 07:30 | 272 | 272
2018-05-18 08:00 | 274 | 274
2018-05-18 08:30 | 262 | 262
2018-05-18 09:00 | 255 | 255
2018-05-18 09:30 | 248 | 248
2018-05-18 10:00 | 244 | 244
2018-05-18 10:30 | 240 | 240
2018-05-18 11:00 | 241 | 241
2018-05-18 11:30 | 241 | 241
2018-05-18 12:00 | 241 | 240
2018-05-18 12:30 | 243 | 243
2018-05-18 13:00 | 246 | 246
2018-05-18 13:30 | 248 | 248
2018-05-18 14:00 | 250 | 250
2018-05-18 14:30 | 254 | 254
2018-05-18 15:00 | 262 | 262
2018-05-18 15:30 | 269 | 269
2018-05-18 16:00 | 276 | 276
2018-05-18 16:30 | 286 | 286
2018-05-18 17:00 | 292 | 291
2018-05-18 17:30 | 293 | 291
2018-05-18 18:00 | 291 | 290
2018-05-18 18:30 | 288 | 288
2018-05-18 19:00 | 283 | 282
2018-05-18 19:30 | 280 | 280
2018-05-18 20:00 | 285 | 285
2018-05-18 20:30 | 288 | 288
2018-05-18 21:00 | 269 | 269
2018-05-18 21:30 | 258 | 258
2018-05-18 22:00 | 257 | 256
2018-05-18 22:30 | 251 | 251
2018-05-18 23:00 | 243 | 242
2018-05-18 23:30 | 231 | 230
2018-05-19 | 237 | 236
2018-05-19 00:30 | 231 | 230
2018-05-19 01:00 | 217 | 216
2018-05-19 01:30 | 196 | 196
2018-05-19 02:00 | 190 | 189
2018-05-19 02:30 | 186 | 185
2018-05-19 03:00 | 187 | 186
2018-05-19 03:30 | 188 | 188
2018-05-19 04:00 | 187 | 186
2018-05-19 04:30 | 189 | 188
2018-05-19 05:00 | 195 | 194
2018-05-19 05:30 | 203 | 203
2018-05-19 06:00 | 212 | 212
2018-05-19 06:30 | 221 | 220
2018-05-19 07:00 | 241 | 241
2018-05-19 07:30 | 265 | 265
2018-05-19 08:00 | 269 | 269
2018-05-19 08:30 | 273 | 273
2018-05-19 09:00 | 271 | 271
2018-05-19 09:30 | 264 | 264
2018-05-19 10:00 | 255 | 255
2018-05-19 10:30 | 247 | 247
2018-05-19 11:00 | 236 | 236
2018-05-19 11:30 | 225 | 225
2018-05-19 12:00 | 228 | 228
2018-05-19 12:30 | 220 | 220
2018-05-19 13:00 | 215 | 215
2018-05-19 13:30 | 221 | 221
2018-05-19 14:00 | 227 | 227
2018-05-19 14:30 | 226 | 225
2018-05-19 15:00 | 238 | 238
2018-05-19 15:30 | 247 | 247
2018-05-19 16:00 | 257 | 257
2018-05-19 16:30 | 266 | 266
2018-05-19 17:00 | 278 | 278
2018-05-19 17:30 | 287 | 287
2018-05-19 18:00 | 280 | 279
2018-05-19 18:30 | 281 | 280
2018-05-19 19:00 | 275 | 273
2018-05-19 19:30 | 272 | 270
2018-05-19 20:00 | 263 | 263
2018-05-19 20:30 | 257 | 257
2018-05-19 21:00 | 254 | 254
2018-05-19 21:30 | 260 | 260
2018-05-19 22:00 | 247 | 247
2018-05-19 22:30 | 249 | 249
2018-05-19 23:00 | 237 | 236
2018-05-19 23:30 | 225 | 223
2018-05-20 | 205 | 204
2018-05-20 00:30 | 192 | 192
2018-05-20 01:00 | 186 | 186
2018-05-20 01:30 | 185 | 184
2018-05-20 02:00 | 179 | 178
2018-05-20 02:30 | 176 | 175
2018-05-20 03:00 | 176 | 175
2018-05-20 03:30 | 175 | 174
2018-05-20 04:00 | 173 | 172
2018-05-20 04:30 | 169 | 168
2018-05-20 05:00 | 173 | 172
2018-05-20 05:30 | 177 | 176
2018-05-20 06:00 | 185 | 184
2018-05-20 06:30 | 193 | 192
2018-05-20 07:00 | 206 | 205
2018-05-20 07:30 | 217 | 216
2018-05-20 08:00 | 224 | 224
2018-05-20 08:30 | 231 | 230
2018-05-20 09:00 | 233 | 232
2018-05-20 09:30 | 231 | 230
2018-05-20 10:00 | 226 | 226
2018-05-20 10:30 | 214 | 213
2018-05-20 11:00 | 208 | 208
2018-05-20 11:30 | 203 | 203
2018-05-20 12:00 | 203 | 203
2018-05-20 12:30 | 208 | 207
2018-05-20 13:00 | 210 | 210
2018-05-20 13:30 | 213 | 213
2018-05-20 14:00 | 217 | 216
2018-05-20 14:30 | 221 | 221
2018-05-20 15:00 | 228 | 228
2018-05-20 15:30 | 242 | 242
2018-05-20 16:00 | 255 | 255
2018-05-20 16:30 | 270 | 270
2018-05-20 17:00 | 285 | 285
2018-05-20 17:30 | 291 | 289
2018-05-20 18:00 | 289 | 286
2018-05-20 18:30 | 285 | 282
2018-05-20 19:00 | 277 | 275
2018-05-20 19:30 | 277 | 275
2018-05-20 20:00 | 277 | 275
2018-05-20 20:30 | 262 | 261
2018-05-20 21:00 | 254 | 253
2018-05-20 21:30 | 242 | 242
2018-05-20 22:00 | 231 | 230
2018-05-20 22:30 | 225 | 224
2018-05-20 23:00 | 215 | 214
2018-05-20 23:30 | 209 | 207
2018-05-21 | 195 | 195
2018-05-21 00:30 | 189 | 188
2018-05-21 01:00 | 186 | 185
2018-05-21 01:30 | 181 | 180
2018-05-21 02:00 | 175 | 175
2018-05-21 02:30 | 172 | 172
2018-05-21 03:00 | 168 | 168
2018-05-21 03:30 | 168 | 168
2018-05-21 04:00 | 168 | 168
2018-05-21 04:30 | 173 | 173
2018-05-21 05:00 | 186 | 186
2018-05-21 05:30 | 206 | 206
2018-05-21 06:00 | 236 | 235
2018-05-21 06:30 | 259 | 259
2018-05-21 07:00 | 272 | 272
2018-05-21 07:30 | 276 | 276
2018-05-21 08:00 | 273 | 273
2018-05-21 08:30 | 265 | 265
2018-05-21 09:00 | 255 | 255
2018-05-21 09:30 | 248 | 247
2018-05-21 10:00 | 242 | 242
2018-05-21 10:30 | 239 | 239
2018-05-21 11:00 | 235 | 235
2018-05-21 11:30 | 228 | 227
2018-05-21 12:00 | 228 | 227
2018-05-21 12:30 | 228 | 227
2018-05-21 13:00 | 232 | 232
2018-05-21 13:30 | 236 | 236
2018-05-21 14:00 | 242 | 242
2018-05-21 14:30 | 245 | 245
2018-05-21 15:00 | 251 | 251
2018-05-21 15:30 | 260 | 260
2018-05-21 16:00 | 273 | 273
2018-05-21 16:30 | 285 | 284
2018-05-21 17:00 | 310 | 309
2018-05-21 17:30 | 323 | 322
2018-05-21 18:00 | 317 | 317
2018-05-21 18:30 | 315 | 314
2018-05-21 19:00 | 299 | 299
2018-05-21 19:30 | 299 | 299
2018-05-21 20:00 | 294 | 294
2018-05-21 20:30 | 283 | 283
2018-05-21 21:00 | 268 | 268
2018-05-21 21:30 | 271 | 271
2018-05-21 22:00 | 257 | 256
2018-05-21 22:30 | 245 | 244
2018-05-21 23:00 | 230 | 229
2018-05-21 23:30 | 222 | 221
2018-05-22 | 205 | 204
2018-05-22 00:30 | 202 | 201
2018-05-22 01:00 | 188 | 187
2018-05-22 01:30 | 181 | 180
2018-05-22 02:00 | 175 | 174
2018-05-22 02:30 | 175 | 174
2018-05-22 03:00 | 174 | 173
2018-05-22 03:30 | 175 | 174
2018-05-22 04:00 | 178 | 177
2018-05-22 04:30 | 183 | 182
2018-05-22 05:00 | 192 | 192
2018-05-22 05:30 | 203 | 203
2018-05-22 06:00 | 228 | 228
2018-05-22 06:30 | 257 | 257
2018-05-22 07:00 | 276 | 276
2018-05-22 07:30 | 277 | 277
2018-05-22 08:00 | 273 | 273
2018-05-22 08:30 | 265 | 265
2018-05-22 09:00 | 265 | 265
2018-05-22 09:30 | 255 | 255
2018-05-22 10:00 | 250 | 250
2018-05-22 10:30 | 243 | 243
2018-05-22 11:00 | 226 | 226
2018-05-22 11:30 | 218 | 218
2018-05-22 12:00 | 218 | 218
2018-05-22 12:30 | 221 | 221
2018-05-22 13:00 | 224 | 224
2018-05-22 13:30 | 229 | 229
2018-05-22 14:00 | 234 | 234
2018-05-22 14:30 | 244 | 244
2018-05-22 15:00 | 251 | 251
2018-05-22 15:30 | 264 | 264
2018-05-22 16:00 | 282 | 281
2018-05-22 16:30 | 292 | 292
2018-05-22 17:00 | 306 | 306
2018-05-22 17:30 | 316 | 316
2018-05-22 18:00 | 315 | 315
2018-05-22 18:30 | 313 | 313
2018-05-22 19:00 | 305 | 304
2018-05-22 19:30 | 304 | 303
2018-05-22 20:00 | 322 | 322
2018-05-22 20:30 | 298 | 298
2018-05-22 21:00 | 281 | 280
2018-05-22 21:30 | 264 | 263
2018-05-22 22:00 | 263 | 263
2018-05-22 22:30 | 252 | 251
2018-05-22 23:00 | 242 | 241
2018-05-22 23:30 | 223 | 222
2018-05-23 | 212 | 212
2018-05-23 00:30 | 204 | 203
2018-05-23 01:00 | 213 | 213
2018-05-23 01:30 | 206 | 205
2018-05-23 02:00 | 192 | 192
2018-05-23 02:30 | 195 | 194
2018-05-23 03:00 | 188 | 187
2018-05-23 03:30 | 186 | 186
2018-05-23 04:00 | 186 | 186
2018-05-23 04:30 | 188 | 188
2018-05-23 05:00 | 200 | 200
2018-05-23 05:30 | 211 | 211
2018-05-23 06:00 | 232 | 232
2018-05-23 06:30 | 256 | 256
2018-05-23 07:00 | 269 | 269
2018-05-23 07:30 | 290 | 290
2018-05-23 08:00 | 312 | 310
2018-05-23 08:30 | 294 | 294
2018-05-23 09:00 | 286 | 286
2018-05-23 09:30 | 282 | 282
2018-05-23 10:00 | 286 | 286
2018-05-23 10:30 | 289 | 289
2018-05-23 11:00 | 279 | 279
2018-05-23 11:30 | 272 | 272
2018-05-23 12:00 | 266 | 266
2018-05-23 12:30 | 268 | 268
2018-05-23 13:00 | 274 | 273
2018-05-23 13:30 | 278 | 278
2018-05-23 14:00 | 288 | 288
2018-05-23 14:30 | 258 | 257
2018-05-23 15:00 | 262 | 261
2018-05-23 15:30 | 270 | 270
2018-05-23 16:00 | 280 | 280
2018-05-23 16:30 | 292 | 291
2018-05-23 17:00 | 308 | 308
2018-05-23 17:30 | 316 | 316
2018-05-23 18:00 | 310 | 310
2018-05-23 18:30 | 305 | 305
2018-05-23 19:00 | 295 | 294
2018-05-23 19:30 | 291 | 290
2018-05-23 20:00 | 287 | 286
2018-05-23 20:30 | 277 | 276
2018-05-23 21:00 | 267 | 267
2018-05-23 21:30 | 254 | 254
2018-05-23 22:00 | 258 | 258
2018-05-23 22:30 | 248 | 248
2018-05-23 23:00 | 237 | 237
2018-05-23 23:30 | 222 | 222
2018-05-24 | 214 | 214
2018-05-24 00:30 | 203 | 203
2018-05-24 01:00 | 197 | 197
2018-05-24 01:30 | 193 | 193
2018-05-24 02:00 | 183 | 182
2018-05-24 02:30 | 180 | 179
2018-05-24 03:00 | 174 | 173
2018-05-24 03:30 | 172 | 171
2018-05-24 04:00 | 175 | 174
2018-05-24 04:30 | 177 | 176
2018-05-24 05:00 | 190 | 190
2018-05-24 05:30 | 208 | 207
2018-05-24 06:00 | 227 | 227
2018-05-24 06:30 | 242 | 241
2018-05-24 07:00 | 253 | 253
2018-05-24 07:30 | 258 | 258
2018-05-24 08:00 | 257 | 257
2018-05-24 08:30 | 258 | 256
2018-05-24 09:00 | 254 | 253
2018-05-24 09:30 | 244 | 242
2018-05-24 10:00 | 233 | 233
2018-05-24 10:30 | 234 | 233
2018-05-24 11:00 | 232 | 232
2018-05-24 11:30 | 231 | 231
2018-05-24 12:00 | 232 | 232
2018-05-24 12:30 | 226 | 226
2018-05-24 13:00 | 232 | 232
2018-05-24 13:30 | 240 | 240
2018-05-24 14:00 | 249 | 248
2018-05-24 14:30 | 258 | 258
2018-05-24 15:00 | 257 | 257
2018-05-24 15:30 | 264 | 264
2018-05-24 16:00 | 275 | 275
2018-05-24 16:30 | 291 | 291
2018-05-24 17:00 | 312 | 312
2018-05-24 17:30 | 328 | 327
2018-05-24 18:00 | 315 | 314
2018-05-24 18:30 | 309 | 308
2018-05-24 19:00 | 295 | 295
2018-05-24 19:30 | 295 | 294
2018-05-24 20:00 | 291 | 291
2018-05-24 20:30 | 279 | 279
2018-05-24 21:00 | 266 | 266
2018-05-24 21:30 | 256 | 256
2018-05-24 22:00 | 248 | 247
2018-05-24 22:30 | 244 | 243
2018-05-24 23:00 | 235 | 234
2018-05-24 23:30 | 221 | 220
2018-05-25 | 208 | 206
2018-05-25 00:30 | 199 | 197
2018-05-25 01:00 | 189 | 187
2018-05-25 01:30 | 183 | 182
2018-05-25 02:00 | 180 | 179
2018-05-25 02:30 | 177 | 176
2018-05-25 03:00 | 178 | 177
2018-05-25 03:30 | 177 | 176
2018-05-25 04:00 | 178 | 177
2018-05-25 04:30 | 182 | 181
2018-05-25 05:00 | 191 | 190
2018-05-25 05:30 | 202 | 202
2018-05-25 06:00 | 228 | 228
2018-05-25 06:30 | 249 | 249
2018-05-25 07:00 | 268 | 268
2018-05-25 07:30 | 276 | 276
2018-05-25 08:00 | 277 | 277
2018-05-25 08:30 | 273 | 273
2018-05-25 09:00 | 268 | 268
2018-05-25 09:30 | 254 | 254
2018-05-25 10:00 | 247 | 247
2018-05-25 10:30 | 243 | 242
2018-05-25 11:00 | 241 | 241
2018-05-25 11:30 | 236 | 236
2018-05-25 12:00 | 236 | 235
2018-05-25 12:30 | 241 | 241
2018-05-25 13:00 | 245 | 244
2018-05-25 13:30 | 250 | 250
2018-05-25 14:00 | 256 | 256
2018-05-25 14:30 | 259 | 258
2018-05-25 15:00 | 263 | 263
2018-05-25 15:30 | 271 | 270
2018-05-25 16:00 | 279 | 279
2018-05-25 16:30 | 293 | 292
2018-05-25 17:00 | 301 | 300
2018-05-25 17:30 | 311 | 310
2018-05-25 18:00 | 303 | 302
2018-05-25 18:30 | 301 | 300
2018-05-25 19:00 | 291 | 290
2018-05-25 19:30 | 290 | 290
2018-05-25 20:00 | 285 | 285
2018-05-25 20:30 | 273 | 273
2018-05-25 21:00 | 261 | 261
2018-05-25 21:30 | 254 | 254
2018-05-25 22:00 | 252 | 252
2018-05-25 22:30 | 245 | 244
2018-05-25 23:00 | 233 | 233
2018-05-25 23:30 | 220 | 218
2018-05-26 | 208 | 206
2018-05-26 00:30 | 201 | 200
2018-05-26 01:00 | 188 | 186
2018-05-26 01:30 | 179 | 178
2018-05-26 02:00 | 177 | 176
2018-05-26 02:30 | 175 | 174
2018-05-26 03:00 | 174 | 173
2018-05-26 03:30 | 173 | 172
2018-05-26 04:00 | 177 | 176
2018-05-26 04:30 | 178 | 177
2018-05-26 05:00 | 183 | 182
2018-05-26 05:30 | 185 | 185
2018-05-26 06:00 | 196 | 196
2018-05-26 06:30 | 212 | 212
2018-05-26 07:00 | 228 | 228
2018-05-26 07:30 | 238 | 238
2018-05-26 08:00 | 264 | 264
2018-05-26 08:30 | 276 | 276
2018-05-26 09:00 | 280 | 280
2018-05-26 09:30 | 256 | 256
2018-05-26 10:00 | 240 | 240
2018-05-26 10:30 | 232 | 232
2018-05-26 11:00 | 231 | 231
2018-05-26 11:30 | 223 | 223
2018-05-26 12:00 | 221 | 221
2018-05-26 12:30 | 212 | 212
2018-05-26 13:00 | 215 | 215
2018-05-26 13:30 | 220 | 219
2018-05-26 14:00 | 223 | 223
2018-05-26 14:30 | 228 | 228
2018-05-26 15:00 | 232 | 232
2018-05-26 15:30 | 236 | 236
2018-05-26 16:00 | 244 | 244
2018-05-26 16:30 | 262 | 262
2018-05-26 17:00 | 282 | 282
2018-05-26 17:30 | 286 | 286
2018-05-26 18:00 | 283 | 283
2018-05-26 18:30 | 276 | 276
2018-05-26 19:00 | 265 | 265
2018-05-26 19:30 | 264 | 264
2018-05-26 20:00 | 259 | 259
2018-05-26 20:30 | 244 | 243
2018-05-26 21:00 | 238 | 237
2018-05-26 21:30 | 233 | 233
2018-05-26 22:00 | 228 | 227
2018-05-26 22:30 | 228 | 228
2018-05-26 23:00 | 220 | 219
2018-05-26 23:30 | 207 | 206
2018-05-27 | 194 | 193
2018-05-27 00:30 | 188 | 187
2018-05-27 01:00 | 181 | 180
2018-05-27 01:30 | 174 | 173
2018-05-27 02:00 | 170 | 170
2018-05-27 02:30 | 169 | 169
2018-05-27 03:00 | 166 | 166
2018-05-27 03:30 | 166 | 166
2018-05-27 04:00 | 166 | 166
2018-05-27 04:30 | 164 | 164
2018-05-27 05:00 | 170 | 170
2018-05-27 05:30 | 172 | 172
2018-05-27 06:00 | 184 | 184
2018-05-27 06:30 | 191 | 191
2018-05-27 07:00 | 203 | 203
2018-05-27 07:30 | 212 | 212
2018-05-27 08:00 | 220 | 220
2018-05-27 08:30 | 224 | 223
2018-05-27 09:00 | 224 | 223
2018-05-27 09:30 | 220 | 219
2018-05-27 10:00 | 217 | 217
2018-05-27 10:30 | 216 | 215
2018-05-27 11:00 | 209 | 208
2018-05-27 11:30 | 207 | 206
2018-05-27 12:00 | 205 | 204
2018-05-27 12:30 | 202 | 201
2018-05-27 13:00 | 203 | 202
2018-05-27 13:30 | 208 | 207
2018-05-27 14:00 | 215 | 214
2018-05-27 14:30 | 224 | 223
2018-05-27 15:00 | 223 | 223
2018-05-27 15:30 | 231 | 230
2018-05-27 16:00 | 250 | 249
2018-05-27 16:30 | 270 | 269
2018-05-27 17:00 | 282 | 281
2018-05-27 17:30 | 280 | 280
2018-05-27 18:00 | 277 | 277
2018-05-27 18:30 | 276 | 275
2018-05-27 19:00 | 268 | 268
2018-05-27 19:30 | 265 | 265
2018-05-27 20:00 | 261 | 261
2018-05-27 20:30 | 254 | 254
2018-05-27 21:00 | 239 | 239
2018-05-27 21:30 | 223 | 223
2018-05-27 22:00 | 216 | 216
2018-05-27 22:30 | 218 | 218
2018-05-27 23:00 | 211 | 210
2018-05-27 23:30 | 201 | 201
2018-05-28 | 189 | 188
2018-05-28 00:30 | 182 | 181
2018-05-28 01:00 | 175 | 175
2018-05-28 01:30 | 169 | 169
2018-05-28 02:00 | 164 | 164
2018-05-28 02:30 | 162 | 162
2018-05-28 03:00 | 162 | 162
2018-05-28 03:30 | 163 | 163
2018-05-28 04:00 | 170 | 170
2018-05-28 04:30 | 176 | 176
2018-05-28 05:00 | 183 | 183
2018-05-28 05:30 | 195 | 195
2018-05-28 06:00 | 215 | 215
2018-05-28 06:30 | 237 | 237
2018-05-28 07:00 | 263 | 262
2018-05-28 07:30 | 269 | 269
2018-05-28 08:00 | 268 | 267
2018-05-28 08:30 | 258 | 258
2018-05-28 09:00 | 256 | 256
2018-05-28 09:30 | 259 | 259
2018-05-28 10:00 | 253 | 253
2018-05-28 10:30 | 237 | 237
2018-05-28 11:00 | 230 | 230
2018-05-28 11:30 | 247 | 247
2018-05-28 12:00 | 242 | 242
2018-05-28 12:30 | 233 | 233
2018-05-28 13:00 | 240 | 240
2018-05-28 13:30 | 245 | 245
2018-05-28 14:00 | 244 | 244
2018-05-28 14:30 | 247 | 247
2018-05-28 15:00 | 258 | 258
2018-05-28 15:30 | 268 | 268
2018-05-28 16:00 | 282 | 282
2018-05-28 16:30 | 298 | 298
2018-05-28 17:00 | 316 | 316
2018-05-28 17:30 | 321 | 321
2018-05-28 18:00 | 316 | 316
2018-05-28 18:30 | 315 | 315
2018-05-28 19:00 | 304 | 304
2018-05-28 19:30 | 301 | 300
2018-05-28 20:00 | 294 | 292
2018-05-28 20:30 | 274 | 274
2018-05-28 21:00 | 258 | 257
2018-05-28 21:30 | 242 | 242
2018-05-28 22:00 | 234 | 234
2018-05-28 22:30 | 229 | 229
2018-05-28 23:00 | 220 | 220
2018-05-28 23:30 | 209 | 209
2018-05-29 | 196 | 196
2018-05-29 00:30 | 190 | 190
2018-05-29 01:00 | 185 | 184
2018-05-29 01:30 | 181 | 180
2018-05-29 02:00 | 180 | 180
2018-05-29 02:30 | 176 | 175
2018-05-29 03:00 | 173 | 172
2018-05-29 03:30 | 165 | 165
2018-05-29 04:00 | 171 | 171
2018-05-29 04:30 | 174 | 174
2018-05-29 05:00 | 183 | 183
2018-05-29 05:30 | 199 | 198
2018-05-29 06:00 | 223 | 222
2018-05-29 06:30 | 241 | 241
2018-05-29 07:00 | 261 | 261
2018-05-29 07:30 | 263 | 263
2018-05-29 08:00 | 263 | 263
2018-05-29 08:30 | 260 | 260
2018-05-29 09:00 | 251 | 251
2018-05-29 09:30 | 241 | 241
2018-05-29 10:00 | 238 | 237
2018-05-29 10:30 | 235 | 235
2018-05-29 11:00 | 236 | 236
2018-05-29 11:30 | 238 | 237
2018-05-29 12:00 | 236 | 236
2018-05-29 12:30 | 241 | 241
2018-05-29 13:00 | 241 | 240
2018-05-29 13:30 | 235 | 235
2018-05-29 14:00 | 236 | 236
2018-05-29 14:30 | 247 | 247
2018-05-29 15:00 | 251 | 251
2018-05-29 15:30 | 264 | 264
2018-05-29 16:00 | 277 | 277
2018-05-29 16:30 | 285 | 285
2018-05-29 17:00 | 299 | 299
2018-05-29 17:30 | 313 | 311
2018-05-29 18:00 | 307 | 305
2018-05-29 18:30 | 305 | 304
2018-05-29 19:00 | 299 | 298
2018-05-29 19:30 | 296 | 295
2018-05-29 20:00 | 297 | 296
2018-05-29 20:30 | 280 | 280
2018-05-29 21:00 | 267 | 266
2018-05-29 21:30 | 254 | 253
2018-05-29 22:00 | 250 | 250
2018-05-29 22:30 | 244 | 244
2018-05-29 23:00 | 234 | 234
2018-05-29 23:30 | 218 | 218
2018-05-30 | 204 | 204
2018-05-30 00:30 | 197 | 196
2018-05-30 01:00 | 188 | 188
2018-05-30 01:30 | 182 | 181
2018-05-30 02:00 | 180 | 180
2018-05-30 02:30 | 178 | 177
2018-05-30 03:00 | 182 | 181
2018-05-30 03:30 | 184 | 183
2018-05-30 04:00 | 186 | 186
2018-05-30 04:30 | 189 | 189
2018-05-30 05:00 | 198 | 197
2018-05-30 05:30 | 206 | 206
2018-05-30 06:00 | 229 | 229
2018-05-30 06:30 | 258 | 258
2018-05-30 07:00 | 274 | 274
2018-05-30 07:30 | 280 | 280
2018-05-30 08:00 | 274 | 273
2018-05-30 08:30 | 266 | 266
2018-05-30 09:00 | 262 | 262
2018-05-30 09:30 | 250 | 250
2018-05-30 10:00 | 244 | 244
2018-05-30 10:30 | 242 | 242
2018-05-30 11:00 | 237 | 237
2018-05-30 11:30 | 238 | 238
2018-05-30 12:00 | 237 | 237
2018-05-30 12:30 | 240 | 240
2018-05-30 13:00 | 244 | 244
2018-05-30 13:30 | 249 | 249
2018-05-30 14:00 | 256 | 256
2018-05-30 14:30 | 257 | 257
2018-05-30 15:00 | 260 | 260
2018-05-30 15:30 | 264 | 264
2018-05-30 16:00 | 276 | 276
2018-05-30 16:30 | 293 | 293
2018-05-30 17:00 | 308 | 308
2018-05-30 17:30 | 311 | 311
2018-05-30 18:00 | 305 | 304
2018-05-30 18:30 | 299 | 299
2018-05-30 19:00 | 284 | 284
2018-05-30 19:30 | 283 | 283
2018-05-30 20:00 | 281 | 281
2018-05-30 20:30 | 269 | 269
2018-05-30 21:00 | 259 | 258
2018-05-30 21:30 | 248 | 246
2018-05-30 22:00 | 241 | 240
2018-05-30 22:30 | 234 | 232
2018-05-30 23:00 | 227 | 225
2018-05-30 23:30 | 216 | 213
2018-05-31 | 200 | 197
2018-05-31 00:30 | 193 | 190
2018-05-31 01:00 | 188 | 186
2018-05-31 01:30 | 185 | 182
2018-05-31 02:00 | 183 | 181
2018-05-31 02:30 | 183 | 180
2018-05-31 03:00 | 183 | 180
2018-05-31 03:30 | 184 | 181
2018-05-31 04:00 | 187 | 184
2018-05-31 04:30 | 189 | 187
2018-05-31 05:00 | 197 | 195
2018-05-31 05:30 | 206 | 205
2018-05-31 06:00 | 231 | 230
2018-05-31 06:30 | 263 | 263
2018-05-31 07:00 | 278 | 278
2018-05-31 07:30 | 275 | 275
2018-05-31 08:00 | 268 | 268
2018-05-31 08:30 | 258 | 258
2018-05-31 09:00 | 246 | 246
2018-05-31 09:30 | 234 | 234
2018-05-31 10:00 | 228 | 228
2018-05-31 10:30 | 224 | 223
2018-05-31 11:00 | 220 | 220
2018-05-31 11:30 | 218 | 218
2018-05-31 12:00 | 216 | 216
2018-05-31 12:30 | 218 | 218
2018-05-31 13:00 | 221 | 221
2018-05-31 13:30 | 226 | 226
2018-05-31 14:00 | 233 | 232
2018-05-31 14:30 | 239 | 239
2018-05-31 15:00 | 243 | 243
2018-05-31 15:30 | 251 | 251
2018-05-31 16:00 | 264 | 264
2018-05-31 16:30 | 281 | 281
2018-05-31 17:00 | 305 | 303
2018-05-31 17:30 | 322 | 321
2018-05-31 18:00 | 323 | 321
2018-05-31 18:30 | 323 | 321
2018-05-31 19:00 | 319 | 316
2018-05-31 19:30 | 309 | 308
2018-05-31 20:00 | 307 | 305
2018-05-31 20:30 | 294 | 291
2018-05-31 21:00 | 284 | 280
2018-05-31 21:30 | 269 | 265
2018-05-31 22:00 | 256 | 256
2018-05-31 22:30 | 250 | 249
2018-05-31 23:00 | 239 | 238
2018-05-31 23:30 | 228 | 227
2018-06-01 | 217 | 216
2018-06-01 00:30 | 210 | 208
2018-06-01 01:00 | 200 | 198
2018-06-01 01:30 | 190 | 187
2018-06-01 02:00 | 189 | 186
2018-06-01 02:30 | 187 | 184
2018-06-01 03:00 | 188 | 185
2018-06-01 03:30 | 187 | 184
2018-06-01 04:00 | 193 | 190
2018-06-01 04:30 | 198 | 196
2018-06-01 05:00 | 207 | 206
2018-06-01 05:30 | 220 | 219
2018-06-01 06:00 | 241 | 240
2018-06-01 06:30 | 272 | 272
2018-06-01 07:00 | 295 | 294
2018-06-01 07:30 | 300 | 298
2018-06-01 08:00 | 287 | 286
2018-06-01 08:30 | 277 | 275
2018-06-01 09:00 | 271 | 269
2018-06-01 09:30 | 261 | 259
2018-06-01 10:00 | 251 | 249
2018-06-01 10:30 | 244 | 242
2018-06-01 11:00 | 243 | 241
2018-06-01 11:30 | 237 | 235
2018-06-01 12:00 | 235 | 235
2018-06-01 12:30 | 235 | 235
2018-06-01 13:00 | 236 | 236
2018-06-01 13:30 | 241 | 241
2018-06-01 14:00 | 247 | 247
2018-06-01 14:30 | 250 | 250
2018-06-01 15:00 | 256 | 256
2018-06-01 15:30 | 269 | 269
2018-06-01 16:00 | 282 | 282
2018-06-01 16:30 | 297 | 296
2018-06-01 17:00 | 315 | 315
2018-06-01 17:30 | 324 | 324
2018-06-01 18:00 | 321 | 320
2018-06-01 18:30 | 319 | 318
2018-06-01 19:00 | 308 | 307
2018-06-01 19:30 | 304 | 304
2018-06-01 20:00 | 306 | 306
2018-06-01 20:30 | 294 | 293
2018-06-01 21:00 | 277 | 276
2018-06-01 21:30 | 268 | 267
2018-06-01 22:00 | 267 | 266
2018-06-01 22:30 | 260 | 259
2018-06-01 23:00 | 253 | 251
2018-06-01 23:30 | 237 | 235
2018-06-02 | 225 | 222
2018-06-02 00:30 | 208 | 204
2018-06-02 01:00 | 202 | 198
2018-06-02 01:30 | 195 | 191
2018-06-02 02:00 | 190 | 188
2018-06-02 02:30 | 190 | 188
2018-06-02 03:00 | 189 | 187
2018-06-02 03:30 | 191 | 189
2018-06-02 04:00 | 195 | 193
2018-06-02 04:30 | 197 | 195
2018-06-02 05:00 | 205 | 204
2018-06-02 05:30 | 210 | 209
2018-06-02 06:00 | 222 | 221
2018-06-02 06:30 | 237 | 237
2018-06-02 07:00 | 256 | 255
2018-06-02 07:30 | 268 | 267
2018-06-02 08:00 | 273 | 273
2018-06-02 08:30 | 270 | 270
2018-06-02 09:00 | 269 | 269
2018-06-02 09:30 | 259 | 258
2018-06-02 10:00 | 249 | 248
2018-06-02 10:30 | 239 | 238
2018-06-02 11:00 | 227 | 227
2018-06-02 11:30 | 221 | 221
2018-06-02 12:00 | 218 | 217
2018-06-02 12:30 | 211 | 210
2018-06-02 13:00 | 215 | 214
2018-06-02 13:30 | 224 | 223
2018-06-02 14:00 | 226 | 226
2018-06-02 14:30 | 231 | 230
2018-06-02 15:00 | 237 | 236
2018-06-02 15:30 | 248 | 247
2018-06-02 16:00 | 258 | 258
2018-06-02 16:30 | 278 | 278
2018-06-02 17:00 | 292 | 292
2018-06-02 17:30 | 299 | 299
2018-06-02 18:00 | 297 | 296
2018-06-02 18:30 | 291 | 290
2018-06-02 19:00 | 284 | 283
2018-06-02 19:30 | 284 | 284
2018-06-02 20:00 | 289 | 289
2018-06-02 20:30 | 273 | 273
2018-06-02 21:00 | 262 | 262
2018-06-02 21:30 | 253 | 253
2018-06-02 22:00 | 247 | 247
2018-06-02 22:30 | 246 | 245
2018-06-02 23:00 | 233 | 233
2018-06-02 23:30 | 221 | 220
2018-06-03 | 212 | 210
2018-06-03 00:30 | 206 | 205
2018-06-03 01:00 | 200 | 198
2018-06-03 01:30 | 194 | 193
2018-06-03 02:00 | 192 | 192
2018-06-03 02:30 | 188 | 188
2018-06-03 03:00 | 186 | 186
2018-06-03 03:30 | 186 | 185
2018-06-03 04:00 | 183 | 182
2018-06-03 04:30 | 182 | 182
2018-06-03 05:00 | 187 | 186
2018-06-03 05:30 | 191 | 191
2018-06-03 06:00 | 199 | 198
2018-06-03 06:30 | 205 | 205
2018-06-03 07:00 | 217 | 217
2018-06-03 07:30 | 224 | 224
2018-06-03 08:00 | 232 | 232
2018-06-03 08:30 | 237 | 237
2018-06-03 09:00 | 237 | 237
2018-06-03 09:30 | 236 | 236
2018-06-03 10:00 | 231 | 231
2018-06-03 10:30 | 227 | 227
2018-06-03 11:00 | 221 | 220
2018-06-03 11:30 | 214 | 214
2018-06-03 12:00 | 211 | 210
2018-06-03 12:30 | 211 | 211
2018-06-03 13:00 | 215 | 214
2018-06-03 13:30 | 220 | 220
2018-06-03 14:00 | 220 | 220
2018-06-03 14:30 | 224 | 223
2018-06-03 15:00 | 236 | 236
2018-06-03 15:30 | 250 | 250
2018-06-03 16:00 | 261 | 261
2018-06-03 16:30 | 274 | 274
2018-06-03 17:00 | 287 | 287
2018-06-03 17:30 | 296 | 296
2018-06-03 18:00 | 290 | 290
2018-06-03 18:30 | 287 | 287
2018-06-03 19:00 | 277 | 277
2018-06-03 19:30 | 277 | 277
2018-06-03 20:00 | 279 | 278
2018-06-03 20:30 | 266 | 265
2018-06-03 21:00 | 257 | 256
2018-06-03 21:30 | 249 | 248
2018-06-03 22:00 | 236 | 235
2018-06-03 22:30 | 234 | 234
2018-06-03 23:00 | 227 | 226
2018-06-03 23:30 | 215 | 213
2018-06-04 | 203 | 202
2018-06-04 00:30 | 195 | 195
2018-06-04 01:00 | 193 | 192
2018-06-04 01:30 | 192 | 192
2018-06-04 02:00 | 188 | 187
2018-06-04 02:30 | 186 | 185
2018-06-04 03:00 | 185 | 185
2018-06-04 03:30 | 181 | 180
2018-06-04 04:00 | 184 | 184
2018-06-04 04:30 | 187 | 187
2018-06-04 05:00 | 201 | 201
2018-06-04 05:30 | 215 | 215
2018-06-04 06:00 | 242 | 241
2018-06-04 06:30 | 249 | 249
2018-06-04 07:00 | 264 | 264
2018-06-04 07:30 | 265 | 265
2018-06-04 08:00 | 249 | 249
2018-06-04 08:30 | 234 | 234
2018-06-04 09:00 | 227 | 227
2018-06-04 09:30 | 221 | 220
2018-06-04 10:00 | 220 | 219
2018-06-04 10:30 | 215 | 215
2018-06-04 11:00 | 207 | 207
2018-06-04 11:30 | 196 | 196
2018-06-04 12:00 | 196 | 195
2018-06-04 12:30 | 202 | 202
2018-06-04 13:00 | 210 | 209
2018-06-04 13:30 | 211 | 211
2018-06-04 14:00 | 218 | 218
2018-06-04 14:30 | 221 | 221
2018-06-04 15:00 | 232 | 232
2018-06-04 15:30 | 265 | 265
2018-06-04 16:00 | 282 | 281
2018-06-04 16:30 | 299 | 299
2018-06-04 17:00 | 318 | 317
2018-06-04 17:30 | 328 | 328
2018-06-04 18:00 | 325 | 325
2018-06-04 18:30 | 324 | 323
2018-06-04 19:00 | 315 | 314
2018-06-04 19:30 | 312 | 311
2018-06-04 20:00 | 311 | 310
2018-06-04 20:30 | 288 | 288
2018-06-04 21:00 | 268 | 268
2018-06-04 21:30 | 253 | 253
2018-06-04 22:00 | 251 | 251
2018-06-04 22:30 | 244 | 244
2018-06-04 23:00 | 236 | 236
2018-06-04 23:30 | 223 | 222
2018-06-05 | 210 | 209
2018-06-05 00:30 | 200 | 199
2018-06-05 01:00 | 193 | 192
2018-06-05 01:30 | 191 | 191
2018-06-05 02:00 | 190 | 190
2018-06-05 02:30 | 183 | 183
2018-06-05 03:00 | 182 | 182
2018-06-05 03:30 | 180 | 180
2018-06-05 04:00 | 181 | 181
2018-06-05 04:30 | 182 | 182
2018-06-05 05:00 | 197 | 197
2018-06-05 05:30 | 216 | 216
2018-06-05 06:00 | 243 | 243
2018-06-05 06:30 | 270 | 270
2018-06-05 07:00 | 288 | 288
2018-06-05 07:30 | 291 | 291
2018-06-05 08:00 | 282 | 282
2018-06-05 08:30 | 266 | 266
2018-06-05 09:00 | 261 | 261
2018-06-05 09:30 | 254 | 254
2018-06-05 10:00 | 247 | 247
2018-06-05 10:30 | 243 | 242
2018-06-05 11:00 | 235 | 235
2018-06-05 11:30 | 231 | 231
2018-06-05 12:00 | 225 | 225
2018-06-05 12:30 | 223 | 222
2018-06-05 13:00 | 227 | 226
2018-06-05 13:30 | 234 | 233
2018-06-05 14:00 | 240 | 239
2018-06-05 14:30 | 243 | 242
2018-06-05 15:00 | 255 | 253
2018-06-05 15:30 | 272 | 271
2018-06-05 16:00 | 289 | 287
2018-06-05 16:30 | 307 | 306
2018-06-05 17:00 | 335 | 334
2018-06-05 17:30 | 319 | 317
2018-06-05 18:00 | 322 | 320
2018-06-05 18:30 | 318 | 317
2018-06-05 19:00 | 303 | 302
2018-06-05 19:30 | 310 | 310
2018-06-05 20:00 | 300 | 300
2018-06-05 20:30 | 280 | 280
2018-06-05 21:00 | 264 | 264
2018-06-05 21:30 | 248 | 248
2018-06-05 22:00 | 244 | 243
2018-06-05 22:30 | 238 | 237
2018-06-05 23:00 | 228 | 226
2018-06-05 23:30 | 213 | 211
2018-06-06 | 198 | 198
2018-06-06 00:30 | 189 | 188
2018-06-06 01:00 | 181 | 180
2018-06-06 01:30 | 174 | 173
2018-06-06 02:00 | 171 | 170
2018-06-06 02:30 | 168 | 167
2018-06-06 03:00 | 167 | 166
2018-06-06 03:30 | 165 | 163
2018-06-06 04:00 | 166 | 165
2018-06-06 04:30 | 169 | 168
2018-06-06 05:00 | 180 | 179
2018-06-06 05:30 | 199 | 199
2018-06-06 06:00 | 229 | 229
2018-06-06 06:30 | 262 | 261
2018-06-06 07:00 | 276 | 276
2018-06-06 07:30 | 282 | 282
2018-06-06 08:00 | 275 | 275
2018-06-06 08:30 | 274 | 274
2018-06-06 09:00 | 283 | 283
2018-06-06 09:30 | 262 | 262
2018-06-06 10:00 | 251 | 251
2018-06-06 10:30 | 244 | 244
2018-06-06 11:00 | 245 | 245
2018-06-06 11:30 | 243 | 243
2018-06-06 12:00 | 254 | 254
2018-06-06 12:30 | 246 | 246
2018-06-06 13:00 | 243 | 242
2018-06-06 13:30 | 242 | 242
2018-06-06 14:00 | 248 | 248
2018-06-06 14:30 | 252 | 251
2018-06-06 15:00 | 268 | 267
2018-06-06 15:30 | 287 | 287
2018-06-06 16:00 | 301 | 300
2018-06-06 16:30 | 333 | 333
2018-06-06 17:00 | 330 | 330
2018-06-06 17:30 | 328 | 328
2018-06-06 18:00 | 324 | 323
2018-06-06 18:30 | 318 | 318
2018-06-06 19:00 | 312 | 312
2018-06-06 19:30 | 312 | 311
2018-06-06 20:00 | 308 | 307
2018-06-06 20:30 | 294 | 294
2018-06-06 21:00 | 278 | 277
2018-06-06 21:30 | 264 | 264
2018-06-06 22:00 | 254 | 254
2018-06-06 22:30 | 252 | 251
2018-06-06 23:00 | 241 | 240
2018-06-06 23:30 | 227 | 226
2018-06-07 | 209 | 208
2018-06-07 00:30 | 191 | 191
2018-06-07 01:00 | 179 | 178
2018-06-07 01:30 | 172 | 171
2018-06-07 02:00 | 169 | 168
2018-06-07 02:30 | 168 | 168
2018-06-07 03:00 | 169 | 168
2018-06-07 03:30 | 169 | 168
2018-06-07 04:00 | 167 | 166
2018-06-07 04:30 | 173 | 172
2018-06-07 05:00 | 180 | 179
2018-06-07 05:30 | 197 | 197
2018-06-07 06:00 | 231 | 231
2018-06-07 06:30 | 265 | 264
2018-06-07 07:00 | 293 | 293
2018-06-07 07:30 | 310 | 310
2018-06-07 08:00 | 313 | 313
2018-06-07 08:30 | 309 | 309
2018-06-07 09:00 | 306 | 306
2018-06-07 09:30 | 297 | 296
2018-06-07 10:00 | 289 | 288
2018-06-07 10:30 | 281 | 281
2018-06-07 11:00 | 264 | 263
2018-06-07 11:30 | 251 | 251
2018-06-07 12:00 | 263 | 263
2018-06-07 12:30 | 263 | 262
2018-06-07 13:00 | 254 | 254
2018-06-07 13:30 | 258 | 258
2018-06-07 14:00 | 263 | 263
2018-06-07 14:30 | 266 | 266
2018-06-07 15:00 | 275 | 275
2018-06-07 15:30 | 281 | 281
2018-06-07 16:00 | 292 | 291
2018-06-07 16:30 | 309 | 308
2018-06-07 17:00 | 333 | 332
2018-06-07 17:30 | 343 | 343
2018-06-07 18:00 | 333 | 332
2018-06-07 18:30 | 339 | 338
2018-06-07 19:00 | 323 | 322
2018-06-07 19:30 | 314 | 314
2018-06-07 20:00 | 309 | 309
2018-06-07 20:30 | 299 | 299
2018-06-07 21:00 | 285 | 285
2018-06-07 21:30 | 277 | 277
2018-06-07 22:00 | 266 | 266
2018-06-07 22:30 | 257 | 257
2018-06-07 23:00 | 249 | 248
2018-06-07 23:30 | 235 | 234
2018-06-08 | 235 | 234
2018-06-08 00:30 | 211 | 210
2018-06-08 01:00 | 198 | 197
2018-06-08 01:30 | 193 | 193
2018-06-08 02:00 | 188 | 187
2018-06-08 02:30 | 192 | 191
2018-06-08 03:00 | 189 | 189
2018-06-08 03:30 | 186 | 185
2018-06-08 04:00 | 187 | 186
2018-06-08 04:30 | 187 | 186
2018-06-08 05:00 | 199 | 199
2018-06-08 05:30 | 213 | 213
2018-06-08 06:00 | 236 | 236
2018-06-08 06:30 | 264 | 263
2018-06-08 07:00 | 285 | 284
2018-06-08 07:30 | 296 | 294
2018-06-08 08:00 | 295 | 294
2018-06-08 08:30 | 283 | 282
2018-06-08 09:00 | 270 | 269
2018-06-08 09:30 | 267 | 266
2018-06-08 10:00 | 243 | 242
2018-06-08 10:30 | 239 | 238
2018-06-08 11:00 | 243 | 243
2018-06-08 11:30 | 237 | 237
2018-06-08 12:00 | 234 | 234
2018-06-08 12:30 | 255 | 254
2018-06-08 13:00 | 255 | 255
2018-06-08 13:30 | 261 | 261
2018-06-08 14:00 | 274 | 274
2018-06-08 14:30 | 274 | 273
2018-06-08 15:00 | 295 | 294
2018-06-08 15:30 | 323 | 321
2018-06-08 16:00 | 334 | 332
2018-06-08 16:30 | 348 | 346
2018-06-08 17:00 | 348 | 348
2018-06-08 17:30 | 360 | 360
2018-06-08 18:00 | 355 | 355
2018-06-08 18:30 | 353 | 353
2018-06-08 19:00 | 342 | 342
2018-06-08 19:30 | 344 | 343
2018-06-08 20:00 | 339 | 338
2018-06-08 20:30 | 309 | 308
2018-06-08 21:00 | 302 | 302
2018-06-08 21:30 | 300 | 299
2018-06-08 22:00 | 268 | 267
2018-06-08 22:30 | 262 | 262
2018-06-08 23:00 | 253 | 253
2018-06-08 23:30 | 247 | 247
2018-06-09 | 245 | 245
2018-06-09 00:30 | 239 | 239
2018-06-09 01:00 | 205 | 205
2018-06-09 01:30 | 193 | 192
2018-06-09 02:00 | 190 | 189
2018-06-09 02:30 | 190 | 190
2018-06-09 03:00 | 190 | 190
2018-06-09 03:30 | 191 | 190
2018-06-09 04:00 | 192 | 191
2018-06-09 04:30 | 196 | 196
2018-06-09 05:00 | 199 | 198
2018-06-09 05:30 | 200 | 200
2018-06-09 06:00 | 210 | 210
2018-06-09 06:30 | 219 | 219
2018-06-09 07:00 | 239 | 239
2018-06-09 07:30 | 252 | 251
2018-06-09 08:00 | 263 | 263
2018-06-09 08:30 | 272 | 272
2018-06-09 09:00 | 290 | 290
2018-06-09 09:30 | 294 | 294
2018-06-09 10:00 | 293 | 293
2018-06-09 10:30 | 286 | 286
2018-06-09 11:00 | 289 | 289
2018-06-09 11:30 | 286 | 286
2018-06-09 12:00 | 276 | 276
2018-06-09 12:30 | 263 | 263
2018-06-09 13:00 | 258 | 257
2018-06-09 13:30 | 264 | 264
2018-06-09 14:00 | 263 | 263
2018-06-09 14:30 | 260 | 259
2018-06-09 15:00 | 258 | 257
2018-06-09 15:30 | 259 | 259
2018-06-09 16:00 | 267 | 266
2018-06-09 16:30 | 285 | 285
2018-06-09 17:00 | 313 | 313
2018-06-09 17:30 | 304 | 303
2018-06-09 18:00 | 302 | 302
2018-06-09 18:30 | 306 | 306
2018-06-09 19:00 | 310 | 310
2018-06-09 19:30 | 304 | 304
2018-06-09 20:00 | 305 | 305
2018-06-09 20:30 | 288 | 287
2018-06-09 21:00 | 273 | 272
2018-06-09 21:30 | 266 | 265
2018-06-09 22:00 | 255 | 255
2018-06-09 22:30 | 253 | 252
2018-06-09 23:00 | 247 | 246
2018-06-09 23:30 | 231 | 230
2018-06-10 | 220 | 219
2018-06-10 00:30 | 209 | 208
2018-06-10 01:00 | 196 | 195
2018-06-10 01:30 | 189 | 188
2018-06-10 02:00 | 184 | 183
2018-06-10 02:30 | 181 | 180
2018-06-10 03:00 | 184 | 183
2018-06-10 03:30 | 182 | 181
2018-06-10 04:00 | 184 | 183
2018-06-10 04:30 | 187 | 186
2018-06-10 05:00 | 186 | 185
2018-06-10 05:30 | 188 | 187
2018-06-10 06:00 | 199 | 198
2018-06-10 06:30 | 207 | 207
2018-06-10 07:00 | 220 | 219
2018-06-10 07:30 | 234 | 234
2018-06-10 08:00 | 250 | 250
2018-06-10 08:30 | 261 | 261
2018-06-10 09:00 | 276 | 276
2018-06-10 09:30 | 268 | 268
2018-06-10 10:00 | 256 | 256
2018-06-10 10:30 | 232 | 232
2018-06-10 11:00 | 234 | 234
2018-06-10 11:30 | 219 | 218
2018-06-10 12:00 | 215 | 214
2018-06-10 12:30 | 212 | 212
2018-06-10 13:00 | 212 | 212
2018-06-10 13:30 | 215 | 214
2018-06-10 14:00 | 221 | 221
2018-06-10 14:30 | 227 | 226
2018-06-10 15:00 | 233 | 233
2018-06-10 15:30 | 239 | 238
2018-06-10 16:00 | 255 | 255
2018-06-10 16:30 | 271 | 271
2018-06-10 17:00 | 287 | 287
2018-06-10 17:30 | 295 | 295
2018-06-10 18:00 | 292 | 290
2018-06-10 18:30 | 284 | 284
2018-06-10 19:00 | 276 | 276
2018-06-10 19:30 | 268 | 268
2018-06-10 20:00 | 268 | 268
2018-06-10 20:30 | 256 | 256
2018-06-10 21:00 | 250 | 250
2018-06-10 21:30 | 247 | 247
2018-06-10 22:00 | 239 | 239
2018-06-10 22:30 | 237 | 237
2018-06-10 23:00 | 225 | 225
2018-06-10 23:30 | 214 | 214
2018-06-11 | 203 | 203
2018-06-11 00:30 | 200 | 199
2018-06-11 01:00 | 194 | 194
2018-06-11 01:30 | 191 | 190
2018-06-11 02:00 | 187 | 186
2018-06-11 02:30 | 184 | 183
2018-06-11 03:00 | 182 | 181
2018-06-11 03:30 | 182 | 181
2018-06-11 04:00 | 184 | 184
2018-06-11 04:30 | 189 | 189
2018-06-11 05:00 | 197 | 197
2018-06-11 05:30 | 208 | 207
2018-06-11 06:00 | 222 | 222
2018-06-11 06:30 | 238 | 238
2018-06-11 07:00 | 256 | 256
2018-06-11 07:30 | 263 | 262
2018-06-11 08:00 | 260 | 259
2018-06-11 08:30 | 256 | 256
2018-06-11 09:00 | 247 | 247
2018-06-11 09:30 | 232 | 232
2018-06-11 10:00 | 226 | 225
2018-06-11 10:30 | 222 | 221
2018-06-11 11:00 | 213 | 213
2018-06-11 11:30 | 210 | 209
2018-06-11 12:00 | 205 | 204
2018-06-11 12:30 | 223 | 222
2018-06-11 13:00 | 229 | 229
2018-06-11 13:30 | 234 | 233
2018-06-11 14:00 | 231 | 231
2018-06-11 14:30 | 233 | 233
2018-06-11 15:00 | 235 | 234
2018-06-11 15:30 | 245 | 245
2018-06-11 16:00 | 262 | 262
2018-06-11 16:30 | 282 | 280
2018-06-11 17:00 | 307 | 306
2018-06-11 17:30 | 317 | 317
2018-06-11 18:00 | 315 | 314
2018-06-11 18:30 | 313 | 312
2018-06-11 19:00 | 308 | 306
2018-06-11 19:30 | 295 | 295
2018-06-11 20:00 | 285 | 285
2018-06-11 20:30 | 276 | 276
2018-06-11 21:00 | 262 | 262
2018-06-11 21:30 | 242 | 242
2018-06-11 22:00 | 235 | 235
2018-06-11 22:30 | 234 | 234
2018-06-11 23:00 | 226 | 225
2018-06-11 23:30 | 216 | 216
2018-06-12 | 200 | 199
2018-06-12 00:30 | 195 | 194
2018-06-12 01:00 | 189 | 188
2018-06-12 01:30 | 186 | 185
2018-06-12 02:00 | 183 | 182
2018-06-12 02:30 | 180 | 179
2018-06-12 03:00 | 183 | 182
2018-06-12 03:30 | 185 | 184
2018-06-12 04:00 | 189 | 188
2018-06-12 04:30 | 185 | 185
2018-06-12 05:00 | 198 | 198
2018-06-12 05:30 | 210 | 210
2018-06-12 06:00 | 240 | 240
2018-06-12 06:30 | 266 | 266
2018-06-12 07:00 | 284 | 284
2018-06-12 07:30 | 288 | 288
2018-06-12 08:00 | 283 | 283
2018-06-12 08:30 | 273 | 272
2018-06-12 09:00 | 266 | 265
2018-06-12 09:30 | 262 | 261
2018-06-12 10:00 | 241 | 241
2018-06-12 10:30 | 230 | 229
2018-06-12 11:00 | 236 | 234
2018-06-12 11:30 | 235 | 233
2018-06-12 12:00 | 231 | 230
2018-06-12 12:30 | 234 | 233
2018-06-12 13:00 | 240 | 239
2018-06-12 13:30 | 247 | 246
2018-06-12 14:00 | 251 | 250
2018-06-12 14:30 | 244 | 243
2018-06-12 15:00 | 247 | 247
2018-06-12 15:30 | 249 | 249
2018-06-12 16:00 | 263 | 262
2018-06-12 16:30 | 285 | 284
2018-06-12 17:00 | 309 | 308
2018-06-12 17:30 | 322 | 322
2018-06-12 18:00 | 322 | 322
2018-06-12 18:30 | 314 | 314
2018-06-12 19:00 | 306 | 305
2018-06-12 19:30 | 304 | 304
2018-06-12 20:00 | 302 | 302
2018-06-12 20:30 | 288 | 288
2018-06-12 21:00 | 276 | 276
2018-06-12 21:30 | 258 | 258
2018-06-12 22:00 | 247 | 247
2018-06-12 22:30 | 243 | 242
2018-06-12 23:00 | 232 | 232
2018-06-12 23:30 | 220 | 220
2018-06-13 | 210 | 209
2018-06-13 00:30 | 203 | 203
2018-06-13 01:00 | 193 | 193
2018-06-13 01:30 | 187 | 187
2018-06-13 02:00 | 184 | 184
2018-06-13 02:30 | 181 | 181
2018-06-13 03:00 | 180 | 180
2018-06-13 03:30 | 183 | 182
2018-06-13 04:00 | 185 | 185
2018-06-13 04:30 | 187 | 187
2018-06-13 05:00 | 195 | 194
2018-06-13 05:30 | 208 | 208
2018-06-13 06:00 | 234 | 234
2018-06-13 06:30 | 261 | 261
2018-06-13 07:00 | 281 | 281
2018-06-13 07:30 | 282 | 282
2018-06-13 08:00 | 272 | 272
2018-06-13 08:30 | 256 | 256
2018-06-13 09:00 | 244 | 244
2018-06-13 09:30 | 238 | 238
2018-06-13 10:00 | 241 | 241
2018-06-13 10:30 | 234 | 233
2018-06-13 11:00 | 238 | 237
2018-06-13 11:30 | 232 | 232
2018-06-13 12:00 | 232 | 231
2018-06-13 12:30 | 238 | 238
2018-06-13 13:00 | 229 | 229
2018-06-13 13:30 | 232 | 232
2018-06-13 14:00 | 243 | 243
2018-06-13 14:30 | 241 | 241
2018-06-13 15:00 | 236 | 236
2018-06-13 15:30 | 251 | 251
2018-06-13 16:00 | 263 | 263
2018-06-13 16:30 | 281 | 280
2018-06-13 17:00 | 308 | 307
2018-06-13 17:30 | 323 | 322
2018-06-13 18:00 | 317 | 316
2018-06-13 18:30 | 317 | 316
2018-06-13 19:00 | 310 | 308
2018-06-13 19:30 | 309 | 307
2018-06-13 20:00 | 305 | 303
2018-06-13 20:30 | 298 | 295
2018-06-13 21:00 | 277 | 276
2018-06-13 21:30 | 260 | 260
2018-06-13 22:00 | 251 | 250
2018-06-13 22:30 | 243 | 242
2018-06-13 23:00 | 228 | 227
2018-06-13 23:30 | 215 | 213
2018-06-14 | 200 | 199
2018-06-14 00:30 | 193 | 192
2018-06-14 01:00 | 184 | 184
2018-06-14 01:30 | 178 | 177
2018-06-14 02:00 | 178 | 177
2018-06-14 02:30 | 173 | 172
2018-06-14 03:00 | 171 | 171
2018-06-14 03:30 | 172 | 171
2018-06-14 04:00 | 174 | 173
2018-06-14 04:30 | 177 | 177
2018-06-14 05:00 | 187 | 187
2018-06-14 05:30 | 198 | 198
2018-06-14 06:00 | 225 | 225
2018-06-14 06:30 | 254 | 254
2018-06-14 07:00 | 266 | 266
2018-06-14 07:30 | 263 | 263
2018-06-14 08:00 | 254 | 254
2018-06-14 08:30 | 242 | 242
2018-06-14 09:00 | 235 | 235
2018-06-14 09:30 | 227 | 227
2018-06-14 10:00 | 225 | 224
2018-06-14 10:30 | 216 | 216
2018-06-14 11:00 | 212 | 211
2018-06-14 11:30 | 210 | 210
2018-06-14 12:00 | 214 | 214
2018-06-14 12:30 | 211 | 211
2018-06-14 13:00 | 208 | 208
2018-06-14 13:30 | 216 | 216
2018-06-14 14:00 | 225 | 225
2018-06-14 14:30 | 228 | 228
2018-06-14 15:00 | 234 | 234
2018-06-14 15:30 | 244 | 244
2018-06-14 16:00 | 260 | 259
2018-06-14 16:30 | 274 | 273
2018-06-14 17:00 | 290 | 290
2018-06-14 17:30 | 298 | 298
2018-06-14 18:00 | 293 | 292
2018-06-14 18:30 | 295 | 295
2018-06-14 19:00 | 291 | 290
2018-06-14 19:30 | 291 | 290
2018-06-14 20:00 | 287 | 285
2018-06-14 20:30 | 278 | 276
2018-06-14 21:00 | 260 | 259
2018-06-14 21:30 | 248 | 247
2018-06-14 22:00 | 238 | 238
2018-06-14 22:30 | 232 | 231
2018-06-14 23:00 | 223 | 222
2018-06-14 23:30 | 210 | 209
2018-06-15 | 195 | 194
2018-06-15 00:30 | 186 | 185
2018-06-15 01:00 | 175 | 174
2018-06-15 01:30 | 169 | 167
2018-06-15 02:00 | 168 | 166
2018-06-15 02:30 | 165 | 164
2018-06-15 03:00 | 163 | 162
2018-06-15 03:30 | 160 | 158
2018-06-15 04:00 | 162 | 160
2018-06-15 04:30 | 165 | 164
2018-06-15 05:00 | 176 | 175
2018-06-15 05:30 | 196 | 195
2018-06-15 06:00 | 223 | 223
2018-06-15 06:30 | 253 | 253
2018-06-15 07:00 | 279 | 279
2018-06-15 07:30 | 285 | 284
2018-06-15 08:00 | 271 | 270
2018-06-15 08:30 | 260 | 258
2018-06-15 09:00 | 247 | 245
2018-06-15 09:30 | 229 | 228
2018-06-15 10:00 | 219 | 219
2018-06-15 10:30 | 212 | 212
2018-06-15 11:00 | 205 | 205
2018-06-15 11:30 | 200 | 200
2018-06-15 12:00 | 198 | 198
2018-06-15 12:30 | 198 | 198
2018-06-15 13:00 | 201 | 201
2018-06-15 13:30 | 203 | 203
2018-06-15 14:00 | 213 | 213
2018-06-15 14:30 | 218 | 218
2018-06-15 15:00 | 225 | 225
2018-06-15 15:30 | 238 | 238
2018-06-15 16:00 | 251 | 251
2018-06-15 16:30 | 267 | 267
2018-06-15 17:00 | 296 | 296
2018-06-15 17:30 | 307 | 307
2018-06-15 18:00 | 299 | 299
2018-06-15 18:30 | 300 | 299
2018-06-15 19:00 | 292 | 291
2018-06-15 19:30 | 291 | 289
2018-06-15 20:00 | 291 | 289
2018-06-15 20:30 | 276 | 275
2018-06-15 21:00 | 265 | 264
2018-06-15 21:30 | 254 | 254
2018-06-15 22:00 | 248 | 247
2018-06-15 22:30 | 245 | 244
2018-06-15 23:00 | 234 | 233
2018-06-15 23:30 | 219 | 218
2018-06-16 | 205 | 205
2018-06-16 00:30 | 194 | 193
2018-06-16 01:00 | 185 | 184
2018-06-16 01:30 | 180 | 179
2018-06-16 02:00 | 177 | 175
2018-06-16 02:30 | 171 | 170
2018-06-16 03:00 | 165 | 164
2018-06-16 03:30 | 164 | 164
2018-06-16 04:00 | 167 | 167
2018-06-16 04:30 | 161 | 161
2018-06-16 05:00 | 155 | 155
2018-06-16 05:30 | 169 | 169
2018-06-16 06:00 | 184 | 184
2018-06-16 06:30 | 174 | 173
2018-06-16 07:00 | 218 | 218
2018-06-16 07:30 | 230 | 230
2018-06-16 08:00 | 236 | 235
2018-06-16 08:30 | 233 | 233
2018-06-16 09:00 | 230 | 230
2018-06-16 09:30 | 216 | 216
2018-06-16 10:00 | 206 | 206
2018-06-16 10:30 | 197 | 196
2018-06-16 11:00 | 186 | 186
2018-06-16 11:30 | 180 | 179
2018-06-16 12:00 | 176 | 175
2018-06-16 12:30 | 175 | 175
2018-06-16 13:00 | 179 | 178
2018-06-16 13:30 | 184 | 183
2018-06-16 14:00 | 190 | 189
2018-06-16 14:30 | 202 | 201
2018-06-16 15:00 | 208 | 207
2018-06-16 15:30 | 217 | 216
2018-06-16 16:00 | 232 | 232
2018-06-16 16:30 | 250 | 250
2018-06-16 17:00 | 275 | 274
2018-06-16 17:30 | 283 | 282
2018-06-16 18:00 | 277 | 276
2018-06-16 18:30 | 276 | 274
2018-06-16 19:00 | 272 | 271
2018-06-16 19:30 | 268 | 267
2018-06-16 20:00 | 264 | 264
2018-06-16 20:30 | 259 | 259
2018-06-16 21:00 | 252 | 252
2018-06-16 21:30 | 246 | 246
2018-06-16 22:00 | 236 | 236
2018-06-16 22:30 | 236 | 235
2018-06-16 23:00 | 228 | 227
2018-06-16 23:30 | 217 | 216
2018-06-17 | 204 | 202
2018-06-17 00:30 | 199 | 197
2018-06-17 01:00 | 189 | 186
2018-06-17 01:30 | 183 | 180
2018-06-17 02:00 | 179 | 176
2018-06-17 02:30 | 176 | 174
2018-06-17 03:00 | 173 | 172
2018-06-17 03:30 | 168 | 167
2018-06-17 04:00 | 163 | 161
2018-06-17 04:30 | 163 | 162
2018-06-17 05:00 | 170 | 169
2018-06-17 05:30 | 183 | 182
2018-06-17 06:00 | 192 | 191
2018-06-17 06:30 | 200 | 200
2018-06-17 07:00 | 215 | 215
2018-06-17 07:30 | 219 | 219
2018-06-17 08:00 | 229 | 229
2018-06-17 08:30 | 232 | 232
2018-06-17 09:00 | 229 | 229
2018-06-17 09:30 | 224 | 224
2018-06-17 10:00 | 218 | 218
2018-06-17 10:30 | 214 | 214
2018-06-17 11:00 | 209 | 209
2018-06-17 11:30 | 205 | 205
2018-06-17 12:00 | 202 | 202
2018-06-17 12:30 | 199 | 199
2018-06-17 13:00 | 201 | 201
2018-06-17 13:30 | 202 | 202
2018-06-17 14:00 | 207 | 207
2018-06-17 14:30 | 215 | 215
2018-06-17 15:00 | 219 | 219
2018-06-17 15:30 | 233 | 233
2018-06-17 16:00 | 244 | 244
2018-06-17 16:30 | 263 | 263
2018-06-17 17:00 | 290 | 289
2018-06-17 17:30 | 304 | 304
2018-06-17 18:00 | 304 | 303
2018-06-17 18:30 | 304 | 303
2018-06-17 19:00 | 298 | 297
2018-06-17 19:30 | 291 | 290
2018-06-17 20:00 | 285 | 284
2018-06-17 20:30 | 273 | 272
2018-06-17 21:00 | 264 | 263
2018-06-17 21:30 | 252 | 250
2018-06-17 22:00 | 240 | 238
2018-06-17 22:30 | 236 | 234
2018-06-17 23:00 | 230 | 226
2018-06-17 23:30 | 218 | 213
2018-06-18 | 203 | 200
2018-06-18 00:30 | 192 | 191
2018-06-18 01:00 | 186 | 185
2018-06-18 01:30 | 180 | 178
2018-06-18 02:00 | 180 | 178
2018-06-18 02:30 | 179 | 177
2018-06-18 03:00 | 176 | 175
2018-06-18 03:30 | 174 | 173
2018-06-18 04:00 | 179 | 177
2018-06-18 04:30 | 184 | 183
2018-06-18 05:00 | 196 | 195
2018-06-18 05:30 | 213 | 213
2018-06-18 06:00 | 242 | 242
2018-06-18 06:30 | 277 | 277
2018-06-18 07:00 | 304 | 302
2018-06-18 07:30 | 316 | 315
2018-06-18 08:00 | 306 | 304
2018-06-18 08:30 | 285 | 284
2018-06-18 09:00 | 272 | 269
2018-06-18 09:30 | 257 | 254
2018-06-18 10:00 | 242 | 241
2018-06-18 10:30 | 229 | 229
2018-06-18 11:00 | 221 | 221
2018-06-18 11:30 | 216 | 216
2018-06-18 12:00 | 211 | 211
2018-06-18 12:30 | 213 | 213
2018-06-18 13:00 | 213 | 213
2018-06-18 13:30 | 219 | 219
2018-06-18 14:00 | 225 | 225
2018-06-18 14:30 | 232 | 232
2018-06-18 15:00 | 243 | 243
2018-06-18 15:30 | 258 | 258
2018-06-18 16:00 | 274 | 273
2018-06-18 16:30 | 302 | 302
2018-06-18 17:00 | 340 | 340
2018-06-18 17:30 | 362 | 360
2018-06-18 18:00 | 359 | 358
2018-06-18 18:30 | 355 | 353
2018-06-18 19:00 | 347 | 345
2018-06-18 19:30 | 342 | 340
2018-06-18 20:00 | 338 | 337
2018-06-18 20:30 | 308 | 308
2018-06-18 21:00 | 289 | 288
2018-06-18 21:30 | 275 | 273
2018-06-18 22:00 | 257 | 257
2018-06-18 22:30 | 252 | 251
2018-06-18 23:00 | 243 | 243
2018-06-18 23:30 | 230 | 229
2018-06-19 | 214 | 213
2018-06-19 00:30 | 208 | 205
2018-06-19 01:00 | 202 | 199
2018-06-19 01:30 | 196 | 193
2018-06-19 02:00 | 195 | 192
2018-06-19 02:30 | 193 | 190
2018-06-19 03:00 | 197 | 195
2018-06-19 03:30 | 198 | 196
2018-06-19 04:00 | 200 | 198
2018-06-19 04:30 | 205 | 203
2018-06-19 05:00 | 217 | 216
2018-06-19 05:30 | 232 | 232
2018-06-19 06:00 | 259 | 259
2018-06-19 06:30 | 295 | 295
2018-06-19 07:00 | 315 | 314
2018-06-19 07:30 | 316 | 315
2018-06-19 08:00 | 300 | 299
2018-06-19 08:30 | 281 | 279
2018-06-19 09:00 | 264 | 263
2018-06-19 09:30 | 248 | 247
2018-06-19 10:00 | 235 | 234
2018-06-19 10:30 | 230 | 229
2018-06-19 11:00 | 223 | 222
2018-06-19 11:30 | 219 | 217
2018-06-19 12:00 | 220 | 218
2018-06-19 12:30 | 223 | 221
2018-06-19 13:00 | 225 | 222
2018-06-19 13:30 | 229 | 227
2018-06-19 14:00 | 237 | 235
2018-06-19 14:30 | 241 | 240
2018-06-19 15:00 | 249 | 247
2018-06-19 15:30 | 261 | 259
2018-06-19 16:00 | 280 | 278
2018-06-19 16:30 | 305 | 304
2018-06-19 17:00 | 338 | 338
2018-06-19 17:30 | 357 | 355
2018-06-19 18:00 | 360 | 358
2018-06-19 18:30 | 359 | 356
2018-06-19 19:00 | 351 | 349
2018-06-19 19:30 | 346 | 345
2018-06-19 20:00 | 340 | 338
2018-06-19 20:30 | 316 | 315
2018-06-19 21:00 | 297 | 296
2018-06-19 21:30 | 282 | 282
2018-06-19 22:00 | 279 | 278
2018-06-19 22:30 | 271 | 270
2018-06-19 23:00 | 257 | 257
2018-06-19 23:30 | 237 | 237
2018-06-20 | 218 | 218
2018-06-20 00:30 | 211 | 211
2018-06-20 01:00 | 207 | 206
2018-06-20 01:30 | 203 | 203
2018-06-20 02:00 | 196 | 195
2018-06-20 02:30 | 187 | 186
2018-06-20 03:00 | 185 | 184
2018-06-20 03:30 | 186 | 185
2018-06-20 04:00 | 197 | 197
2018-06-20 04:30 | 204 | 203
2018-06-20 05:00 | 208 | 207
2018-06-20 05:30 | 220 | 220
2018-06-20 06:00 | 246 | 246
2018-06-20 06:30 | 281 | 281
2018-06-20 07:00 | 312 | 312
2018-06-20 07:30 | 319 | 318
2018-06-20 08:00 | 303 | 303
2018-06-20 08:30 | 283 | 282
2018-06-20 09:00 | 265 | 264
2018-06-20 09:30 | 251 | 250
2018-06-20 10:00 | 243 | 242
2018-06-20 10:30 | 232 | 232
2018-06-20 11:00 | 225 | 225
2018-06-20 11:30 | 220 | 220
2018-06-20 12:00 | 217 | 217
2018-06-20 12:30 | 218 | 218
2018-06-20 13:00 | 226 | 226
2018-06-20 13:30 | 230 | 230
2018-06-20 14:00 | 239 | 239
2018-06-20 14:30 | 240 | 240
2018-06-20 15:00 | 249 | 249
2018-06-20 15:30 | 263 | 263
2018-06-20 16:00 | 284 | 284
2018-06-20 16:30 | 312 | 311
2018-06-20 17:00 | 335 | 334
2018-06-20 17:30 | 353 | 353
2018-06-20 18:00 | 355 | 354
2018-06-20 18:30 | 352 | 351
2018-06-20 19:00 | 342 | 340
2018-06-20 19:30 | 336 | 334
2018-06-20 20:00 | 332 | 329
2018-06-20 20:30 | 313 | 311
2018-06-20 21:00 | 288 | 288
2018-06-20 21:30 | 270 | 269
2018-06-20 22:00 | 258 | 258
2018-06-20 22:30 | 247 | 247
2018-06-20 23:00 | 236 | 235
2018-06-20 23:30 | 223 | 221
2018-06-21 | 209 | 208
2018-06-21 00:30 | 201 | 199
2018-06-21 01:00 | 197 | 195
2018-06-21 01:30 | 193 | 191
2018-06-21 02:00 | 190 | 187
2018-06-21 02:30 | 189 | 186
2018-06-21 03:00 | 187 | 184
2018-06-21 03:30 | 184 | 181
2018-06-21 04:00 | 187 | 184
2018-06-21 04:30 | 192 | 189
2018-06-21 05:00 | 205 | 204
2018-06-21 05:30 | 222 | 221
2018-06-21 06:00 | 247 | 247
2018-06-21 06:30 | 279 | 278
2018-06-21 07:00 | 300 | 299
2018-06-21 07:30 | 318 | 317
2018-06-21 08:00 | 335 | 334
2018-06-21 08:30 | 325 | 324
2018-06-21 09:00 | 312 | 312
2018-06-21 09:30 | 286 | 285
2018-06-21 10:00 | 280 | 279
2018-06-21 10:30 | 284 | 283
2018-06-21 11:00 | 276 | 275
2018-06-21 11:30 | 274 | 273
2018-06-21 12:00 | 268 | 266
2018-06-21 12:30 | 268 | 266
2018-06-21 13:00 | 266 | 264
2018-06-21 13:30 | 275 | 273
2018-06-21 14:00 | 280 | 278
2018-06-21 14:30 | 292 | 290
2018-06-21 15:00 | 304 | 303
2018-06-21 15:30 | 293 | 292
2018-06-21 16:00 | 300 | 298
2018-06-21 16:30 | 313 | 312
2018-06-21 17:00 | 345 | 345
2018-06-21 17:30 | 379 | 379
2018-06-21 18:00 | 385 | 385
2018-06-21 18:30 | 378 | 377
2018-06-21 19:00 | 371 | 370
2018-06-21 19:30 | 354 | 353
2018-06-21 20:00 | 359 | 358
2018-06-21 20:30 | 337 | 335
2018-06-21 21:00 | 303 | 300
2018-06-21 21:30 | 278 | 278
2018-06-21 22:00 | 278 | 278
2018-06-21 22:30 | 270 | 270
2018-06-21 23:00 | 260 | 259
2018-06-21 23:30 | 246 | 244
2018-06-22 | 232 | 230
2018-06-22 00:30 | 221 | 219
2018-06-22 01:00 | 215 | 212
2018-06-22 01:30 | 207 | 204
2018-06-22 02:00 | 207 | 205
2018-06-22 02:30 | 200 | 197
2018-06-22 03:00 | 197 | 194
2018-06-22 03:30 | 197 | 194
2018-06-22 04:00 | 196 | 193
2018-06-22 04:30 | 193 | 190
2018-06-22 05:00 | 205 | 203
2018-06-22 05:30 | 228 | 227
2018-06-22 06:00 | 258 | 258
2018-06-22 06:30 | 288 | 288
2018-06-22 07:00 | 313 | 313
2018-06-22 07:30 | 317 | 316
2018-06-22 08:00 | 317 | 316
2018-06-22 08:30 | 287 | 286
2018-06-22 09:00 | 272 | 271
2018-06-22 09:30 | 263 | 262
2018-06-22 10:00 | 265 | 265
2018-06-22 10:30 | 250 | 249
2018-06-22 11:00 | 246 | 246
2018-06-22 11:30 | 234 | 234
2018-06-22 12:00 | 230 | 230
2018-06-22 12:30 | 232 | 232
2018-06-22 13:00 | 234 | 234
2018-06-22 13:30 | 239 | 239
2018-06-22 14:00 | 245 | 245
2018-06-22 14:30 | 252 | 252
2018-06-22 15:00 | 259 | 258
2018-06-22 15:30 | 274 | 272
2018-06-22 16:00 | 293 | 291
2018-06-22 16:30 | 304 | 302
2018-06-22 17:00 | 325 | 324
2018-06-22 17:30 | 334 | 334
2018-06-22 18:00 | 339 | 338
2018-06-22 18:30 | 352 | 352
2018-06-22 19:00 | 353 | 353
2018-06-22 19:30 | 337 | 336
2018-06-22 20:00 | 335 | 333
2018-06-22 20:30 | 322 | 321
2018-06-22 21:00 | 328 | 326
2018-06-22 21:30 | 305 | 303
2018-06-22 22:00 | 280 | 279
2018-06-22 22:30 | 271 | 270
2018-06-22 23:00 | 257 | 257
2018-06-22 23:30 | 242 | 241
2018-06-23 | 225 | 223
2018-06-23 00:30 | 213 | 210
2018-06-23 01:00 | 205 | 202
2018-06-23 01:30 | 203 | 200
2018-06-23 02:00 | 198 | 195
2018-06-23 02:30 | 193 | 189
2018-06-23 03:00 | 187 | 184
2018-06-23 03:30 | 187 | 183
2018-06-23 04:00 | 185 | 181
2018-06-23 04:30 | 186 | 182
2018-06-23 05:00 | 188 | 185
2018-06-23 05:30 | 193 | 190
2018-06-23 06:00 | 212 | 210
2018-06-23 06:30 | 229 | 228
2018-06-23 07:00 | 248 | 248
2018-06-23 07:30 | 264 | 264
2018-06-23 08:00 | 271 | 271
2018-06-23 08:30 | 268 | 268
2018-06-23 09:00 | 293 | 292
2018-06-23 09:30 | 282 | 282
2018-06-23 10:00 | 273 | 272
2018-06-23 10:30 | 255 | 254
2018-06-23 11:00 | 237 | 237
2018-06-23 11:30 | 218 | 217
2018-06-23 12:00 | 211 | 209
2018-06-23 12:30 | 208 | 206
2018-06-23 13:00 | 209 | 206
2018-06-23 13:30 | 211 | 209
2018-06-23 14:00 | 215 | 213
2018-06-23 14:30 | 221 | 219
2018-06-23 15:00 | 222 | 220
2018-06-23 15:30 | 241 | 239
2018-06-23 16:00 | 231 | 229
2018-06-23 16:30 | 273 | 272
2018-06-23 17:00 | 289 | 288
2018-06-23 17:30 | 299 | 297
2018-06-23 18:00 | 297 | 295
2018-06-23 18:30 | 292 | 291
2018-06-23 19:00 | 286 | 285
2018-06-23 19:30 | 287 | 287
2018-06-23 20:00 | 289 | 289
2018-06-23 20:30 | 283 | 283
2018-06-23 21:00 | 274 | 274
2018-06-23 21:30 | 269 | 269
2018-06-23 22:00 | 264 | 264
2018-06-23 22:30 | 263 | 262
2018-06-23 23:00 | 252 | 252
2018-06-23 23:30 | 236 | 235
2018-06-24 | 218 | 217
2018-06-24 00:30 | 207 | 205
2018-06-24 01:00 | 199 | 197
2018-06-24 01:30 | 194 | 192
2018-06-24 02:00 | 186 | 181
2018-06-24 02:30 | 186 | 181
2018-06-24 03:00 | 191 | 186
2018-06-24 03:30 | 191 | 186
2018-06-24 04:00 | 191 | 186
2018-06-24 04:30 | 188 | 184
2018-06-24 05:00 | 189 | 185
2018-06-24 05:30 | 192 | 188
2018-06-24 06:00 | 201 | 198
2018-06-24 06:30 | 210 | 208
2018-06-24 07:00 | 222 | 221
2018-06-24 07:30 | 235 | 234
2018-06-24 08:00 | 248 | 247
2018-06-24 08:30 | 251 | 251
2018-06-24 09:00 | 248 | 248
2018-06-24 09:30 | 238 | 238
2018-06-24 10:00 | 227 | 227
2018-06-24 10:30 | 217 | 216
2018-06-24 11:00 | 210 | 209
2018-06-24 11:30 | 207 | 207
2018-06-24 12:00 | 205 | 204
2018-06-24 12:30 | 204 | 203
2018-06-24 13:00 | 208 | 207
2018-06-24 13:30 | 218 | 218
2018-06-24 14:00 | 221 | 220
2018-06-24 14:30 | 231 | 230
2018-06-24 15:00 | 238 | 238
2018-06-24 15:30 | 247 | 247
2018-06-24 16:00 | 263 | 263
2018-06-24 16:30 | 292 | 290
2018-06-24 17:00 | 310 | 306
2018-06-24 17:30 | 327 | 323
2018-06-24 18:00 | 324 | 320
2018-06-24 18:30 | 321 | 318
2018-06-24 19:00 | 314 | 311
2018-06-24 19:30 | 314 | 311
2018-06-24 20:00 | 309 | 306
2018-06-24 20:30 | 297 | 297
2018-06-24 21:00 | 285 | 285
2018-06-24 21:30 | 269 | 269
2018-06-24 22:00 | 260 | 260
2018-06-24 22:30 | 253 | 253
2018-06-24 23:00 | 239 | 239
2018-06-24 23:30 | 222 | 222
2018-06-25 | 203 | 203
2018-06-25 00:30 | 193 | 193
2018-06-25 01:00 | 187 | 187
2018-06-25 01:30 | 183 | 182
2018-06-25 02:00 | 180 | 179
2018-06-25 02:30 | 182 | 181
2018-06-25 03:00 | 182 | 181
2018-06-25 03:30 | 185 | 184
2018-06-25 04:00 | 190 | 189
2018-06-25 04:30 | 195 | 194
2018-06-25 05:00 | 201 | 201
2018-06-25 05:30 | 220 | 220
2018-06-25 06:00 | 254 | 254
2018-06-25 06:30 | 285 | 285
2018-06-25 07:00 | 294 | 294
2018-06-25 07:30 | 325 | 324
2018-06-25 08:00 | 325 | 324
2018-06-25 08:30 | 311 | 310
2018-06-25 09:00 | 297 | 296
2018-06-25 09:30 | 291 | 289
2018-06-25 10:00 | 287 | 287
2018-06-25 10:30 | 268 | 268
2018-06-25 11:00 | 247 | 247
2018-06-25 11:30 | 241 | 241
2018-06-25 12:00 | 239 | 239
2018-06-25 12:30 | 250 | 250
2018-06-25 13:00 | 246 | 246
2018-06-25 13:30 | 248 | 247
2018-06-25 14:00 | 258 | 258
2018-06-25 14:30 | 263 | 263
2018-06-25 15:00 | 264 | 264
2018-06-25 15:30 | 264 | 263
2018-06-25 16:00 | 282 | 281
2018-06-25 16:30 | 308 | 306
2018-06-25 17:00 | 333 | 332
2018-06-25 17:30 | 354 | 354
2018-06-25 18:00 | 353 | 352
2018-06-25 18:30 | 351 | 350
2018-06-25 19:00 | 338 | 336
2018-06-25 19:30 | 331 | 329
2018-06-25 20:00 | 325 | 323
2018-06-25 20:30 | 312 | 309
2018-06-25 21:00 | 295 | 292
2018-06-25 21:30 | 275 | 275
2018-06-25 22:00 | 294 | 294
2018-06-25 22:30 | 264 | 262
2018-06-25 23:00 | 243 | 241
2018-06-25 23:30 | 220 | 219
2018-06-26 | 207 | 205
2018-06-26 00:30 | 199 | 197
2018-06-26 01:00 | 190 | 187
2018-06-26 01:30 | 182 | 179
2018-06-26 02:00 | 181 | 177
2018-06-26 02:30 | 179 | 175
2018-06-26 03:00 | 177 | 175
2018-06-26 03:30 | 175 | 174
2018-06-26 04:00 | 180 | 179
2018-06-26 04:30 | 181 | 180
2018-06-26 05:00 | 192 | 192
2018-06-26 05:30 | 210 | 210
2018-06-26 06:00 | 241 | 241
2018-06-26 06:30 | 273 | 273
2018-06-26 07:00 | 284 | 284
2018-06-26 07:30 | 286 | 285
2018-06-26 08:00 | 281 | 281
2018-06-26 08:30 | 269 | 268
2018-06-26 09:00 | 256 | 256
2018-06-26 09:30 | 246 | 246
2018-06-26 10:00 | 243 | 243
2018-06-26 10:30 | 234 | 234
2018-06-26 11:00 | 226 | 226
2018-06-26 11:30 | 232 | 232
2018-06-26 12:00 | 237 | 237
2018-06-26 12:30 | 237 | 237
2018-06-26 13:00 | 247 | 247
2018-06-26 13:30 | 240 | 240
2018-06-26 14:00 | 242 | 242
2018-06-26 14:30 | 248 | 248
2018-06-26 15:00 | 255 | 255
2018-06-26 15:30 | 262 | 262
2018-06-26 16:00 | 279 | 279
2018-06-26 16:30 | 302 | 301
2018-06-26 17:00 | 321 | 320
2018-06-26 17:30 | 329 | 328
2018-06-26 18:00 | 327 | 326
2018-06-26 18:30 | 325 | 325
2018-06-26 19:00 | 316 | 315
2018-06-26 19:30 | 310 | 309
2018-06-26 20:00 | 306 | 305
2018-06-26 20:30 | 292 | 291
2018-06-26 21:00 | 274 | 274
2018-06-26 21:30 | 261 | 261
2018-06-26 22:00 | 254 | 253
2018-06-26 22:30 | 251 | 251
2018-06-26 23:00 | 237 | 236
2018-06-26 23:30 | 218 | 217
2018-06-27 | 203 | 201
2018-06-27 00:30 | 194 | 191
2018-06-27 01:00 | 186 | 183
2018-06-27 01:30 | 180 | 177
2018-06-27 02:00 | 176 | 173
2018-06-27 02:30 | 175 | 172
2018-06-27 03:00 | 175 | 172
2018-06-27 03:30 | 176 | 173
2018-06-27 04:00 | 181 | 178
2018-06-27 04:30 | 186 | 184
2018-06-27 05:00 | 194 | 192
2018-06-27 05:30 | 206 | 205
2018-06-27 06:00 | 236 | 236
2018-06-27 06:30 | 258 | 258
2018-06-27 07:00 | 281 | 281
2018-06-27 07:30 | 295 | 295
2018-06-27 08:00 | 296 | 295
2018-06-27 08:30 | 287 | 286
2018-06-27 09:00 | 276 | 275
2018-06-27 09:30 | 275 | 275
2018-06-27 10:00 | 282 | 282
2018-06-27 10:30 | 283 | 283
2018-06-27 11:00 | 279 | 278
2018-06-27 11:30 | 276 | 275
2018-06-27 12:00 | 276 | 276
2018-06-27 12:30 | 279 | 278
2018-06-27 13:00 | 277 | 276
2018-06-27 13:30 | 275 | 274
2018-06-27 14:00 | 277 | 276
2018-06-27 14:30 | 280 | 279
2018-06-27 15:00 | 286 | 285
2018-06-27 15:30 | 297 | 296
2018-06-27 16:00 | 310 | 309
2018-06-27 16:30 | 323 | 323
2018-06-27 17:00 | 337 | 337
2018-06-27 17:30 | 346 | 346
2018-06-27 18:00 | 342 | 342
2018-06-27 18:30 | 341 | 340
2018-06-27 19:00 | 330 | 329
2018-06-27 19:30 | 326 | 324
2018-06-27 20:00 | 320 | 318
2018-06-27 20:30 | 302 | 301
2018-06-27 21:00 | 283 | 283
2018-06-27 21:30 | 269 | 269
2018-06-27 22:00 | 260 | 260
2018-06-27 22:30 | 258 | 257
2018-06-27 23:00 | 243 | 242
2018-06-27 23:30 | 224 | 223
2018-06-28 | 208 | 205
2018-06-28 00:30 | 197 | 195
2018-06-28 01:00 | 189 | 187
2018-06-28 01:30 | 182 | 180
2018-06-28 02:00 | 180 | 177
2018-06-28 02:30 | 178 | 174
2018-06-28 03:00 | 178 | 174
2018-06-28 03:30 | 179 | 176
2018-06-28 04:00 | 184 | 181
2018-06-28 04:30 | 190 | 188
2018-06-28 05:00 | 202 | 201
2018-06-28 05:30 | 216 | 215
2018-06-28 06:00 | 237 | 236
2018-06-28 06:30 | 258 | 258
2018-06-28 07:00 | 283 | 283
2018-06-28 07:30 | 293 | 292
2018-06-28 08:00 | 290 | 288
2018-06-28 08:30 | 279 | 277
2018-06-28 09:00 | 266 | 265
2018-06-28 09:30 | 267 | 266
2018-06-28 10:00 | 262 | 261
2018-06-28 10:30 | 257 | 257
2018-06-28 11:00 | 254 | 253
2018-06-28 11:30 | 257 | 256
2018-06-28 12:00 | 251 | 251
2018-06-28 12:30 | 243 | 242
2018-06-28 13:00 | 235 | 234
2018-06-28 13:30 | 237 | 236
2018-06-28 14:00 | 239 | 238
2018-06-28 14:30 | 241 | 240
2018-06-28 15:00 | 264 | 263
2018-06-28 15:30 | 282 | 281
2018-06-28 16:00 | 285 | 284
2018-06-28 16:30 | 315 | 315
2018-06-28 17:00 | 329 | 329
2018-06-28 17:30 | 356 | 355
2018-06-28 18:00 | 356 | 354
2018-06-28 18:30 | 334 | 332
2018-06-28 19:00 | 327 | 324
2018-06-28 19:30 | 322 | 320
2018-06-28 20:00 | 319 | 318
2018-06-28 20:30 | 309 | 308
2018-06-28 21:00 | 289 | 288
2018-06-28 21:30 | 270 | 270
2018-06-28 22:00 | 265 | 265
2018-06-28 22:30 | 261 | 261
2018-06-28 23:00 | 250 | 249
2018-06-28 23:30 | 236 | 235
2018-06-29 | 215 | 214
2018-06-29 00:30 | 203 | 201
2018-06-29 01:00 | 194 | 192
2018-06-29 01:30 | 187 | 183
2018-06-29 02:00 | 181 | 178
2018-06-29 02:30 | 177 | 176
2018-06-29 03:00 | 177 | 176
2018-06-29 03:30 | 179 | 177
2018-06-29 04:00 | 181 | 180
2018-06-29 04:30 | 182 | 182
2018-06-29 05:00 | 192 | 191
2018-06-29 05:30 | 205 | 204
2018-06-29 06:00 | 224 | 224
2018-06-29 06:30 | 256 | 255
2018-06-29 07:00 | 279 | 279
2018-06-29 07:30 | 289 | 289
2018-06-29 08:00 | 281 | 281
2018-06-29 08:30 | 267 | 266
2018-06-29 09:00 | 264 | 264
2018-06-29 09:30 | 253 | 253
2018-06-29 10:00 | 245 | 245
2018-06-29 10:30 | 232 | 232
2018-06-29 11:00 | 225 | 225
2018-06-29 11:30 | 221 | 221
2018-06-29 12:00 | 221 | 221
2018-06-29 12:30 | 220 | 220
2018-06-29 13:00 | 223 | 223
2018-06-29 13:30 | 224 | 224
2018-06-29 14:00 | 229 | 229
2018-06-29 14:30 | 233 | 233
2018-06-29 15:00 | 238 | 238
2018-06-29 15:30 | 252 | 252
2018-06-29 16:00 | 265 | 265
2018-06-29 16:30 | 282 | 282
2018-06-29 17:00 | 303 | 301
2018-06-29 17:30 | 312 | 310
2018-06-29 18:00 | 314 | 311
2018-06-29 18:30 | 308 | 306
2018-06-29 19:00 | 291 | 290
2018-06-29 19:30 | 285 | 285
2018-06-29 20:00 | 286 | 286
2018-06-29 20:30 | 277 | 277
2018-06-29 21:00 | 270 | 270
2018-06-29 21:30 | 258 | 258
2018-06-29 22:00 | 255 | 255
2018-06-29 22:30 | 251 | 251
2018-06-29 23:00 | 244 | 243
2018-06-29 23:30 | 230 | 229
2018-06-30 | 209 | 207
2018-06-30 00:30 | 195 | 193
2018-06-30 01:00 | 185 | 182
2018-06-30 01:30 | 176 | 174
2018-06-30 02:00 | 173 | 172
2018-06-30 02:30 | 173 | 171
2018-06-30 03:00 | 172 | 171
2018-06-30 03:30 | 170 | 169
2018-06-30 04:00 | 172 | 170
2018-06-30 04:30 | 175 | 174
2018-06-30 05:00 | 180 | 179
2018-06-30 05:30 | 186 | 186
2018-06-30 06:00 | 196 | 195
2018-06-30 06:30 | 208 | 208
2018-06-30 07:00 | 226 | 226
2018-06-30 07:30 | 248 | 248
2018-06-30 08:00 | 264 | 264
2018-06-30 08:30 | 267 | 267
2018-06-30 09:00 | 272 | 272
2018-06-30 09:30 | 264 | 264
2018-06-30 10:00 | 250 | 250
2018-06-30 10:30 | 236 | 236
2018-06-30 11:00 | 222 | 222
2018-06-30 11:30 | 219 | 219
2018-06-30 12:00 | 215 | 215
2018-06-30 12:30 | 212 | 212
2018-06-30 13:00 | 212 | 212
2018-06-30 13:30 | 216 | 216
2018-06-30 14:00 | 213 | 213
2018-06-30 14:30 | 215 | 215
2018-06-30 15:00 | 223 | 223
2018-06-30 15:30 | 236 | 236
2018-06-30 16:00 | 246 | 246
2018-06-30 16:30 | 270 | 270
2018-06-30 17:00 | 289 | 289
2018-06-30 17:30 | 293 | 292
2018-06-30 18:00 | 290 | 289
2018-06-30 18:30 | 287 | 285
2018-06-30 19:00 | 280 | 279
2018-06-30 19:30 | 277 | 277
2018-06-30 20:00 | 280 | 280
2018-06-30 20:30 | 273 | 273
2018-06-30 21:00 | 266 | 266
2018-06-30 21:30 | 264 | 264
2018-06-30 22:00 | 256 | 255
2018-06-30 22:30 | 255 | 253
2018-06-30 23:00 | 242 | 239
2018-06-30 23:30 | 227 | 224
2018-07-01 | 205 | 203
2018-07-01 00:30 | 193 | 190
2018-07-01 01:00 | 185 | 182
2018-07-01 01:30 | 180 | 177
2018-07-01 02:00 | 175 | 173
2018-07-01 02:30 | 172 | 171
2018-07-01 03:00 | 173 | 172
2018-07-01 03:30 | 172 | 170
2018-07-01 04:00 | 170 | 168
2018-07-01 04:30 | 172 | 171
2018-07-01 05:00 | 174 | 172
2018-07-01 05:30 | 179 | 178
2018-07-01 06:00 | 187 | 186
2018-07-01 06:30 | 196 | 195
2018-07-01 07:00 | 206 | 205
2018-07-01 07:30 | 225 | 225
2018-07-01 08:00 | 240 | 240
2018-07-01 08:30 | 246 | 246
2018-07-01 09:00 | 252 | 252
2018-07-01 09:30 | 249 | 249
2018-07-01 10:00 | 251 | 251
2018-07-01 10:30 | 244 | 244
2018-07-01 11:00 | 226 | 226
2018-07-01 11:30 | 223 | 222
2018-07-01 12:00 | 226 | 226
2018-07-01 12:30 | 216 | 216
2018-07-01 13:00 | 213 | 213
2018-07-01 13:30 | 215 | 214
2018-07-01 14:00 | 221 | 221
2018-07-01 14:30 | 226 | 225
2018-07-01 15:00 | 232 | 232
2018-07-01 15:30 | 241 | 241
2018-07-01 16:00 | 259 | 259
2018-07-01 16:30 | 272 | 272
2018-07-01 17:00 | 290 | 290
2018-07-01 17:30 | 303 | 301
2018-07-01 18:00 | 302 | 300
2018-07-01 18:30 | 291 | 290
2018-07-01 19:00 | 274 | 273
2018-07-01 19:30 | 270 | 269
2018-07-01 20:00 | 267 | 265
2018-07-01 20:30 | 258 | 258
2018-07-01 21:00 | 249 | 248
2018-07-01 21:30 | 241 | 241
2018-07-01 22:00 | 236 | 235
2018-07-01 22:30 | 234 | 233
2018-07-01 23:00 | 219 | 218
2018-07-01 23:30 | 197 | 195
2018-07-02 | 185 | 183
2018-07-02 00:30 | 177 | 176
2018-07-02 01:00 | 170 | 169
2018-07-02 01:30 | 165 | 163
2018-07-02 02:00 | 162 | 161
2018-07-02 02:30 | 165 | 163
2018-07-02 03:00 | 164 | 163
2018-07-02 03:30 | 164 | 162
2018-07-02 04:00 | 168 | 167
2018-07-02 04:30 | 172 | 171
2018-07-02 05:00 | 178 | 177
2018-07-02 05:30 | 191 | 191
2018-07-02 06:00 | 217 | 217
2018-07-02 06:30 | 240 | 240
2018-07-02 07:00 | 259 | 259
2018-07-02 07:30 | 275 | 275
2018-07-02 08:00 | 287 | 287
2018-07-02 08:30 | 272 | 270
2018-07-02 09:00 | 261 | 259
2018-07-02 09:30 | 248 | 248
2018-07-02 10:00 | 238 | 237
2018-07-02 10:30 | 231 | 231
2018-07-02 11:00 | 232 | 232
2018-07-02 11:30 | 230 | 230
2018-07-02 12:00 | 224 | 224
2018-07-02 12:30 | 224 | 224
2018-07-02 13:00 | 230 | 230
2018-07-02 13:30 | 231 | 230
2018-07-02 14:00 | 235 | 235
2018-07-02 14:30 | 236 | 235
2018-07-02 15:00 | 241 | 240
2018-07-02 15:30 | 252 | 251
2018-07-02 16:00 | 274 | 274
2018-07-02 16:30 | 296 | 295
2018-07-02 17:00 | 309 | 308
2018-07-02 17:30 | 324 | 322
2018-07-02 18:00 | 318 | 315
2018-07-02 18:30 | 305 | 303
2018-07-02 19:00 | 292 | 291
2018-07-02 19:30 | 288 | 288
2018-07-02 20:00 | 285 | 285
2018-07-02 20:30 | 267 | 267
2018-07-02 21:00 | 254 | 254
2018-07-02 21:30 | 238 | 238
2018-07-02 22:00 | 228 | 228
2018-07-02 22:30 | 223 | 223
2018-07-02 23:00 | 210 | 210
2018-07-02 23:30 | 197 | 197
2018-07-03 | 182 | 182
2018-07-03 00:30 | 174 | 173
2018-07-03 01:00 | 164 | 163
2018-07-03 01:30 | 159 | 157
2018-07-03 02:00 | 158 | 157
2018-07-03 02:30 | 159 | 158
2018-07-03 03:00 | 160 | 159
2018-07-03 03:30 | 162 | 160
2018-07-03 04:00 | 162 | 160
2018-07-03 04:30 | 165 | 164
2018-07-03 05:00 | 174 | 173
2018-07-03 05:30 | 185 | 185
2018-07-03 06:00 | 204 | 204
2018-07-03 06:30 | 227 | 227
2018-07-03 07:00 | 245 | 245
2018-07-03 07:30 | 255 | 255
2018-07-03 08:00 | 256 | 256
2018-07-03 08:30 | 247 | 247
2018-07-03 09:00 | 238 | 238
2018-07-03 09:30 | 233 | 233
2018-07-03 10:00 | 223 | 222
2018-07-03 10:30 | 211 | 211
2018-07-03 11:00 | 205 | 205
2018-07-03 11:30 | 209 | 209
2018-07-03 12:00 | 207 | 207
2018-07-03 12:30 | 207 | 207
2018-07-03 13:00 | 215 | 215
2018-07-03 13:30 | 211 | 211
2018-07-03 14:00 | 213 | 213
2018-07-03 14:30 | 215 | 215
2018-07-03 15:00 | 218 | 218
2018-07-03 15:30 | 226 | 226
2018-07-03 16:00 | 239 | 239
2018-07-03 16:30 | 257 | 257
2018-07-03 17:00 | 280 | 280
2018-07-03 17:30 | 298 | 297
2018-07-03 18:00 | 298 | 297
2018-07-03 18:30 | 296 | 294
2018-07-03 19:00 | 291 | 291
2018-07-03 19:30 | 287 | 287
2018-07-03 20:00 | 280 | 280
2018-07-03 20:30 | 262 | 262
2018-07-03 21:00 | 249 | 249
2018-07-03 21:30 | 235 | 234
2018-07-03 22:00 | 224 | 223
2018-07-03 22:30 | 218 | 217
2018-07-03 23:00 | 207 | 206
2018-07-03 23:30 | 194 | 192
2018-07-04 | 181 | 179
2018-07-04 00:30 | 172 | 170
2018-07-04 01:00 | 167 | 165
2018-07-04 01:30 | 165 | 164
2018-07-04 02:00 | 156 | 155
2018-07-04 02:30 | 158 | 157
2018-07-04 03:00 | 154 | 152
2018-07-04 03:30 | 156 | 155
2018-07-04 04:00 | 156 | 155
2018-07-04 04:30 | 158 | 157
2018-07-04 05:00 | 169 | 168
2018-07-04 05:30 | 180 | 180
2018-07-04 06:00 | 207 | 207
2018-07-04 06:30 | 226 | 226
2018-07-04 07:00 | 251 | 251
2018-07-04 07:30 | 263 | 263
2018-07-04 08:00 | 267 | 267
2018-07-04 08:30 | 258 | 258
2018-07-04 09:00 | 245 | 245
2018-07-04 09:30 | 234 | 234
2018-07-04 10:00 | 226 | 226
2018-07-04 10:30 | 215 | 215
2018-07-04 11:00 | 215 | 215
2018-07-04 11:30 | 211 | 211
2018-07-04 12:00 | 206 | 206
2018-07-04 12:30 | 207 | 207
2018-07-04 13:00 | 210 | 210
2018-07-04 13:30 | 214 | 214
2018-07-04 14:00 | 221 | 221
2018-07-04 14:30 | 229 | 229
2018-07-04 15:00 | 241 | 241
2018-07-04 15:30 | 250 | 250
2018-07-04 16:00 | 260 | 260
2018-07-04 16:30 | 258 | 258
2018-07-04 17:00 | 277 | 277
2018-07-04 17:30 | 294 | 293
2018-07-04 18:00 | 290 | 289
2018-07-04 18:30 | 289 | 288
2018-07-04 19:00 | 277 | 276
2018-07-04 19:30 | 273 | 272
2018-07-04 20:00 | 256 | 255
2018-07-04 20:30 | 234 | 234
2018-07-04 21:00 | 243 | 243
2018-07-04 21:30 | 226 | 226
2018-07-04 22:00 | 218 | 218
2018-07-04 22:30 | 214 | 214
2018-07-04 23:00 | 206 | 206
2018-07-04 23:30 | 193 | 193
2018-07-05 | 165 | 164
2018-07-05 00:30 | 176 | 175
2018-07-05 01:00 | 163 | 162
2018-07-05 01:30 | 154 | 152
2018-07-05 02:00 | 151 | 149
2018-07-05 02:30 | 152 | 151
2018-07-05 03:00 | 153 | 151
2018-07-05 03:30 | 142 | 141
2018-07-05 04:00 | 155 | 154
2018-07-05 04:30 | 156 | 155
2018-07-05 05:00 | 165 | 164
2018-07-05 05:30 | 183 | 182
2018-07-05 06:00 | 199 | 199
2018-07-05 06:30 | 216 | 216
2018-07-05 07:00 | 241 | 241
2018-07-05 07:30 | 254 | 254
2018-07-05 08:00 | 254 | 254
2018-07-05 08:30 | 250 | 250
2018-07-05 09:00 | 246 | 246
2018-07-05 09:30 | 243 | 243
2018-07-05 10:00 | 242 | 242
2018-07-05 10:30 | 231 | 231
2018-07-05 11:00 | 223 | 223
2018-07-05 11:30 | 222 | 222
2018-07-05 12:00 | 223 | 223
2018-07-05 12:30 | 220 | 220
2018-07-05 13:00 | 224 | 223
2018-07-05 13:30 | 230 | 230
2018-07-05 14:00 | 239 | 239
2018-07-05 14:30 | 237 | 237
2018-07-05 15:00 | 243 | 243
2018-07-05 15:30 | 238 | 238
2018-07-05 16:00 | 245 | 245
2018-07-05 16:30 | 256 | 256
2018-07-05 17:00 | 275 | 275
2018-07-05 17:30 | 286 | 285
2018-07-05 18:00 | 281 | 281
2018-07-05 18:30 | 280 | 279
2018-07-05 19:00 | 272 | 271
2018-07-05 19:30 | 259 | 258
2018-07-05 20:00 | 248 | 248
2018-07-05 20:30 | 247 | 247
2018-07-05 21:00 | 236 | 235
2018-07-05 21:30 | 225 | 225
2018-07-05 22:00 | 220 | 219
2018-07-05 22:30 | 212 | 212
2018-07-05 23:00 | 203 | 202
2018-07-05 23:30 | 193 | 191
2018-07-06 | 178 | 176
2018-07-06 00:30 | 170 | 167
2018-07-06 01:00 | 166 | 163
2018-07-06 01:30 | 161 | 158
2018-07-06 02:00 | 159 | 158
2018-07-06 02:30 | 160 | 158
2018-07-06 03:00 | 156 | 155
2018-07-06 03:30 | 162 | 160
2018-07-06 04:00 | 164 | 163
2018-07-06 04:30 | 165 | 164
2018-07-06 05:00 | 170 | 170
2018-07-06 05:30 | 180 | 180
2018-07-06 06:00 | 197 | 197
2018-07-06 06:30 | 214 | 214
2018-07-06 07:00 | 236 | 236
2018-07-06 07:30 | 247 | 247
2018-07-06 08:00 | 251 | 251
2018-07-06 08:30 | 243 | 242
2018-07-06 09:00 | 237 | 236
2018-07-06 09:30 | 236 | 235
2018-07-06 10:00 | 235 | 235
2018-07-06 10:30 | 245 | 244
2018-07-06 11:00 | 243 | 242
2018-07-06 11:30 | 244 | 244
2018-07-06 12:00 | 232 | 232
2018-07-06 12:30 | 226 | 226
2018-07-06 13:00 | 234 | 233
2018-07-06 13:30 | 231 | 231
2018-07-06 14:00 | 228 | 228
2018-07-06 14:30 | 230 | 230
2018-07-06 15:00 | 236 | 236
2018-07-06 15:30 | 236 | 236
2018-07-06 16:00 | 246 | 246
2018-07-06 16:30 | 255 | 255
2018-07-06 17:00 | 267 | 267
2018-07-06 17:30 | 280 | 279
2018-07-06 18:00 | 277 | 277
2018-07-06 18:30 | 274 | 273
2018-07-06 19:00 | 267 | 266
2018-07-06 19:30 | 263 | 263
2018-07-06 20:00 | 255 | 254
2018-07-06 20:30 | 241 | 241
2018-07-06 21:00 | 230 | 230
2018-07-06 21:30 | 226 | 226
2018-07-06 22:00 | 223 | 223
2018-07-06 22:30 | 222 | 222
2018-07-06 23:00 | 211 | 211
2018-07-06 23:30 | 200 | 199
2018-07-07 | 181 | 181
2018-07-07 00:30 | 175 | 175
2018-07-07 01:00 | 169 | 168
2018-07-07 01:30 | 166 | 165
2018-07-07 02:00 | 162 | 161
2018-07-07 02:30 | 166 | 165
2018-07-07 03:00 | 156 | 154
2018-07-07 03:30 | 160 | 159
2018-07-07 04:00 | 164 | 163
2018-07-07 04:30 | 163 | 161
2018-07-07 05:00 | 167 | 166
2018-07-07 05:30 | 166 | 165
2018-07-07 06:00 | 177 | 177
2018-07-07 06:30 | 183 | 183
2018-07-07 07:00 | 197 | 197
2018-07-07 07:30 | 211 | 211
2018-07-07 08:00 | 220 | 220
2018-07-07 08:30 | 230 | 230
2018-07-07 09:00 | 238 | 238
2018-07-07 09:30 | 231 | 231
2018-07-07 10:00 | 232 | 232
2018-07-07 10:30 | 214 | 214
2018-07-07 11:00 | 206 | 206
2018-07-07 11:30 | 202 | 202
2018-07-07 12:00 | 216 | 216
2018-07-07 12:30 | 213 | 213
2018-07-07 13:00 | 211 | 211
2018-07-07 13:30 | 203 | 203
2018-07-07 14:00 | 205 | 205
2018-07-07 14:30 | 208 | 208
2018-07-07 15:00 | 203 | 203
2018-07-07 15:30 | 213 | 213
2018-07-07 16:00 | 223 | 223
2018-07-07 16:30 | 237 | 237
2018-07-07 17:00 | 250 | 250
2018-07-07 17:30 | 261 | 261
2018-07-07 18:00 | 258 | 258
2018-07-07 18:30 | 255 | 255
2018-07-07 19:00 | 246 | 246
2018-07-07 19:30 | 240 | 240
2018-07-07 20:00 | 237 | 237
2018-07-07 20:30 | 227 | 227
2018-07-07 21:00 | 221 | 221
2018-07-07 21:30 | 218 | 217
2018-07-07 22:00 | 215 | 214
2018-07-07 22:30 | 214 | 214
2018-07-07 23:00 | 208 | 207
2018-07-07 23:30 | 197 | 195
2018-07-08 | 182 | 180
2018-07-08 00:30 | 172 | 171
2018-07-08 01:00 | 167 | 165
2018-07-08 01:30 | 161 | 160
2018-07-08 02:00 | 155 | 153
2018-07-08 02:30 | 149 | 148
2018-07-08 03:00 | 150 | 148
2018-07-08 03:30 | 151 | 149
2018-07-08 04:00 | 150 | 148
2018-07-08 04:30 | 151 | 149
2018-07-08 05:00 | 157 | 156
2018-07-08 05:30 | 167 | 166
2018-07-08 06:00 | 171 | 170
2018-07-08 06:30 | 178 | 177
2018-07-08 07:00 | 189 | 188
2018-07-08 07:30 | 200 | 200
2018-07-08 08:00 | 208 | 208
2018-07-08 08:30 | 209 | 209
2018-07-08 09:00 | 204 | 204
2018-07-08 09:30 | 192 | 192
2018-07-08 10:00 | 181 | 181
2018-07-08 10:30 | 171 | 171
2018-07-08 11:00 | 172 | 172
2018-07-08 11:30 | 192 | 192
2018-07-08 12:00 | 191 | 191
2018-07-08 12:30 | 190 | 190
2018-07-08 13:00 | 190 | 190
2018-07-08 13:30 | 192 | 192
2018-07-08 14:00 | 198 | 198
2018-07-08 14:30 | 205 | 205
2018-07-08 15:00 | 209 | 209
2018-07-08 15:30 | 214 | 214
2018-07-08 16:00 | 227 | 227
2018-07-08 16:30 | 246 | 246
2018-07-08 17:00 | 267 | 267
2018-07-08 17:30 | 285 | 285
2018-07-08 18:00 | 294 | 292
2018-07-08 18:30 | 293 | 292
2018-07-08 19:00 | 290 | 289
2018-07-08 19:30 | 282 | 282
2018-07-08 20:00 | 271 | 271
2018-07-08 20:30 | 262 | 262
2018-07-08 21:00 | 251 | 251
2018-07-08 21:30 | 239 | 238
2018-07-08 22:00 | 232 | 231
2018-07-08 22:30 | 224 | 224
2018-07-08 23:00 | 212 | 211
2018-07-08 23:30 | 198 | 196
2018-07-09 | 188 | 185
2018-07-09 00:30 | 181 | 179
2018-07-09 01:00 | 175 | 174
2018-07-09 01:30 | 168 | 167
2018-07-09 02:00 | 166 | 165
2018-07-09 02:30 | 166 | 165
2018-07-09 03:00 | 167 | 166
2018-07-09 03:30 | 169 | 168
2018-07-09 04:00 | 173 | 172
2018-07-09 04:30 | 174 | 174
2018-07-09 05:00 | 188 | 187
2018-07-09 05:30 | 198 | 198
2018-07-09 06:00 | 221 | 221
2018-07-09 06:30 | 253 | 253
2018-07-09 07:00 | 270 | 270
2018-07-09 07:30 | 277 | 276
2018-07-09 08:00 | 276 | 276
2018-07-09 08:30 | 271 | 271
2018-07-09 09:00 | 261 | 260
2018-07-09 09:30 | 247 | 247
2018-07-09 10:00 | 231 | 231
2018-07-09 10:30 | 213 | 213
2018-07-09 11:00 | 203 | 203
2018-07-09 11:30 | 208 | 208
2018-07-09 12:00 | 209 | 209
2018-07-09 12:30 | 200 | 200
2018-07-09 13:00 | 197 | 197
2018-07-09 13:30 | 200 | 200
2018-07-09 14:00 | 217 | 217
2018-07-09 14:30 | 225 | 225
2018-07-09 15:00 | 236 | 236
2018-07-09 15:30 | 248 | 248
2018-07-09 16:00 | 264 | 264
2018-07-09 16:30 | 280 | 280
2018-07-09 17:00 | 306 | 306
2018-07-09 17:30 | 333 | 333
2018-07-09 18:00 | 334 | 332
2018-07-09 18:30 | 332 | 330
2018-07-09 19:00 | 319 | 317
2018-07-09 19:30 | 305 | 305
2018-07-09 20:00 | 311 | 311
2018-07-09 20:30 | 300 | 300
2018-07-09 21:00 | 284 | 283
2018-07-09 21:30 | 263 | 262
2018-07-09 22:00 | 240 | 240
2018-07-09 22:30 | 235 | 235
2018-07-09 23:00 | 228 | 228
2018-07-09 23:30 | 219 | 219
2018-07-10 | 200 | 199
2018-07-10 00:30 | 189 | 188
2018-07-10 01:00 | 180 | 179
2018-07-10 01:30 | 176 | 175
2018-07-10 02:00 | 170 | 168
2018-07-10 02:30 | 169 | 168
2018-07-10 03:00 | 172 | 170
2018-07-10 03:30 | 174 | 172
2018-07-10 04:00 | 178 | 177
2018-07-10 04:30 | 179 | 178
2018-07-10 05:00 | 189 | 189
2018-07-10 05:30 | 203 | 202
2018-07-10 06:00 | 229 | 229
2018-07-10 06:30 | 264 | 264
2018-07-10 07:00 | 280 | 280
2018-07-10 07:30 | 301 | 299
2018-07-10 08:00 | 301 | 297
2018-07-10 08:30 | 285 | 283
2018-07-10 09:00 | 273 | 273
2018-07-10 09:30 | 260 | 260
2018-07-10 10:00 | 251 | 250
2018-07-10 10:30 | 238 | 238
2018-07-10 11:00 | 227 | 227
2018-07-10 11:30 | 222 | 222
2018-07-10 12:00 | 217 | 217
2018-07-10 12:30 | 213 | 213
2018-07-10 13:00 | 216 | 216
2018-07-10 13:30 | 218 | 218
2018-07-10 14:00 | 221 | 221
2018-07-10 14:30 | 230 | 230
2018-07-10 15:00 | 239 | 239
2018-07-10 15:30 | 246 | 246
2018-07-10 16:00 | 263 | 263
2018-07-10 16:30 | 287 | 286
2018-07-10 17:00 | 307 | 307
2018-07-10 17:30 | 327 | 325
2018-07-10 18:00 | 327 | 324
2018-07-10 18:30 | 323 | 321
2018-07-10 19:00 | 315 | 313
2018-07-10 19:30 | 317 | 314
2018-07-10 20:00 | 314 | 311
2018-07-10 20:30 | 295 | 292
2018-07-10 21:00 | 275 | 274
2018-07-10 21:30 | 262 | 261
2018-07-10 22:00 | 256 | 254
2018-07-10 22:30 | 251 | 249
2018-07-10 23:00 | 235 | 235
2018-07-10 23:30 | 220 | 220
2018-07-11 | 198 | 197
2018-07-11 00:30 | 189 | 188
2018-07-11 01:00 | 184 | 184
2018-07-11 01:30 | 176 | 175
2018-07-11 02:00 | 173 | 172
2018-07-11 02:30 | 170 | 169
2018-07-11 03:00 | 171 | 170
2018-07-11 03:30 | 172 | 171
2018-07-11 04:00 | 175 | 175
2018-07-11 04:30 | 179 | 179
2018-07-11 05:00 | 188 | 187
2018-07-11 05:30 | 203 | 203
2018-07-11 06:00 | 234 | 234
2018-07-11 06:30 | 265 | 265
2018-07-11 07:00 | 282 | 282
2018-07-11 07:30 | 293 | 293
2018-07-11 08:00 | 294 | 293
2018-07-11 08:30 | 283 | 282
2018-07-11 09:00 | 274 | 273
2018-07-11 09:30 | 263 | 261
2018-07-11 10:00 | 246 | 245
2018-07-11 10:30 | 231 | 231
2018-07-11 11:00 | 227 | 227
2018-07-11 11:30 | 224 | 224
2018-07-11 12:00 | 226 | 226
2018-07-11 12:30 | 227 | 227
2018-07-11 13:00 | 228 | 228
2018-07-11 13:30 | 231 | 231
2018-07-11 14:00 | 242 | 242
2018-07-11 14:30 | 244 | 244
2018-07-11 15:00 | 247 | 247
2018-07-11 15:30 | 254 | 254
2018-07-11 16:00 | 264 | 264
2018-07-11 16:30 | 281 | 281
2018-07-11 17:00 | 309 | 308
2018-07-11 17:30 | 327 | 327
2018-07-11 18:00 | 329 | 328
2018-07-11 18:30 | 323 | 323
2018-07-11 19:00 | 313 | 313
2018-07-11 19:30 | 313 | 312
2018-07-11 20:00 | 305 | 304
2018-07-11 20:30 | 290 | 290
2018-07-11 21:00 | 275 | 275
2018-07-11 21:30 | 260 | 259
2018-07-11 22:00 | 256 | 256
2018-07-11 22:30 | 249 | 248
2018-07-11 23:00 | 238 | 238
2018-07-11 23:30 | 227 | 226
2018-07-12 | 207 | 206
2018-07-12 00:30 | 194 | 191
2018-07-12 01:00 | 182 | 180
2018-07-12 01:30 | 174 | 173
2018-07-12 02:00 | 174 | 172
2018-07-12 02:30 | 174 | 172
2018-07-12 03:00 | 172 | 171
2018-07-12 03:30 | 173 | 172
2018-07-12 04:00 | 173 | 172
2018-07-12 04:30 | 176 | 175
2018-07-12 05:00 | 185 | 185
2018-07-12 05:30 | 200 | 199
2018-07-12 06:00 | 227 | 227
2018-07-12 06:30 | 259 | 259
2018-07-12 07:00 | 284 | 283
2018-07-12 07:30 | 299 | 298
2018-07-12 08:00 | 339 | 338
2018-07-12 08:30 | 337 | 334
2018-07-12 09:00 | 342 | 341
2018-07-12 09:30 | 320 | 319
2018-07-12 10:00 | 279 | 278
2018-07-12 10:30 | 259 | 259
2018-07-12 11:00 | 241 | 241
2018-07-12 11:30 | 233 | 233
2018-07-12 12:00 | 227 | 227
2018-07-12 12:30 | 235 | 235
2018-07-12 13:00 | 242 | 242
2018-07-12 13:30 | 242 | 242
2018-07-12 14:00 | 245 | 245
2018-07-12 14:30 | 247 | 247
2018-07-12 15:00 | 246 | 246
2018-07-12 15:30 | 254 | 254
2018-07-12 16:00 | 272 | 272
2018-07-12 16:30 | 289 | 289
2018-07-12 17:00 | 309 | 307
2018-07-12 17:30 | 337 | 336
2018-07-12 18:00 | 350 | 349
2018-07-12 18:30 | 333 | 331
2018-07-12 19:00 | 325 | 323
2018-07-12 19:30 | 337 | 334
2018-07-12 20:00 | 340 | 338
2018-07-12 20:30 | 332 | 330
2018-07-12 21:00 | 320 | 317
2018-07-12 21:30 | 280 | 278
2018-07-12 22:00 | 272 | 272
2018-07-12 22:30 | 270 | 270
2018-07-12 23:00 | 262 | 261
2018-07-12 23:30 | 258 | 258
2018-07-13 | 219 | 218
2018-07-13 00:30 | 202 | 201
2018-07-13 01:00 | 190 | 188
2018-07-13 01:30 | 183 | 180
2018-07-13 02:00 | 179 | 178
2018-07-13 02:30 | 177 | 176
2018-07-13 03:00 | 176 | 175
2018-07-13 03:30 | 175 | 174
2018-07-13 04:00 | 175 | 175
2018-07-13 04:30 | 178 | 177
2018-07-13 05:00 | 185 | 185
2018-07-13 05:30 | 199 | 199
2018-07-13 06:00 | 229 | 229
2018-07-13 06:30 | 261 | 261
2018-07-13 07:00 | 282 | 281
2018-07-13 07:30 | 296 | 295
2018-07-13 08:00 | 294 | 294
2018-07-13 08:30 | 293 | 293
2018-07-13 09:00 | 275 | 275
2018-07-13 09:30 | 262 | 261
2018-07-13 10:00 | 241 | 241
2018-07-13 10:30 | 235 | 235
2018-07-13 11:00 | 223 | 223
2018-07-13 11:30 | 214 | 214
2018-07-13 12:00 | 212 | 212
2018-07-13 12:30 | 208 | 208
2018-07-13 13:00 | 208 | 208
2018-07-13 13:30 | 210 | 210
2018-07-13 14:00 | 214 | 214
2018-07-13 14:30 | 216 | 216
2018-07-13 15:00 | 218 | 218
2018-07-13 15:30 | 228 | 228
2018-07-13 16:00 | 243 | 243
2018-07-13 16:30 | 264 | 264
2018-07-13 17:00 | 285 | 285
2018-07-13 17:30 | 307 | 307
2018-07-13 18:00 | 313 | 313
2018-07-13 18:30 | 325 | 325
2018-07-13 19:00 | 317 | 317
2018-07-13 19:30 | 315 | 315
2018-07-13 20:00 | 313 | 313
2018-07-13 20:30 | 314 | 313
2018-07-13 21:00 | 306 | 306
2018-07-13 21:30 | 295 | 294
2018-07-13 22:00 | 290 | 289
2018-07-13 22:30 | 285 | 285
2018-07-13 23:00 | 270 | 269
2018-07-13 23:30 | 250 | 250
2018-07-14 | 226 | 225
2018-07-14 00:30 | 215 | 214
2018-07-14 01:00 | 203 | 201
2018-07-14 01:30 | 195 | 193
2018-07-14 02:00 | 188 | 185
2018-07-14 02:30 | 182 | 181
2018-07-14 03:00 | 184 | 183
2018-07-14 03:30 | 183 | 182
2018-07-14 04:00 | 182 | 181
2018-07-14 04:30 | 182 | 181
2018-07-14 05:00 | 186 | 186
2018-07-14 05:30 | 193 | 193
2018-07-14 06:00 | 208 | 208
2018-07-14 06:30 | 230 | 230
2018-07-14 07:00 | 252 | 252
2018-07-14 07:30 | 271 | 271
2018-07-14 08:00 | 283 | 283
2018-07-14 08:30 | 289 | 288
2018-07-14 09:00 | 286 | 285
2018-07-14 09:30 | 273 | 271
2018-07-14 10:00 | 247 | 246
2018-07-14 10:30 | 230 | 230
2018-07-14 11:00 | 216 | 216
2018-07-14 11:30 | 197 | 196
2018-07-14 12:00 | 192 | 192
2018-07-14 12:30 | 202 | 201
2018-07-14 13:00 | 202 | 202
2018-07-14 13:30 | 203 | 203
2018-07-14 14:00 | 216 | 215
2018-07-14 14:30 | 217 | 216
2018-07-14 15:00 | 221 | 221
2018-07-14 15:30 | 228 | 227
2018-07-14 16:00 | 242 | 241
2018-07-14 16:30 | 271 | 271
2018-07-14 17:00 | 301 | 301
2018-07-14 17:30 | 323 | 323
2018-07-14 18:00 | 330 | 330
2018-07-14 18:30 | 329 | 328
2018-07-14 19:00 | 321 | 320
2018-07-14 19:30 | 318 | 317
2018-07-14 20:00 | 313 | 313
2018-07-14 20:30 | 305 | 304
2018-07-14 21:00 | 282 | 282
2018-07-14 21:30 | 267 | 267
2018-07-14 22:00 | 258 | 258
2018-07-14 22:30 | 255 | 255
2018-07-14 23:00 | 246 | 245
2018-07-14 23:30 | 238 | 237
2018-07-15 | 213 | 211
2018-07-15 00:30 | 201 | 198
2018-07-15 01:00 | 190 | 186
2018-07-15 01:30 | 179 | 178
2018-07-15 02:00 | 175 | 173
2018-07-15 02:30 | 172 | 171
2018-07-15 03:00 | 172 | 171
2018-07-15 03:30 | 172 | 170
2018-07-15 04:00 | 172 | 171
2018-07-15 04:30 | 174 | 172
2018-07-15 05:00 | 179 | 178
2018-07-15 05:30 | 188 | 187
2018-07-15 06:00 | 196 | 195
2018-07-15 06:30 | 209 | 208
2018-07-15 07:00 | 226 | 226
2018-07-15 07:30 | 239 | 239
2018-07-15 08:00 | 250 | 250
2018-07-15 08:30 | 252 | 252
2018-07-15 09:00 | 251 | 251
2018-07-15 09:30 | 242 | 241
2018-07-15 10:00 | 230 | 229
2018-07-15 10:30 | 212 | 211
2018-07-15 11:00 | 203 | 202
2018-07-15 11:30 | 199 | 198
2018-07-15 12:00 | 187 | 186
2018-07-15 12:30 | 187 | 186
2018-07-15 13:00 | 188 | 188
2018-07-15 13:30 | 190 | 189
2018-07-15 14:00 | 190 | 189
2018-07-15 14:30 | 200 | 200
2018-07-15 15:00 | 207 | 206
2018-07-15 15:30 | 214 | 214
2018-07-15 16:00 | 234 | 233
2018-07-15 16:30 | 258 | 258
2018-07-15 17:00 | 284 | 284
2018-07-15 17:30 | 314 | 314
2018-07-15 18:00 | 326 | 325
2018-07-15 18:30 | 329 | 328
2018-07-15 19:00 | 320 | 319
2018-07-15 19:30 | 318 | 316
2018-07-15 20:00 | 311 | 308
2018-07-15 20:30 | 301 | 298
2018-07-15 21:00 | 293 | 289
2018-07-15 21:30 | 276 | 271
2018-07-15 22:00 | 259 | 255
2018-07-15 22:30 | 244 | 243
2018-07-15 23:00 | 234 | 233
2018-07-15 23:30 | 222 | 221
2018-07-16 | 203 | 201
2018-07-16 00:30 | 195 | 192
2018-07-16 01:00 | 187 | 184
2018-07-16 01:30 | 181 | 178
2018-07-16 02:00 | 178 | 175
2018-07-16 02:30 | 172 | 169
2018-07-16 03:00 | 170 | 169
2018-07-16 03:30 | 173 | 172
2018-07-16 04:00 | 176 | 175
2018-07-16 04:30 | 179 | 179
2018-07-16 05:00 | 187 | 187
2018-07-16 05:30 | 197 | 197
2018-07-16 06:00 | 239 | 239
2018-07-16 06:30 | 276 | 276
2018-07-16 07:00 | 301 | 301
2018-07-16 07:30 | 306 | 305
2018-07-16 08:00 | 303 | 301
2018-07-16 08:30 | 288 | 287
2018-07-16 09:00 | 275 | 274
2018-07-16 09:30 | 262 | 261
2018-07-16 10:00 | 247 | 247
2018-07-16 10:30 | 235 | 234
2018-07-16 11:00 | 231 | 230
2018-07-16 11:30 | 228 | 227
2018-07-16 12:00 | 223 | 221
2018-07-16 12:30 | 218 | 218
2018-07-16 13:00 | 219 | 219
2018-07-16 13:30 | 222 | 222
2018-07-16 14:00 | 228 | 228
2018-07-16 14:30 | 230 | 230
2018-07-16 15:00 | 238 | 238
2018-07-16 15:30 | 250 | 250
2018-07-16 16:00 | 266 | 266
2018-07-16 16:30 | 299 | 296
2018-07-16 17:00 | 322 | 319
2018-07-16 17:30 | 341 | 340
2018-07-16 18:00 | 339 | 337
2018-07-16 18:30 | 343 | 341
2018-07-16 19:00 | 338 | 336
2018-07-16 19:30 | 334 | 332
2018-07-16 20:00 | 324 | 321
2018-07-16 20:30 | 306 | 306
2018-07-16 21:00 | 292 | 291
2018-07-16 21:30 | 276 | 274
2018-07-16 22:00 | 263 | 260
2018-07-16 22:30 | 247 | 246
2018-07-16 23:00 | 235 | 234
2018-07-16 23:30 | 221 | 220
2018-07-17 | 204 | 203
2018-07-17 00:30 | 194 | 192
2018-07-17 01:00 | 185 | 182
2018-07-17 01:30 | 177 | 174
2018-07-17 02:00 | 174 | 171
2018-07-17 02:30 | 168 | 167
2018-07-17 03:00 | 167 | 166
2018-07-17 03:30 | 169 | 168
2018-07-17 04:00 | 172 | 171
2018-07-17 04:30 | 177 | 177
2018-07-17 05:00 | 191 | 191
2018-07-17 05:30 | 208 | 208
2018-07-17 06:00 | 246 | 245
2018-07-17 06:30 | 282 | 281
2018-07-17 07:00 | 304 | 304
2018-07-17 07:30 | 308 | 308
2018-07-17 08:00 | 300 | 300
2018-07-17 08:30 | 290 | 290
2018-07-17 09:00 | 271 | 271
2018-07-17 09:30 | 253 | 252
2018-07-17 10:00 | 236 | 235
2018-07-17 10:30 | 222 | 222
2018-07-17 11:00 | 214 | 214
2018-07-17 11:30 | 210 | 210
2018-07-17 12:00 | 204 | 204
2018-07-17 12:30 | 202 | 202
2018-07-17 13:00 | 200 | 200
2018-07-17 13:30 | 205 | 205
2018-07-17 14:00 | 209 | 209
2018-07-17 14:30 | 217 | 217
2018-07-17 15:00 | 219 | 219
2018-07-17 15:30 | 229 | 229
2018-07-17 16:00 | 246 | 246
2018-07-17 16:30 | 274 | 273
2018-07-17 17:00 | 298 | 297
2018-07-17 17:30 | 321 | 321
2018-07-17 18:00 | 327 | 327
2018-07-17 18:30 | 329 | 328
2018-07-17 19:00 | 325 | 324
2018-07-17 19:30 | 324 | 323
2018-07-17 20:00 | 317 | 317
2018-07-17 20:30 | 303 | 303
2018-07-17 21:00 | 288 | 288
2018-07-17 21:30 | 271 | 270
2018-07-17 22:00 | 256 | 256
2018-07-17 22:30 | 248 | 248
2018-07-17 23:00 | 238 | 238
2018-07-17 23:30 | 223 | 222
2018-07-18 | 200 | 199
2018-07-18 00:30 | 193 | 192
2018-07-18 01:00 | 186 | 185
2018-07-18 01:30 | 179 | 178
2018-07-18 02:00 | 175 | 174
2018-07-18 02:30 | 170 | 168
2018-07-18 03:00 | 169 | 167
2018-07-18 03:30 | 169 | 166
2018-07-18 04:00 | 172 | 170
2018-07-18 04:30 | 177 | 176
2018-07-18 05:00 | 193 | 192
2018-07-18 05:30 | 215 | 215
2018-07-18 06:00 | 249 | 249
2018-07-18 06:30 | 285 | 285
2018-07-18 07:00 | 311 | 311
2018-07-18 07:30 | 317 | 315
2018-07-18 08:00 | 303 | 302
2018-07-18 08:30 | 296 | 294
2018-07-18 09:00 | 281 | 278
2018-07-18 09:30 | 258 | 258
2018-07-18 10:00 | 242 | 242
2018-07-18 10:30 | 230 | 229
2018-07-18 11:00 | 221 | 221
2018-07-18 11:30 | 212 | 212
2018-07-18 12:00 | 205 | 205
2018-07-18 12:30 | 206 | 206
2018-07-18 13:00 | 207 | 207
2018-07-18 13:30 | 206 | 206
2018-07-18 14:00 | 210 | 210
2018-07-18 14:30 | 214 | 214
2018-07-18 15:00 | 217 | 217
2018-07-18 15:30 | 231 | 231
2018-07-18 16:00 | 246 | 246
2018-07-18 16:30 | 270 | 270
2018-07-18 17:00 | 296 | 296
2018-07-18 17:30 | 316 | 315
2018-07-18 18:00 | 317 | 317
2018-07-18 18:30 | 319 | 319
2018-07-18 19:00 | 319 | 318
2018-07-18 19:30 | 318 | 317
2018-07-18 20:00 | 311 | 310
2018-07-18 20:30 | 301 | 300
2018-07-18 21:00 | 288 | 288
2018-07-18 21:30 | 271 | 270
2018-07-18 22:00 | 258 | 257
2018-07-18 22:30 | 251 | 251
2018-07-18 23:00 | 239 | 237
2018-07-18 23:30 | 226 | 225
2018-07-19 | 203 | 201
2018-07-19 00:30 | 192 | 191
2018-07-19 01:00 | 182 | 180
2018-07-19 01:30 | 177 | 175
2018-07-19 02:00 | 171 | 171
2018-07-19 02:30 | 169 | 169
2018-07-19 03:00 | 168 | 167
2018-07-19 03:30 | 168 | 167
2018-07-19 04:00 | 172 | 171
2018-07-19 04:30 | 178 | 178
2018-07-19 05:00 | 191 | 191
2018-07-19 05:30 | 213 | 213
2018-07-19 06:00 | 249 | 248
2018-07-19 06:30 | 289 | 289
2018-07-19 07:00 | 312 | 311
2018-07-19 07:30 | 318 | 316
2018-07-19 08:00 | 308 | 307
2018-07-19 08:30 | 301 | 301
2018-07-19 09:00 | 291 | 291
2018-07-19 09:30 | 275 | 274
2018-07-19 10:00 | 254 | 254
2018-07-19 10:30 | 244 | 244
2018-07-19 11:00 | 233 | 233
2018-07-19 11:30 | 223 | 223
2018-07-19 12:00 | 216 | 216
2018-07-19 12:30 | 211 | 210
2018-07-19 13:00 | 216 | 216
2018-07-19 13:30 | 215 | 215
2018-07-19 14:00 | 217 | 217
2018-07-19 14:30 | 223 | 223
2018-07-19 15:00 | 231 | 230
2018-07-19 15:30 | 237 | 237
2018-07-19 16:00 | 259 | 259
2018-07-19 16:30 | 280 | 280
2018-07-19 17:00 | 308 | 308
2018-07-19 17:30 | 327 | 326
2018-07-19 18:00 | 331 | 331
2018-07-19 18:30 | 331 | 330
2018-07-19 19:00 | 327 | 327
2018-07-19 19:30 | 325 | 324
2018-07-19 20:00 | 323 | 322
2018-07-19 20:30 | 311 | 311
2018-07-19 21:00 | 301 | 300
2018-07-19 21:30 | 285 | 284
2018-07-19 22:00 | 271 | 270
2018-07-19 22:30 | 261 | 261
2018-07-19 23:00 | 246 | 246
2018-07-19 23:30 | 233 | 233
2018-07-20 | 210 | 210
2018-07-20 00:30 | 200 | 199
2018-07-20 01:00 | 189 | 189
2018-07-20 01:30 | 178 | 177
2018-07-20 02:00 | 173 | 173
2018-07-20 02:30 | 171 | 170
2018-07-20 03:00 | 169 | 168
2018-07-20 03:30 | 171 | 170
2018-07-20 04:00 | 173 | 173
2018-07-20 04:30 | 185 | 185
2018-07-20 05:00 | 197 | 197
2018-07-20 05:30 | 219 | 219
2018-07-20 06:00 | 251 | 250
2018-07-20 06:30 | 277 | 277
2018-07-20 07:00 | 299 | 299
2018-07-20 07:30 | 310 | 310
2018-07-20 08:00 | 299 | 299
2018-07-20 08:30 | 284 | 284
2018-07-20 09:00 | 279 | 279
2018-07-20 09:30 | 264 | 264
2018-07-20 10:00 | 261 | 260
2018-07-20 10:30 | 240 | 239
2018-07-20 11:00 | 225 | 224
2018-07-20 11:30 | 221 | 221
2018-07-20 12:00 | 223 | 223
2018-07-20 12:30 | 237 | 237
2018-07-20 13:00 | 232 | 232
2018-07-20 13:30 | 231 | 231
2018-07-20 14:00 | 256 | 255
2018-07-20 14:30 | 259 | 259
2018-07-20 15:00 | 244 | 244
2018-07-20 15:30 | 247 | 247
2018-07-20 16:00 | 259 | 259
2018-07-20 16:30 | 282 | 281
2018-07-20 17:00 | 303 | 303
2018-07-20 17:30 | 321 | 320
2018-07-20 18:00 | 318 | 316
2018-07-20 18:30 | 314 | 312
2018-07-20 19:00 | 304 | 304
2018-07-20 19:30 | 307 | 306
2018-07-20 20:00 | 306 | 305
2018-07-20 20:30 | 302 | 301
2018-07-20 21:00 | 287 | 286
2018-07-20 21:30 | 269 | 269
2018-07-20 22:00 | 266 | 266
2018-07-20 22:30 | 269 | 268
2018-07-20 23:00 | 257 | 257
2018-07-20 23:30 | 243 | 243
2018-07-21 | 217 | 216
2018-07-21 00:30 | 205 | 203
2018-07-21 01:00 | 195 | 193
2018-07-21 01:30 | 188 | 185
2018-07-21 02:00 | 184 | 181
2018-07-21 02:30 | 181 | 179
2018-07-21 03:00 | 181 | 179
2018-07-21 03:30 | 181 | 178
2018-07-21 04:00 | 182 | 179
2018-07-21 04:30 | 183 | 181
2018-07-21 05:00 | 188 | 186
2018-07-21 05:30 | 194 | 193
2018-07-21 06:00 | 210 | 209
2018-07-21 06:30 | 228 | 227
2018-07-21 07:00 | 249 | 248
2018-07-21 07:30 | 257 | 257
2018-07-21 08:00 | 262 | 262
2018-07-21 08:30 | 270 | 270
2018-07-21 09:00 | 270 | 270
2018-07-21 09:30 | 258 | 257
2018-07-21 10:00 | 245 | 244
2018-07-21 10:30 | 233 | 232
2018-07-21 11:00 | 222 | 221
2018-07-21 11:30 | 214 | 212
2018-07-21 12:00 | 208 | 206
2018-07-21 12:30 | 204 | 203
2018-07-21 13:00 | 203 | 201
2018-07-21 13:30 | 214 | 212
2018-07-21 14:00 | 219 | 218
2018-07-21 14:30 | 220 | 219
2018-07-21 15:00 | 232 | 230
2018-07-21 15:30 | 237 | 235
2018-07-21 16:00 | 245 | 244
2018-07-21 16:30 | 271 | 271
2018-07-21 17:00 | 303 | 302
2018-07-21 17:30 | 325 | 325
2018-07-21 18:00 | 329 | 328
2018-07-21 18:30 | 327 | 327
2018-07-21 19:00 | 317 | 316
2018-07-21 19:30 | 318 | 318
2018-07-21 20:00 | 315 | 314
2018-07-21 20:30 | 304 | 302
2018-07-21 21:00 | 293 | 292
2018-07-21 21:30 | 285 | 285
2018-07-21 22:00 | 279 | 279
2018-07-21 22:30 | 278 | 277
2018-07-21 23:00 | 268 | 267
2018-07-21 23:30 | 253 | 251
2018-07-22 | 224 | 222
2018-07-22 00:30 | 210 | 208
2018-07-22 01:00 | 202 | 200
2018-07-22 01:30 | 196 | 193
2018-07-22 02:00 | 194 | 191
2018-07-22 02:30 | 191 | 189
2018-07-22 03:00 | 190 | 188
2018-07-22 03:30 | 190 | 187
2018-07-22 04:00 | 190 | 188
2018-07-22 04:30 | 193 | 191
2018-07-22 05:00 | 191 | 189
2018-07-22 05:30 | 195 | 194
2018-07-22 06:00 | 204 | 203
2018-07-22 06:30 | 220 | 219
2018-07-22 07:00 | 231 | 230
2018-07-22 07:30 | 245 | 245
2018-07-22 08:00 | 254 | 254
2018-07-22 08:30 | 257 | 257
2018-07-22 09:00 | 261 | 261
2018-07-22 09:30 | 253 | 253
2018-07-22 10:00 | 237 | 237
2018-07-22 10:30 | 219 | 219
2018-07-22 11:00 | 201 | 200
2018-07-22 11:30 | 198 | 198
2018-07-22 12:00 | 194 | 194
2018-07-22 12:30 | 199 | 199
2018-07-22 13:00 | 197 | 196
2018-07-22 13:30 | 195 | 194
2018-07-22 14:00 | 204 | 203
2018-07-22 14:30 | 217 | 217
2018-07-22 15:00 | 225 | 224
2018-07-22 15:30 | 232 | 232
2018-07-22 16:00 | 246 | 246
2018-07-22 16:30 | 269 | 269
2018-07-22 17:00 | 293 | 293
2018-07-22 17:30 | 317 | 317
2018-07-22 18:00 | 323 | 323
2018-07-22 18:30 | 323 | 323
2018-07-22 19:00 | 317 | 316
2018-07-22 19:30 | 313 | 313
2018-07-22 20:00 | 309 | 308
2018-07-22 20:30 | 295 | 294
2018-07-22 21:00 | 283 | 282
2018-07-22 21:30 | 269 | 268
2018-07-22 22:00 | 254 | 254
2018-07-22 22:30 | 250 | 250
2018-07-22 23:00 | 241 | 240
2018-07-22 23:30 | 224 | 223
2018-07-23 | 207 | 206
2018-07-23 00:30 | 196 | 194
2018-07-23 01:00 | 195 | 193
2018-07-23 01:30 | 187 | 184
2018-07-23 02:00 | 183 | 181
2018-07-23 02:30 | 180 | 177
2018-07-23 03:00 | 180 | 177
2018-07-23 03:30 | 180 | 177
2018-07-23 04:00 | 184 | 181
2018-07-23 04:30 | 187 | 185
2018-07-23 05:00 | 201 | 200
2018-07-23 05:30 | 223 | 222
2018-07-23 06:00 | 258 | 258
2018-07-23 06:30 | 291 | 290
2018-07-23 07:00 | 305 | 304
2018-07-23 07:30 | 303 | 301
2018-07-23 08:00 | 285 | 283
2018-07-23 08:30 | 263 | 260
2018-07-23 09:00 | 244 | 243
2018-07-23 09:30 | 226 | 226
2018-07-23 10:00 | 216 | 215
2018-07-23 10:30 | 204 | 203
2018-07-23 11:00 | 198 | 198
2018-07-23 11:30 | 196 | 196
2018-07-23 12:00 | 197 | 197
2018-07-23 12:30 | 200 | 200
2018-07-23 13:00 | 199 | 199
2018-07-23 13:30 | 202 | 202
2018-07-23 14:00 | 209 | 209
2018-07-23 14:30 | 212 | 211
2018-07-23 15:00 | 219 | 219
2018-07-23 15:30 | 230 | 230
2018-07-23 16:00 | 247 | 247
2018-07-23 16:30 | 268 | 267
2018-07-23 17:00 | 306 | 306
2018-07-23 17:30 | 335 | 335
2018-07-23 18:00 | 339 | 339
2018-07-23 18:30 | 339 | 339
2018-07-23 19:00 | 331 | 331
2018-07-23 19:30 | 329 | 328
2018-07-23 20:00 | 323 | 323
2018-07-23 20:30 | 308 | 307
2018-07-23 21:00 | 290 | 289
2018-07-23 21:30 | 272 | 270
2018-07-23 22:00 | 263 | 262
2018-07-23 22:30 | 253 | 252
2018-07-23 23:00 | 238 | 238
2018-07-23 23:30 | 223 | 223
2018-07-24 | 203 | 202
2018-07-24 00:30 | 192 | 191
2018-07-24 01:00 | 184 | 182
2018-07-24 01:30 | 176 | 174
2018-07-24 02:00 | 172 | 170
2018-07-24 02:30 | 169 | 167
2018-07-24 03:00 | 170 | 168
2018-07-24 03:30 | 170 | 168
2018-07-24 04:00 | 173 | 171
2018-07-24 04:30 | 182 | 180
2018-07-24 05:00 | 200 | 199
2018-07-24 05:30 | 222 | 222
2018-07-24 06:00 | 257 | 257
2018-07-24 06:30 | 292 | 291
2018-07-24 07:00 | 316 | 315
2018-07-24 07:30 | 312 | 310
2018-07-24 08:00 | 292 | 290
2018-07-24 08:30 | 268 | 266
2018-07-24 09:00 | 254 | 251
2018-07-24 09:30 | 240 | 239
2018-07-24 10:00 | 224 | 224
2018-07-24 10:30 | 212 | 212
2018-07-24 11:00 | 207 | 207
2018-07-24 11:30 | 199 | 199
2018-07-24 12:00 | 199 | 199
2018-07-24 12:30 | 194 | 194
2018-07-24 13:00 | 199 | 199
2018-07-24 13:30 | 202 | 202
2018-07-24 14:00 | 208 | 208
2018-07-24 14:30 | 215 | 215
2018-07-24 15:00 | 223 | 223
2018-07-24 15:30 | 237 | 236
2018-07-24 16:00 | 252 | 251
2018-07-24 16:30 | 270 | 269
2018-07-24 17:00 | 290 | 290
2018-07-24 17:30 | 312 | 312
2018-07-24 18:00 | 316 | 316
2018-07-24 18:30 | 316 | 316
2018-07-24 19:00 | 309 | 308
2018-07-24 19:30 | 305 | 305
2018-07-24 20:00 | 299 | 299
2018-07-24 20:30 | 284 | 284
2018-07-24 21:00 | 271 | 271
2018-07-24 21:30 | 258 | 258
2018-07-24 22:00 | 250 | 250
2018-07-24 22:30 | 245 | 245
2018-07-24 23:00 | 231 | 230
2018-07-24 23:30 | 215 | 214
2018-07-25 | 200 | 198
2018-07-25 00:30 | 188 | 186
2018-07-25 01:00 | 181 | 179
2018-07-25 01:30 | 175 | 172
2018-07-25 02:00 | 167 | 166
2018-07-25 02:30 | 166 | 165
2018-07-25 03:00 | 166 | 165
2018-07-25 03:30 | 166 | 166
2018-07-25 04:00 | 169 | 168
2018-07-25 04:30 | 177 | 177
2018-07-25 05:00 | 194 | 194
2018-07-25 05:30 | 215 | 215
2018-07-25 06:00 | 246 | 246
2018-07-25 06:30 | 274 | 274
2018-07-25 07:00 | 300 | 299
2018-07-25 07:30 | 306 | 306
2018-07-25 08:00 | 300 | 300
2018-07-25 08:30 | 297 | 297
2018-07-25 09:00 | 291 | 291
2018-07-25 09:30 | 284 | 283
2018-07-25 10:00 | 278 | 277
2018-07-25 10:30 | 264 | 264
2018-07-25 11:00 | 250 | 250
2018-07-25 11:30 | 238 | 237
2018-07-25 12:00 | 226 | 225
2018-07-25 12:30 | 217 | 216
2018-07-25 13:00 | 212 | 212
2018-07-25 13:30 | 222 | 222
2018-07-25 14:00 | 235 | 234
2018-07-25 14:30 | 242 | 241
2018-07-25 15:00 | 246 | 245
2018-07-25 15:30 | 256 | 255
2018-07-25 16:00 | 265 | 264
2018-07-25 16:30 | 281 | 280
2018-07-25 17:00 | 300 | 300
2018-07-25 17:30 | 318 | 318
2018-07-25 18:00 | 318 | 318
2018-07-25 18:30 | 317 | 317
2018-07-25 19:00 | 309 | 309
2018-07-25 19:30 | 305 | 305
2018-07-25 20:00 | 300 | 299
2018-07-25 20:30 | 284 | 284
2018-07-25 21:00 | 262 | 261
2018-07-25 21:30 | 244 | 244
2018-07-25 22:00 | 241 | 241
2018-07-25 22:30 | 236 | 236
2018-07-25 23:00 | 223 | 223
2018-07-25 23:30 | 210 | 209
2018-07-26 | 192 | 191
2018-07-26 00:30 | 183 | 181
2018-07-26 01:00 | 176 | 173
2018-07-26 01:30 | 167 | 164
2018-07-26 02:00 | 164 | 163
2018-07-26 02:30 | 164 | 163
2018-07-26 03:00 | 161 | 160
2018-07-26 03:30 | 163 | 161
2018-07-26 04:00 | 164 | 163
2018-07-26 04:30 | 169 | 168
2018-07-26 05:00 | 175 | 175
2018-07-26 05:30 | 187 | 187
2018-07-26 06:00 | 216 | 216
2018-07-26 06:30 | 252 | 251
2018-07-26 07:00 | 275 | 274
2018-07-26 07:30 | 279 | 278
2018-07-26 08:00 | 278 | 277
2018-07-26 08:30 | 268 | 267
2018-07-26 09:00 | 255 | 254
2018-07-26 09:30 | 247 | 245
2018-07-26 10:00 | 236 | 234
2018-07-26 10:30 | 228 | 227
2018-07-26 11:00 | 220 | 219
2018-07-26 11:30 | 212 | 211
2018-07-26 12:00 | 209 | 208
2018-07-26 12:30 | 206 | 205
2018-07-26 13:00 | 208 | 207
2018-07-26 13:30 | 211 | 210
2018-07-26 14:00 | 214 | 213
2018-07-26 14:30 | 217 | 216
2018-07-26 15:00 | 224 | 223
2018-07-26 15:30 | 230 | 228
2018-07-26 16:00 | 242 | 241
2018-07-26 16:30 | 257 | 256
2018-07-26 17:00 | 275 | 274
2018-07-26 17:30 | 304 | 303
2018-07-26 18:00 | 318 | 316
2018-07-26 18:30 | 315 | 313
2018-07-26 19:00 | 300 | 298
2018-07-26 19:30 | 295 | 295
2018-07-26 20:00 | 296 | 296
2018-07-26 20:30 | 282 | 282
2018-07-26 21:00 | 270 | 269
2018-07-26 21:30 | 250 | 250
2018-07-26 22:00 | 244 | 244
2018-07-26 22:30 | 241 | 241
2018-07-26 23:00 | 230 | 230
2018-07-26 23:30 | 213 | 213
2018-07-27 | 190 | 190
2018-07-27 00:30 | 178 | 178
2018-07-27 01:00 | 169 | 168
2018-07-27 01:30 | 140 | 139
2018-07-27 02:00 | 117 | 116
2018-07-27 02:30 | 114 | 113
2018-07-27 03:00 | 141 | 140
2018-07-27 03:30 | 164 | 163
2018-07-27 04:00 | 151 | 150
2018-07-27 04:30 | 161 | 161
2018-07-27 05:00 | 173 | 173
2018-07-27 05:30 | 187 | 187
2018-07-27 06:00 | 214 | 214
2018-07-27 06:30 | 241 | 241
2018-07-27 07:00 | 264 | 264
2018-07-27 07:30 | 268 | 267
2018-07-27 08:00 | 264 | 264
2018-07-27 08:30 | 251 | 251
2018-07-27 09:00 | 245 | 245
2018-07-27 09:30 | 237 | 237
2018-07-27 10:00 | 227 | 227
2018-07-27 10:30 | 221 | 221
2018-07-27 11:00 | 214 | 214
2018-07-27 11:30 | 207 | 207
2018-07-27 12:00 | 167 | 167
2018-07-27 12:30 | 195 | 194
2018-07-27 13:00 | 202 | 202
2018-07-27 13:30 | 187 | 187
2018-07-27 14:00 | 205 | 205
2018-07-27 14:30 | 188 | 188
2018-07-27 15:00 | 176 | 176
2018-07-27 15:30 | 225 | 225
2018-07-27 16:00 | 245 | 245
2018-07-27 16:30 | 259 | 259
2018-07-27 17:00 | 267 | 267
2018-07-27 17:30 | 289 | 288
2018-07-27 18:00 | 289 | 288
2018-07-27 18:30 | 287 | 286
2018-07-27 19:00 | 283 | 281
2018-07-27 19:30 | 284 | 282
2018-07-27 20:00 | 274 | 274
2018-07-27 20:30 | 261 | 261
2018-07-27 21:00 | 254 | 254
2018-07-27 21:30 | 246 | 246
2018-07-27 22:00 | 225 | 225
2018-07-27 22:30 | 244 | 243
2018-07-27 23:00 | 230 | 229
2018-07-27 23:30 | 218 | 217
2018-07-28 | 198 | 196
2018-07-28 00:30 | 189 | 186
2018-07-28 01:00 | 179 | 177
2018-07-28 01:30 | 170 | 169
2018-07-28 02:00 | 166 | 165
2018-07-28 02:30 | 165 | 163
2018-07-28 03:00 | 165 | 163
2018-07-28 03:30 | 163 | 162
2018-07-28 04:00 | 163 | 162
2018-07-28 04:30 | 163 | 162
2018-07-28 05:00 | 166 | 165
2018-07-28 05:30 | 172 | 171
2018-07-28 06:00 | 182 | 181
2018-07-28 06:30 | 189 | 189
2018-07-28 07:00 | 206 | 206
2018-07-28 07:30 | 220 | 220
2018-07-28 08:00 | 230 | 230
2018-07-28 08:30 | 231 | 231
2018-07-28 09:00 | 231 | 230
2018-07-28 09:30 | 228 | 227
2018-07-28 10:00 | 222 | 221
2018-07-28 10:30 | 213 | 213
2018-07-28 11:00 | 204 | 204
2018-07-28 11:30 | 198 | 198
2018-07-28 12:00 | 194 | 194
2018-07-28 12:30 | 191 | 191
2018-07-28 13:00 | 189 | 189
2018-07-28 13:30 | 177 | 177
2018-07-28 14:00 | 201 | 201
2018-07-28 14:30 | 204 | 204
2018-07-28 15:00 | 188 | 188
2018-07-28 15:30 | 211 | 211
2018-07-28 16:00 | 225 | 225
2018-07-28 16:30 | 246 | 245
2018-07-28 17:00 | 261 | 261
2018-07-28 17:30 | 270 | 270
2018-07-28 18:00 | 266 | 265
2018-07-28 18:30 | 263 | 263
2018-07-28 19:00 | 254 | 254
2018-07-28 19:30 | 253 | 253
2018-07-28 20:00 | 246 | 246
2018-07-28 20:30 | 233 | 233
2018-07-28 21:00 | 224 | 223
2018-07-28 21:30 | 216 | 215
2018-07-28 22:00 | 191 | 191
2018-07-28 22:30 | 214 | 213
2018-07-28 23:00 | 195 | 194
2018-07-28 23:30 | 198 | 196
2018-07-29 | 183 | 181
2018-07-29 00:30 | 174 | 171
2018-07-29 01:00 | 163 | 162
2018-07-29 01:30 | 160 | 159
2018-07-29 02:00 | 159 | 158
2018-07-29 02:30 | 159 | 158
2018-07-29 03:00 | 152 | 150
2018-07-29 03:30 | 145 | 143
2018-07-29 04:00 | 151 | 149
2018-07-29 04:30 | 151 | 149
2018-07-29 05:00 | 155 | 153
2018-07-29 05:30 | 157 | 156
2018-07-29 06:00 | 173 | 172
2018-07-29 06:30 | 179 | 178
2018-07-29 07:00 | 187 | 187
2018-07-29 07:30 | 195 | 194
2018-07-29 08:00 | 202 | 202
2018-07-29 08:30 | 206 | 206
2018-07-29 09:00 | 208 | 208
2018-07-29 09:30 | 199 | 199
2018-07-29 10:00 | 200 | 200
2018-07-29 10:30 | 196 | 196
2018-07-29 11:00 | 194 | 194
2018-07-29 11:30 | 183 | 183
2018-07-29 12:00 | 147 | 147
2018-07-29 12:30 | 171 | 171
2018-07-29 13:00 | 145 | 145
2018-07-29 13:30 | 186 | 186
2018-07-29 14:00 | 192 | 192
2018-07-29 14:30 | 199 | 199
2018-07-29 15:00 | 206 | 206
2018-07-29 15:30 | 213 | 213
2018-07-29 16:00 | 222 | 222
2018-07-29 16:30 | 230 | 230
2018-07-29 17:00 | 237 | 237
2018-07-29 17:30 | 263 | 262
2018-07-29 18:00 | 262 | 260
2018-07-29 18:30 | 259 | 257
2018-07-29 19:00 | 252 | 250
2018-07-29 19:30 | 248 | 247
2018-07-29 20:00 | 244 | 243
2018-07-29 20:30 | 234 | 234
2018-07-29 21:00 | 224 | 224
2018-07-29 21:30 | 214 | 214
2018-07-29 22:00 | 213 | 212
2018-07-29 22:30 | 214 | 213
2018-07-29 23:00 | 206 | 205
2018-07-29 23:30 | 195 | 193
2018-07-30 | 163 | 160
2018-07-30 00:30 | 169 | 165
2018-07-30 01:00 | 171 | 167
2018-07-30 01:30 | 161 | 157
2018-07-30 02:00 | 157 | 155
2018-07-30 02:30 | 156 | 155
2018-07-30 03:00 | 157 | 155
2018-07-30 03:30 | 158 | 157
2018-07-30 04:00 | 162 | 161
2018-07-30 04:30 | 168 | 167
2018-07-30 05:00 | 180 | 180
2018-07-30 05:30 | 190 | 190
2018-07-30 06:00 | 206 | 206
2018-07-30 06:30 | 235 | 235
2018-07-30 07:00 | 252 | 252
2018-07-30 07:30 | 262 | 261
2018-07-30 08:00 | 259 | 259
2018-07-30 08:30 | 244 | 244
2018-07-30 09:00 | 235 | 235
2018-07-30 09:30 | 227 | 227
2018-07-30 10:00 | 218 | 218
2018-07-30 10:30 | 211 | 211
2018-07-30 11:00 | 206 | 206
2018-07-30 11:30 | 201 | 201
2018-07-30 12:00 | 199 | 199
2018-07-30 12:30 | 187 | 187
2018-07-30 13:00 | 201 | 201
2018-07-30 13:30 | 200 | 200
2018-07-30 14:00 | 203 | 203
2018-07-30 14:30 | 200 | 200
2018-07-30 15:00 | 208 | 208
2018-07-30 15:30 | 215 | 215
2018-07-30 16:00 | 232 | 232
2018-07-30 16:30 | 242 | 242
2018-07-30 17:00 | 264 | 264
2018-07-30 17:30 | 292 | 291
2018-07-30 18:00 | 297 | 296
2018-07-30 18:30 | 296 | 295
2018-07-30 19:00 | 285 | 284
2018-07-30 19:30 | 278 | 277
2018-07-30 20:00 | 270 | 270
2018-07-30 20:30 | 259 | 259
2018-07-30 21:00 | 248 | 247
2018-07-30 21:30 | 232 | 232
2018-07-30 22:00 | 227 | 226
2018-07-30 22:30 | 226 | 225
2018-07-30 23:00 | 217 | 216
2018-07-30 23:30 | 202 | 200
2018-07-31 | 187 | 184
2018-07-31 00:30 | 177 | 174
2018-07-31 01:00 | 170 | 167
2018-07-31 01:30 | 164 | 160
2018-07-31 02:00 | 157 | 155
2018-07-31 02:30 | 156 | 154
2018-07-31 03:00 | 157 | 156
2018-07-31 03:30 | 154 | 153
2018-07-31 04:00 | 160 | 159
2018-07-31 04:30 | 166 | 165
2018-07-31 05:00 | 171 | 171
2018-07-31 05:30 | 198 | 198
2018-07-31 06:00 | 228 | 228
2018-07-31 06:30 | 269 | 269
2018-07-31 07:00 | 297 | 296
2018-07-31 07:30 | 295 | 292
2018-07-31 08:00 | 275 | 273
2018-07-31 08:30 | 258 | 256
2018-07-31 09:00 | 249 | 247
2018-07-31 09:30 | 237 | 237
2018-07-31 10:00 | 224 | 224
2018-07-31 10:30 | 218 | 218
2018-07-31 11:00 | 203 | 203
2018-07-31 11:30 | 182 | 182
2018-07-31 12:00 | 159 | 159
2018-07-31 12:30 | 169 | 169
2018-07-31 13:00 | 161 | 161
2018-07-31 13:30 | 166 | 166
2018-07-31 14:00 | 196 | 196
2018-07-31 14:30 | 211 | 211
2018-07-31 15:00 | 212 | 212
2018-07-31 15:30 | 222 | 222
2018-07-31 16:00 | 238 | 238
2018-07-31 16:30 | 252 | 252
2018-07-31 17:00 | 269 | 269
2018-07-31 17:30 | 305 | 303
2018-07-31 18:00 | 307 | 305
2018-07-31 18:30 | 309 | 307
2018-07-31 19:00 | 300 | 299
2018-07-31 19:30 | 300 | 299
2018-07-31 20:00 | 299 | 298
2018-07-31 20:30 | 288 | 286
2018-07-31 21:00 | 268 | 266
2018-07-31 21:30 | 244 | 244
2018-07-31 22:00 | 236 | 236
2018-07-31 22:30 | 233 | 233
2018-07-31 23:00 | 218 | 218
2018-07-31 23:30 | 209 | 208
2018-08-01 | 191 | 188
2018-08-01 00:30 | 185 | 183
2018-08-01 01:00 | 182 | 179
2018-08-01 01:30 | 176 | 173
2018-08-01 02:00 | 172 | 168
2018-08-01 02:30 | 166 | 162
2018-08-01 03:00 | 165 | 161
2018-08-01 03:30 | 164 | 160
2018-08-01 04:00 | 165 | 162
2018-08-01 04:30 | 171 | 168
2018-08-01 05:00 | 196 | 194
2018-08-01 05:30 | 213 | 212
2018-08-01 06:00 | 247 | 247
2018-08-01 06:30 | 280 | 280
2018-08-01 07:00 | 309 | 308
2018-08-01 07:30 | 308 | 308
2018-08-01 08:00 | 287 | 287
2018-08-01 08:30 | 268 | 267
2018-08-01 09:00 | 254 | 253
2018-08-01 09:30 | 241 | 240
2018-08-01 10:00 | 225 | 225
2018-08-01 10:30 | 217 | 217
2018-08-01 11:00 | 214 | 214
2018-08-01 11:30 | 210 | 210
2018-08-01 12:00 | 207 | 207
2018-08-01 12:30 | 206 | 206
2018-08-01 13:00 | 208 | 208
2018-08-01 13:30 | 215 | 215
2018-08-01 14:00 | 223 | 223
2018-08-01 14:30 | 226 | 226
2018-08-01 15:00 | 227 | 227
2018-08-01 15:30 | 237 | 237
2018-08-01 16:00 | 251 | 251
2018-08-01 16:30 | 267 | 267
2018-08-01 17:00 | 290 | 289
2018-08-01 17:30 | 315 | 315
2018-08-01 18:00 | 321 | 321
2018-08-01 18:30 | 327 | 327
2018-08-01 19:00 | 319 | 318
2018-08-01 19:30 | 313 | 312
2018-08-01 20:00 | 304 | 304
2018-08-01 20:30 | 295 | 294
2018-08-01 21:00 | 280 | 278
2018-08-01 21:30 | 267 | 265
2018-08-01 22:00 | 256 | 255
2018-08-01 22:30 | 249 | 249
2018-08-01 23:00 | 240 | 240
2018-08-01 23:30 | 227 | 227
2018-08-02 | 205 | 204
2018-08-02 00:30 | 191 | 191
2018-08-02 01:00 | 185 | 185
2018-08-02 01:30 | 178 | 177
2018-08-02 02:00 | 172 | 171
2018-08-02 02:30 | 165 | 164
2018-08-02 03:00 | 163 | 161
2018-08-02 03:30 | 157 | 155
2018-08-02 04:00 | 164 | 163
2018-08-02 04:30 | 167 | 166
2018-08-02 05:00 | 181 | 180
2018-08-02 05:30 | 196 | 195
2018-08-02 06:00 | 225 | 225
2018-08-02 06:30 | 266 | 266
2018-08-02 07:00 | 287 | 287
2018-08-02 07:30 | 288 | 288
2018-08-02 08:00 | 270 | 269
2018-08-02 08:30 | 251 | 251
2018-08-02 09:00 | 239 | 239
2018-08-02 09:30 | 227 | 227
2018-08-02 10:00 | 215 | 215
2018-08-02 10:30 | 209 | 209
2018-08-02 11:00 | 203 | 203
2018-08-02 11:30 | 183 | 183
2018-08-02 12:00 | 199 | 199
2018-08-02 12:30 | 195 | 195
2018-08-02 13:00 | 201 | 201
2018-08-02 13:30 | 202 | 202
2018-08-02 14:00 | 205 | 205
2018-08-02 14:30 | 207 | 207
2018-08-02 15:00 | 213 | 213
2018-08-02 15:30 | 220 | 220
2018-08-02 16:00 | 235 | 235
2018-08-02 16:30 | 254 | 254
2018-08-02 17:00 | 279 | 278
2018-08-02 17:30 | 295 | 295
2018-08-02 18:00 | 300 | 299
2018-08-02 18:30 | 302 | 302
2018-08-02 19:00 | 300 | 299
2018-08-02 19:30 | 302 | 301
2018-08-02 20:00 | 298 | 297
2018-08-02 20:30 | 285 | 283
2018-08-02 21:00 | 272 | 270
2018-08-02 21:30 | 254 | 254
2018-08-02 22:00 | 247 | 247
2018-08-02 22:30 | 246 | 246
2018-08-02 23:00 | 236 | 235
2018-08-02 23:30 | 224 | 223
2018-08-03 | 205 | 203
2018-08-03 00:30 | 195 | 193
2018-08-03 01:00 | 189 | 187
2018-08-03 01:30 | 182 | 180
2018-08-03 02:00 | 173 | 170
2018-08-03 02:30 | 170 | 167
2018-08-03 03:00 | 172 | 168
2018-08-03 03:30 | 171 | 168
2018-08-03 04:00 | 173 | 169
2018-08-03 04:30 | 175 | 173
2018-08-03 05:00 | 182 | 180
2018-08-03 05:30 | 198 | 197
2018-08-03 06:00 | 221 | 221
2018-08-03 06:30 | 249 | 249
2018-08-03 07:00 | 247 | 247
2018-08-03 07:30 | 270 | 270
2018-08-03 08:00 | 263 | 263
2018-08-03 08:30 | 248 | 248
2018-08-03 09:00 | 235 | 235
2018-08-03 09:30 | 220 | 220
2018-08-03 10:00 | 210 | 210
2018-08-03 10:30 | 204 | 204
2018-08-03 11:00 | 201 | 201
2018-08-03 11:30 | 198 | 198
2018-08-03 12:00 | 192 | 192
2018-08-03 12:30 | 193 | 193
2018-08-03 13:00 | 191 | 191
2018-08-03 13:30 | 191 | 191
2018-08-03 14:00 | 195 | 195
2018-08-03 14:30 | 199 | 199
2018-08-03 15:00 | 209 | 209
2018-08-03 15:30 | 220 | 220
2018-08-03 16:00 | 235 | 235
2018-08-03 16:30 | 254 | 254
2018-08-03 17:00 | 263 | 263
2018-08-03 17:30 | 273 | 272
2018-08-03 18:00 | 273 | 272
2018-08-03 18:30 | 280 | 279
2018-08-03 19:00 | 267 | 266
2018-08-03 19:30 | 263 | 262
2018-08-03 20:00 | 254 | 253
2018-08-03 20:30 | 246 | 246
2018-08-03 21:00 | 238 | 238
2018-08-03 21:30 | 226 | 225
2018-08-03 22:00 | 222 | 221
2018-08-03 22:30 | 219 | 219
2018-08-03 23:00 | 211 | 210
2018-08-03 23:30 | 203 | 201
2018-08-04 | 180 | 177
2018-08-04 00:30 | 171 | 168
2018-08-04 01:00 | 159 | 158
2018-08-04 01:30 | 152 | 151
2018-08-04 02:00 | 150 | 148
2018-08-04 02:30 | 148 | 146
2018-08-04 03:00 | 146 | 145
2018-08-04 03:30 | 145 | 144
2018-08-04 04:00 | 141 | 139
2018-08-04 04:30 | 147 | 145
2018-08-04 05:00 | 151 | 150
2018-08-04 05:30 | 162 | 161
2018-08-04 06:00 | 175 | 175
2018-08-04 06:30 | 184 | 183
2018-08-04 07:00 | 194 | 194
2018-08-04 07:30 | 202 | 202
2018-08-04 08:00 | 210 | 210
2018-08-04 08:30 | 211 | 211
2018-08-04 09:00 | 206 | 206
2018-08-04 09:30 | 199 | 199
2018-08-04 10:00 | 195 | 195
2018-08-04 10:30 | 188 | 188
2018-08-04 11:00 | 184 | 184
2018-08-04 11:30 | 180 | 180
2018-08-04 12:00 | 156 | 156
2018-08-04 12:30 | 142 | 142
2018-08-04 13:00 | 182 | 182
2018-08-04 13:30 | 175 | 175
2018-08-04 14:00 | 185 | 185
2018-08-04 14:30 | 177 | 177
2018-08-04 15:00 | 192 | 192
2018-08-04 15:30 | 200 | 200
2018-08-04 16:00 | 211 | 211
2018-08-04 16:30 | 223 | 223
2018-08-04 17:00 | 231 | 231
2018-08-04 17:30 | 247 | 247
2018-08-04 18:00 | 256 | 256
2018-08-04 18:30 | 254 | 254
2018-08-04 19:00 | 245 | 245
2018-08-04 19:30 | 242 | 242
2018-08-04 20:00 | 238 | 238
2018-08-04 20:30 | 228 | 228
2018-08-04 21:00 | 218 | 217
2018-08-04 21:30 | 211 | 211
2018-08-04 22:00 | 213 | 213
2018-08-04 22:30 | 219 | 219
2018-08-04 23:00 | 208 | 207
2018-08-04 23:30 | 197 | 195
2018-08-05 | 181 | 178
2018-08-05 00:30 | 170 | 169
2018-08-05 01:00 | 158 | 157
2018-08-05 01:30 | 152 | 151
2018-08-05 02:00 | 145 | 143
2018-08-05 02:30 | 134 | 133
2018-08-05 03:00 | 112 | 112
2018-08-05 03:30 | 107 | 107
2018-08-05 04:00 | 108 | 108
2018-08-05 04:30 | 110 | 110
2018-08-05 05:00 | 136 | 136
2018-08-05 05:30 | 122 | 122
2018-08-05 06:00 | 155 | 155
2018-08-05 06:30 | 155 | 155
2018-08-05 07:00 | 179 | 179
2018-08-05 07:30 | 199 | 198
2018-08-05 08:00 | 199 | 199
2018-08-05 08:30 | 202 | 202
2018-08-05 09:00 | 199 | 199
2018-08-05 09:30 | 176 | 176
2018-08-05 10:00 | 189 | 189
2018-08-05 10:30 | 163 | 163
2018-08-05 11:00 | 155 | 155
2018-08-05 11:30 | 165 | 165
2018-08-05 12:00 | 161 | 161
2018-08-05 12:30 | 139 | 139
2018-08-05 13:00 | 159 | 158
2018-08-05 13:30 | 157 | 157
2018-08-05 14:00 | 174 | 174
2018-08-05 14:30 | 170 | 170
2018-08-05 15:00 | 155 | 155
2018-08-05 15:30 | 177 | 177
2018-08-05 16:00 | 213 | 213
2018-08-05 16:30 | 227 | 227
2018-08-05 17:00 | 235 | 234
2018-08-05 17:30 | 246 | 246
2018-08-05 18:00 | 256 | 255
2018-08-05 18:30 | 257 | 256
2018-08-05 19:00 | 247 | 247
2018-08-05 19:30 | 245 | 245
2018-08-05 20:00 | 242 | 242
2018-08-05 20:30 | 234 | 234
2018-08-05 21:00 | 222 | 222
2018-08-05 21:30 | 210 | 210
2018-08-05 22:00 | 203 | 203
2018-08-05 22:30 | 202 | 202
2018-08-05 23:00 | 197 | 197
2018-08-05 23:30 | 188 | 188
2018-08-06 | 172 | 172
2018-08-06 00:30 | 164 | 163
2018-08-06 01:00 | 157 | 156
2018-08-06 01:30 | 150 | 149
2018-08-06 02:00 | 148 | 146
2018-08-06 02:30 | 145 | 143
2018-08-06 03:00 | 150 | 149
2018-08-06 03:30 | 145 | 144
2018-08-06 04:00 | 131 | 130
2018-08-06 04:30 | 154 | 153
2018-08-06 05:00 | 163 | 162
2018-08-06 05:30 | 178 | 177
2018-08-06 06:00 | 198 | 198
2018-08-06 06:30 | 221 | 221
2018-08-06 07:00 | 242 | 241
2018-08-06 07:30 | 250 | 249
2018-08-06 08:00 | 247 | 247
2018-08-06 08:30 | 242 | 242
2018-08-06 09:00 | 238 | 237
2018-08-06 09:30 | 232 | 232
2018-08-06 10:00 | 225 | 225
2018-08-06 10:30 | 217 | 217
2018-08-06 11:00 | 213 | 213
2018-08-06 11:30 | 207 | 206
2018-08-06 12:00 | 208 | 208
2018-08-06 12:30 | 204 | 204
2018-08-06 13:00 | 198 | 198
2018-08-06 13:30 | 203 | 203
2018-08-06 14:00 | 209 | 209
2018-08-06 14:30 | 212 | 212
2018-08-06 15:00 | 224 | 224
2018-08-06 15:30 | 232 | 231
2018-08-06 16:00 | 251 | 251
2018-08-06 16:30 | 264 | 264
2018-08-06 17:00 | 283 | 283
2018-08-06 17:30 | 307 | 306
2018-08-06 18:00 | 315 | 313
2018-08-06 18:30 | 311 | 309
2018-08-06 19:00 | 293 | 290
2018-08-06 19:30 | 284 | 284
2018-08-06 20:00 | 279 | 279
2018-08-06 20:30 | 265 | 265
2018-08-06 21:00 | 245 | 244
2018-08-06 21:30 | 231 | 230
2018-08-06 22:00 | 228 | 227
2018-08-06 22:30 | 224 | 223
2018-08-06 23:00 | 216 | 214
2018-08-06 23:30 | 205 | 203
2018-08-07 | 183 | 181
2018-08-07 00:30 | 173 | 172
2018-08-07 01:00 | 164 | 163
2018-08-07 01:30 | 156 | 155
2018-08-07 02:00 | 149 | 148
2018-08-07 02:30 | 133 | 132
2018-08-07 03:00 | 130 | 128
2018-08-07 03:30 | 130 | 128
2018-08-07 04:00 | 139 | 137
2018-08-07 04:30 | 151 | 150
2018-08-07 05:00 | 168 | 168
2018-08-07 05:30 | 180 | 180
2018-08-07 06:00 | 201 | 201
2018-08-07 06:30 | 228 | 228
2018-08-07 07:00 | 251 | 251
2018-08-07 07:30 | 261 | 260
2018-08-07 08:00 | 257 | 257
2018-08-07 08:30 | 240 | 240
2018-08-07 09:00 | 229 | 229
2018-08-07 09:30 | 216 | 216
2018-08-07 10:00 | 201 | 201
2018-08-07 10:30 | 190 | 190
2018-08-07 11:00 | 188 | 188
2018-08-07 11:30 | 187 | 187
2018-08-07 12:00 | 193 | 193
2018-08-07 12:30 | 199 | 199
2018-08-07 13:00 | 197 | 197
2018-08-07 13:30 | 196 | 196
2018-08-07 14:00 | 189 | 189
2018-08-07 14:30 | 190 | 190
2018-08-07 15:00 | 195 | 195
2018-08-07 15:30 | 212 | 212
2018-08-07 16:00 | 227 | 227
2018-08-07 16:30 | 248 | 248
2018-08-07 17:00 | 270 | 270
2018-08-07 17:30 | 296 | 296
2018-08-07 18:00 | 303 | 302
2018-08-07 18:30 | 306 | 305
2018-08-07 19:00 | 296 | 296
2018-08-07 19:30 | 300 | 299
2018-08-07 20:00 | 291 | 291
2018-08-07 20:30 | 276 | 276
2018-08-07 21:00 | 263 | 263
2018-08-07 21:30 | 250 | 250
2018-08-07 22:00 | 241 | 241
2018-08-07 22:30 | 236 | 235
2018-08-07 23:00 | 234 | 233
2018-08-07 23:30 | 220 | 219
2018-08-08 | 199 | 197
2018-08-08 00:30 | 186 | 183
2018-08-08 01:00 | 175 | 171
2018-08-08 01:30 | 167 | 163
2018-08-08 02:00 | 157 | 153
2018-08-08 02:30 | 136 | 132
2018-08-08 03:00 | 152 | 149
2018-08-08 03:30 | 154 | 151
2018-08-08 04:00 | 138 | 136
2018-08-08 04:30 | 141 | 139
2018-08-08 05:00 | 181 | 180
2018-08-08 05:30 | 203 | 202
2018-08-08 06:00 | 233 | 231
2018-08-08 06:30 | 267 | 265
2018-08-08 07:00 | 288 | 285
2018-08-08 07:30 | 291 | 286
2018-08-08 08:00 | 278 | 273
2018-08-08 08:30 | 258 | 253
2018-08-08 09:00 | 244 | 240
2018-08-08 09:30 | 233 | 229
2018-08-08 10:00 | 218 | 217
2018-08-08 10:30 | 208 | 207
2018-08-08 11:00 | 201 | 200
2018-08-08 11:30 | 197 | 195
2018-08-08 12:00 | 187 | 185
2018-08-08 12:30 | 190 | 189
2018-08-08 13:00 | 189 | 188
2018-08-08 13:30 | 184 | 182
2018-08-08 14:00 | 196 | 195
2018-08-08 14:30 | 194 | 192
2018-08-08 15:00 | 204 | 203
2018-08-08 15:30 | 223 | 222
2018-08-08 16:00 | 245 | 243
2018-08-08 16:30 | 267 | 264
2018-08-08 17:00 | 285 | 281
2018-08-08 17:30 | 311 | 309
2018-08-08 18:00 | 325 | 323
2018-08-08 18:30 | 326 | 325
2018-08-08 19:00 | 314 | 313
2018-08-08 19:30 | 313 | 311
2018-08-08 20:00 | 312 | 310
2018-08-08 20:30 | 301 | 299
2018-08-08 21:00 | 284 | 281
2018-08-08 21:30 | 270 | 267
2018-08-08 22:00 | 259 | 255
2018-08-08 22:30 | 256 | 251
2018-08-08 23:00 | 249 | 243
2018-08-08 23:30 | 237 | 229
2018-08-09 | 214 | 207
2018-08-09 00:30 | 199 | 192
2018-08-09 01:00 | 182 | 177
2018-08-09 01:30 | 170 | 165
2018-08-09 02:00 | 155 | 149
2018-08-09 02:30 | 138 | 131
2018-08-09 03:00 | 155 | 149
2018-08-09 03:30 | 163 | 157
2018-08-09 04:00 | 167 | 161
2018-08-09 04:30 | 174 | 170
2018-08-09 05:00 | 188 | 185
2018-08-09 05:30 | 211 | 210
2018-08-09 06:00 | 247 | 246
2018-08-09 06:30 | 283 | 282
2018-08-09 07:00 | 316 | 314
2018-08-09 07:30 | 317 | 315
2018-08-09 08:00 | 295 | 293
2018-08-09 08:30 | 273 | 270
2018-08-09 09:00 | 257 | 255
2018-08-09 09:30 | 242 | 241
2018-08-09 10:00 | 232 | 231
2018-08-09 10:30 | 222 | 221
2018-08-09 11:00 | 207 | 206
2018-08-09 11:30 | 180 | 179
2018-08-09 12:00 | 181 | 180
2018-08-09 12:30 | 151 | 149
2018-08-09 13:00 | 200 | 198
2018-08-09 13:30 | 171 | 169
2018-08-09 14:00 | 210 | 209
2018-08-09 14:30 | 216 | 215
2018-08-09 15:00 | 225 | 223
2018-08-09 15:30 | 238 | 236
2018-08-09 16:00 | 251 | 250
2018-08-09 16:30 | 272 | 270
2018-08-09 17:00 | 293 | 290
2018-08-09 17:30 | 316 | 314
2018-08-09 18:00 | 326 | 325
2018-08-09 18:30 | 327 | 326
2018-08-09 19:00 | 322 | 321
2018-08-09 19:30 | 324 | 322
2018-08-09 20:00 | 318 | 315
2018-08-09 20:30 | 306 | 303
2018-08-09 21:00 | 287 | 282
2018-08-09 21:30 | 268 | 265
2018-08-09 22:00 | 261 | 258
2018-08-09 22:30 | 252 | 249
2018-08-09 23:00 | 231 | 227
2018-08-09 23:30 | 226 | 221
2018-08-10 | 210 | 205
2018-08-10 00:30 | 200 | 193
2018-08-10 01:00 | 192 | 184
2018-08-10 01:30 | 186 | 177
2018-08-10 02:00 | 179 | 174
2018-08-10 02:30 | 177 | 172
2018-08-10 03:00 | 178 | 173
2018-08-10 03:30 | 179 | 175
2018-08-10 04:00 | 185 | 180
2018-08-10 04:30 | 192 | 188
2018-08-10 05:00 | 207 | 204
2018-08-10 05:30 | 203 | 201
2018-08-10 06:00 | 235 | 234
2018-08-10 06:30 | 280 | 279
2018-08-10 07:00 | 297 | 296
2018-08-10 07:30 | 293 | 293
2018-08-10 08:00 | 279 | 279
2018-08-10 08:30 | 256 | 255
2018-08-10 09:00 | 240 | 239
2018-08-10 09:30 | 231 | 231
2018-08-10 10:00 | 218 | 217
2018-08-10 10:30 | 210 | 209
2018-08-10 11:00 | 197 | 196
2018-08-10 11:30 | 191 | 190
2018-08-10 12:00 | 186 | 185
2018-08-10 12:30 | 188 | 187
2018-08-10 13:00 | 191 | 189
2018-08-10 13:30 | 193 | 191
2018-08-10 14:00 | 197 | 196
2018-08-10 14:30 | 199 | 198
2018-08-10 15:00 | 208 | 207
2018-08-10 15:30 | 219 | 217
2018-08-10 16:00 | 238 | 237
2018-08-10 16:30 | 254 | 253
2018-08-10 17:00 | 266 | 265
2018-08-10 17:30 | 287 | 285
2018-08-10 18:00 | 291 | 288
2018-08-10 18:30 | 290 | 286
2018-08-10 19:00 | 280 | 278
2018-08-10 19:30 | 279 | 278
2018-08-10 20:00 | 277 | 276
2018-08-10 20:30 | 267 | 265
2018-08-10 21:00 | 256 | 254
2018-08-10 21:30 | 247 | 244
2018-08-10 22:00 | 238 | 235
2018-08-10 22:30 | 236 | 233
2018-08-10 23:00 | 230 | 226
2018-08-10 23:30 | 217 | 213
2018-08-11 | 198 | 192
2018-08-11 00:30 | 185 | 177
2018-08-11 01:00 | 174 | 165
2018-08-11 01:30 | 163 | 156
2018-08-11 02:00 | 157 | 151
2018-08-11 02:30 | 155 | 149
2018-08-11 03:00 | 156 | 150
2018-08-11 03:30 | 155 | 148
2018-08-11 04:00 | 157 | 151
2018-08-11 04:30 | 157 | 151
2018-08-11 05:00 | 163 | 158
2018-08-11 05:30 | 170 | 166
2018-08-11 06:00 | 176 | 172
2018-08-11 06:30 | 193 | 190
2018-08-11 07:00 | 211 | 209
2018-08-11 07:30 | 228 | 227
2018-08-11 08:00 | 237 | 236
2018-08-11 08:30 | 239 | 239
2018-08-11 09:00 | 242 | 241
2018-08-11 09:30 | 234 | 232
2018-08-11 10:00 | 222 | 220
2018-08-11 10:30 | 208 | 206
2018-08-11 11:00 | 202 | 199
2018-08-11 11:30 | 189 | 185
2018-08-11 12:00 | 180 | 176
2018-08-11 12:30 | 180 | 176
2018-08-11 13:00 | 175 | 170
2018-08-11 13:30 | 183 | 178
2018-08-11 14:00 | 186 | 182
2018-08-11 14:30 | 193 | 189
2018-08-11 15:00 | 199 | 195
2018-08-11 15:30 | 208 | 204
2018-08-11 16:00 | 220 | 217
2018-08-11 16:30 | 235 | 233
2018-08-11 17:00 | 243 | 241
2018-08-11 17:30 | 250 | 249
2018-08-11 18:00 | 250 | 248
2018-08-11 18:30 | 249 | 247
2018-08-11 19:00 | 245 | 243
2018-08-11 19:30 | 240 | 238
2018-08-11 20:00 | 239 | 237
2018-08-11 20:30 | 238 | 235
2018-08-11 21:00 | 234 | 231
2018-08-11 21:30 | 229 | 226
2018-08-11 22:00 | 225 | 221
2018-08-11 22:30 | 227 | 223
2018-08-11 23:00 | 222 | 217
2018-08-11 23:30 | 210 | 204
2018-08-12 | 185 | 178
2018-08-12 00:30 | 176 | 171
2018-08-12 01:00 | 175 | 169
2018-08-12 01:30 | 170 | 164
2018-08-12 02:00 | 166 | 159
2018-08-12 02:30 | 163 | 156
2018-08-12 03:00 | 162 | 155
2018-08-12 03:30 | 162 | 155
2018-08-12 04:00 | 163 | 156
2018-08-12 04:30 | 162 | 155
2018-08-12 05:00 | 165 | 159
2018-08-12 05:30 | 172 | 166
2018-08-12 06:00 | 178 | 172
2018-08-12 06:30 | 186 | 180
2018-08-12 07:00 | 196 | 192
2018-08-12 07:30 | 206 | 202
2018-08-12 08:00 | 212 | 210
2018-08-12 08:30 | 215 | 213
2018-08-12 09:00 | 215 | 213
2018-08-12 09:30 | 209 | 208
2018-08-12 10:00 | 205 | 204
2018-08-12 10:30 | 212 | 211
2018-08-12 11:00 | 205 | 204
2018-08-12 11:30 | 200 | 199
2018-08-12 12:00 | 196 | 195
2018-08-12 12:30 | 191 | 190
2018-08-12 13:00 | 181 | 180
2018-08-12 13:30 | 177 | 175
2018-08-12 14:00 | 185 | 184
2018-08-12 14:30 | 189 | 187
2018-08-12 15:00 | 192 | 190
2018-08-12 15:30 | 193 | 191
2018-08-12 16:00 | 207 | 205
2018-08-12 16:30 | 230 | 229
2018-08-12 17:00 | 249 | 248
2018-08-12 17:30 | 270 | 267
2018-08-12 18:00 | 279 | 274
2018-08-12 18:30 | 280 | 275
2018-08-12 19:00 | 275 | 270
2018-08-12 19:30 | 264 | 264
2018-08-12 20:00 | 262 | 262
2018-08-12 20:30 | 255 | 255
2018-08-12 21:00 | 245 | 244
2018-08-12 21:30 | 233 | 232
2018-08-12 22:00 | 227 | 226
2018-08-12 22:30 | 224 | 222
2018-08-12 23:00 | 213 | 211
2018-08-12 23:30 | 202 | 199
2018-08-13 | 185 | 183
2018-08-13 00:30 | 144 | 142
2018-08-13 01:00 | 150 | 147
2018-08-13 01:30 | 155 | 152
2018-08-13 02:00 | 169 | 166
2018-08-13 02:30 | 162 | 160
2018-08-13 03:00 | 163 | 161
2018-08-13 03:30 | 165 | 163
2018-08-13 04:00 | 170 | 168
2018-08-13 04:30 | 168 | 166
2018-08-13 05:00 | 179 | 178
2018-08-13 05:30 | 196 | 196
2018-08-13 06:00 | 227 | 227
2018-08-13 06:30 | 266 | 266
2018-08-13 07:00 | 289 | 289
2018-08-13 07:30 | 298 | 298
2018-08-13 08:00 | 290 | 290
2018-08-13 08:30 | 270 | 270
2018-08-13 09:00 | 259 | 258
2018-08-13 09:30 | 247 | 247
2018-08-13 10:00 | 230 | 229
2018-08-13 10:30 | 220 | 219
2018-08-13 11:00 | 213 | 212
2018-08-13 11:30 | 209 | 208
2018-08-13 12:00 | 207 | 207
2018-08-13 12:30 | 203 | 202
2018-08-13 13:00 | 203 | 202
2018-08-13 13:30 | 206 | 205
2018-08-13 14:00 | 212 | 211
2018-08-13 14:30 | 224 | 223
2018-08-13 15:00 | 229 | 228
2018-08-13 15:30 | 240 | 240
2018-08-13 16:00 | 261 | 261
2018-08-13 16:30 | 281 | 281
2018-08-13 17:00 | 295 | 295
2018-08-13 17:30 | 320 | 320
2018-08-13 18:00 | 335 | 334
2018-08-13 18:30 | 338 | 336
2018-08-13 19:00 | 322 | 320
2018-08-13 19:30 | 320 | 318
2018-08-13 20:00 | 315 | 313
2018-08-13 20:30 | 307 | 306
2018-08-13 21:00 | 299 | 299
2018-08-13 21:30 | 290 | 289
2018-08-13 22:00 | 270 | 268
2018-08-13 22:30 | 259 | 259
2018-08-13 23:00 | 249 | 249
2018-08-13 23:30 | 249 | 249
2018-08-14 | 216 | 215
2018-08-14 00:30 | 207 | 206
2018-08-14 01:00 | 202 | 201
2018-08-14 01:30 | 197 | 196
2018-08-14 02:00 | 170 | 167
2018-08-14 02:30 | 173 | 171
2018-08-14 03:00 | 180 | 178
2018-08-14 03:30 | 182 | 179
2018-08-14 04:00 | 187 | 185
2018-08-14 04:30 | 194 | 192
2018-08-14 05:00 | 210 | 209
2018-08-14 05:30 | 220 | 220
2018-08-14 06:00 | 255 | 255
2018-08-14 06:30 | 290 | 289
2018-08-14 07:00 | 311 | 311
2018-08-14 07:30 | 310 | 308
2018-08-14 08:00 | 294 | 292
2018-08-14 08:30 | 271 | 269
2018-08-14 09:00 | 250 | 249
2018-08-14 09:30 | 243 | 241
2018-08-14 10:00 | 219 | 217
2018-08-14 10:30 | 168 | 168
2018-08-14 11:00 | 209 | 209
2018-08-14 11:30 | 207 | 207
2018-08-14 12:00 | 203 | 203
2018-08-14 12:30 | 203 | 203
2018-08-14 13:00 | 203 | 203
2018-08-14 13:30 | 207 | 207
2018-08-14 14:00 | 214 | 214
2018-08-14 14:30 | 221 | 221
2018-08-14 15:00 | 229 | 229
2018-08-14 15:30 | 243 | 243
2018-08-14 16:00 | 256 | 256
2018-08-14 16:30 | 273 | 271
2018-08-14 17:00 | 291 | 289
2018-08-14 17:30 | 317 | 314
2018-08-14 18:00 | 320 | 317
2018-08-14 18:30 | 321 | 317
2018-08-14 19:00 | 315 | 310
2018-08-14 19:30 | 306 | 305
2018-08-14 20:00 | 303 | 302
2018-08-14 20:30 | 292 | 291
2018-08-14 21:00 | 272 | 272
2018-08-14 21:30 | 261 | 260
2018-08-14 22:00 | 253 | 252
2018-08-14 22:30 | 246 | 244
2018-08-14 23:00 | 232 | 230
2018-08-14 23:30 | 223 | 220
2018-08-15 | 203 | 200
2018-08-15 00:30 | 185 | 183
2018-08-15 01:00 | 162 | 159
2018-08-15 01:30 | 143 | 141
2018-08-15 02:00 | 170 | 169
2018-08-15 02:30 | 169 | 168
2018-08-15 03:00 | 169 | 168
2018-08-15 03:30 | 171 | 170
2018-08-15 04:00 | 176 | 175
2018-08-15 04:30 | 182 | 181
2018-08-15 05:00 | 188 | 187
2018-08-15 05:30 | 201 | 201
2018-08-15 06:00 | 236 | 235
2018-08-15 06:30 | 270 | 270
2018-08-15 07:00 | 295 | 294
2018-08-15 07:30 | 291 | 290
2018-08-15 08:00 | 272 | 272
2018-08-15 08:30 | 252 | 251
2018-08-15 09:00 | 241 | 240
2018-08-15 09:30 | 231 | 230
2018-08-15 10:00 | 219 | 218
2018-08-15 10:30 | 208 | 208
2018-08-15 11:00 | 203 | 202
2018-08-15 11:30 | 193 | 192
2018-08-15 12:00 | 175 | 175
2018-08-15 12:30 | 175 | 175
2018-08-15 13:00 | 180 | 179
2018-08-15 13:30 | 165 | 164
2018-08-15 14:00 | 162 | 161
2018-08-15 14:30 | 178 | 177
2018-08-15 15:00 | 217 | 217
2018-08-15 15:30 | 232 | 232
2018-08-15 16:00 | 244 | 244
2018-08-15 16:30 | 259 | 259
2018-08-15 17:00 | 275 | 275
2018-08-15 17:30 | 295 | 294
2018-08-15 18:00 | 302 | 299
2018-08-15 18:30 | 303 | 300
2018-08-15 19:00 | 300 | 297
2018-08-15 19:30 | 292 | 291
2018-08-15 20:00 | 285 | 285
2018-08-15 20:30 | 272 | 271
2018-08-15 21:00 | 263 | 262
2018-08-15 21:30 | 245 | 244
2018-08-15 22:00 | 240 | 240
2018-08-15 22:30 | 240 | 240
2018-08-15 23:00 | 233 | 233
2018-08-15 23:30 | 221 | 221
2018-08-16 | 194 | 194
2018-08-16 00:30 | 181 | 181
2018-08-16 01:00 | 172 | 171
2018-08-16 01:30 | 164 | 164
2018-08-16 02:00 | 151 | 150
2018-08-16 02:30 | 127 | 126
2018-08-16 03:00 | 136 | 135
2018-08-16 03:30 | 160 | 159
2018-08-16 04:00 | 165 | 164
2018-08-16 04:30 | 168 | 168
2018-08-16 05:00 | 182 | 182
2018-08-16 05:30 | 205 | 204
2018-08-16 06:00 | 236 | 236
2018-08-16 06:30 | 261 | 261
2018-08-16 07:00 | 282 | 281
2018-08-16 07:30 | 286 | 285
2018-08-16 08:00 | 277 | 276
2018-08-16 08:30 | 258 | 257
2018-08-16 09:00 | 246 | 244
2018-08-16 09:30 | 233 | 231
2018-08-16 10:00 | 215 | 214
2018-08-16 10:30 | 206 | 205
2018-08-16 11:00 | 203 | 203
2018-08-16 11:30 | 204 | 204
2018-08-16 12:00 | 202 | 202
2018-08-16 12:30 | 200 | 200
2018-08-16 13:00 | 206 | 206
2018-08-16 13:30 | 209 | 209
2018-08-16 14:00 | 216 | 216
2018-08-16 14:30 | 220 | 220
2018-08-16 15:00 | 222 | 222
2018-08-16 15:30 | 234 | 234
2018-08-16 16:00 | 253 | 253
2018-08-16 16:30 | 274 | 274
2018-08-16 17:00 | 284 | 284
2018-08-16 17:30 | 308 | 308
2018-08-16 18:00 | 320 | 320
2018-08-16 18:30 | 312 | 312
2018-08-16 19:00 | 307 | 307
2018-08-16 19:30 | 317 | 317
2018-08-16 20:00 | 310 | 310
2018-08-16 20:30 | 298 | 298
2018-08-16 21:00 | 279 | 279
2018-08-16 21:30 | 265 | 264
2018-08-16 22:00 | 252 | 252
2018-08-16 22:30 | 245 | 245
2018-08-16 23:00 | 233 | 233
2018-08-16 23:30 | 220 | 220
2018-08-17 | 199 | 198
2018-08-17 00:30 | 185 | 185
2018-08-17 01:00 | 179 | 179
2018-08-17 01:30 | 172 | 171
2018-08-17 02:00 | 167 | 166
2018-08-17 02:30 | 165 | 165
2018-08-17 03:00 | 161 | 161
2018-08-17 03:30 | 162 | 162
2018-08-17 04:00 | 166 | 166
2018-08-17 04:30 | 170 | 170
2018-08-17 05:00 | 183 | 183
2018-08-17 05:30 | 205 | 205
2018-08-17 06:00 | 233 | 232
2018-08-17 06:30 | 261 | 261
2018-08-17 07:00 | 284 | 283
2018-08-17 07:30 | 282 | 281
2018-08-17 08:00 | 271 | 270
2018-08-17 08:30 | 256 | 256
2018-08-17 09:00 | 239 | 238
2018-08-17 09:30 | 224 | 224
2018-08-17 10:00 | 216 | 216
2018-08-17 10:30 | 210 | 210
2018-08-17 11:00 | 199 | 199
2018-08-17 11:30 | 190 | 189
2018-08-17 12:00 | 186 | 185
2018-08-17 12:30 | 185 | 184
2018-08-17 13:00 | 185 | 184
2018-08-17 13:30 | 188 | 187
2018-08-17 14:00 | 190 | 189
2018-08-17 14:30 | 193 | 192
2018-08-17 15:00 | 201 | 200
2018-08-17 15:30 | 221 | 221
2018-08-17 16:00 | 237 | 237
2018-08-17 16:30 | 251 | 250
2018-08-17 17:00 | 268 | 268
2018-08-17 17:30 | 288 | 287
2018-08-17 18:00 | 297 | 293
2018-08-17 18:30 | 299 | 295
2018-08-17 19:00 | 291 | 288
2018-08-17 19:30 | 290 | 288
2018-08-17 20:00 | 300 | 297
2018-08-17 20:30 | 290 | 288
2018-08-17 21:00 | 275 | 274
2018-08-17 21:30 | 265 | 264
2018-08-17 22:00 | 264 | 263
2018-08-17 22:30 | 257 | 255
2018-08-17 23:00 | 245 | 243
2018-08-17 23:30 | 228 | 224
2018-08-18 | 211 | 206
2018-08-18 00:30 | 195 | 189
2018-08-18 01:00 | 182 | 178
2018-08-18 01:30 | 171 | 167
2018-08-18 02:00 | 151 | 146
2018-08-18 02:30 | 149 | 143
2018-08-18 03:00 | 144 | 139
2018-08-18 03:30 | 161 | 156
2018-08-18 04:00 | 160 | 155
2018-08-18 04:30 | 162 | 158
2018-08-18 05:00 | 170 | 166
2018-08-18 05:30 | 181 | 178
2018-08-18 06:00 | 193 | 191
2018-08-18 06:30 | 201 | 199
2018-08-18 07:00 | 215 | 214
2018-08-18 07:30 | 231 | 231
2018-08-18 08:00 | 234 | 233
2018-08-18 08:30 | 228 | 228
2018-08-18 09:00 | 209 | 208
2018-08-18 09:30 | 170 | 170
2018-08-18 10:00 | 161 | 160
2018-08-18 10:30 | 177 | 177
2018-08-18 11:00 | 166 | 166
2018-08-18 11:30 | 150 | 149
2018-08-18 12:00 | 146 | 145
2018-08-18 12:30 | 146 | 145
2018-08-18 13:00 | 148 | 147
2018-08-18 13:30 | 168 | 167
2018-08-18 14:00 | 170 | 169
2018-08-18 14:30 | 173 | 172
2018-08-18 15:00 | 192 | 191
2018-08-18 15:30 | 201 | 201
2018-08-18 16:00 | 217 | 216
2018-08-18 16:30 | 231 | 231
2018-08-18 17:00 | 242 | 242
2018-08-18 17:30 | 257 | 256
2018-08-18 18:00 | 266 | 264
2018-08-18 18:30 | 266 | 263
2018-08-18 19:00 | 263 | 260
2018-08-18 19:30 | 262 | 261
2018-08-18 20:00 | 259 | 257
2018-08-18 20:30 | 252 | 250
2018-08-18 21:00 | 243 | 241
2018-08-18 21:30 | 235 | 233
2018-08-18 22:00 | 235 | 232
2018-08-18 22:30 | 237 | 235
2018-08-18 23:00 | 230 | 226
2018-08-18 23:30 | 208 | 203
2018-08-19 | 182 | 178
2018-08-19 00:30 | 171 | 167
2018-08-19 01:00 | 164 | 160
2018-08-19 01:30 | 148 | 143
2018-08-19 02:00 | 141 | 135
2018-08-19 02:30 | 149 | 144
2018-08-19 03:00 | 139 | 133
2018-08-19 03:30 | 139 | 133
2018-08-19 04:00 | 140 | 134
2018-08-19 04:30 | 142 | 136
2018-08-19 05:00 | 147 | 142
2018-08-19 05:30 | 163 | 160
2018-08-19 06:00 | 177 | 174
2018-08-19 06:30 | 188 | 185
2018-08-19 07:00 | 194 | 192
2018-08-19 07:30 | 209 | 207
2018-08-19 08:00 | 210 | 209
2018-08-19 08:30 | 208 | 207
2018-08-19 09:00 | 209 | 208
2018-08-19 09:30 | 202 | 201
2018-08-19 10:00 | 194 | 194
2018-08-19 10:30 | 188 | 187
2018-08-19 11:00 | 183 | 183
2018-08-19 11:30 | 176 | 175
2018-08-19 12:00 | 175 | 174
2018-08-19 12:30 | 173 | 172
2018-08-19 13:00 | 177 | 176
2018-08-19 13:30 | 173 | 172
2018-08-19 14:00 | 165 | 164
2018-08-19 14:30 | 190 | 190
2018-08-19 15:00 | 203 | 202
2018-08-19 15:30 | 213 | 213
2018-08-19 16:00 | 225 | 224
2018-08-19 16:30 | 249 | 249
2018-08-19 17:00 | 266 | 265
2018-08-19 17:30 | 281 | 281
2018-08-19 18:00 | 287 | 286
2018-08-19 18:30 | 287 | 286
2018-08-19 19:00 | 283 | 282
2018-08-19 19:30 | 283 | 281
2018-08-19 20:00 | 283 | 281
2018-08-19 20:30 | 274 | 272
2018-08-19 21:00 | 263 | 260
2018-08-19 21:30 | 250 | 246
2018-08-19 22:00 | 245 | 240
2018-08-19 22:30 | 243 | 239
2018-08-19 23:00 | 232 | 227
2018-08-19 23:30 | 214 | 209
2018-08-20 | 199 | 194
2018-08-20 00:30 | 190 | 184
2018-08-20 01:00 | 183 | 177
2018-08-20 01:30 | 177 | 170
2018-08-20 02:00 | 174 | 167
2018-08-20 02:30 | 169 | 164
2018-08-20 03:00 | 168 | 164
2018-08-20 03:30 | 170 | 166
2018-08-20 04:00 | 169 | 166
2018-08-20 04:30 | 175 | 172
2018-08-20 05:00 | 188 | 186
2018-08-20 05:30 | 209 | 208
2018-08-20 06:00 | 243 | 242
2018-08-20 06:30 | 268 | 268
2018-08-20 07:00 | 288 | 288
2018-08-20 07:30 | 284 | 284
2018-08-20 08:00 | 267 | 266
2018-08-20 08:30 | 248 | 247
2018-08-20 09:00 | 234 | 233
2018-08-20 09:30 | 222 | 221
2018-08-20 10:00 | 217 | 215
2018-08-20 10:30 | 205 | 205
2018-08-20 11:00 | 194 | 194
2018-08-20 11:30 | 189 | 188
2018-08-20 12:00 | 187 | 186
2018-08-20 12:30 | 187 | 186
2018-08-20 13:00 | 190 | 189
2018-08-20 13:30 | 194 | 193
2018-08-20 14:00 | 202 | 201
2018-08-20 14:30 | 211 | 210
2018-08-20 15:00 | 220 | 219
2018-08-20 15:30 | 236 | 235
2018-08-20 16:00 | 257 | 257
2018-08-20 16:30 | 277 | 276
2018-08-20 17:00 | 297 | 297
2018-08-20 17:30 | 339 | 339
2018-08-20 18:00 | 348 | 347
2018-08-20 18:30 | 341 | 340
2018-08-20 19:00 | 335 | 334
2018-08-20 19:30 | 331 | 330
2018-08-20 20:00 | 326 | 326
2018-08-20 20:30 | 315 | 314
2018-08-20 21:00 | 296 | 294
2018-08-20 21:30 | 278 | 276
2018-08-20 22:00 | 263 | 260
2018-08-20 22:30 | 254 | 252
2018-08-20 23:00 | 242 | 242
2018-08-20 23:30 | 230 | 230
2018-08-21 | 208 | 208
2018-08-21 00:30 | 188 | 188
2018-08-21 01:00 | 187 | 186
2018-08-21 01:30 | 181 | 180
2018-08-21 02:00 | 171 | 170
2018-08-21 02:30 | 167 | 166
2018-08-21 03:00 | 163 | 162
2018-08-21 03:30 | 164 | 164
2018-08-21 04:00 | 168 | 168
2018-08-21 04:30 | 170 | 170
2018-08-21 05:00 | 197 | 197
2018-08-21 05:30 | 229 | 229
2018-08-21 06:00 | 266 | 265
2018-08-21 06:30 | 299 | 299
2018-08-21 07:00 | 321 | 321
2018-08-21 07:30 | 336 | 336
2018-08-21 08:00 | 303 | 302
2018-08-21 08:30 | 276 | 276
2018-08-21 09:00 | 263 | 263
2018-08-21 09:30 | 251 | 250
2018-08-21 10:00 | 232 | 231
2018-08-21 10:30 | 219 | 219
2018-08-21 11:00 | 207 | 207
2018-08-21 11:30 | 202 | 202
2018-08-21 12:00 | 199 | 199
2018-08-21 12:30 | 199 | 199
2018-08-21 13:00 | 200 | 200
2018-08-21 13:30 | 204 | 204
2018-08-21 14:00 | 209 | 209
2018-08-21 14:30 | 215 | 215
2018-08-21 15:00 | 226 | 226
2018-08-21 15:30 | 238 | 238
2018-08-21 16:00 | 255 | 255
2018-08-21 16:30 | 272 | 272
2018-08-21 17:00 | 289 | 289
2018-08-21 17:30 | 318 | 317
2018-08-21 18:00 | 331 | 329
2018-08-21 18:30 | 333 | 331
2018-08-21 19:00 | 326 | 325
2018-08-21 19:30 | 327 | 326
2018-08-21 20:00 | 324 | 323
2018-08-21 20:30 | 308 | 308
2018-08-21 21:00 | 284 | 284
2018-08-21 21:30 | 270 | 270
2018-08-21 22:00 | 258 | 258
2018-08-21 22:30 | 257 | 256
2018-08-21 23:00 | 248 | 247
2018-08-21 23:30 | 236 | 234
2018-08-22 | 214 | 213
2018-08-22 00:30 | 196 | 196
2018-08-22 01:00 | 188 | 187
2018-08-22 01:30 | 176 | 175
2018-08-22 02:00 | 169 | 168
2018-08-22 02:30 | 166 | 165
2018-08-22 03:00 | 166 | 165
2018-08-22 03:30 | 167 | 166
2018-08-22 04:00 | 174 | 173
2018-08-22 04:30 | 183 | 183
2018-08-22 05:00 | 202 | 201
2018-08-22 05:30 | 225 | 225
2018-08-22 06:00 | 249 | 249
2018-08-22 06:30 | 263 | 263
2018-08-22 07:00 | 292 | 292
2018-08-22 07:30 | 295 | 295
2018-08-22 08:00 | 276 | 275
2018-08-22 08:30 | 250 | 249
2018-08-22 09:00 | 241 | 239
2018-08-22 09:30 | 231 | 229
2018-08-22 10:00 | 219 | 218
2018-08-22 10:30 | 212 | 211
2018-08-22 11:00 | 202 | 202
2018-08-22 11:30 | 194 | 194
2018-08-22 12:00 | 196 | 195
2018-08-22 12:30 | 199 | 199
2018-08-22 13:00 | 204 | 203
2018-08-22 13:30 | 207 | 206
2018-08-22 14:00 | 209 | 209
2018-08-22 14:30 | 212 | 212
2018-08-22 15:00 | 219 | 219
2018-08-22 15:30 | 225 | 225
2018-08-22 16:00 | 237 | 237
2018-08-22 16:30 | 253 | 253
2018-08-22 17:00 | 268 | 268
2018-08-22 17:30 | 301 | 301
2018-08-22 18:00 | 321 | 319
2018-08-22 18:30 | 323 | 321
2018-08-22 19:00 | 312 | 310
2018-08-22 19:30 | 308 | 307
2018-08-22 20:00 | 302 | 301
2018-08-22 20:30 | 286 | 286
2018-08-22 21:00 | 270 | 270
2018-08-22 21:30 | 256 | 256
2018-08-22 22:00 | 243 | 242
2018-08-22 22:30 | 235 | 234
2018-08-22 23:00 | 228 | 227
2018-08-22 23:30 | 217 | 216
2018-08-23 | 193 | 193
2018-08-23 00:30 | 182 | 182
2018-08-23 01:00 | 173 | 172
2018-08-23 01:30 | 167 | 166
2018-08-23 02:00 | 165 | 164
2018-08-23 02:30 | 166 | 165
2018-08-23 03:00 | 165 | 164
2018-08-23 03:30 | 155 | 155
2018-08-23 04:00 | 163 | 163
2018-08-23 04:30 | 167 | 167
2018-08-23 05:00 | 184 | 183
2018-08-23 05:30 | 199 | 199
2018-08-23 06:00 | 244 | 244
2018-08-23 06:30 | 284 | 284
2018-08-23 07:00 | 279 | 279
2018-08-23 07:30 | 283 | 283
2018-08-23 08:00 | 272 | 271
2018-08-23 08:30 | 252 | 250
2018-08-23 09:00 | 239 | 238
2018-08-23 09:30 | 229 | 228
2018-08-23 10:00 | 221 | 221
2018-08-23 10:30 | 213 | 213
2018-08-23 11:00 | 206 | 206
2018-08-23 11:30 | 203 | 203
2018-08-23 12:00 | 199 | 199
2018-08-23 12:30 | 198 | 198
2018-08-23 13:00 | 197 | 197
2018-08-23 13:30 | 204 | 204
2018-08-23 14:00 | 210 | 210
2018-08-23 14:30 | 212 | 212
2018-08-23 15:00 | 217 | 217
2018-08-23 15:30 | 228 | 228
2018-08-23 16:00 | 245 | 245
2018-08-23 16:30 | 261 | 261
2018-08-23 17:00 | 284 | 284
2018-08-23 17:30 | 308 | 308
2018-08-23 18:00 | 320 | 319
2018-08-23 18:30 | 324 | 324
2018-08-23 19:00 | 318 | 318
2018-08-23 19:30 | 315 | 314
2018-08-23 20:00 | 306 | 306
2018-08-23 20:30 | 293 | 292
2018-08-23 21:00 | 271 | 271
2018-08-23 21:30 | 253 | 253
2018-08-23 22:00 | 247 | 246
2018-08-23 22:30 | 242 | 241
2018-08-23 23:00 | 229 | 228
2018-08-23 23:30 | 216 | 215
2018-08-24 | 199 | 198
2018-08-24 00:30 | 186 | 186
2018-08-24 01:00 | 179 | 179
2018-08-24 01:30 | 172 | 171
2018-08-24 02:00 | 165 | 164
2018-08-24 02:30 | 165 | 164
2018-08-24 03:00 | 167 | 166
2018-08-24 03:30 | 166 | 164
2018-08-24 04:00 | 166 | 165
2018-08-24 04:30 | 174 | 174
2018-08-24 05:00 | 190 | 190
2018-08-24 05:30 | 209 | 209
2018-08-24 06:00 | 237 | 237
2018-08-24 06:30 | 261 | 261
2018-08-24 07:00 | 276 | 275
2018-08-24 07:30 | 270 | 269
2018-08-24 08:00 | 261 | 260
2018-08-24 08:30 | 245 | 245
2018-08-24 09:00 | 234 | 234
2018-08-24 09:30 | 228 | 228
2018-08-24 10:00 | 222 | 221
2018-08-24 10:30 | 212 | 212
2018-08-24 11:00 | 204 | 204
2018-08-24 11:30 | 200 | 200
2018-08-24 12:00 | 198 | 198
2018-08-24 12:30 | 224 | 224
2018-08-24 13:00 | 244 | 244
2018-08-24 13:30 | 241 | 241
2018-08-24 14:00 | 231 | 231
2018-08-24 14:30 | 226 | 225
2018-08-24 15:00 | 227 | 227
2018-08-24 15:30 | 240 | 240
2018-08-24 16:00 | 255 | 255
2018-08-24 16:30 | 274 | 273
2018-08-24 17:00 | 285 | 285
2018-08-24 17:30 | 303 | 303
2018-08-24 18:00 | 311 | 310
2018-08-24 18:30 | 311 | 311
2018-08-24 19:00 | 300 | 300
2018-08-24 19:30 | 292 | 291
2018-08-24 20:00 | 286 | 285
2018-08-24 20:30 | 275 | 273
2018-08-24 21:00 | 264 | 262
2018-08-24 21:30 | 248 | 248
2018-08-24 22:00 | 245 | 244
2018-08-24 22:30 | 241 | 241
2018-08-24 23:00 | 232 | 231
2018-08-24 23:30 | 219 | 218
2018-08-25 | 198 | 198
2018-08-25 00:30 | 187 | 187
2018-08-25 01:00 | 178 | 178
2018-08-25 01:30 | 174 | 173
2018-08-25 02:00 | 175 | 175
2018-08-25 02:30 | 176 | 175
2018-08-25 03:00 | 179 | 179
2018-08-25 03:30 | 180 | 179
2018-08-25 04:00 | 176 | 176
2018-08-25 04:30 | 180 | 179
2018-08-25 05:00 | 184 | 183
2018-08-25 05:30 | 189 | 188
2018-08-25 06:00 | 200 | 200
2018-08-25 06:30 | 213 | 213
2018-08-25 07:00 | 229 | 229
2018-08-25 07:30 | 240 | 240
2018-08-25 08:00 | 246 | 246
2018-08-25 08:30 | 248 | 248
2018-08-25 09:00 | 245 | 245
2018-08-25 09:30 | 236 | 236
2018-08-25 10:00 | 223 | 222
2018-08-25 10:30 | 212 | 212
2018-08-25 11:00 | 207 | 207
2018-08-25 11:30 | 182 | 182
2018-08-25 12:00 | 203 | 203
2018-08-25 12:30 | 202 | 202
2018-08-25 13:00 | 208 | 208
2018-08-25 13:30 | 208 | 207
2018-08-25 14:00 | 201 | 201
2018-08-25 14:30 | 191 | 190
2018-08-25 15:00 | 213 | 213
2018-08-25 15:30 | 242 | 242
2018-08-25 16:00 | 264 | 264
2018-08-25 16:30 | 276 | 276
2018-08-25 17:00 | 275 | 275
2018-08-25 17:30 | 302 | 302
2018-08-25 18:00 | 310 | 310
2018-08-25 18:30 | 314 | 314
2018-08-25 19:00 | 303 | 302
2018-08-25 19:30 | 289 | 289
2018-08-25 20:00 | 274 | 274
2018-08-25 20:30 | 260 | 260
2018-08-25 21:00 | 254 | 254
2018-08-25 21:30 | 260 | 260
2018-08-25 22:00 | 257 | 257
2018-08-25 22:30 | 255 | 255
2018-08-25 23:00 | 259 | 259
2018-08-25 23:30 | 243 | 243
2018-08-26 | 227 | 227
2018-08-26 00:30 | 216 | 216
2018-08-26 01:00 | 207 | 207
2018-08-26 01:30 | 194 | 193
2018-08-26 02:00 | 193 | 193
2018-08-26 02:30 | 189 | 189
2018-08-26 03:00 | 189 | 188
2018-08-26 03:30 | 188 | 188
2018-08-26 04:00 | 180 | 179
2018-08-26 04:30 | 172 | 171
2018-08-26 05:00 | 183 | 183
2018-08-26 05:30 | 193 | 193
2018-08-26 06:00 | 203 | 203
2018-08-26 06:30 | 215 | 215
2018-08-26 07:00 | 236 | 235
2018-08-26 07:30 | 253 | 253
2018-08-26 08:00 | 268 | 268
2018-08-26 08:30 | 282 | 282
2018-08-26 09:00 | 286 | 286
2018-08-26 09:30 | 291 | 291
2018-08-26 10:00 | 291 | 291
2018-08-26 10:30 | 278 | 278
2018-08-26 11:00 | 271 | 271
2018-08-26 11:30 | 272 | 272
2018-08-26 12:00 | 242 | 242
2018-08-26 12:30 | 246 | 246
2018-08-26 13:00 | 246 | 245
2018-08-26 13:30 | 258 | 258
2018-08-26 14:00 | 255 | 254
2018-08-26 14:30 | 262 | 261
2018-08-26 15:00 | 261 | 261
2018-08-26 15:30 | 278 | 277
2018-08-26 16:00 | 291 | 291
2018-08-26 16:30 | 299 | 299
2018-08-26 17:00 | 318 | 317
2018-08-26 17:30 | 318 | 317
2018-08-26 18:00 | 329 | 329
2018-08-26 18:30 | 319 | 318
2018-08-26 19:00 | 307 | 306
2018-08-26 19:30 | 301 | 299
2018-08-26 20:00 | 295 | 293
2018-08-26 20:30 | 283 | 281
2018-08-26 21:00 | 266 | 265
2018-08-26 21:30 | 253 | 252
2018-08-26 22:00 | 246 | 246
2018-08-26 22:30 | 242 | 241
2018-08-26 23:00 | 231 | 229
2018-08-26 23:30 | 219 | 217
2018-08-27 | 198 | 197
2018-08-27 00:30 | 192 | 192
2018-08-27 01:00 | 185 | 184
2018-08-27 01:30 | 172 | 172
2018-08-27 02:00 | 170 | 170
2018-08-27 02:30 | 165 | 165
2018-08-27 03:00 | 164 | 163
2018-08-27 03:30 | 165 | 165
2018-08-27 04:00 | 171 | 171
2018-08-27 04:30 | 180 | 179
2018-08-27 05:00 | 195 | 195
2018-08-27 05:30 | 217 | 215
2018-08-27 06:00 | 244 | 243
2018-08-27 06:30 | 265 | 265
2018-08-27 07:00 | 278 | 278
2018-08-27 07:30 | 272 | 272
2018-08-27 08:00 | 261 | 261
2018-08-27 08:30 | 249 | 249
2018-08-27 09:00 | 238 | 238
2018-08-27 09:30 | 232 | 231
2018-08-27 10:00 | 220 | 220
2018-08-27 10:30 | 219 | 219
2018-08-27 11:00 | 215 | 215
2018-08-27 11:30 | 215 | 215
2018-08-27 12:00 | 215 | 215
2018-08-27 12:30 | 221 | 221
2018-08-27 13:00 | 227 | 227
2018-08-27 13:30 | 233 | 233
2018-08-27 14:00 | 230 | 230
2018-08-27 14:30 | 231 | 231
2018-08-27 15:00 | 235 | 235
2018-08-27 15:30 | 238 | 238
2018-08-27 16:00 | 257 | 257
2018-08-27 16:30 | 275 | 274
2018-08-27 17:00 | 297 | 296
2018-08-27 17:30 | 324 | 324
2018-08-27 18:00 | 331 | 331
2018-08-27 18:30 | 330 | 329
2018-08-27 19:00 | 328 | 328
2018-08-27 19:30 | 315 | 315
2018-08-27 20:00 | 312 | 311
2018-08-27 20:30 | 293 | 293
2018-08-27 21:00 | 272 | 272
2018-08-27 21:30 | 257 | 257
2018-08-27 22:00 | 246 | 246
2018-08-27 22:30 | 244 | 243
2018-08-27 23:00 | 240 | 239
2018-08-27 23:30 | 227 | 226
2018-08-28 | 209 | 207
2018-08-28 00:30 | 198 | 195
2018-08-28 01:00 | 188 | 186
2018-08-28 01:30 | 178 | 176
2018-08-28 02:00 | 175 | 174
2018-08-28 02:30 | 166 | 165
2018-08-28 03:00 | 163 | 161
2018-08-28 03:30 | 161 | 160
2018-08-28 04:00 | 169 | 167
2018-08-28 04:30 | 172 | 171
2018-08-28 05:00 | 188 | 187
2018-08-28 05:30 | 207 | 207
2018-08-28 06:00 | 227 | 227
2018-08-28 06:30 | 262 | 262
2018-08-28 07:00 | 278 | 278
2018-08-28 07:30 | 283 | 283
2018-08-28 08:00 | 270 | 270
2018-08-28 08:30 | 252 | 252
2018-08-28 09:00 | 240 | 240
2018-08-28 09:30 | 231 | 231
2018-08-28 10:00 | 221 | 221
2018-08-28 10:30 | 215 | 215
2018-08-28 11:00 | 210 | 210
2018-08-28 11:30 | 208 | 208
2018-08-28 12:00 | 206 | 206
2018-08-28 12:30 | 208 | 208
2018-08-28 13:00 | 207 | 207
2018-08-28 13:30 | 210 | 210
2018-08-28 14:00 | 213 | 213
2018-08-28 14:30 | 218 | 218
2018-08-28 15:00 | 223 | 223
2018-08-28 15:30 | 236 | 236
2018-08-28 16:00 | 252 | 252
2018-08-28 16:30 | 272 | 272
2018-08-28 17:00 | 288 | 287
2018-08-28 17:30 | 309 | 309
2018-08-28 18:00 | 324 | 324
2018-08-28 18:30 | 323 | 323
2018-08-28 19:00 | 330 | 330
2018-08-28 19:30 | 313 | 312
2018-08-28 20:00 | 311 | 311
2018-08-28 20:30 | 290 | 290
2018-08-28 21:00 | 276 | 276
2018-08-28 21:30 | 261 | 261
2018-08-28 22:00 | 248 | 247
2018-08-28 22:30 | 244 | 244
2018-08-28 23:00 | 237 | 236
2018-08-28 23:30 | 226 | 224
2018-08-29 | 200 | 198
2018-08-29 00:30 | 188 | 185
2018-08-29 01:00 | 183 | 180
2018-08-29 01:30 | 177 | 174
2018-08-29 02:00 | 170 | 168
2018-08-29 02:30 | 172 | 171
2018-08-29 03:00 | 167 | 166
2018-08-29 03:30 | 163 | 162
2018-08-29 04:00 | 142 | 141
2018-08-29 04:30 | 160 | 159
2018-08-29 05:00 | 174 | 173
2018-08-29 05:30 | 200 | 200
2018-08-29 06:00 | 236 | 236
2018-08-29 06:30 | 259 | 259
2018-08-29 07:00 | 280 | 280
2018-08-29 07:30 | 275 | 275
2018-08-29 08:00 | 277 | 277
2018-08-29 08:30 | 257 | 257
2018-08-29 09:00 | 230 | 229
2018-08-29 09:30 | 209 | 208
2018-08-29 10:00 | 210 | 209
2018-08-29 10:30 | 204 | 203
2018-08-29 11:00 | 192 | 192
2018-08-29 11:30 | 186 | 186
2018-08-29 12:00 | 170 | 169
2018-08-29 12:30 | 149 | 148
2018-08-29 13:00 | 165 | 164
2018-08-29 13:30 | 177 | 176
2018-08-29 14:00 | 191 | 191
2018-08-29 14:30 | 196 | 195
2018-08-29 15:00 | 194 | 193
2018-08-29 15:30 | 210 | 209
2018-08-29 16:00 | 236 | 235
2018-08-29 16:30 | 265 | 264
2018-08-29 17:00 | 268 | 268
2018-08-29 17:30 | 298 | 298
2018-08-29 18:00 | 333 | 330
2018-08-29 18:30 | 340 | 337
2018-08-29 19:00 | 316 | 314
2018-08-29 19:30 | 293 | 292
2018-08-29 20:00 | 293 | 292
2018-08-29 20:30 | 278 | 278
2018-08-29 21:00 | 264 | 263
2018-08-29 21:30 | 250 | 248
2018-08-29 22:00 | 243 | 241
2018-08-29 22:30 | 240 | 240
2018-08-29 23:00 | 221 | 221
2018-08-29 23:30 | 212 | 212
2018-08-30 | 206 | 205
2018-08-30 00:30 | 191 | 190
2018-08-30 01:00 | 180 | 179
2018-08-30 01:30 | 168 | 166
2018-08-30 02:00 | 170 | 169
2018-08-30 02:30 | 149 | 147
2018-08-30 03:00 | 140 | 138
2018-08-30 03:30 | 138 | 136
2018-08-30 04:00 | 155 | 153
2018-08-30 04:30 | 151 | 150
2018-08-30 05:00 | 181 | 181
2018-08-30 05:30 | 208 | 208
2018-08-30 06:00 | 239 | 239
2018-08-30 06:30 | 268 | 268
2018-08-30 07:00 | 280 | 280
2018-08-30 07:30 | 278 | 278
2018-08-30 08:00 | 266 | 266
2018-08-30 08:30 | 252 | 252
2018-08-30 09:00 | 242 | 242
2018-08-30 09:30 | 226 | 226
2018-08-30 10:00 | 220 | 220
2018-08-30 10:30 | 212 | 212
2018-08-30 11:00 | 209 | 209
2018-08-30 11:30 | 206 | 206
2018-08-30 12:00 | 204 | 204
2018-08-30 12:30 | 205 | 205
2018-08-30 13:00 | 209 | 209
2018-08-30 13:30 | 210 | 210
2018-08-30 14:00 | 217 | 217
2018-08-30 14:30 | 223 | 223
2018-08-30 15:00 | 230 | 230
2018-08-30 15:30 | 243 | 243
2018-08-30 16:00 | 257 | 257
2018-08-30 16:30 | 264 | 264
2018-08-30 17:00 | 272 | 272
2018-08-30 17:30 | 293 | 293
2018-08-30 18:00 | 307 | 306
2018-08-30 18:30 | 306 | 305
2018-08-30 19:00 | 298 | 298
2018-08-30 19:30 | 302 | 302
2018-08-30 20:00 | 298 | 298
2018-08-30 20:30 | 289 | 289
2018-08-30 21:00 | 270 | 270
2018-08-30 21:30 | 250 | 250
2018-08-30 22:00 | 244 | 243
2018-08-30 22:30 | 241 | 240
2018-08-30 23:00 | 228 | 227
2018-08-30 23:30 | 218 | 216
2018-08-31 | 192 | 191
2018-08-31 00:30 | 183 | 182
2018-08-31 01:00 | 174 | 173
2018-08-31 01:30 | 172 | 170
2018-08-31 02:00 | 163 | 162
2018-08-31 02:30 | 160 | 158
2018-08-31 03:00 | 161 | 160
2018-08-31 03:30 | 162 | 160
2018-08-31 04:00 | 161 | 159
2018-08-31 04:30 | 162 | 160
2018-08-31 05:00 | 162 | 161
2018-08-31 05:30 | 175 | 174
2018-08-31 06:00 | 198 | 197
2018-08-31 06:30 | 218 | 217
2018-08-31 07:00 | 240 | 240
2018-08-31 07:30 | 248 | 248
2018-08-31 08:00 | 243 | 243
2018-08-31 08:30 | 236 | 235
2018-08-31 09:00 | 231 | 231
2018-08-31 09:30 | 223 | 223
2018-08-31 10:00 | 215 | 215
2018-08-31 10:30 | 208 | 208
2018-08-31 11:00 | 205 | 205
2018-08-31 11:30 | 199 | 199
2018-08-31 12:00 | 194 | 194
2018-08-31 12:30 | 194 | 194
2018-08-31 13:00 | 195 | 194
2018-08-31 13:30 | 200 | 200
2018-08-31 14:00 | 207 | 207
2018-08-31 14:30 | 213 | 213
2018-08-31 15:00 | 217 | 217
2018-08-31 15:30 | 222 | 222
2018-08-31 16:00 | 241 | 241
2018-08-31 16:30 | 255 | 255
2018-08-31 17:00 | 264 | 264
2018-08-31 17:30 | 273 | 273
2018-08-31 18:00 | 285 | 283
2018-08-31 18:30 | 285 | 283
2018-08-31 19:00 | 281 | 279
2018-08-31 19:30 | 281 | 279
2018-08-31 20:00 | 279 | 277
2018-08-31 20:30 | 280 | 278
2018-08-31 21:00 | 261 | 260
2018-08-31 21:30 | 246 | 246
2018-08-31 22:00 | 245 | 245
2018-08-31 22:30 | 257 | 256
2018-08-31 23:00 | 246 | 245
2018-08-31 23:30 | 230 | 229
2018-09-01 | 199 | 197
2018-09-01 00:30 | 186 | 183
2018-09-01 01:00 | 176 | 173
2018-09-01 01:30 | 172 | 171
2018-09-01 02:00 | 163 | 162
2018-09-01 02:30 | 155 | 154
2018-09-01 03:00 | 151 | 150
2018-09-01 03:30 | 148 | 147
2018-09-01 04:00 | 152 | 151
2018-09-01 04:30 | 153 | 152
2018-09-01 05:00 | 162 | 161
2018-09-01 05:30 | 171 | 170
2018-09-01 06:00 | 185 | 184
2018-09-01 06:30 | 193 | 192
2018-09-01 07:00 | 204 | 204
2018-09-01 07:30 | 214 | 214
2018-09-01 08:00 | 226 | 225
2018-09-01 08:30 | 224 | 224
2018-09-01 09:00 | 226 | 226
2018-09-01 09:30 | 216 | 216
2018-09-01 10:00 | 204 | 204
2018-09-01 10:30 | 196 | 196
2018-09-01 11:00 | 181 | 181
2018-09-01 11:30 | 174 | 174
2018-09-01 12:00 | 169 | 169
2018-09-01 12:30 | 173 | 172
2018-09-01 13:00 | 144 | 144
2018-09-01 13:30 | 161 | 161
2018-09-01 14:00 | 160 | 160
2018-09-01 14:30 | 192 | 192
2018-09-01 15:00 | 197 | 197
2018-09-01 15:30 | 208 | 208
2018-09-01 16:00 | 224 | 224
2018-09-01 16:30 | 234 | 234
2018-09-01 17:00 | 236 | 236
2018-09-01 17:30 | 250 | 250
2018-09-01 18:00 | 262 | 259
2018-09-01 18:30 | 261 | 258
2018-09-01 19:00 | 251 | 249
2018-09-01 19:30 | 246 | 246
2018-09-01 20:00 | 245 | 245
2018-09-01 20:30 | 241 | 241
2018-09-01 21:00 | 235 | 235
2018-09-01 21:30 | 230 | 229
2018-09-01 22:00 | 222 | 221
2018-09-01 22:30 | 222 | 221
2018-09-01 23:00 | 215 | 213
2018-09-01 23:30 | 204 | 202
2018-09-02 | 184 | 181
2018-09-02 00:30 | 171 | 168
2018-09-02 01:00 | 165 | 161
2018-09-02 01:30 | 159 | 156
2018-09-02 02:00 | 151 | 150
2018-09-02 02:30 | 152 | 151
2018-09-02 03:00 | 153 | 152
2018-09-02 03:30 | 156 | 154
2018-09-02 04:00 | 158 | 156
2018-09-02 04:30 | 155 | 154
2018-09-02 05:00 | 162 | 161
2018-09-02 05:30 | 168 | 167
2018-09-02 06:00 | 169 | 168
2018-09-02 06:30 | 176 | 175
2018-09-02 07:00 | 186 | 186
2018-09-02 07:30 | 196 | 195
2018-09-02 08:00 | 204 | 204
2018-09-02 08:30 | 209 | 209
2018-09-02 09:00 | 210 | 210
2018-09-02 09:30 | 205 | 205
2018-09-02 10:00 | 198 | 198
2018-09-02 10:30 | 189 | 189
2018-09-02 11:00 | 183 | 183
2018-09-02 11:30 | 179 | 179
2018-09-02 12:00 | 171 | 170
2018-09-02 12:30 | 168 | 168
2018-09-02 13:00 | 170 | 169
2018-09-02 13:30 | 171 | 171
2018-09-02 14:00 | 176 | 175
2018-09-02 14:30 | 188 | 187
2018-09-02 15:00 | 202 | 201
2018-09-02 15:30 | 212 | 211
2018-09-02 16:00 | 227 | 227
2018-09-02 16:30 | 234 | 234
2018-09-02 17:00 | 240 | 240
2018-09-02 17:30 | 256 | 256
2018-09-02 18:00 | 274 | 273
2018-09-02 18:30 | 280 | 278
2018-09-02 19:00 | 263 | 262
2018-09-02 19:30 | 257 | 257
2018-09-02 20:00 | 258 | 257
2018-09-02 20:30 | 248 | 247
2018-09-02 21:00 | 237 | 236
2018-09-02 21:30 | 226 | 225
2018-09-02 22:00 | 217 | 216
2018-09-02 22:30 | 217 | 216
2018-09-02 23:00 | 208 | 206
2018-09-02 23:30 | 199 | 196
2018-09-03 | 181 | 177
2018-09-03 00:30 | 173 | 169
2018-09-03 01:00 | 166 | 162
2018-09-03 01:30 | 156 | 154
2018-09-03 02:00 | 151 | 149
2018-09-03 02:30 | 152 | 150
2018-09-03 03:00 | 154 | 153
2018-09-03 03:30 | 155 | 153
2018-09-03 04:00 | 155 | 153
2018-09-03 04:30 | 159 | 158
2018-09-03 05:00 | 169 | 168
2018-09-03 05:30 | 183 | 183
2018-09-03 06:00 | 207 | 207
2018-09-03 06:30 | 241 | 240
2018-09-03 07:00 | 264 | 264
2018-09-03 07:30 | 276 | 276
2018-09-03 08:00 | 286 | 286
2018-09-03 08:30 | 270 | 270
2018-09-03 09:00 | 258 | 258
2018-09-03 09:30 | 247 | 247
2018-09-03 10:00 | 231 | 230
2018-09-03 10:30 | 232 | 232
2018-09-03 11:00 | 236 | 235
2018-09-03 11:30 | 228 | 227
2018-09-03 12:00 | 224 | 223
2018-09-03 12:30 | 226 | 225
2018-09-03 13:00 | 231 | 230
2018-09-03 13:30 | 235 | 235
2018-09-03 14:00 | 235 | 235
2018-09-03 14:30 | 235 | 234
2018-09-03 15:00 | 247 | 247
2018-09-03 15:30 | 251 | 250
2018-09-03 16:00 | 255 | 255
2018-09-03 16:30 | 281 | 280
2018-09-03 17:00 | 296 | 293
2018-09-03 17:30 | 318 | 316
2018-09-03 18:00 | 325 | 322
2018-09-03 18:30 | 322 | 320
2018-09-03 19:00 | 315 | 312
2018-09-03 19:30 | 281 | 281
2018-09-03 20:00 | 282 | 282
2018-09-03 20:30 | 282 | 282
2018-09-03 21:00 | 265 | 264
2018-09-03 21:30 | 249 | 248
2018-09-03 22:00 | 240 | 238
2018-09-03 22:30 | 235 | 233
2018-09-03 23:00 | 222 | 219
2018-09-03 23:30 | 210 | 208
2018-09-04 | 191 | 188
2018-09-04 00:30 | 183 | 179
2018-09-04 01:00 | 177 | 173
2018-09-04 01:30 | 168 | 164
2018-09-04 02:00 | 161 | 157
2018-09-04 02:30 | 160 | 156
2018-09-04 03:00 | 159 | 155
2018-09-04 03:30 | 157 | 153
2018-09-04 04:00 | 158 | 154
2018-09-04 04:30 | 160 | 157
2018-09-04 05:00 | 176 | 173
2018-09-04 05:30 | 193 | 191
2018-09-04 06:00 | 224 | 223
2018-09-04 06:30 | 255 | 255
2018-09-04 07:00 | 273 | 273
2018-09-04 07:30 | 280 | 279
2018-09-04 08:00 | 282 | 280
2018-09-04 08:30 | 270 | 268
2018-09-04 09:00 | 259 | 257
2018-09-04 09:30 | 250 | 249
2018-09-04 10:00 | 234 | 234
2018-09-04 10:30 | 231 | 230
2018-09-04 11:00 | 221 | 220
2018-09-04 11:30 | 218 | 218
2018-09-04 12:00 | 231 | 231
2018-09-04 12:30 | 217 | 217
2018-09-04 13:00 | 207 | 207
2018-09-04 13:30 | 215 | 215
2018-09-04 14:00 | 225 | 225
2018-09-04 14:30 | 220 | 220
2018-09-04 15:00 | 222 | 222
2018-09-04 15:30 | 242 | 242
2018-09-04 16:00 | 270 | 270
2018-09-04 16:30 | 287 | 286
2018-09-04 17:00 | 303 | 301
2018-09-04 17:30 | 325 | 324
2018-09-04 18:00 | 332 | 331
2018-09-04 18:30 | 330 | 330
2018-09-04 19:00 | 319 | 318
2018-09-04 19:30 | 309 | 308
2018-09-04 20:00 | 301 | 299
2018-09-04 20:30 | 298 | 295
2018-09-04 21:00 | 282 | 279
2018-09-04 21:30 | 259 | 256
2018-09-04 22:00 | 242 | 242
2018-09-04 22:30 | 232 | 232
2018-09-04 23:00 | 224 | 222
2018-09-04 23:30 | 212 | 210
2018-09-05 | 195 | 192
2018-09-05 00:30 | 187 | 184
2018-09-05 01:00 | 180 | 177
2018-09-05 01:30 | 172 | 168
2018-09-05 02:00 | 164 | 161
2018-09-05 02:30 | 157 | 156
2018-09-05 03:00 | 152 | 150
2018-09-05 03:30 | 150 | 149
2018-09-05 04:00 | 155 | 154
2018-09-05 04:30 | 157 | 156
2018-09-05 05:00 | 174 | 173
2018-09-05 05:30 | 194 | 194
2018-09-05 06:00 | 226 | 226
2018-09-05 06:30 | 260 | 260
2018-09-05 07:00 | 279 | 278
2018-09-05 07:30 | 281 | 279
2018-09-05 08:00 | 273 | 271
2018-09-05 08:30 | 257 | 255
2018-09-05 09:00 | 239 | 237
2018-09-05 09:30 | 225 | 223
2018-09-05 10:00 | 213 | 213
2018-09-05 10:30 | 205 | 205
2018-09-05 11:00 | 198 | 198
2018-09-05 11:30 | 201 | 201
2018-09-05 12:00 | 197 | 197
2018-09-05 12:30 | 207 | 207
2018-09-05 13:00 | 214 | 214
2018-09-05 13:30 | 218 | 218
2018-09-05 14:00 | 223 | 223
2018-09-05 14:30 | 223 | 223
2018-09-05 15:00 | 226 | 226
2018-09-05 15:30 | 232 | 232
2018-09-05 16:00 | 242 | 242
2018-09-05 16:30 | 261 | 261
2018-09-05 17:00 | 284 | 283
2018-09-05 17:30 | 301 | 301
2018-09-05 18:00 | 315 | 315
2018-09-05 18:30 | 311 | 311
2018-09-05 19:00 | 301 | 301
2018-09-05 19:30 | 294 | 294
2018-09-05 20:00 | 286 | 285
2018-09-05 20:30 | 272 | 271
2018-09-05 21:00 | 262 | 261
2018-09-05 21:30 | 246 | 246
2018-09-05 22:00 | 225 | 225
2018-09-05 22:30 | 210 | 210
2018-09-05 23:00 | 213 | 213
2018-09-05 23:30 | 204 | 202
2018-09-06 | 187 | 184
2018-09-06 00:30 | 178 | 174
2018-09-06 01:00 | 171 | 167
2018-09-06 01:30 | 160 | 156
2018-09-06 02:00 | 159 | 154
2018-09-06 02:30 | 164 | 160
2018-09-06 03:00 | 164 | 160
2018-09-06 03:30 | 168 | 164
2018-09-06 04:00 | 166 | 162
2018-09-06 04:30 | 169 | 166
2018-09-06 05:00 | 174 | 171
2018-09-06 05:30 | 195 | 193
2018-09-06 06:00 | 222 | 221
2018-09-06 06:30 | 261 | 260
2018-09-06 07:00 | 274 | 273
2018-09-06 07:30 | 275 | 275
2018-09-06 08:00 | 265 | 265
2018-09-06 08:30 | 243 | 243
2018-09-06 09:00 | 237 | 237
2018-09-06 09:30 | 223 | 223
2018-09-06 10:00 | 207 | 206
2018-09-06 10:30 | 209 | 208
2018-09-06 11:00 | 200 | 198
2018-09-06 11:30 | 205 | 203
2018-09-06 12:00 | 202 | 201
2018-09-06 12:30 | 200 | 198
2018-09-06 13:00 | 189 | 188
2018-09-06 13:30 | 214 | 213
2018-09-06 14:00 | 207 | 205
2018-09-06 14:30 | 221 | 219
2018-09-06 15:00 | 232 | 231
2018-09-06 15:30 | 244 | 243
2018-09-06 16:00 | 251 | 250
2018-09-06 16:30 | 260 | 258
2018-09-06 17:00 | 278 | 277
2018-09-06 17:30 | 291 | 291
2018-09-06 18:00 | 297 | 297
2018-09-06 18:30 | 298 | 297
2018-09-06 19:00 | 295 | 294
2018-09-06 19:30 | 284 | 283
2018-09-06 20:00 | 286 | 285
2018-09-06 20:30 | 275 | 274
2018-09-06 21:00 | 255 | 253
2018-09-06 21:30 | 242 | 240
2018-09-06 22:00 | 235 | 232
2018-09-06 22:30 | 231 | 227
2018-09-06 23:00 | 216 | 211
2018-09-06 23:30 | 198 | 194
2018-09-07 | 188 | 184
2018-09-07 00:30 | 181 | 177
2018-09-07 01:00 | 177 | 173
2018-09-07 01:30 | 154 | 148
2018-09-07 02:00 | 159 | 153
2018-09-07 02:30 | 134 | 130
2018-09-07 03:00 | 134 | 131
2018-09-07 03:30 | 143 | 141
2018-09-07 04:00 | 160 | 158
2018-09-07 04:30 | 163 | 161
2018-09-07 05:00 | 167 | 166
2018-09-07 05:30 | 186 | 185
2018-09-07 06:00 | 212 | 212
2018-09-07 06:30 | 234 | 233
2018-09-07 07:00 | 246 | 246
2018-09-07 07:30 | 253 | 252
2018-09-07 08:00 | 266 | 263
2018-09-07 08:30 | 253 | 250
2018-09-07 09:00 | 248 | 245
2018-09-07 09:30 | 231 | 228
2018-09-07 10:00 | 225 | 223
2018-09-07 10:30 | 225 | 223
2018-09-07 11:00 | 230 | 228
2018-09-07 11:30 | 230 | 228
2018-09-07 12:00 | 228 | 226
2018-09-07 12:30 | 229 | 227
2018-09-07 13:00 | 223 | 221
2018-09-07 13:30 | 217 | 215
2018-09-07 14:00 | 219 | 217
2018-09-07 14:30 | 222 | 220
2018-09-07 15:00 | 232 | 229
2018-09-07 15:30 | 243 | 240
2018-09-07 16:00 | 251 | 249
2018-09-07 16:30 | 265 | 263
2018-09-07 17:00 | 276 | 274
2018-09-07 17:30 | 287 | 286
2018-09-07 18:00 | 291 | 290
2018-09-07 18:30 | 293 | 291
2018-09-07 19:00 | 288 | 286
2018-09-07 19:30 | 285 | 282
2018-09-07 20:00 | 292 | 290
2018-09-07 20:30 | 284 | 282
2018-09-07 21:00 | 272 | 268
2018-09-07 21:30 | 255 | 251
2018-09-07 22:00 | 262 | 260
2018-09-07 22:30 | 262 | 260
2018-09-07 23:00 | 250 | 247
2018-09-07 23:30 | 234 | 230
2018-09-08 | 219 | 214
2018-09-08 00:30 | 210 | 204
2018-09-08 01:00 | 203 | 196
2018-09-08 01:30 | 195 | 190
2018-09-08 02:00 | 188 | 184
2018-09-08 02:30 | 185 | 181
2018-09-08 03:00 | 184 | 180
2018-09-08 03:30 | 183 | 179
2018-09-08 04:00 | 184 | 180
2018-09-08 04:30 | 186 | 182
2018-09-08 05:00 | 191 | 188
2018-09-08 05:30 | 198 | 194
2018-09-08 06:00 | 207 | 204
2018-09-08 06:30 | 222 | 220
2018-09-08 07:00 | 242 | 241
2018-09-08 07:30 | 256 | 255
2018-09-08 08:00 | 265 | 264
2018-09-08 08:30 | 244 | 242
2018-09-08 09:00 | 263 | 263
2018-09-08 09:30 | 265 | 263
2018-09-08 10:00 | 265 | 263
2018-09-08 10:30 | 252 | 251
2018-09-08 11:00 | 237 | 237
2018-09-08 11:30 | 222 | 222
2018-09-08 12:00 | 216 | 216
2018-09-08 12:30 | 209 | 209
2018-09-08 13:00 | 206 | 206
2018-09-08 13:30 | 213 | 213
2018-09-08 14:00 | 207 | 207
2018-09-08 14:30 | 220 | 220
2018-09-08 15:00 | 231 | 231
2018-09-08 15:30 | 232 | 232
2018-09-08 16:00 | 244 | 244
2018-09-08 16:30 | 260 | 260
2018-09-08 17:00 | 266 | 266
2018-09-08 17:30 | 277 | 277
2018-09-08 18:00 | 279 | 279
2018-09-08 18:30 | 277 | 276
2018-09-08 19:00 | 274 | 273
2018-09-08 19:30 | 274 | 273
2018-09-08 20:00 | 275 | 274
2018-09-08 20:30 | 258 | 258
2018-09-08 21:00 | 247 | 247
2018-09-08 21:30 | 241 | 241
2018-09-08 22:00 | 238 | 238
2018-09-08 22:30 | 243 | 243
2018-09-08 23:00 | 233 | 232
2018-09-08 23:30 | 222 | 222
2018-09-09 | 207 | 206
2018-09-09 00:30 | 193 | 193
2018-09-09 01:00 | 178 | 178
2018-09-09 01:30 | 167 | 167
2018-09-09 02:00 | 161 | 161
2018-09-09 02:30 | 159 | 159
2018-09-09 03:00 | 156 | 156
2018-09-09 03:30 | 158 | 158
2018-09-09 04:00 | 159 | 159
2018-09-09 04:30 | 162 | 162
2018-09-09 05:00 | 141 | 141
2018-09-09 05:30 | 142 | 142
2018-09-09 06:00 | 157 | 157
2018-09-09 06:30 | 165 | 165
2018-09-09 07:00 | 168 | 168
2018-09-09 07:30 | 188 | 188
2018-09-09 08:00 | 172 | 172
2018-09-09 08:30 | 198 | 198
2018-09-09 09:00 | 199 | 198
2018-09-09 09:30 | 200 | 199
2018-09-09 10:00 | 197 | 196
2018-09-09 10:30 | 189 | 188
2018-09-09 11:00 | 190 | 189
2018-09-09 11:30 | 157 | 155
2018-09-09 12:00 | 172 | 171
2018-09-09 12:30 | 176 | 175
2018-09-09 13:00 | 169 | 167
2018-09-09 13:30 | 172 | 170
2018-09-09 14:00 | 162 | 160
2018-09-09 14:30 | 182 | 180
2018-09-09 15:00 | 185 | 183
2018-09-09 15:30 | 197 | 195
2018-09-09 16:00 | 213 | 212
2018-09-09 16:30 | 224 | 223
2018-09-09 17:00 | 243 | 241
2018-09-09 17:30 | 261 | 259
2018-09-09 18:00 | 278 | 274
2018-09-09 18:30 | 279 | 275
2018-09-09 19:00 | 272 | 267
2018-09-09 19:30 | 263 | 259
2018-09-09 20:00 | 255 | 253
2018-09-09 20:30 | 245 | 242
2018-09-09 21:00 | 238 | 235
2018-09-09 21:30 | 229 | 225
2018-09-09 22:00 | 226 | 222
2018-09-09 22:30 | 223 | 218
2018-09-09 23:00 | 220 | 214
2018-09-09 23:30 | 210 | 203
2018-09-10 | 191 | 182
2018-09-10 00:30 | 181 | 172
2018-09-10 01:00 | 172 | 161
2018-09-10 01:30 | 171 | 159
2018-09-10 02:00 | 166 | 156
2018-09-10 02:30 | 164 | 157
2018-09-10 03:00 | 164 | 157
2018-09-10 03:30 | 163 | 156
2018-09-10 04:00 | 167 | 161
2018-09-10 04:30 | 174 | 168
2018-09-10 05:00 | 188 | 184
2018-09-10 05:30 | 201 | 198
2018-09-10 06:00 | 227 | 225
2018-09-10 06:30 | 248 | 246
2018-09-10 07:00 | 267 | 265
2018-09-10 07:30 | 268 | 266
2018-09-10 08:00 | 259 | 257
2018-09-10 08:30 | 246 | 244
2018-09-10 09:00 | 238 | 236
2018-09-10 09:30 | 229 | 227
2018-09-10 10:00 | 223 | 221
2018-09-10 10:30 | 215 | 214
2018-09-10 11:00 | 204 | 203
2018-09-10 11:30 | 199 | 197
2018-09-10 12:00 | 199 | 197
2018-09-10 12:30 | 200 | 198
2018-09-10 13:00 | 202 | 200
2018-09-10 13:30 | 211 | 209
2018-09-10 14:00 | 219 | 217
2018-09-10 14:30 | 223 | 221
2018-09-10 15:00 | 232 | 230
2018-09-10 15:30 | 242 | 240
2018-09-10 16:00 | 257 | 255
2018-09-10 16:30 | 269 | 266
2018-09-10 17:00 | 277 | 275
2018-09-10 17:30 | 297 | 296
2018-09-10 18:00 | 304 | 303
2018-09-10 18:30 | 302 | 301
2018-09-10 19:00 | 312 | 311
2018-09-10 19:30 | 297 | 296
2018-09-10 20:00 | 282 | 281
2018-09-10 20:30 | 268 | 268
2018-09-10 21:00 | 256 | 256
2018-09-10 21:30 | 254 | 254
2018-09-10 22:00 | 243 | 242
2018-09-10 22:30 | 240 | 240
2018-09-10 23:00 | 241 | 240
2018-09-10 23:30 | 227 | 225
2018-09-11 | 198 | 196
2018-09-11 00:30 | 184 | 183
2018-09-11 01:00 | 173 | 171
2018-09-11 01:30 | 170 | 169
2018-09-11 02:00 | 166 | 165
2018-09-11 02:30 | 161 | 160
2018-09-11 03:00 | 161 | 161
2018-09-11 03:30 | 144 | 144
2018-09-11 04:00 | 158 | 158
2018-09-11 04:30 | 161 | 161
2018-09-11 05:00 | 175 | 175
2018-09-11 05:30 | 192 | 192
2018-09-11 06:00 | 217 | 217
2018-09-11 06:30 | 245 | 245
2018-09-11 07:00 | 267 | 266
2018-09-11 07:30 | 263 | 263
2018-09-11 08:00 | 251 | 251
2018-09-11 08:30 | 236 | 235
2018-09-11 09:00 | 232 | 232
2018-09-11 09:30 | 222 | 221
2018-09-11 10:00 | 217 | 217
2018-09-11 10:30 | 215 | 215
2018-09-11 11:00 | 210 | 210
2018-09-11 11:30 | 207 | 207
2018-09-11 12:00 | 207 | 207
2018-09-11 12:30 | 209 | 209
2018-09-11 13:00 | 209 | 208
2018-09-11 13:30 | 216 | 215
2018-09-11 14:00 | 218 | 218
2018-09-11 14:30 | 220 | 220
2018-09-11 15:00 | 230 | 229
2018-09-11 15:30 | 240 | 240
2018-09-11 16:00 | 245 | 245
2018-09-11 16:30 | 263 | 263
2018-09-11 17:00 | 278 | 278
2018-09-11 17:30 | 293 | 293
2018-09-11 18:00 | 298 | 298
2018-09-11 18:30 | 295 | 295
2018-09-11 19:00 | 290 | 290
2018-09-11 19:30 | 281 | 281
2018-09-11 20:00 | 279 | 279
2018-09-11 20:30 | 267 | 266
2018-09-11 21:00 | 251 | 250
2018-09-11 21:30 | 237 | 237
2018-09-11 22:00 | 226 | 226
2018-09-11 22:30 | 223 | 223
2018-09-11 23:00 | 215 | 215
2018-09-11 23:30 | 205 | 204
2018-09-12 | 187 | 187
2018-09-12 00:30 | 175 | 174
2018-09-12 01:00 | 167 | 166
2018-09-12 01:30 | 162 | 161
2018-09-12 02:00 | 148 | 146
2018-09-12 02:30 | 160 | 159
2018-09-12 03:00 | 160 | 159
2018-09-12 03:30 | 159 | 158
2018-09-12 04:00 | 159 | 157
2018-09-12 04:30 | 163 | 162
2018-09-12 05:00 | 179 | 178
2018-09-12 05:30 | 192 | 192
2018-09-12 06:00 | 215 | 215
2018-09-12 06:30 | 242 | 242
2018-09-12 07:00 | 257 | 257
2018-09-12 07:30 | 263 | 263
2018-09-12 08:00 | 257 | 257
2018-09-12 08:30 | 248 | 248
2018-09-12 09:00 | 237 | 237
2018-09-12 09:30 | 233 | 233
2018-09-12 10:00 | 223 | 223
2018-09-12 10:30 | 217 | 217
2018-09-12 11:00 | 205 | 205
2018-09-12 11:30 | 209 | 209
2018-09-12 12:00 | 209 | 209
2018-09-12 12:30 | 206 | 206
2018-09-12 13:00 | 207 | 207
2018-09-12 13:30 | 212 | 211
2018-09-12 14:00 | 215 | 215
2018-09-12 14:30 | 218 | 218
2018-09-12 15:00 | 225 | 225
2018-09-12 15:30 | 240 | 240
2018-09-12 16:00 | 255 | 255
2018-09-12 16:30 | 269 | 269
2018-09-12 17:00 | 283 | 283
2018-09-12 17:30 | 297 | 297
2018-09-12 18:00 | 309 | 309
2018-09-12 18:30 | 312 | 312
2018-09-12 19:00 | 306 | 305
2018-09-12 19:30 | 303 | 301
2018-09-12 20:00 | 295 | 293
2018-09-12 20:30 | 283 | 282
2018-09-12 21:00 | 270 | 270
2018-09-12 21:30 | 258 | 258
2018-09-12 22:00 | 254 | 253
2018-09-12 22:30 | 250 | 250
2018-09-12 23:00 | 237 | 237
2018-09-12 23:30 | 221 | 221
2018-09-13 | 201 | 199
2018-09-13 00:30 | 193 | 191
2018-09-13 01:00 | 186 | 184
2018-09-13 01:30 | 176 | 173
2018-09-13 02:00 | 157 | 156
2018-09-13 02:30 | 154 | 152
2018-09-13 03:00 | 166 | 165
2018-09-13 03:30 | 168 | 167
2018-09-13 04:00 | 172 | 171
2018-09-13 04:30 | 177 | 176
2018-09-13 05:00 | 187 | 187
2018-09-13 05:30 | 190 | 189
2018-09-13 06:00 | 224 | 222
2018-09-13 06:30 | 251 | 250
2018-09-13 07:00 | 261 | 261
2018-09-13 07:30 | 264 | 263
2018-09-13 08:00 | 255 | 253
2018-09-13 08:30 | 239 | 238
2018-09-13 09:00 | 225 | 224
2018-09-13 09:30 | 218 | 217
2018-09-13 10:00 | 212 | 211
2018-09-13 10:30 | 203 | 202
2018-09-13 11:00 | 204 | 203
2018-09-13 11:30 | 206 | 205
2018-09-13 12:00 | 203 | 202
2018-09-13 12:30 | 202 | 202
2018-09-13 13:00 | 206 | 206
2018-09-13 13:30 | 210 | 209
2018-09-13 14:00 | 217 | 216
2018-09-13 14:30 | 222 | 221
2018-09-13 15:00 | 233 | 232
2018-09-13 15:30 | 243 | 242
2018-09-13 16:00 | 258 | 257
2018-09-13 16:30 | 270 | 269
2018-09-13 17:00 | 278 | 277
2018-09-13 17:30 | 293 | 292
2018-09-13 18:00 | 303 | 303
2018-09-13 18:30 | 305 | 304
2018-09-13 19:00 | 295 | 294
2018-09-13 19:30 | 294 | 293
2018-09-13 20:00 | 289 | 288
2018-09-13 20:30 | 277 | 276
2018-09-13 21:00 | 264 | 264
2018-09-13 21:30 | 249 | 248
2018-09-13 22:00 | 244 | 243
2018-09-13 22:30 | 241 | 240
2018-09-13 23:00 | 229 | 228
2018-09-13 23:30 | 213 | 210
2018-09-14 | 191 | 188
2018-09-14 00:30 | 179 | 175
2018-09-14 01:00 | 174 | 169
2018-09-14 01:30 | 170 | 165
2018-09-14 02:00 | 170 | 165
2018-09-14 02:30 | 168 | 163
2018-09-14 03:00 | 168 | 162
2018-09-14 03:30 | 174 | 169
2018-09-14 04:00 | 172 | 167
2018-09-14 04:30 | 166 | 162
2018-09-14 05:00 | 184 | 181
2018-09-14 05:30 | 189 | 186
2018-09-14 06:00 | 206 | 204
2018-09-14 06:30 | 228 | 227
2018-09-14 07:00 | 236 | 236
2018-09-14 07:30 | 235 | 234
2018-09-14 08:00 | 228 | 227
2018-09-14 08:30 | 211 | 211
2018-09-14 09:00 | 222 | 222
2018-09-14 09:30 | 212 | 211
2018-09-14 10:00 | 203 | 203
2018-09-14 10:30 | 192 | 192
2018-09-14 11:00 | 182 | 182
2018-09-14 11:30 | 160 | 159
2018-09-14 12:00 | 176 | 175
2018-09-14 12:30 | 181 | 180
2018-09-14 13:00 | 174 | 173
2018-09-14 13:30 | 186 | 185
2018-09-14 14:00 | 191 | 191
2018-09-14 14:30 | 201 | 200
2018-09-14 15:00 | 214 | 213
2018-09-14 15:30 | 216 | 216
2018-09-14 16:00 | 224 | 224
2018-09-14 16:30 | 250 | 249
2018-09-14 17:00 | 258 | 257
2018-09-14 17:30 | 266 | 266
2018-09-14 18:00 | 276 | 274
2018-09-14 18:30 | 278 | 275
2018-09-14 19:00 | 268 | 265
2018-09-14 19:30 | 264 | 261
2018-09-14 20:00 | 254 | 252
2018-09-14 20:30 | 244 | 244
2018-09-14 21:00 | 237 | 237
2018-09-14 21:30 | 229 | 228
2018-09-14 22:00 | 228 | 227
2018-09-14 22:30 | 225 | 224
2018-09-14 23:00 | 214 | 213
2018-09-14 23:30 | 198 | 195
2018-09-15 | 189 | 186
2018-09-15 00:30 | 182 | 178
2018-09-15 01:00 | 179 | 175
2018-09-15 01:30 | 149 | 144
2018-09-15 02:00 | 146 | 139
2018-09-15 02:30 | 145 | 141
2018-09-15 03:00 | 147 | 144
2018-09-15 03:30 | 143 | 140
2018-09-15 04:00 | 134 | 132
2018-09-15 04:30 | 137 | 135
2018-09-15 05:00 | 159 | 158
2018-09-15 05:30 | 149 | 146
2018-09-15 06:00 | 160 | 159
2018-09-15 06:30 | 172 | 171
2018-09-15 07:00 | 175 | 175
2018-09-15 07:30 | 194 | 194
2018-09-15 08:00 | 207 | 206
2018-09-15 08:30 | 207 | 206
2018-09-15 09:00 | 204 | 204
2018-09-15 09:30 | 200 | 200
2018-09-15 10:00 | 171 | 170
2018-09-15 10:30 | 184 | 184
2018-09-15 11:00 | 159 | 159
2018-09-15 11:30 | 162 | 161
2018-09-15 12:00 | 157 | 157
2018-09-15 12:30 | 171 | 171
2018-09-15 13:00 | 152 | 151
2018-09-15 13:30 | 182 | 182
2018-09-15 14:00 | 186 | 185
2018-09-15 14:30 | 172 | 172
2018-09-15 15:00 | 189 | 189
2018-09-15 15:30 | 217 | 217
2018-09-15 16:00 | 229 | 229
2018-09-15 16:30 | 239 | 239
2018-09-15 17:00 | 243 | 243
2018-09-15 17:30 | 259 | 259
2018-09-15 18:00 | 266 | 264
2018-09-15 18:30 | 268 | 265
2018-09-15 19:00 | 263 | 260
2018-09-15 19:30 | 253 | 252
2018-09-15 20:00 | 244 | 242
2018-09-15 20:30 | 237 | 235
2018-09-15 21:00 | 227 | 225
2018-09-15 21:30 | 225 | 222
2018-09-15 22:00 | 224 | 221
2018-09-15 22:30 | 222 | 219
2018-09-15 23:00 | 214 | 210
2018-09-15 23:30 | 203 | 197
2018-09-16 | 185 | 180
2018-09-16 00:30 | 176 | 172
2018-09-16 01:00 | 168 | 163
2018-09-16 01:30 | 158 | 152
2018-09-16 02:00 | 153 | 148
2018-09-16 02:30 | 144 | 142
2018-09-16 03:00 | 145 | 142
2018-09-16 03:30 | 144 | 142
2018-09-16 04:00 | 160 | 158
2018-09-16 04:30 | 143 | 141
2018-09-16 05:00 | 137 | 134
2018-09-16 05:30 | 148 | 145
2018-09-16 06:00 | 165 | 162
2018-09-16 06:30 | 175 | 173
2018-09-16 07:00 | 170 | 169
2018-09-16 07:30 | 181 | 180
2018-09-16 08:00 | 207 | 207
2018-09-16 08:30 | 202 | 201
2018-09-16 09:00 | 200 | 199
2018-09-16 09:30 | 204 | 203
2018-09-16 10:00 | 203 | 203
2018-09-16 10:30 | 199 | 198
2018-09-16 11:00 | 179 | 178
2018-09-16 11:30 | 155 | 153
2018-09-16 12:00 | 155 | 153
2018-09-16 12:30 | 164 | 162
2018-09-16 13:00 | 166 | 164
2018-09-16 13:30 | 177 | 176
2018-09-16 14:00 | 165 | 163
2018-09-16 14:30 | 184 | 182
2018-09-16 15:00 | 191 | 190
2018-09-16 15:30 | 211 | 210
2018-09-16 16:00 | 221 | 220
2018-09-16 16:30 | 231 | 231
2018-09-16 17:00 | 247 | 247
2018-09-16 17:30 | 263 | 263
2018-09-16 18:00 | 274 | 273
2018-09-16 18:30 | 274 | 273
2018-09-16 19:00 | 271 | 269
2018-09-16 19:30 | 270 | 269
2018-09-16 20:00 | 261 | 260
2018-09-16 20:30 | 252 | 251
2018-09-16 21:00 | 241 | 238
2018-09-16 21:30 | 231 | 227
2018-09-16 22:00 | 228 | 224
2018-09-16 22:30 | 225 | 222
2018-09-16 23:00 | 219 | 215
2018-09-16 23:30 | 205 | 199
2018-09-17 | 187 | 183
2018-09-17 00:30 | 182 | 177
2018-09-17 01:00 | 174 | 169
2018-09-17 01:30 | 170 | 165
2018-09-17 02:00 | 167 | 161
2018-09-17 02:30 | 161 | 155
2018-09-17 03:00 | 159 | 153
2018-09-17 03:30 | 160 | 154
2018-09-17 04:00 | 174 | 169
2018-09-17 04:30 | 176 | 171
2018-09-17 05:00 | 184 | 181
2018-09-17 05:30 | 194 | 191
2018-09-17 06:00 | 214 | 212
2018-09-17 06:30 | 210 | 209
2018-09-17 07:00 | 214 | 213
2018-09-17 07:30 | 210 | 210
2018-09-17 08:00 | 198 | 198
2018-09-17 08:30 | 186 | 186
2018-09-17 09:00 | 178 | 178
2018-09-17 09:30 | 171 | 171
2018-09-17 10:00 | 168 | 168
2018-09-17 10:30 | 165 | 165
2018-09-17 11:00 | 164 | 164
2018-09-17 11:30 | 166 | 166
2018-09-17 12:00 | 173 | 173
2018-09-17 12:30 | 174 | 174
2018-09-17 13:00 | 175 | 175
2018-09-17 13:30 | 176 | 176
2018-09-17 14:00 | 178 | 178
2018-09-17 14:30 | 188 | 188
2018-09-17 15:00 | 197 | 197
2018-09-17 15:30 | 207 | 207
2018-09-17 16:00 | 237 | 237
2018-09-17 16:30 | 253 | 253
2018-09-17 17:00 | 272 | 269
2018-09-17 17:30 | 286 | 284
2018-09-17 18:00 | 296 | 295
2018-09-17 18:30 | 298 | 297
2018-09-17 19:00 | 291 | 289
2018-09-17 19:30 | 288 | 286
2018-09-17 20:00 | 283 | 280
2018-09-17 20:30 | 268 | 265
2018-09-17 21:00 | 250 | 248
2018-09-17 21:30 | 237 | 235
2018-09-17 22:00 | 229 | 227
2018-09-17 22:30 | 231 | 228
2018-09-17 23:00 | 221 | 218
2018-09-17 23:30 | 206 | 202
2018-09-18 | 191 | 185
2018-09-18 00:30 | 179 | 172
2018-09-18 01:00 | 174 | 166
2018-09-18 01:30 | 172 | 164
2018-09-18 02:00 | 169 | 161
2018-09-18 02:30 | 167 | 159
2018-09-18 03:00 | 158 | 150
2018-09-18 03:30 | 159 | 155
2018-09-18 04:00 | 165 | 161
2018-09-18 04:30 | 147 | 143
2018-09-18 05:00 | 169 | 166
2018-09-18 05:30 | 186 | 183
2018-09-18 06:00 | 213 | 212
2018-09-18 06:30 | 232 | 231
2018-09-18 07:00 | 241 | 241
2018-09-18 07:30 | 236 | 236
2018-09-18 08:00 | 225 | 224
2018-09-18 08:30 | 211 | 210
2018-09-18 09:00 | 212 | 211
2018-09-18 09:30 | 211 | 210
2018-09-18 10:00 | 215 | 214
2018-09-18 10:30 | 221 | 221
2018-09-18 11:00 | 210 | 210
2018-09-18 11:30 | 201 | 201
2018-09-18 12:00 | 197 | 196
2018-09-18 12:30 | 197 | 196
2018-09-18 13:00 | 192 | 192
2018-09-18 13:30 | 196 | 195
2018-09-18 14:00 | 202 | 202
2018-09-18 14:30 | 206 | 206
2018-09-18 15:00 | 209 | 208
2018-09-18 15:30 | 223 | 223
2018-09-18 16:00 | 233 | 233
2018-09-18 16:30 | 248 | 248
2018-09-18 17:00 | 260 | 260
2018-09-18 17:30 | 273 | 272
2018-09-18 18:00 | 293 | 291
2018-09-18 18:30 | 295 | 293
2018-09-18 19:00 | 283 | 280
2018-09-18 19:30 | 273 | 271
2018-09-18 20:00 | 267 | 266
2018-09-18 20:30 | 254 | 254
2018-09-18 21:00 | 243 | 242
2018-09-18 21:30 | 231 | 230
2018-09-18 22:00 | 227 | 226
2018-09-18 22:30 | 224 | 223
2018-09-18 23:00 | 213 | 211
2018-09-18 23:30 | 202 | 200
2018-09-19 | 182 | 179
2018-09-19 00:30 | 175 | 171
2018-09-19 01:00 | 173 | 169
2018-09-19 01:30 | 169 | 165
2018-09-19 02:00 | 167 | 162
2018-09-19 02:30 | 165 | 160
2018-09-19 03:00 | 164 | 159
2018-09-19 03:30 | 164 | 159
2018-09-19 04:00 | 169 | 164
2018-09-19 04:30 | 174 | 170
2018-09-19 05:00 | 178 | 175
2018-09-19 05:30 | 189 | 187
2018-09-19 06:00 | 215 | 213
2018-09-19 06:30 | 233 | 232
2018-09-19 07:00 | 242 | 242
2018-09-19 07:30 | 247 | 247
2018-09-19 08:00 | 249 | 249
2018-09-19 08:30 | 244 | 243
2018-09-19 09:00 | 231 | 230
2018-09-19 09:30 | 218 | 218
2018-09-19 10:00 | 208 | 207
2018-09-19 10:30 | 198 | 197
2018-09-19 11:00 | 197 | 196
2018-09-19 11:30 | 199 | 199
2018-09-19 12:00 | 198 | 197
2018-09-19 12:30 | 198 | 198
2018-09-19 13:00 | 193 | 193
2018-09-19 13:30 | 201 | 201
2018-09-19 14:00 | 198 | 197
2018-09-19 14:30 | 203 | 202
2018-09-19 15:00 | 210 | 208
2018-09-19 15:30 | 224 | 223
2018-09-19 16:00 | 237 | 236
2018-09-19 16:30 | 252 | 251
2018-09-19 17:00 | 264 | 263
2018-09-19 17:30 | 273 | 272
2018-09-19 18:00 | 284 | 284
2018-09-19 18:30 | 284 | 283
2018-09-19 19:00 | 274 | 272
2018-09-19 19:30 | 272 | 269
2018-09-19 20:00 | 264 | 262
2018-09-19 20:30 | 250 | 250
2018-09-19 21:00 | 245 | 244
2018-09-19 21:30 | 231 | 231
2018-09-19 22:00 | 228 | 228
2018-09-19 22:30 | 233 | 232
2018-09-19 23:00 | 227 | 227
2018-09-19 23:30 | 219 | 218
2018-09-20 | 197 | 196
2018-09-20 00:30 | 190 | 189
2018-09-20 01:00 | 188 | 186
2018-09-20 01:30 | 187 | 185
2018-09-20 02:00 | 177 | 176
2018-09-20 02:30 | 175 | 175
2018-09-20 03:00 | 175 | 174
2018-09-20 03:30 | 177 | 177
2018-09-20 04:00 | 177 | 176
2018-09-20 04:30 | 179 | 179
2018-09-20 05:00 | 188 | 188
2018-09-20 05:30 | 198 | 198
2018-09-20 06:00 | 217 | 217
2018-09-20 06:30 | 229 | 229
2018-09-20 07:00 | 233 | 233
2018-09-20 07:30 | 233 | 233
2018-09-20 08:00 | 226 | 225
2018-09-20 08:30 | 228 | 228
2018-09-20 09:00 | 229 | 228
2018-09-20 09:30 | 240 | 240
2018-09-20 10:00 | 239 | 239
2018-09-20 10:30 | 232 | 232
2018-09-20 11:00 | 217 | 217
2018-09-20 11:30 | 206 | 206
2018-09-20 12:00 | 214 | 213
2018-09-20 12:30 | 214 | 213
2018-09-20 13:00 | 208 | 208
2018-09-20 13:30 | 209 | 208
2018-09-20 14:00 | 187 | 186
2018-09-20 14:30 | 205 | 205
2018-09-20 15:00 | 219 | 219
2018-09-20 15:30 | 223 | 223
2018-09-20 16:00 | 239 | 239
2018-09-20 16:30 | 251 | 251
2018-09-20 17:00 | 265 | 265
2018-09-20 17:30 | 277 | 277
2018-09-20 18:00 | 289 | 289
2018-09-20 18:30 | 292 | 291
2018-09-20 19:00 | 282 | 282
2018-09-20 19:30 | 278 | 278
2018-09-20 20:00 | 272 | 271
2018-09-20 20:30 | 255 | 255
2018-09-20 21:00 | 233 | 233
2018-09-20 21:30 | 238 | 238
2018-09-20 22:00 | 233 | 233
2018-09-20 22:30 | 222 | 222
2018-09-20 23:00 | 213 | 213
2018-09-20 23:30 | 201 | 201
2018-09-21 | 190 | 190
2018-09-21 00:30 | 183 | 182
2018-09-21 01:00 | 183 | 182
2018-09-21 01:30 | 179 | 179
2018-09-21 02:00 | 178 | 177
2018-09-21 02:30 | 176 | 175
2018-09-21 03:00 | 172 | 172
2018-09-21 03:30 | 175 | 175
2018-09-21 04:00 | 179 | 179
2018-09-21 04:30 | 172 | 172
2018-09-21 05:00 | 184 | 184
2018-09-21 05:30 | 200 | 200
2018-09-21 06:00 | 196 | 195
2018-09-21 06:30 | 224 | 223
2018-09-21 07:00 | 247 | 246
2018-09-21 07:30 | 248 | 248
2018-09-21 08:00 | 241 | 241
2018-09-21 08:30 | 224 | 224
2018-09-21 09:00 | 226 | 226
2018-09-21 09:30 | 219 | 219
2018-09-21 10:00 | 216 | 216
2018-09-21 10:30 | 214 | 214
2018-09-21 11:00 | 215 | 215
2018-09-21 11:30 | 214 | 214
2018-09-21 12:00 | 210 | 210
2018-09-21 12:30 | 206 | 206
2018-09-21 13:00 | 206 | 205
2018-09-21 13:30 | 211 | 211
2018-09-21 14:00 | 213 | 213
2018-09-21 14:30 | 216 | 215
2018-09-21 15:00 | 224 | 224
2018-09-21 15:30 | 230 | 230
2018-09-21 16:00 | 241 | 240
2018-09-21 16:30 | 256 | 255
2018-09-21 17:00 | 268 | 267
2018-09-21 17:30 | 275 | 274
2018-09-21 18:00 | 282 | 281
2018-09-21 18:30 | 282 | 281
2018-09-21 19:00 | 279 | 279
2018-09-21 19:30 | 266 | 266
2018-09-21 20:00 | 266 | 266
2018-09-21 20:30 | 265 | 265
2018-09-21 21:00 | 259 | 259
2018-09-21 21:30 | 254 | 253
2018-09-21 22:00 | 261 | 260
2018-09-21 22:30 | 251 | 250
2018-09-21 23:00 | 239 | 238
2018-09-21 23:30 | 227 | 225
2018-09-22 | 200 | 197
2018-09-22 00:30 | 191 | 188
2018-09-22 01:00 | 186 | 182
2018-09-22 01:30 | 184 | 180
2018-09-22 02:00 | 180 | 176
2018-09-22 02:30 | 181 | 177
2018-09-22 03:00 | 179 | 175
2018-09-22 03:30 | 178 | 174
2018-09-22 04:00 | 177 | 173
2018-09-22 04:30 | 176 | 171
2018-09-22 05:00 | 182 | 178
2018-09-22 05:30 | 189 | 184
2018-09-22 06:00 | 195 | 191
2018-09-22 06:30 | 201 | 198
2018-09-22 07:00 | 208 | 205
2018-09-22 07:30 | 215 | 213
2018-09-22 08:00 | 214 | 213
2018-09-22 08:30 | 209 | 208
2018-09-22 09:00 | 207 | 207
2018-09-22 09:30 | 207 | 206
2018-09-22 10:00 | 205 | 205
2018-09-22 10:30 | 197 | 197
2018-09-22 11:00 | 191 | 191
2018-09-22 11:30 | 183 | 183
2018-09-22 12:00 | 173 | 172
2018-09-22 12:30 | 167 | 166
2018-09-22 13:00 | 167 | 166
2018-09-22 13:30 | 170 | 169
2018-09-22 14:00 | 175 | 174
2018-09-22 14:30 | 181 | 180
2018-09-22 15:00 | 187 | 186
2018-09-22 15:30 | 199 | 198
2018-09-22 16:00 | 219 | 218
2018-09-22 16:30 | 230 | 230
2018-09-22 17:00 | 232 | 232
2018-09-22 17:30 | 246 | 246
2018-09-22 18:00 | 254 | 254
2018-09-22 18:30 | 255 | 255
2018-09-22 19:00 | 249 | 248
2018-09-22 19:30 | 245 | 244
2018-09-22 20:00 | 239 | 238
2018-09-22 20:30 | 232 | 231
2018-09-22 21:00 | 225 | 224
2018-09-22 21:30 | 221 | 220
2018-09-22 22:00 | 221 | 219
2018-09-22 22:30 | 226 | 225
2018-09-22 23:00 | 222 | 221
2018-09-22 23:30 | 205 | 203
2018-09-23 | 181 | 178
2018-09-23 00:30 | 170 | 166
2018-09-23 01:00 | 163 | 157
2018-09-23 01:30 | 156 | 154
2018-09-23 02:00 | 145 | 142
2018-09-23 02:30 | 158 | 156
2018-09-23 03:00 | 147 | 144
2018-09-23 03:30 | 154 | 152
2018-09-23 04:00 | 159 | 156
2018-09-23 04:30 | 156 | 154
2018-09-23 05:00 | 157 | 154
2018-09-23 05:30 | 160 | 157
2018-09-23 06:00 | 163 | 161
2018-09-23 06:30 | 169 | 167
2018-09-23 07:00 | 175 | 174
2018-09-23 07:30 | 182 | 181
2018-09-23 08:00 | 188 | 188
2018-09-23 08:30 | 188 | 188
2018-09-23 09:00 | 180 | 180
2018-09-23 09:30 | 180 | 180
2018-09-23 10:00 | 179 | 179
2018-09-23 10:30 | 174 | 174
2018-09-23 11:00 | 169 | 169
2018-09-23 11:30 | 165 | 165
2018-09-23 12:00 | 164 | 164
2018-09-23 12:30 | 162 | 162
2018-09-23 13:00 | 163 | 163
2018-09-23 13:30 | 166 | 166
2018-09-23 14:00 | 161 | 161
2018-09-23 14:30 | 177 | 177
2018-09-23 15:00 | 186 | 186
2018-09-23 15:30 | 198 | 198
2018-09-23 16:00 | 212 | 212
2018-09-23 16:30 | 230 | 230
2018-09-23 17:00 | 239 | 238
2018-09-23 17:30 | 248 | 247
2018-09-23 18:00 | 261 | 261
2018-09-23 18:30 | 262 | 262
2018-09-23 19:00 | 254 | 254
2018-09-23 19:30 | 249 | 249
2018-09-23 20:00 | 247 | 246
2018-09-23 20:30 | 236 | 236
2018-09-23 21:00 | 226 | 225
2018-09-23 21:30 | 218 | 216
2018-09-23 22:00 | 216 | 215
2018-09-23 22:30 | 215 | 213
2018-09-23 23:00 | 210 | 208
2018-09-23 23:30 | 203 | 200
2018-09-24 | 182 | 179
2018-09-24 00:30 | 174 | 170
2018-09-24 01:00 | 166 | 161
2018-09-24 01:30 | 161 | 156
2018-09-24 02:00 | 160 | 154
2018-09-24 02:30 | 158 | 152
2018-09-24 03:00 | 159 | 153
2018-09-24 03:30 | 160 | 154
2018-09-24 04:00 | 160 | 154
2018-09-24 04:30 | 161 | 156
2018-09-24 05:00 | 166 | 162
2018-09-24 05:30 | 179 | 175
2018-09-24 06:00 | 193 | 190
2018-09-24 06:30 | 206 | 204
2018-09-24 07:00 | 218 | 217
2018-09-24 07:30 | 227 | 226
2018-09-24 08:00 | 230 | 229
2018-09-24 08:30 | 199 | 198
2018-09-24 09:00 | 190 | 190
2018-09-24 09:30 | 190 | 189
2018-09-24 10:00 | 191 | 191
2018-09-24 10:30 | 189 | 189
2018-09-24 11:00 | 190 | 190
2018-09-24 11:30 | 194 | 194
2018-09-24 12:00 | 193 | 193
2018-09-24 12:30 | 196 | 196
2018-09-24 13:00 | 199 | 198
2018-09-24 13:30 | 208 | 208
2018-09-24 14:00 | 205 | 205
2018-09-24 14:30 | 212 | 212
2018-09-24 15:00 | 225 | 225
2018-09-24 15:30 | 238 | 238
2018-09-24 16:00 | 245 | 245
2018-09-24 16:30 | 256 | 255
2018-09-24 17:00 | 271 | 270
2018-09-24 17:30 | 287 | 286
2018-09-24 18:00 | 300 | 300
2018-09-24 18:30 | 301 | 301
2018-09-24 19:00 | 290 | 290
2018-09-24 19:30 | 283 | 283
2018-09-24 20:00 | 280 | 280
2018-09-24 20:30 | 270 | 270
2018-09-24 21:00 | 254 | 253
2018-09-24 21:30 | 239 | 238
2018-09-24 22:00 | 237 | 235
2018-09-24 22:30 | 231 | 230
2018-09-24 23:00 | 217 | 215
2018-09-24 23:30 | 204 | 202
2018-09-25 | 187 | 184
2018-09-25 00:30 | 180 | 176
2018-09-25 01:00 | 176 | 172
2018-09-25 01:30 | 171 | 167
2018-09-25 02:00 | 170 | 165
2018-09-25 02:30 | 167 | 162
2018-09-25 03:00 | 168 | 163
2018-09-25 03:30 | 170 | 165
2018-09-25 04:00 | 172 | 167
2018-09-25 04:30 | 176 | 172
2018-09-25 05:00 | 182 | 179
2018-09-25 05:30 | 186 | 183
2018-09-25 06:00 | 207 | 205
2018-09-25 06:30 | 223 | 222
2018-09-25 07:00 | 242 | 242
2018-09-25 07:30 | 252 | 252
2018-09-25 08:00 | 252 | 251
2018-09-25 08:30 | 241 | 241
2018-09-25 09:00 | 242 | 242
2018-09-25 09:30 | 234 | 233
2018-09-25 10:00 | 224 | 224
2018-09-25 10:30 | 234 | 234
2018-09-25 11:00 | 241 | 241
2018-09-25 11:30 | 254 | 254
2018-09-25 12:00 | 260 | 260
2018-09-25 12:30 | 256 | 256
2018-09-25 13:00 | 236 | 236
2018-09-25 13:30 | 238 | 238
2018-09-25 14:00 | 253 | 252
2018-09-25 14:30 | 257 | 257
2018-09-25 15:00 | 257 | 256
2018-09-25 15:30 | 263 | 262
2018-09-25 16:00 | 282 | 281
2018-09-25 16:30 | 301 | 300
2018-09-25 17:00 | 313 | 311
2018-09-25 17:30 | 311 | 310
2018-09-25 18:00 | 322 | 321
2018-09-25 18:30 | 327 | 326
2018-09-25 19:00 | 300 | 298
2018-09-25 19:30 | 286 | 286
2018-09-25 20:00 | 278 | 277
2018-09-25 20:30 | 266 | 265
2018-09-25 21:00 | 256 | 254
2018-09-25 21:30 | 239 | 237
2018-09-25 22:00 | 236 | 234
2018-09-25 22:30 | 232 | 229
2018-09-25 23:00 | 223 | 219
2018-09-25 23:30 | 209 | 204
2018-09-26 | 188 | 185
2018-09-26 00:30 | 185 | 181
2018-09-26 01:00 | 195 | 191
2018-09-26 01:30 | 192 | 188
2018-09-26 02:00 | 187 | 184
2018-09-26 02:30 | 168 | 163
2018-09-26 03:00 | 168 | 163
2018-09-26 03:30 | 169 | 164
2018-09-26 04:00 | 169 | 164
2018-09-26 04:30 | 171 | 167
2018-09-26 05:00 | 177 | 174
2018-09-26 05:30 | 184 | 181
2018-09-26 06:00 | 203 | 201
2018-09-26 06:30 | 219 | 218
2018-09-26 07:00 | 236 | 236
2018-09-26 07:30 | 240 | 239
2018-09-26 08:00 | 234 | 232
2018-09-26 08:30 | 223 | 221
2018-09-26 09:00 | 224 | 222
2018-09-26 09:30 | 229 | 227
2018-09-26 10:00 | 231 | 230
2018-09-26 10:30 | 219 | 218
2018-09-26 11:00 | 226 | 225
2018-09-26 11:30 | 225 | 224
2018-09-26 12:00 | 216 | 215
2018-09-26 12:30 | 219 | 219
2018-09-26 13:00 | 216 | 216
2018-09-26 13:30 | 210 | 210
2018-09-26 14:00 | 219 | 219
2018-09-26 14:30 | 236 | 234
2018-09-26 15:00 | 244 | 241
2018-09-26 15:30 | 241 | 238
2018-09-26 16:00 | 256 | 254
2018-09-26 16:30 | 271 | 269
2018-09-26 17:00 | 285 | 283
2018-09-26 17:30 | 294 | 292
2018-09-26 18:00 | 298 | 296
2018-09-26 18:30 | 297 | 295
2018-09-26 19:00 | 289 | 287
2018-09-26 19:30 | 284 | 282
2018-09-26 20:00 | 274 | 274
2018-09-26 20:30 | 262 | 261
2018-09-26 21:00 | 252 | 251
2018-09-26 21:30 | 240 | 238
2018-09-26 22:00 | 236 | 234
2018-09-26 22:30 | 234 | 231
2018-09-26 23:00 | 224 | 220
2018-09-26 23:30 | 207 | 202
2018-09-27 | 191 | 185
2018-09-27 00:30 | 184 | 177
2018-09-27 01:00 | 173 | 169
2018-09-27 01:30 | 167 | 162
2018-09-27 02:00 | 163 | 158
2018-09-27 02:30 | 159 | 154
2018-09-27 03:00 | 161 | 155
2018-09-27 03:30 | 160 | 154
2018-09-27 04:00 | 163 | 158
2018-09-27 04:30 | 171 | 167
2018-09-27 05:00 | 181 | 178
2018-09-27 05:30 | 193 | 190
2018-09-27 06:00 | 208 | 207
2018-09-27 06:30 | 224 | 223
2018-09-27 07:00 | 237 | 236
2018-09-27 07:30 | 234 | 234
2018-09-27 08:00 | 233 | 233
2018-09-27 08:30 | 230 | 229
2018-09-27 09:00 | 233 | 232
2018-09-27 09:30 | 228 | 228
2018-09-27 10:00 | 228 | 228
2018-09-27 10:30 | 233 | 233
2018-09-27 11:00 | 236 | 236
2018-09-27 11:30 | 236 | 236
2018-09-27 12:00 | 237 | 237
2018-09-27 12:30 | 239 | 239
2018-09-27 13:00 | 232 | 232
2018-09-27 13:30 | 226 | 226
2018-09-27 14:00 | 217 | 217
2018-09-27 14:30 | 218 | 218
2018-09-27 15:00 | 225 | 224
2018-09-27 15:30 | 234 | 233
2018-09-27 16:00 | 241 | 241
2018-09-27 16:30 | 245 | 245
2018-09-27 17:00 | 255 | 254
2018-09-27 17:30 | 278 | 278
2018-09-27 18:00 | 292 | 291
2018-09-27 18:30 | 291 | 291
2018-09-27 19:00 | 280 | 280
2018-09-27 19:30 | 275 | 275
2018-09-27 20:00 | 265 | 264
2018-09-27 20:30 | 254 | 253
2018-09-27 21:00 | 241 | 240
2018-09-27 21:30 | 228 | 228
2018-09-27 22:00 | 223 | 223
2018-09-27 22:30 | 220 | 220
2018-09-27 23:00 | 207 | 207
2018-09-27 23:30 | 189 | 189
2018-09-28 | 174 | 174
2018-09-28 00:30 | 165 | 164
2018-09-28 01:00 | 159 | 157
2018-09-28 01:30 | 161 | 158
2018-09-28 02:00 | 162 | 159
2018-09-28 02:30 | 162 | 159
2018-09-28 03:00 | 162 | 159
2018-09-28 03:30 | 161 | 158
2018-09-28 04:00 | 164 | 161
2018-09-28 04:30 | 170 | 168
2018-09-28 05:00 | 178 | 176
2018-09-28 05:30 | 184 | 182
2018-09-28 06:00 | 193 | 192
2018-09-28 06:30 | 209 | 209
2018-09-28 07:00 | 221 | 221
2018-09-28 07:30 | 229 | 229
2018-09-28 08:00 | 246 | 246
2018-09-28 08:30 | 247 | 247
2018-09-28 09:00 | 250 | 250
2018-09-28 09:30 | 244 | 244
2018-09-28 10:00 | 235 | 235
2018-09-28 10:30 | 224 | 224
2018-09-28 11:00 | 223 | 223
2018-09-28 11:30 | 221 | 221
2018-09-28 12:00 | 219 | 219
2018-09-28 12:30 | 220 | 220
2018-09-28 13:00 | 222 | 222
2018-09-28 13:30 | 228 | 228
2018-09-28 14:00 | 228 | 228
2018-09-28 14:30 | 228 | 228
2018-09-28 15:00 | 234 | 233
2018-09-28 15:30 | 238 | 237
2018-09-28 16:00 | 238 | 238
2018-09-28 16:30 | 247 | 247
2018-09-28 17:00 | 252 | 252
2018-09-28 17:30 | 263 | 262
2018-09-28 18:00 | 275 | 275
2018-09-28 18:30 | 276 | 276
2018-09-28 19:00 | 267 | 267
2018-09-28 19:30 | 256 | 256
2018-09-28 20:00 | 248 | 248
2018-09-28 20:30 | 241 | 241
2018-09-28 21:00 | 233 | 233
2018-09-28 21:30 | 222 | 222
2018-09-28 22:00 | 218 | 217
2018-09-28 22:30 | 212 | 211
2018-09-28 23:00 | 201 | 201
2018-09-28 23:30 | 183 | 183
2018-09-29 | 170 | 170
2018-09-29 00:30 | 158 | 158
2018-09-29 01:00 | 155 | 154
2018-09-29 01:30 | 151 | 151
2018-09-29 02:00 | 151 | 151
2018-09-29 02:30 | 147 | 147
2018-09-29 03:00 | 153 | 153
2018-09-29 03:30 | 145 | 145
2018-09-29 04:00 | 146 | 146
2018-09-29 04:30 | 152 | 152
2018-09-29 05:00 | 151 | 151
2018-09-29 05:30 | 154 | 154
2018-09-29 06:00 | 159 | 159
2018-09-29 06:30 | 169 | 169
2018-09-29 07:00 | 181 | 180
2018-09-29 07:30 | 188 | 188
2018-09-29 08:00 | 200 | 199
2018-09-29 08:30 | 197 | 195
2018-09-29 09:00 | 195 | 193
2018-09-29 09:30 | 194 | 191
2018-09-29 10:00 | 189 | 186
2018-09-29 10:30 | 184 | 180
2018-09-29 11:00 | 181 | 177
2018-09-29 11:30 | 180 | 176
2018-09-29 12:00 | 185 | 182
2018-09-29 12:30 | 186 | 182
2018-09-29 13:00 | 187 | 183
2018-09-29 13:30 | 189 | 186
2018-09-29 14:00 | 195 | 191
2018-09-29 14:30 | 207 | 204
2018-09-29 15:00 | 216 | 215
2018-09-29 15:30 | 225 | 225
2018-09-29 16:00 | 233 | 232
2018-09-29 16:30 | 236 | 235
2018-09-29 17:00 | 234 | 233
2018-09-29 17:30 | 245 | 245
2018-09-29 18:00 | 254 | 253
2018-09-29 18:30 | 254 | 253
2018-09-29 19:00 | 247 | 246
2018-09-29 19:30 | 245 | 244
2018-09-29 20:00 | 239 | 237
2018-09-29 20:30 | 228 | 228
2018-09-29 21:00 | 220 | 220
2018-09-29 21:30 | 215 | 215
2018-09-29 22:00 | 216 | 215
2018-09-29 22:30 | 220 | 220
2018-09-29 23:00 | 215 | 214
2018-09-29 23:30 | 200 | 199
2018-09-30 | 184 | 183
2018-09-30 00:30 | 175 | 174
2018-09-30 01:00 | 166 | 165
2018-09-30 01:30 | 162 | 161
2018-09-30 02:00 | 159 | 157
2018-09-30 02:30 | 160 | 158
2018-09-30 03:00 | 159 | 157
2018-09-30 03:30 | 159 | 157
2018-09-30 04:00 | 158 | 156
2018-09-30 04:30 | 158 | 156
2018-09-30 05:00 | 162 | 160
2018-09-30 05:30 | 165 | 163
2018-09-30 06:00 | 171 | 169
2018-09-30 06:30 | 179 | 177
2018-09-30 07:00 | 196 | 195
2018-09-30 07:30 | 212 | 211
2018-09-30 08:00 | 224 | 224
2018-09-30 08:30 | 231 | 230
2018-09-30 09:00 | 234 | 234
2018-09-30 09:30 | 233 | 233
2018-09-30 10:00 | 237 | 237
2018-09-30 10:30 | 239 | 239
2018-09-30 11:00 | 233 | 233
2018-09-30 11:30 | 237 | 237
2018-09-30 12:00 | 237 | 237
2018-09-30 12:30 | 236 | 236
2018-09-30 13:00 | 219 | 219
2018-09-30 13:30 | 193 | 193
2018-09-30 14:00 | 200 | 199
2018-09-30 14:30 | 204 | 203
2018-09-30 15:00 | 208 | 208
2018-09-30 15:30 | 206 | 206
2018-09-30 16:00 | 213 | 212
2018-09-30 16:30 | 227 | 227
2018-09-30 17:00 | 236 | 236
2018-09-30 17:30 | 249 | 249
2018-09-30 18:00 | 267 | 266
2018-09-30 18:30 | 266 | 264
2018-09-30 19:00 | 253 | 250
2018-09-30 19:30 | 247 | 243
2018-09-30 20:00 | 238 | 236
2018-09-30 20:30 | 229 | 228
2018-09-30 21:00 | 218 | 218
2018-09-30 21:30 | 215 | 214
2018-09-30 22:00 | 214 | 213
2018-09-30 22:30 | 213 | 212
2018-09-30 23:00 | 204 | 203
2018-09-30 23:30 | 193 | 191
2018-10-01 | 179 | 177
2018-10-01 00:30 | 173 | 170
2018-10-01 01:00 | 167 | 164
2018-10-01 01:30 | 164 | 161
2018-10-01 02:00 | 160 | 157
2018-10-01 02:30 | 158 | 155
2018-10-01 03:00 | 154 | 151
2018-10-01 03:30 | 151 | 150
2018-10-01 04:00 | 152 | 151
2018-10-01 04:30 | 153 | 152
2018-10-01 05:00 | 162 | 161
2018-10-01 05:30 | 165 | 164
2018-10-01 06:00 | 169 | 168
2018-10-01 06:30 | 170 | 169
2018-10-01 07:00 | 174 | 174
2018-10-01 07:30 | 175 | 175
2018-10-01 08:00 | 179 | 179
2018-10-01 08:30 | 178 | 178
2018-10-01 09:00 | 179 | 179
2018-10-01 09:30 | 179 | 179
2018-10-01 10:00 | 179 | 179
2018-10-01 10:30 | 174 | 173
2018-10-01 11:00 | 169 | 169
2018-10-01 11:30 | 170 | 170
2018-10-01 12:00 | 172 | 172
2018-10-01 12:30 | 169 | 169
2018-10-01 13:00 | 166 | 166
2018-10-01 13:30 | 167 | 167
2018-10-01 14:00 | 171 | 171
2018-10-01 14:30 | 180 | 180
2018-10-01 15:00 | 192 | 191
2018-10-01 15:30 | 204 | 204
2018-10-01 16:00 | 221 | 221
2018-10-01 16:30 | 236 | 236
2018-10-01 17:00 | 245 | 245
2018-10-01 17:30 | 258 | 258
2018-10-01 18:00 | 280 | 278
2018-10-01 18:30 | 282 | 281
2018-10-01 19:00 | 269 | 267
2018-10-01 19:30 | 260 | 257
2018-10-01 20:00 | 249 | 246
2018-10-01 20:30 | 238 | 238
2018-10-01 21:00 | 230 | 229
2018-10-01 21:30 | 222 | 221
2018-10-01 22:00 | 220 | 219
2018-10-01 22:30 | 220 | 219
2018-10-01 23:00 | 209 | 208
2018-10-01 23:30 | 198 | 196
2018-10-02 | 184 | 182
2018-10-02 00:30 | 175 | 173
2018-10-02 01:00 | 169 | 166
2018-10-02 01:30 | 164 | 161
2018-10-02 02:00 | 159 | 156
2018-10-02 02:30 | 157 | 154
2018-10-02 03:00 | 157 | 154
2018-10-02 03:30 | 158 | 155
2018-10-02 04:00 | 162 | 159
2018-10-02 04:30 | 168 | 166
2018-10-02 05:00 | 180 | 178
2018-10-02 05:30 | 190 | 189
2018-10-02 06:00 | 205 | 204
2018-10-02 06:30 | 211 | 211
2018-10-02 07:00 | 219 | 219
2018-10-02 07:30 | 218 | 218
2018-10-02 08:00 | 214 | 214
2018-10-02 08:30 | 211 | 210
2018-10-02 09:00 | 216 | 216
2018-10-02 09:30 | 218 | 218
2018-10-02 10:00 | 213 | 213
2018-10-02 10:30 | 206 | 206
2018-10-02 11:00 | 201 | 200
2018-10-02 11:30 | 196 | 196
2018-10-02 12:00 | 189 | 189
2018-10-02 12:30 | 188 | 188
2018-10-02 13:00 | 188 | 188
2018-10-02 13:30 | 190 | 190
2018-10-02 14:00 | 200 | 199
2018-10-02 14:30 | 207 | 207
2018-10-02 15:00 | 218 | 217
2018-10-02 15:30 | 231 | 231
2018-10-02 16:00 | 242 | 242
2018-10-02 16:30 | 253 | 253
2018-10-02 17:00 | 266 | 266
2018-10-02 17:30 | 276 | 274
2018-10-02 18:00 | 292 | 291
2018-10-02 18:30 | 289 | 289
2018-10-02 19:00 | 281 | 280
2018-10-02 19:30 | 269 | 269
2018-10-02 20:00 | 265 | 265
2018-10-02 20:30 | 253 | 252
2018-10-02 21:00 | 241 | 241
2018-10-02 21:30 | 229 | 229
2018-10-02 22:00 | 223 | 223
2018-10-02 22:30 | 221 | 221
2018-10-02 23:00 | 214 | 214
2018-10-02 23:30 | 196 | 196
2018-10-03 | 177 | 176
2018-10-03 00:30 | 167 | 167
2018-10-03 01:00 | 160 | 159
2018-10-03 01:30 | 161 | 161
2018-10-03 02:00 | 158 | 157
2018-10-03 02:30 | 152 | 152
2018-10-03 03:00 | 152 | 152
2018-10-03 03:30 | 152 | 152
2018-10-03 04:00 | 153 | 153
2018-10-03 04:30 | 155 | 155
2018-10-03 05:00 | 162 | 162
2018-10-03 05:30 | 170 | 170
2018-10-03 06:00 | 182 | 182
2018-10-03 06:30 | 194 | 194
2018-10-03 07:00 | 208 | 208
2018-10-03 07:30 | 209 | 209
2018-10-03 08:00 | 213 | 212
2018-10-03 08:30 | 199 | 198
2018-10-03 09:00 | 192 | 191
2018-10-03 09:30 | 184 | 184
2018-10-03 10:00 | 182 | 182
2018-10-03 10:30 | 174 | 174
2018-10-03 11:00 | 169 | 169
2018-10-03 11:30 | 165 | 165
2018-10-03 12:00 | 164 | 164
2018-10-03 12:30 | 165 | 165
2018-10-03 13:00 | 167 | 167
2018-10-03 13:30 | 173 | 173
2018-10-03 14:00 | 198 | 198
2018-10-03 14:30 | 213 | 213
2018-10-03 15:00 | 224 | 224
2018-10-03 15:30 | 238 | 238
2018-10-03 16:00 | 248 | 248
2018-10-03 16:30 | 262 | 262
2018-10-03 17:00 | 271 | 271
2018-10-03 17:30 | 278 | 278
2018-10-03 18:00 | 293 | 293
2018-10-03 18:30 | 296 | 296
2018-10-03 19:00 | 285 | 285
2018-10-03 19:30 | 275 | 274
2018-10-03 20:00 | 268 | 268
2018-10-03 20:30 | 258 | 258
2018-10-03 21:00 | 244 | 243
2018-10-03 21:30 | 228 | 227
2018-10-03 22:00 | 221 | 221
2018-10-03 22:30 | 220 | 220
2018-10-03 23:00 | 214 | 214
2018-10-03 23:30 | 199 | 199
2018-10-04 | 179 | 179
2018-10-04 00:30 | 172 | 172
2018-10-04 01:00 | 164 | 163
2018-10-04 01:30 | 156 | 155
2018-10-04 02:00 | 151 | 150
2018-10-04 02:30 | 149 | 148
2018-10-04 03:00 | 148 | 147
2018-10-04 03:30 | 150 | 150
2018-10-04 04:00 | 152 | 151
2018-10-04 04:30 | 159 | 158
2018-10-04 05:00 | 167 | 167
2018-10-04 05:30 | 171 | 171
2018-10-04 06:00 | 186 | 186
2018-10-04 06:30 | 196 | 196
2018-10-04 07:00 | 198 | 197
2018-10-04 07:30 | 199 | 198
2018-10-04 08:00 | 192 | 192
2018-10-04 08:30 | 187 | 187
2018-10-04 09:00 | 181 | 181
2018-10-04 09:30 | 176 | 176
2018-10-04 10:00 | 175 | 175
2018-10-04 10:30 | 170 | 170
2018-10-04 11:00 | 168 | 168
2018-10-04 11:30 | 167 | 167
2018-10-04 12:00 | 167 | 167
2018-10-04 12:30 | 168 | 168
2018-10-04 13:00 | 171 | 171
2018-10-04 13:30 | 184 | 184
2018-10-04 14:00 | 192 | 192
2018-10-04 14:30 | 199 | 199
2018-10-04 15:00 | 209 | 209
2018-10-04 15:30 | 221 | 221
2018-10-04 16:00 | 232 | 232
2018-10-04 16:30 | 247 | 247
2018-10-04 17:00 | 256 | 256
2018-10-04 17:30 | 266 | 266
2018-10-04 18:00 | 287 | 287
2018-10-04 18:30 | 292 | 292
2018-10-04 19:00 | 281 | 281
2018-10-04 19:30 | 266 | 266
2018-10-04 20:00 | 267 | 267
2018-10-04 20:30 | 252 | 251
2018-10-04 21:00 | 236 | 235
2018-10-04 21:30 | 223 | 223
2018-10-04 22:00 | 218 | 218
2018-10-04 22:30 | 213 | 213
2018-10-04 23:00 | 201 | 201
2018-10-04 23:30 | 188 | 187
2018-10-05 | 171 | 171
2018-10-05 00:30 | 164 | 164
2018-10-05 01:00 | 157 | 157
2018-10-05 01:30 | 154 | 153
2018-10-05 02:00 | 150 | 150
2018-10-05 02:30 | 147 | 147
2018-10-05 03:00 | 144 | 143
2018-10-05 03:30 | 144 | 143
2018-10-05 04:00 | 142 | 142
2018-10-05 04:30 | 150 | 150
2018-10-05 05:00 | 151 | 150
2018-10-05 05:30 | 158 | 157
2018-10-05 06:00 | 183 | 182
2018-10-05 06:30 | 199 | 199
2018-10-05 07:00 | 222 | 220
2018-10-05 07:30 | 227 | 224
2018-10-05 08:00 | 225 | 223
2018-10-05 08:30 | 222 | 221
2018-10-05 09:00 | 223 | 221
2018-10-05 09:30 | 207 | 206
2018-10-05 10:00 | 208 | 207
2018-10-05 10:30 | 215 | 214
2018-10-05 11:00 | 215 | 215
2018-10-05 11:30 | 221 | 220
2018-10-05 12:00 | 228 | 228
2018-10-05 12:30 | 224 | 223
2018-10-05 13:00 | 220 | 219
2018-10-05 13:30 | 219 | 218
2018-10-05 14:00 | 234 | 234
2018-10-05 14:30 | 247 | 245
2018-10-05 15:00 | 246 | 244
2018-10-05 15:30 | 254 | 252
2018-10-05 16:00 | 256 | 255
2018-10-05 16:30 | 256 | 254
2018-10-05 17:00 | 260 | 258
2018-10-05 17:30 | 260 | 258
2018-10-05 18:00 | 264 | 262
2018-10-05 18:30 | 267 | 265
2018-10-05 19:00 | 263 | 261
2018-10-05 19:30 | 261 | 258
2018-10-05 20:00 | 257 | 253
2018-10-05 20:30 | 249 | 245
2018-10-05 21:00 | 242 | 238
2018-10-05 21:30 | 233 | 231
2018-10-05 22:00 | 232 | 230
2018-10-05 22:30 | 231 | 229
2018-10-05 23:00 | 223 | 221
2018-10-05 23:30 | 213 | 210
2018-10-06 | 199 | 195
2018-10-06 00:30 | 189 | 184
2018-10-06 01:00 | 180 | 174
2018-10-06 01:30 | 176 | 169
2018-10-06 02:00 | 176 | 169
2018-10-06 02:30 | 175 | 169
2018-10-06 03:00 | 174 | 168
2018-10-06 03:30 | 174 | 168
2018-10-06 04:00 | 173 | 167
2018-10-06 04:30 | 176 | 169
2018-10-06 05:00 | 182 | 176
2018-10-06 05:30 | 180 | 173
2018-10-06 06:00 | 186 | 180
2018-10-06 06:30 | 192 | 188
2018-10-06 07:00 | 202 | 198
2018-10-06 07:30 | 218 | 216
2018-10-06 08:00 | 231 | 230
2018-10-06 08:30 | 238 | 237
2018-10-06 09:00 | 255 | 254
2018-10-06 09:30 | 258 | 257
2018-10-06 10:00 | 246 | 246
2018-10-06 10:30 | 241 | 241
2018-10-06 11:00 | 237 | 237
2018-10-06 11:30 | 230 | 230
2018-10-06 12:00 | 232 | 231
2018-10-06 12:30 | 235 | 235
2018-10-06 13:00 | 243 | 242
2018-10-06 13:30 | 247 | 246
2018-10-06 14:00 | 243 | 242
2018-10-06 14:30 | 253 | 253
2018-10-06 15:00 | 252 | 251
2018-10-06 15:30 | 235 | 234
2018-10-06 16:00 | 232 | 231
2018-10-06 16:30 | 240 | 239
2018-10-06 17:00 | 251 | 250
2018-10-06 17:30 | 260 | 260
2018-10-06 18:00 | 280 | 279
2018-10-06 18:30 | 283 | 282
2018-10-06 19:00 | 257 | 257
2018-10-06 19:30 | 250 | 250
2018-10-06 20:00 | 249 | 249
2018-10-06 20:30 | 244 | 244
2018-10-06 21:00 | 239 | 238
2018-10-06 21:30 | 232 | 232
2018-10-06 22:00 | 230 | 229
2018-10-06 22:30 | 224 | 223
2018-10-06 23:00 | 209 | 208
2018-10-06 23:30 | 194 | 192
2018-10-07 | 183 | 181
2018-10-07 00:30 | 173 | 172
2018-10-07 01:00 | 169 | 168
2018-10-07 01:30 | 167 | 167
2018-10-07 02:00 | 167 | 166
2018-10-07 02:30 | 164 | 164
2018-10-07 03:00 | 166 | 166
2018-10-07 03:30 | 164 | 164
2018-10-07 04:00 | 164 | 163
2018-10-07 04:30 | 166 | 165
2018-10-07 05:00 | 164 | 163
2018-10-07 05:30 | 166 | 165
2018-10-07 06:00 | 168 | 167
2018-10-07 06:30 | 171 | 171
2018-10-07 07:00 | 175 | 175
2018-10-07 07:30 | 178 | 178
2018-10-07 08:00 | 180 | 180
2018-10-07 08:30 | 184 | 184
2018-10-07 09:00 | 188 | 188
2018-10-07 09:30 | 189 | 189
2018-10-07 10:00 | 183 | 183
2018-10-07 10:30 | 182 | 181
2018-10-07 11:00 | 179 | 179
2018-10-07 11:30 | 179 | 178
2018-10-07 12:00 | 179 | 179
2018-10-07 12:30 | 180 | 180
2018-10-07 13:00 | 179 | 179
2018-10-07 13:30 | 185 | 185
2018-10-07 14:00 | 193 | 193
2018-10-07 14:30 | 205 | 204
2018-10-07 15:00 | 209 | 208
2018-10-07 15:30 | 213 | 213
2018-10-07 16:00 | 221 | 220
2018-10-07 16:30 | 235 | 235
2018-10-07 17:00 | 245 | 245
2018-10-07 17:30 | 249 | 249
2018-10-07 18:00 | 258 | 257
2018-10-07 18:30 | 258 | 258
2018-10-07 19:00 | 253 | 252
2018-10-07 19:30 | 248 | 248
2018-10-07 20:00 | 237 | 237
2018-10-07 20:30 | 227 | 227
2018-10-07 21:00 | 217 | 217
2018-10-07 21:30 | 205 | 205
2018-10-07 22:00 | 201 | 201
2018-10-07 22:30 | 201 | 201
2018-10-07 23:00 | 191 | 191
2018-10-07 23:30 | 183 | 183
2018-10-08 | 175 | 175
2018-10-08 00:30 | 172 | 172
2018-10-08 01:00 | 165 | 164
2018-10-08 01:30 | 160 | 159
2018-10-08 02:00 | 159 | 158
2018-10-08 02:30 | 158 | 157
2018-10-08 03:00 | 160 | 159
2018-10-08 03:30 | 160 | 159
2018-10-08 04:00 | 169 | 169
2018-10-08 04:30 | 171 | 171
2018-10-08 05:00 | 181 | 180
2018-10-08 05:30 | 193 | 193
2018-10-08 06:00 | 204 | 204
2018-10-08 06:30 | 215 | 215
2018-10-08 07:00 | 229 | 228
2018-10-08 07:30 | 232 | 230
2018-10-08 08:00 | 235 | 234
2018-10-08 08:30 | 207 | 206
2018-10-08 09:00 | 201 | 201
2018-10-08 09:30 | 195 | 195
2018-10-08 10:00 | 190 | 190
2018-10-08 10:30 | 187 | 186
2018-10-08 11:00 | 187 | 187
2018-10-08 11:30 | 192 | 192
2018-10-08 12:00 | 192 | 192
2018-10-08 12:30 | 193 | 193
2018-10-08 13:00 | 203 | 203
2018-10-08 13:30 | 219 | 219
2018-10-08 14:00 | 244 | 244
2018-10-08 14:30 | 244 | 244
2018-10-08 15:00 | 230 | 230
2018-10-08 15:30 | 246 | 245
2018-10-08 16:00 | 267 | 266
2018-10-08 16:30 | 273 | 272
2018-10-08 17:00 | 284 | 283
2018-10-08 17:30 | 286 | 285
2018-10-08 18:00 | 290 | 290
2018-10-08 18:30 | 288 | 288
2018-10-08 19:00 | 282 | 281
2018-10-08 19:30 | 276 | 274
2018-10-08 20:00 | 267 | 267
2018-10-08 20:30 | 254 | 254
2018-10-08 21:00 | 242 | 242
2018-10-08 21:30 | 235 | 235
2018-10-08 22:00 | 229 | 229
2018-10-08 22:30 | 224 | 224
2018-10-08 23:00 | 214 | 213
2018-10-08 23:30 | 197 | 196
2018-10-09 | 180 | 178
2018-10-09 00:30 | 177 | 175
2018-10-09 01:00 | 175 | 173
2018-10-09 01:30 | 164 | 162
2018-10-09 02:00 | 157 | 156
2018-10-09 02:30 | 152 | 151
2018-10-09 03:00 | 154 | 153
2018-10-09 03:30 | 158 | 157
2018-10-09 04:00 | 163 | 163
2018-10-09 04:30 | 171 | 170
2018-10-09 05:00 | 176 | 175
2018-10-09 05:30 | 182 | 182
2018-10-09 06:00 | 200 | 200
2018-10-09 06:30 | 216 | 216
2018-10-09 07:00 | 223 | 222
2018-10-09 07:30 | 212 | 212
2018-10-09 08:00 | 203 | 202
2018-10-09 08:30 | 206 | 205
2018-10-09 09:00 | 213 | 213
2018-10-09 09:30 | 212 | 212
2018-10-09 10:00 | 224 | 223
2018-10-09 10:30 | 223 | 223
2018-10-09 11:00 | 224 | 224
2018-10-09 11:30 | 196 | 195
2018-10-09 12:00 | 194 | 194
2018-10-09 12:30 | 184 | 183
2018-10-09 13:00 | 192 | 192
2018-10-09 13:30 | 205 | 205
2018-10-09 14:00 | 213 | 213
2018-10-09 14:30 | 220 | 220
2018-10-09 15:00 | 233 | 233
2018-10-09 15:30 | 232 | 232
2018-10-09 16:00 | 246 | 246
2018-10-09 16:30 | 256 | 256
2018-10-09 17:00 | 260 | 260
2018-10-09 17:30 | 268 | 268
2018-10-09 18:00 | 276 | 276
2018-10-09 18:30 | 274 | 274
2018-10-09 19:00 | 270 | 269
2018-10-09 19:30 | 264 | 264
2018-10-09 20:00 | 258 | 258
2018-10-09 20:30 | 253 | 253
2018-10-09 21:00 | 241 | 240
2018-10-09 21:30 | 225 | 224
2018-10-09 22:00 | 217 | 216
2018-10-09 22:30 | 215 | 213
2018-10-09 23:00 | 202 | 200
2018-10-09 23:30 | 192 | 189
2018-10-10 | 175 | 173
2018-10-10 00:30 | 170 | 168
2018-10-10 01:00 | 166 | 163
2018-10-10 01:30 | 157 | 156
2018-10-10 02:00 | 155 | 154
2018-10-10 02:30 | 146 | 145
2018-10-10 03:00 | 143 | 142
2018-10-10 03:30 | 143 | 142
2018-10-10 04:00 | 145 | 144
2018-10-10 04:30 | 157 | 156
2018-10-10 05:00 | 171 | 170
2018-10-10 05:30 | 185 | 185
2018-10-10 06:00 | 202 | 202
2018-10-10 06:30 | 227 | 227
2018-10-10 07:00 | 235 | 235
2018-10-10 07:30 | 216 | 216
2018-10-10 08:00 | 205 | 205
2018-10-10 08:30 | 200 | 200
2018-10-10 09:00 | 202 | 201
2018-10-10 09:30 | 198 | 198
2018-10-10 10:00 | 198 | 197
2018-10-10 10:30 | 197 | 196
2018-10-10 11:00 | 195 | 193
2018-10-10 11:30 | 196 | 194
2018-10-10 12:00 | 197 | 195
2018-10-10 12:30 | 200 | 198
2018-10-10 13:00 | 207 | 205
2018-10-10 13:30 | 216 | 215
2018-10-10 14:00 | 225 | 225
2018-10-10 14:30 | 241 | 241
2018-10-10 15:00 | 248 | 246
2018-10-10 15:30 | 258 | 256
2018-10-10 16:00 | 268 | 265
2018-10-10 16:30 | 274 | 271
2018-10-10 17:00 | 275 | 272
2018-10-10 17:30 | 281 | 277
2018-10-10 18:00 | 290 | 288
2018-10-10 18:30 | 291 | 290
2018-10-10 19:00 | 281 | 279
2018-10-10 19:30 | 275 | 275
2018-10-10 20:00 | 264 | 263
2018-10-10 20:30 | 244 | 244
2018-10-10 21:00 | 231 | 231
2018-10-10 21:30 | 215 | 215
2018-10-10 22:00 | 212 | 212
2018-10-10 22:30 | 208 | 207
2018-10-10 23:00 | 200 | 199
2018-10-10 23:30 | 190 | 188
2018-10-11 | 172 | 170
2018-10-11 00:30 | 165 | 163
2018-10-11 01:00 | 160 | 157
2018-10-11 01:30 | 155 | 152
2018-10-11 02:00 | 148 | 147
2018-10-11 02:30 | 144 | 143
2018-10-11 03:00 | 142 | 141
2018-10-11 03:30 | 141 | 140
2018-10-11 04:00 | 152 | 151
2018-10-11 04:30 | 159 | 158
2018-10-11 05:00 | 177 | 176
2018-10-11 05:30 | 192 | 192
2018-10-11 06:00 | 214 | 214
2018-10-11 06:30 | 238 | 238
2018-10-11 07:00 | 240 | 240
2018-10-11 07:30 | 236 | 236
2018-10-11 08:00 | 219 | 219
2018-10-11 08:30 | 215 | 215
2018-10-11 09:00 | 214 | 214
2018-10-11 09:30 | 217 | 217
2018-10-11 10:00 | 223 | 222
2018-10-11 10:30 | 234 | 233
2018-10-11 11:00 | 240 | 239
2018-10-11 11:30 | 243 | 242
2018-10-11 12:00 | 238 | 238
2018-10-11 12:30 | 250 | 249
2018-10-11 13:00 | 250 | 250
2018-10-11 13:30 | 225 | 225
2018-10-11 14:00 | 202 | 202
2018-10-11 14:30 | 224 | 224
2018-10-11 15:00 | 227 | 227
2018-10-11 15:30 | 237 | 237
2018-10-11 16:00 | 242 | 242
2018-10-11 16:30 | 257 | 257
2018-10-11 17:00 | 265 | 265
2018-10-11 17:30 | 283 | 283
2018-10-11 18:00 | 300 | 300
2018-10-11 18:30 | 291 | 290
2018-10-11 19:00 | 305 | 304
2018-10-11 19:30 | 310 | 309
2018-10-11 20:00 | 302 | 301
2018-10-11 20:30 | 255 | 255
2018-10-11 21:00 | 241 | 241
2018-10-11 21:30 | 218 | 218
2018-10-11 22:00 | 211 | 210
2018-10-11 22:30 | 209 | 208
2018-10-11 23:00 | 197 | 196
2018-10-11 23:30 | 185 | 183
2018-10-12 | 170 | 168
2018-10-12 00:30 | 156 | 153
2018-10-12 01:00 | 151 | 148
2018-10-12 01:30 | 149 | 145
2018-10-12 02:00 | 147 | 143
2018-10-12 02:30 | 145 | 141
2018-10-12 03:00 | 142 | 139
2018-10-12 03:30 | 142 | 140
2018-10-12 04:00 | 141 | 140
2018-10-12 04:30 | 148 | 147
2018-10-12 05:00 | 166 | 165
2018-10-12 05:30 | 185 | 185
2018-10-12 06:00 | 205 | 204
2018-10-12 06:30 | 221 | 220
2018-10-12 07:00 | 228 | 228
2018-10-12 07:30 | 233 | 233
2018-10-12 08:00 | 238 | 238
2018-10-12 08:30 | 237 | 237
2018-10-12 09:00 | 232 | 232
2018-10-12 09:30 | 239 | 239
2018-10-12 10:00 | 243 | 243
2018-10-12 10:30 | 247 | 247
2018-10-12 11:00 | 240 | 240
2018-10-12 11:30 | 228 | 227
2018-10-12 12:00 | 225 | 225
2018-10-12 12:30 | 233 | 233
2018-10-12 13:00 | 239 | 239
2018-10-12 13:30 | 251 | 250
2018-10-12 14:00 | 253 | 252
2018-10-12 14:30 | 254 | 253
2018-10-12 15:00 | 249 | 248
2018-10-12 15:30 | 252 | 251
2018-10-12 16:00 | 257 | 256
2018-10-12 16:30 | 266 | 265
2018-10-12 17:00 | 268 | 267
2018-10-12 17:30 | 274 | 274
2018-10-12 18:00 | 274 | 272
2018-10-12 18:30 | 275 | 273
2018-10-12 19:00 | 270 | 268
2018-10-12 19:30 | 255 | 254
2018-10-12 20:00 | 243 | 243
2018-10-12 20:30 | 235 | 235
2018-10-12 21:00 | 224 | 224
2018-10-12 21:30 | 221 | 221
2018-10-12 22:00 | 214 | 214
2018-10-12 22:30 | 219 | 218
2018-10-12 23:00 | 207 | 206
2018-10-12 23:30 | 193 | 191
2018-10-13 | 180 | 178
2018-10-13 00:30 | 169 | 166
2018-10-13 01:00 | 159 | 156
2018-10-13 01:30 | 153 | 151
2018-10-13 02:00 | 153 | 152
2018-10-13 02:30 | 153 | 152
2018-10-13 03:00 | 152 | 151
2018-10-13 03:30 | 148 | 147
2018-10-13 04:00 | 150 | 149
2018-10-13 04:30 | 150 | 149
2018-10-13 05:00 | 154 | 153
2018-10-13 05:30 | 161 | 160
2018-10-13 06:00 | 188 | 188
2018-10-13 06:30 | 207 | 207
2018-10-13 07:00 | 226 | 226
2018-10-13 07:30 | 221 | 220
2018-10-13 08:00 | 228 | 228
2018-10-13 08:30 | 229 | 229
2018-10-13 09:00 | 232 | 232
2018-10-13 09:30 | 238 | 238
2018-10-13 10:00 | 241 | 241
2018-10-13 10:30 | 233 | 233
2018-10-13 11:00 | 232 | 232
2018-10-13 11:30 | 233 | 233
2018-10-13 12:00 | 235 | 235
2018-10-13 12:30 | 233 | 233
2018-10-13 13:00 | 224 | 224
2018-10-13 13:30 | 222 | 222
2018-10-13 14:00 | 225 | 225
2018-10-13 14:30 | 225 | 225
2018-10-13 15:00 | 224 | 224
2018-10-13 15:30 | 229 | 229
2018-10-13 16:00 | 235 | 235
2018-10-13 16:30 | 234 | 234
2018-10-13 17:00 | 241 | 241
2018-10-13 17:30 | 254 | 253
2018-10-13 18:00 | 260 | 260
2018-10-13 18:30 | 265 | 264
2018-10-13 19:00 | 255 | 253
2018-10-13 19:30 | 244 | 243
2018-10-13 20:00 | 243 | 242
2018-10-13 20:30 | 241 | 240
2018-10-13 21:00 | 231 | 231
2018-10-13 21:30 | 225 | 224
2018-10-13 22:00 | 222 | 222
2018-10-13 22:30 | 220 | 219
2018-10-13 23:00 | 207 | 206
2018-10-13 23:30 | 200 | 199
2018-10-14 | 184 | 181
2018-10-14 00:30 | 180 | 177
2018-10-14 01:00 | 172 | 169
2018-10-14 01:30 | 166 | 163
2018-10-14 02:00 | 162 | 159
2018-10-14 02:30 | 157 | 153
2018-10-14 03:00 | 160 | 157
2018-10-14 03:30 | 158 | 155
2018-10-14 04:00 | 154 | 150
2018-10-14 04:30 | 153 | 149
2018-10-14 05:00 | 161 | 158
2018-10-14 05:30 | 167 | 164
2018-10-14 06:00 | 173 | 170
2018-10-14 06:30 | 178 | 176
2018-10-14 07:00 | 196 | 194
2018-10-14 07:30 | 213 | 212
2018-10-14 08:00 | 223 | 222
2018-10-14 08:30 | 229 | 229
2018-10-14 09:00 | 229 | 229
2018-10-14 09:30 | 232 | 232
2018-10-14 10:00 | 240 | 240
2018-10-14 10:30 | 233 | 232
2018-10-14 11:00 | 228 | 227
2018-10-14 11:30 | 229 | 229
2018-10-14 12:00 | 236 | 235
2018-10-14 12:30 | 231 | 230
2018-10-14 13:00 | 232 | 232
2018-10-14 13:30 | 235 | 234
2018-10-14 14:00 | 233 | 233
2018-10-14 14:30 | 237 | 237
2018-10-14 15:00 | 238 | 238
2018-10-14 15:30 | 239 | 239
2018-10-14 16:00 | 249 | 248
2018-10-14 16:30 | 266 | 266
2018-10-14 17:00 | 270 | 269
2018-10-14 17:30 | 272 | 272
2018-10-14 18:00 | 279 | 278
2018-10-14 18:30 | 282 | 282
2018-10-14 19:00 | 275 | 275
2018-10-14 19:30 | 264 | 264
2018-10-14 20:00 | 253 | 253
2018-10-14 20:30 | 239 | 239
2018-10-14 21:00 | 228 | 228
2018-10-14 21:30 | 221 | 221
2018-10-14 22:00 | 217 | 217
2018-10-14 22:30 | 219 | 219
2018-10-14 23:00 | 214 | 214
2018-10-14 23:30 | 204 | 204
2018-10-15 | 186 | 186
2018-10-15 00:30 | 176 | 176
2018-10-15 01:00 | 170 | 170
2018-10-15 01:30 | 166 | 166
2018-10-15 02:00 | 162 | 162
2018-10-15 02:30 | 158 | 157
2018-10-15 03:00 | 156 | 155
2018-10-15 03:30 | 158 | 157
2018-10-15 04:00 | 162 | 162
2018-10-15 04:30 | 167 | 166
2018-10-15 05:00 | 183 | 183
2018-10-15 05:30 | 203 | 203
2018-10-15 06:00 | 219 | 219
2018-10-15 06:30 | 242 | 242
2018-10-15 07:00 | 262 | 261
2018-10-15 07:30 | 264 | 263
2018-10-15 08:00 | 264 | 263
2018-10-15 08:30 | 267 | 266
2018-10-15 09:00 | 268 | 268
2018-10-15 09:30 | 267 | 267
2018-10-15 10:00 | 269 | 269
2018-10-15 10:30 | 275 | 275
2018-10-15 11:00 | 262 | 262
2018-10-15 11:30 | 260 | 260
2018-10-15 12:00 | 250 | 249
2018-10-15 12:30 | 243 | 242
2018-10-15 13:00 | 250 | 250
2018-10-15 13:30 | 260 | 259
2018-10-15 14:00 | 258 | 258
2018-10-15 14:30 | 256 | 255
2018-10-15 15:00 | 256 | 255
2018-10-15 15:30 | 259 | 259
2018-10-15 16:00 | 267 | 267
2018-10-15 16:30 | 281 | 281
2018-10-15 17:00 | 283 | 283
2018-10-15 17:30 | 289 | 289
2018-10-15 18:00 | 294 | 294
2018-10-15 18:30 | 293 | 292
2018-10-15 19:00 | 286 | 285
2018-10-15 19:30 | 285 | 283
2018-10-15 20:00 | 272 | 270
2018-10-15 20:30 | 263 | 260
2018-10-15 21:00 | 249 | 245
2018-10-15 21:30 | 238 | 233
2018-10-15 22:00 | 234 | 230
2018-10-15 22:30 | 232 | 228
2018-10-15 23:00 | 216 | 210
2018-10-15 23:30 | 210 | 202
2018-10-16 | 192 | 185
2018-10-16 00:30 | 182 | 176
2018-10-16 01:00 | 169 | 162
2018-10-16 01:30 | 167 | 160
2018-10-16 02:00 | 163 | 155
2018-10-16 02:30 | 160 | 152
2018-10-16 03:00 | 159 | 151
2018-10-16 03:30 | 167 | 160
2018-10-16 04:00 | 174 | 168
2018-10-16 04:30 | 176 | 170
2018-10-16 05:00 | 189 | 185
2018-10-16 05:30 | 206 | 202
2018-10-16 06:00 | 224 | 222
2018-10-16 06:30 | 237 | 236
2018-10-16 07:00 | 257 | 256
2018-10-16 07:30 | 262 | 262
2018-10-16 08:00 | 263 | 263
2018-10-16 08:30 | 260 | 260
2018-10-16 09:00 | 255 | 255
2018-10-16 09:30 | 250 | 250
2018-10-16 10:00 | 251 | 251
2018-10-16 10:30 | 239 | 239
2018-10-16 11:00 | 240 | 240
2018-10-16 11:30 | 241 | 241
2018-10-16 12:00 | 240 | 240
2018-10-16 12:30 | 237 | 237
2018-10-16 13:00 | 243 | 243
2018-10-16 13:30 | 252 | 252
2018-10-16 14:00 | 252 | 252
2018-10-16 14:30 | 251 | 251
2018-10-16 15:00 | 249 | 249
2018-10-16 15:30 | 262 | 262
2018-10-16 16:00 | 275 | 275
2018-10-16 16:30 | 280 | 280
2018-10-16 17:00 | 285 | 285
2018-10-16 17:30 | 287 | 287
2018-10-16 18:00 | 290 | 290
2018-10-16 18:30 | 286 | 286
2018-10-16 19:00 | 281 | 280
2018-10-16 19:30 | 280 | 280
2018-10-16 20:00 | 277 | 276
2018-10-16 20:30 | 263 | 262
2018-10-16 21:00 | 249 | 248
2018-10-16 21:30 | 236 | 235
2018-10-16 22:00 | 232 | 231
2018-10-16 22:30 | 235 | 234
2018-10-16 23:00 | 224 | 223
2018-10-16 23:30 | 216 | 215
2018-10-17 | 197 | 195
2018-10-17 00:30 | 187 | 185
2018-10-17 01:00 | 179 | 177
2018-10-17 01:30 | 173 | 171
2018-10-17 02:00 | 169 | 167
2018-10-17 02:30 | 163 | 162
2018-10-17 03:00 | 167 | 166
2018-10-17 03:30 | 171 | 171
2018-10-17 04:00 | 176 | 176
2018-10-17 04:30 | 179 | 179
2018-10-17 05:00 | 191 | 191
2018-10-17 05:30 | 203 | 203
2018-10-17 06:00 | 224 | 224
2018-10-17 06:30 | 242 | 242
2018-10-17 07:00 | 253 | 253
2018-10-17 07:30 | 262 | 261
2018-10-17 08:00 | 256 | 256
2018-10-17 08:30 | 255 | 255
2018-10-17 09:00 | 256 | 255
2018-10-17 09:30 | 247 | 246
2018-10-17 10:00 | 242 | 242
2018-10-17 10:30 | 242 | 242
2018-10-17 11:00 | 238 | 238
2018-10-17 11:30 | 240 | 240
2018-10-17 12:00 | 242 | 242
2018-10-17 12:30 | 246 | 246
2018-10-17 13:00 | 240 | 240
2018-10-17 13:30 | 254 | 254
2018-10-17 14:00 | 266 | 266
2018-10-17 14:30 | 264 | 264
2018-10-17 15:00 | 259 | 259
2018-10-17 15:30 | 273 | 273
2018-10-17 16:00 | 283 | 282
2018-10-17 16:30 | 287 | 287
2018-10-17 17:00 | 288 | 288
2018-10-17 17:30 | 294 | 294
2018-10-17 18:00 | 299 | 299
2018-10-17 18:30 | 302 | 302
2018-10-17 19:00 | 292 | 292
2018-10-17 19:30 | 288 | 288
2018-10-17 20:00 | 281 | 281
2018-10-17 20:30 | 273 | 273
2018-10-17 21:00 | 262 | 262
2018-10-17 21:30 | 255 | 254
2018-10-17 22:00 | 248 | 247
2018-10-17 22:30 | 245 | 244
2018-10-17 23:00 | 236 | 234
2018-10-17 23:30 | 223 | 221
2018-10-18 | 207 | 205
2018-10-18 00:30 | 194 | 193
2018-10-18 01:00 | 185 | 184
2018-10-18 01:30 | 183 | 181
2018-10-18 02:00 | 189 | 187
2018-10-18 02:30 | 188 | 186
2018-10-18 03:00 | 188 | 187
2018-10-18 03:30 | 191 | 189
2018-10-18 04:00 | 195 | 193
2018-10-18 04:30 | 196 | 194
2018-10-18 05:00 | 207 | 207
2018-10-18 05:30 | 223 | 222
2018-10-18 06:00 | 244 | 243
2018-10-18 06:30 | 262 | 261
2018-10-18 07:00 | 274 | 274
2018-10-18 07:30 | 276 | 275
2018-10-18 08:00 | 277 | 276
2018-10-18 08:30 | 279 | 279
2018-10-18 09:00 | 281 | 280
2018-10-18 09:30 | 271 | 271
2018-10-18 10:00 | 272 | 272
2018-10-18 10:30 | 272 | 272
2018-10-18 11:00 | 266 | 266
2018-10-18 11:30 | 270 | 270
2018-10-18 12:00 | 266 | 265
2018-10-18 12:30 | 262 | 262
2018-10-18 13:00 | 276 | 276
2018-10-18 13:30 | 276 | 276
2018-10-18 14:00 | 282 | 282
2018-10-18 14:30 | 292 | 292
2018-10-18 15:00 | 297 | 296
2018-10-18 15:30 | 300 | 299
2018-10-18 16:00 | 303 | 302
2018-10-18 16:30 | 298 | 297
2018-10-18 17:00 | 310 | 309
2018-10-18 17:30 | 326 | 325
2018-10-18 18:00 | 331 | 330
2018-10-18 18:30 | 316 | 314
2018-10-18 19:00 | 324 | 322
2018-10-18 19:30 | 297 | 296
2018-10-18 20:00 | 296 | 296
2018-10-18 20:30 | 283 | 283
2018-10-18 21:00 | 280 | 279
2018-10-18 21:30 | 260 | 259
2018-10-18 22:00 | 255 | 255
2018-10-18 22:30 | 251 | 251
2018-10-18 23:00 | 238 | 238
2018-10-18 23:30 | 225 | 225
2018-10-19 | 208 | 207
2018-10-19 00:30 | 197 | 196
2018-10-19 01:00 | 188 | 187
2018-10-19 01:30 | 188 | 187
2018-10-19 02:00 | 186 | 184
2018-10-19 02:30 | 184 | 182
2018-10-19 03:00 | 183 | 181
2018-10-19 03:30 | 183 | 181
2018-10-19 04:00 | 184 | 183
2018-10-19 04:30 | 191 | 190
2018-10-19 05:00 | 202 | 201
2018-10-19 05:30 | 181 | 179
2018-10-19 06:00 | 189 | 189
2018-10-19 06:30 | 202 | 202
2018-10-19 07:00 | 216 | 216
2018-10-19 07:30 | 219 | 219
2018-10-19 08:00 | 219 | 219
2018-10-19 08:30 | 218 | 218
2018-10-19 09:00 | 213 | 213
2018-10-19 09:30 | 208 | 207
2018-10-19 10:00 | 211 | 211
2018-10-19 10:30 | 216 | 216
2018-10-19 11:00 | 227 | 227
2018-10-19 11:30 | 224 | 223
2018-10-19 12:00 | 214 | 213
2018-10-19 12:30 | 237 | 236
2018-10-19 13:00 | 262 | 261
2018-10-19 13:30 | 263 | 262
2018-10-19 14:00 | 247 | 247
2018-10-19 14:30 | 247 | 247
2018-10-19 15:00 | 252 | 252
2018-10-19 15:30 | 261 | 261
2018-10-19 16:00 | 287 | 287
2018-10-19 16:30 | 278 | 278
2018-10-19 17:00 | 270 | 270
2018-10-19 17:30 | 274 | 273
2018-10-19 18:00 | 277 | 276
2018-10-19 18:30 | 281 | 281
2018-10-19 19:00 | 274 | 273
2018-10-19 19:30 | 267 | 267
2018-10-19 20:00 | 256 | 255
2018-10-19 20:30 | 246 | 246
2018-10-19 21:00 | 240 | 240
2018-10-19 21:30 | 230 | 230
2018-10-19 22:00 | 226 | 226
2018-10-19 22:30 | 222 | 222
2018-10-19 23:00 | 209 | 209
2018-10-19 23:30 | 199 | 198
2018-10-20 | 176 | 175
2018-10-20 00:30 | 164 | 164
2018-10-20 01:00 | 156 | 155
2018-10-20 01:30 | 150 | 149
2018-10-20 02:00 | 146 | 145
2018-10-20 02:30 | 142 | 142
2018-10-20 03:00 | 140 | 140
2018-10-20 03:30 | 140 | 140
2018-10-20 04:00 | 143 | 143
2018-10-20 04:30 | 147 | 147
2018-10-20 05:00 | 149 | 149
2018-10-20 05:30 | 164 | 164
2018-10-20 06:00 | 179 | 179
2018-10-20 06:30 | 196 | 196
2018-10-20 07:00 | 211 | 210
2018-10-20 07:30 | 222 | 222
2018-10-20 08:00 | 232 | 231
2018-10-20 08:30 | 230 | 230
2018-10-20 09:00 | 235 | 234
2018-10-20 09:30 | 234 | 234
2018-10-20 10:00 | 231 | 231
2018-10-20 10:30 | 225 | 224
2018-10-20 11:00 | 214 | 213
2018-10-20 11:30 | 198 | 197
2018-10-20 12:00 | 199 | 198
2018-10-20 12:30 | 195 | 194
2018-10-20 13:00 | 196 | 195
2018-10-20 13:30 | 193 | 192
2018-10-20 14:00 | 197 | 196
2018-10-20 14:30 | 201 | 200
2018-10-20 15:00 | 215 | 214
2018-10-20 15:30 | 226 | 225
2018-10-20 16:00 | 236 | 235
2018-10-20 16:30 | 246 | 245
2018-10-20 17:00 | 251 | 250
2018-10-20 17:30 | 249 | 248
2018-10-20 18:00 | 260 | 260
2018-10-20 18:30 | 266 | 266
2018-10-20 19:00 | 253 | 252
2018-10-20 19:30 | 267 | 267
2018-10-20 20:00 | 270 | 270
2018-10-20 20:30 | 254 | 253
2018-10-20 21:00 | 233 | 232
2018-10-20 21:30 | 218 | 218
2018-10-20 22:00 | 223 | 223
2018-10-20 22:30 | 225 | 225
2018-10-20 23:00 | 214 | 214
2018-10-20 23:30 | 196 | 196
2018-10-21 | 176 | 176
2018-10-21 00:30 | 166 | 166
2018-10-21 01:00 | 161 | 161
2018-10-21 01:30 | 157 | 157
2018-10-21 02:00 | 150 | 150
2018-10-21 02:30 | 151 | 151
2018-10-21 03:00 | 152 | 152
2018-10-21 03:30 | 150 | 150
2018-10-21 04:00 | 150 | 150
2018-10-21 04:30 | 153 | 153
2018-10-21 05:00 | 158 | 158
2018-10-21 05:30 | 165 | 165
2018-10-21 06:00 | 170 | 170
2018-10-21 06:30 | 179 | 179
2018-10-21 07:00 | 187 | 187
2018-10-21 07:30 | 191 | 191
2018-10-21 08:00 | 212 | 211
2018-10-21 08:30 | 210 | 209
2018-10-21 09:00 | 214 | 213
2018-10-21 09:30 | 207 | 206
2018-10-21 10:00 | 225 | 224
2018-10-21 10:30 | 211 | 211
2018-10-21 11:00 | 200 | 200
2018-10-21 11:30 | 202 | 202
2018-10-21 12:00 | 196 | 196
2018-10-21 12:30 | 203 | 203
2018-10-21 13:00 | 194 | 194
2018-10-21 13:30 | 212 | 212
2018-10-21 14:00 | 245 | 245
2018-10-21 14:30 | 254 | 253
2018-10-21 15:00 | 255 | 254
2018-10-21 15:30 | 260 | 260
2018-10-21 16:00 | 254 | 254
2018-10-21 16:30 | 259 | 259
2018-10-21 17:00 | 258 | 258
2018-10-21 17:30 | 252 | 252
2018-10-21 18:00 | 251 | 251
2018-10-21 18:30 | 255 | 255
2018-10-21 19:00 | 249 | 249
2018-10-21 19:30 | 251 | 251
2018-10-21 20:00 | 236 | 236
2018-10-21 20:30 | 227 | 227
2018-10-21 21:00 | 217 | 216
2018-10-21 21:30 | 207 | 207
2018-10-21 22:00 | 202 | 202
2018-10-21 22:30 | 198 | 198
2018-10-21 23:00 | 189 | 189
2018-10-21 23:30 | 180 | 180
2018-10-22 | 168 | 168
2018-10-22 00:30 | 168 | 167
2018-10-22 01:00 | 162 | 162
2018-10-22 01:30 | 157 | 157
2018-10-22 02:00 | 152 | 152
2018-10-22 02:30 | 142 | 142
2018-10-22 03:00 | 137 | 137
2018-10-22 03:30 | 138 | 137
2018-10-22 04:00 | 141 | 140
2018-10-22 04:30 | 150 | 149
2018-10-22 05:00 | 159 | 154
2018-10-22 05:30 | 168 | 164
2018-10-22 06:00 | 187 | 183
2018-10-22 06:30 | 202 | 197
2018-10-22 07:00 | 209 | 204
2018-10-22 07:30 | 207 | 203
2018-10-22 08:00 | 210 | 206
2018-10-22 08:30 | 218 | 213
2018-10-22 09:00 | 231 | 223
2018-10-22 09:30 | 229 | 221
2018-10-22 10:00 | 220 | 218
2018-10-22 10:30 | 215 | 215
2018-10-22 11:00 | 217 | 217
2018-10-22 11:30 | 217 | 217
2018-10-22 12:00 | 212 | 212
2018-10-22 12:30 | 212 | 212
2018-10-22 13:00 | 216 | 216
2018-10-22 13:30 | 217 | 217
2018-10-22 14:00 | 214 | 214
2018-10-22 14:30 | 217 | 217
2018-10-22 15:00 | 224 | 224
2018-10-22 15:30 | 230 | 230
2018-10-22 16:00 | 238 | 238
2018-10-22 16:30 | 248 | 248
2018-10-22 17:00 | 248 | 248
2018-10-22 17:30 | 252 | 252
2018-10-22 18:00 | 260 | 260
2018-10-22 18:30 | 264 | 264
2018-10-22 19:00 | 261 | 261
2018-10-22 19:30 | 259 | 258
2018-10-22 20:00 | 253 | 252
2018-10-22 20:30 | 239 | 239
2018-10-22 21:00 | 226 | 226
2018-10-22 21:30 | 210 | 210
2018-10-22 22:00 | 202 | 202
2018-10-22 22:30 | 202 | 202
2018-10-22 23:00 | 189 | 189
2018-10-22 23:30 | 176 | 176
2018-10-23 | 164 | 163
2018-10-23 00:30 | 159 | 159
2018-10-23 01:00 | 154 | 153
2018-10-23 01:30 | 153 | 152
2018-10-23 02:00 | 150 | 149
2018-10-23 02:30 | 150 | 149
2018-10-23 03:00 | 148 | 147
2018-10-23 03:30 | 149 | 148
2018-10-23 04:00 | 147 | 146
2018-10-23 04:30 | 145 | 144
2018-10-23 05:00 | 157 | 156
2018-10-23 05:30 | 175 | 175
2018-10-23 06:00 | 192 | 192
2018-10-23 06:30 | 208 | 208
2018-10-23 07:00 | 216 | 215
2018-10-23 07:30 | 212 | 212
2018-10-23 08:00 | 208 | 208
2018-10-23 08:30 | 203 | 202
2018-10-23 09:00 | 206 | 205
2018-10-23 09:30 | 208 | 208
2018-10-23 10:00 | 202 | 202
2018-10-23 10:30 | 197 | 197
2018-10-23 11:00 | 197 | 197
2018-10-23 11:30 | 197 | 197
2018-10-23 12:00 | 197 | 197
2018-10-23 12:30 | 199 | 199
2018-10-23 13:00 | 202 | 202
2018-10-23 13:30 | 207 | 207
2018-10-23 14:00 | 209 | 209
2018-10-23 14:30 | 212 | 212
2018-10-23 15:00 | 223 | 223
2018-10-23 15:30 | 243 | 243
2018-10-23 16:00 | 251 | 251
2018-10-23 16:30 | 260 | 260
2018-10-23 17:00 | 259 | 258
2018-10-23 17:30 | 263 | 262
2018-10-23 18:00 | 269 | 269
2018-10-23 18:30 | 278 | 278
2018-10-23 19:00 | 284 | 284
2018-10-23 19:30 | 272 | 271
2018-10-23 20:00 | 261 | 260
2018-10-23 20:30 | 243 | 243
2018-10-23 21:00 | 236 | 236
2018-10-23 21:30 | 219 | 219
2018-10-23 22:00 | 214 | 214
2018-10-23 22:30 | 212 | 212
2018-10-23 23:00 | 196 | 196
2018-10-23 23:30 | 182 | 181
2018-10-24 | 176 | 174
2018-10-24 00:30 | 169 | 168
2018-10-24 01:00 | 162 | 162
2018-10-24 01:30 | 160 | 160
2018-10-24 02:00 | 160 | 160
2018-10-24 02:30 | 159 | 158
2018-10-24 03:00 | 158 | 157
2018-10-24 03:30 | 159 | 159
2018-10-24 04:00 | 161 | 160
2018-10-24 04:30 | 164 | 164
2018-10-24 05:00 | 172 | 172
2018-10-24 05:30 | 195 | 195
2018-10-24 06:00 | 209 | 209
2018-10-24 06:30 | 224 | 224
2018-10-24 07:00 | 235 | 234
2018-10-24 07:30 | 236 | 236
2018-10-24 08:00 | 237 | 236
2018-10-24 08:30 | 235 | 235
2018-10-24 09:00 | 236 | 236
2018-10-24 09:30 | 237 | 237
2018-10-24 10:00 | 240 | 240
2018-10-24 10:30 | 244 | 244
2018-10-24 11:00 | 244 | 244
2018-10-24 11:30 | 249 | 248
2018-10-24 12:00 | 247 | 246
2018-10-24 12:30 | 251 | 251
2018-10-24 13:00 | 271 | 271
2018-10-24 13:30 | 268 | 268
2018-10-24 14:00 | 262 | 261
2018-10-24 14:30 | 265 | 265
2018-10-24 15:00 | 264 | 264
2018-10-24 15:30 | 275 | 275
2018-10-24 16:00 | 283 | 283
2018-10-24 16:30 | 286 | 285
2018-10-24 17:00 | 288 | 288
2018-10-24 17:30 | 289 | 289
2018-10-24 18:00 | 294 | 294
2018-10-24 18:30 | 300 | 300
2018-10-24 19:00 | 284 | 284
2018-10-24 19:30 | 268 | 268
2018-10-24 20:00 | 263 | 263
2018-10-24 20:30 | 252 | 252
2018-10-24 21:00 | 238 | 238
2018-10-24 21:30 | 225 | 225
2018-10-24 22:00 | 221 | 221
2018-10-24 22:30 | 218 | 217
2018-10-24 23:00 | 205 | 204
2018-10-24 23:30 | 193 | 192
2018-10-25 | 186 | 185
2018-10-25 00:30 | 176 | 175
2018-10-25 01:00 | 169 | 169
2018-10-25 01:30 | 167 | 167
2018-10-25 02:00 | 169 | 169
2018-10-25 02:30 | 170 | 170
2018-10-25 03:00 | 170 | 169
2018-10-25 03:30 | 173 | 172
2018-10-25 04:00 | 177 | 177
2018-10-25 04:30 | 179 | 179
2018-10-25 05:00 | 192 | 192
2018-10-25 05:30 | 198 | 198
2018-10-25 06:00 | 211 | 211
2018-10-25 06:30 | 229 | 229
2018-10-25 07:00 | 246 | 246
2018-10-25 07:30 | 257 | 257
2018-10-25 08:00 | 260 | 260
2018-10-25 08:30 | 251 | 251
2018-10-25 09:00 | 246 | 246
2018-10-25 09:30 | 251 | 250
2018-10-25 10:00 | 263 | 263
2018-10-25 10:30 | 260 | 260
2018-10-25 11:00 | 247 | 247
2018-10-25 11:30 | 236 | 235
2018-10-25 12:00 | 232 | 232
2018-10-25 12:30 | 231 | 230
2018-10-25 13:00 | 237 | 237
2018-10-25 13:30 | 245 | 244
2018-10-25 14:00 | 250 | 250
2018-10-25 14:30 | 250 | 250
2018-10-25 15:00 | 270 | 269
2018-10-25 15:30 | 269 | 269
2018-10-25 16:00 | 268 | 268
2018-10-25 16:30 | 271 | 271
2018-10-25 17:00 | 278 | 278
2018-10-25 17:30 | 281 | 281
2018-10-25 18:00 | 287 | 287
2018-10-25 18:30 | 289 | 289
2018-10-25 19:00 | 292 | 292
2018-10-25 19:30 | 302 | 302
2018-10-25 20:00 | 285 | 285
2018-10-25 20:30 | 275 | 274
2018-10-25 21:00 | 254 | 254
2018-10-25 21:30 | 240 | 240
2018-10-25 22:00 | 232 | 232
2018-10-25 22:30 | 231 | 231
2018-10-25 23:00 | 220 | 219
2018-10-25 23:30 | 202 | 202
2018-10-26 | 185 | 184
2018-10-26 00:30 | 175 | 174
2018-10-26 01:00 | 168 | 166
2018-10-26 01:30 | 167 | 166
2018-10-26 02:00 | 169 | 169
2018-10-26 02:30 | 166 | 165
2018-10-26 03:00 | 167 | 166
2018-10-26 03:30 | 167 | 166
2018-10-26 04:00 | 170 | 170
2018-10-26 04:30 | 176 | 175
2018-10-26 05:00 | 192 | 190
2018-10-26 05:30 | 213 | 212
2018-10-26 06:00 | 231 | 230
2018-10-26 06:30 | 246 | 245
2018-10-26 07:00 | 257 | 257
2018-10-26 07:30 | 260 | 259
2018-10-26 08:00 | 260 | 260
2018-10-26 08:30 | 263 | 263
2018-10-26 09:00 | 271 | 271
2018-10-26 09:30 | 267 | 266
2018-10-26 10:00 | 266 | 265
2018-10-26 10:30 | 264 | 263
2018-10-26 11:00 | 267 | 267
2018-10-26 11:30 | 271 | 270
2018-10-26 12:00 | 269 | 268
2018-10-26 12:30 | 278 | 278
2018-10-26 13:00 | 286 | 286
2018-10-26 13:30 | 292 | 292
2018-10-26 14:00 | 296 | 296
2018-10-26 14:30 | 302 | 302
2018-10-26 15:00 | 303 | 303
2018-10-26 15:30 | 308 | 307
2018-10-26 16:00 | 320 | 319
2018-10-26 16:30 | 323 | 323
2018-10-26 17:00 | 320 | 319
2018-10-26 17:30 | 310 | 310
2018-10-26 18:00 | 306 | 306
2018-10-26 18:30 | 308 | 308
2018-10-26 19:00 | 302 | 302
2018-10-26 19:30 | 291 | 291
2018-10-26 20:00 | 283 | 283
2018-10-26 20:30 | 272 | 272
2018-10-26 21:00 | 263 | 263
2018-10-26 21:30 | 254 | 254
2018-10-26 22:00 | 247 | 247
2018-10-26 22:30 | 243 | 243
2018-10-26 23:00 | 230 | 230
2018-10-26 23:30 | 207 | 206
2018-10-27 | 190 | 190
2018-10-27 00:30 | 182 | 182
2018-10-27 01:00 | 179 | 179
2018-10-27 01:30 | 178 | 177
2018-10-27 02:00 | 176 | 176
2018-10-27 02:30 | 176 | 176
2018-10-27 03:00 | 173 | 173
2018-10-27 03:30 | 172 | 171
2018-10-27 04:00 | 173 | 173
2018-10-27 04:30 | 173 | 173
2018-10-27 05:00 | 178 | 178
2018-10-27 05:30 | 183 | 183
2018-10-27 06:00 | 191 | 191
2018-10-27 06:30 | 201 | 200
2018-10-27 07:00 | 211 | 211
2018-10-27 07:30 | 218 | 217
2018-10-27 08:00 | 219 | 219
2018-10-27 08:30 | 223 | 223
2018-10-27 09:00 | 226 | 226
2018-10-27 09:30 | 225 | 224
2018-10-27 10:00 | 224 | 224
2018-10-27 10:30 | 219 | 218
2018-10-27 11:00 | 208 | 207
2018-10-27 11:30 | 205 | 204
2018-10-27 12:00 | 203 | 202
2018-10-27 12:30 | 206 | 205
2018-10-27 13:00 | 210 | 209
2018-10-27 13:30 | 213 | 212
2018-10-27 14:00 | 216 | 215
2018-10-27 14:30 | 222 | 221
2018-10-27 15:00 | 233 | 232
2018-10-27 15:30 | 244 | 243
2018-10-27 16:00 | 251 | 250
2018-10-27 16:30 | 262 | 261
2018-10-27 17:00 | 266 | 265
2018-10-27 17:30 | 266 | 265
2018-10-27 18:00 | 272 | 271
2018-10-27 18:30 | 280 | 280
2018-10-27 19:00 | 278 | 277
2018-10-27 19:30 | 273 | 272
2018-10-27 20:00 | 263 | 263
2018-10-27 20:30 | 251 | 251
2018-10-27 21:00 | 243 | 243
2018-10-27 21:30 | 232 | 232
2018-10-27 22:00 | 233 | 233
2018-10-27 22:30 | 233 | 233
2018-10-27 23:00 | 214 | 213
2018-10-27 23:30 | 197 | 197
2018-10-28 | 183 | 183
2018-10-28 00:30 | 177 | 177
2018-10-28 01:00 | 175 | 175
2018-10-28 01:30 | 171 | 171
2018-10-28 02:00 | 170 | 170
2018-10-28 02:30 | 171 | 170
2018-10-28 03:00 | 169 | 168
2018-10-28 03:30 | 169 | 169
2018-10-28 04:00 | 167 | 167
2018-10-28 04:30 | 168 | 168
2018-10-28 05:00 | 170 | 170
2018-10-28 05:30 | 175 | 175
2018-10-28 06:00 | 180 | 180
2018-10-28 06:30 | 186 | 185
2018-10-28 07:00 | 202 | 201
2018-10-28 07:30 | 204 | 204
2018-10-28 08:00 | 217 | 217
2018-10-28 08:30 | 221 | 221
2018-10-28 09:00 | 210 | 209
2018-10-28 09:30 | 231 | 231
2018-10-28 10:00 | 208 | 208
2018-10-28 10:30 | 210 | 209
2018-10-28 11:00 | 208 | 208
2018-10-28 11:30 | 205 | 204
2018-10-28 12:00 | 206 | 206
2018-10-28 12:30 | 206 | 206
2018-10-28 13:00 | 212 | 211
2018-10-28 13:30 | 218 | 217
2018-10-28 14:00 | 219 | 219
2018-10-28 14:30 | 231 | 230
2018-10-28 15:00 | 232 | 232
2018-10-28 15:30 | 238 | 238
2018-10-28 16:00 | 250 | 249
2018-10-28 16:30 | 254 | 253
2018-10-28 17:00 | 260 | 259
2018-10-28 17:30 | 260 | 259
2018-10-28 18:00 | 261 | 260
2018-10-28 18:30 | 260 | 260
2018-10-28 19:00 | 256 | 255
2018-10-28 19:30 | 250 | 249
2018-10-28 20:00 | 238 | 237
2018-10-28 20:30 | 221 | 221
2018-10-28 21:00 | 210 | 209
2018-10-28 21:30 | 200 | 200
2018-10-28 22:00 | 198 | 198
2018-10-28 22:30 | 196 | 196
2018-10-28 23:00 | 186 | 185
2018-10-28 23:30 | 176 | 176
2018-10-29 | 165 | 164
2018-10-29 00:30 | 158 | 158
2018-10-29 01:00 | 156 | 155
2018-10-29 01:30 | 151 | 151
2018-10-29 02:00 | 151 | 151
2018-10-29 02:30 | 146 | 146
2018-10-29 03:00 | 144 | 144
2018-10-29 03:30 | 145 | 145
2018-10-29 04:00 | 148 | 148
2018-10-29 04:30 | 156 | 156
2018-10-29 05:00 | 173 | 173
2018-10-29 05:30 | 186 | 186
2018-10-29 06:00 | 208 | 207
2018-10-29 06:30 | 227 | 227
2018-10-29 07:00 | 242 | 242
2018-10-29 07:30 | 251 | 251
2018-10-29 08:00 | 257 | 257
2018-10-29 08:30 | 263 | 262
2018-10-29 09:00 | 264 | 263
2018-10-29 09:30 | 265 | 265
2018-10-29 10:00 | 258 | 258
2018-10-29 10:30 | 257 | 257
2018-10-29 11:00 | 249 | 249
2018-10-29 11:30 | 245 | 244
2018-10-29 12:00 | 245 | 245
2018-10-29 12:30 | 246 | 245
2018-10-29 13:00 | 245 | 245
2018-10-29 13:30 | 244 | 243
2018-10-29 14:00 | 237 | 236
2018-10-29 14:30 | 239 | 239
2018-10-29 15:00 | 246 | 245
2018-10-29 15:30 | 255 | 255
2018-10-29 16:00 | 259 | 258
2018-10-29 16:30 | 266 | 265
2018-10-29 17:00 | 267 | 266
2018-10-29 17:30 | 274 | 273
2018-10-29 18:00 | 276 | 275
2018-10-29 18:30 | 280 | 279
2018-10-29 19:00 | 270 | 269
2018-10-29 19:30 | 257 | 256
2018-10-29 20:00 | 243 | 243
2018-10-29 20:30 | 227 | 227
2018-10-29 21:00 | 215 | 215
2018-10-29 21:30 | 206 | 205
2018-10-29 22:00 | 199 | 198
2018-10-29 22:30 | 195 | 194
2018-10-29 23:00 | 183 | 183
2018-10-29 23:30 | 173 | 172
2018-10-30 | 157 | 157
2018-10-30 00:30 | 149 | 148
2018-10-30 01:00 | 147 | 146
2018-10-30 01:30 | 145 | 144
2018-10-30 02:00 | 145 | 144
2018-10-30 02:30 | 145 | 145
2018-10-30 03:00 | 143 | 143
2018-10-30 03:30 | 143 | 143
2018-10-30 04:00 | 143 | 143
2018-10-30 04:30 | 146 | 146
2018-10-30 05:00 | 155 | 155
2018-10-30 05:30 | 176 | 176
2018-10-30 06:00 | 195 | 195
2018-10-30 06:30 | 211 | 211
2018-10-30 07:00 | 220 | 220
2018-10-30 07:30 | 219 | 219
2018-10-30 08:00 | 218 | 217
2018-10-30 08:30 | 218 | 217
2018-10-30 09:00 | 224 | 224
2018-10-30 09:30 | 226 | 226
2018-10-30 10:00 | 229 | 228
2018-10-30 10:30 | 224 | 223
2018-10-30 11:00 | 213 | 212
2018-10-30 11:30 | 205 | 204
2018-10-30 12:00 | 205 | 204
2018-10-30 12:30 | 199 | 199
2018-10-30 13:00 | 195 | 195
2018-10-30 13:30 | 197 | 197
2018-10-30 14:00 | 202 | 201
2018-10-30 14:30 | 215 | 214
2018-10-30 15:00 | 225 | 225
2018-10-30 15:30 | 229 | 229
2018-10-30 16:00 | 249 | 249
2018-10-30 16:30 | 259 | 259
2018-10-30 17:00 | 265 | 265
2018-10-30 17:30 | 267 | 267
2018-10-30 18:00 | 272 | 272
2018-10-30 18:30 | 282 | 282
2018-10-30 19:00 | 275 | 275
2018-10-30 19:30 | 272 | 272
2018-10-30 20:00 | 260 | 259
2018-10-30 20:30 | 245 | 245
2018-10-30 21:00 | 234 | 234
2018-10-30 21:30 | 224 | 224
2018-10-30 22:00 | 216 | 216
2018-10-30 22:30 | 211 | 211
2018-10-30 23:00 | 199 | 199
2018-10-30 23:30 | 184 | 184
2018-10-31 | 165 | 165
2018-10-31 00:30 | 155 | 154
2018-10-31 01:00 | 154 | 153
2018-10-31 01:30 | 150 | 149
2018-10-31 02:00 | 153 | 152
2018-10-31 02:30 | 153 | 152
2018-10-31 03:00 | 153 | 152
2018-10-31 03:30 | 156 | 156
2018-10-31 04:00 | 159 | 158
2018-10-31 04:30 | 160 | 159
2018-10-31 05:00 | 174 | 173
2018-10-31 05:30 | 187 | 187
2018-10-31 06:00 | 199 | 199
2018-10-31 06:30 | 209 | 209
2018-10-31 07:00 | 214 | 213
2018-10-31 07:30 | 224 | 223
2018-10-31 08:00 | 227 | 227
2018-10-31 08:30 | 227 | 227
2018-10-31 09:00 | 226 | 226
2018-10-31 09:30 | 219 | 219
2018-10-31 10:00 | 215 | 215
2018-10-31 10:30 | 212 | 212
2018-10-31 11:00 | 212 | 212
2018-10-31 11:30 | 214 | 214
2018-10-31 12:00 | 217 | 217
2018-10-31 12:30 | 220 | 220
2018-10-31 13:00 | 225 | 225
2018-10-31 13:30 | 233 | 233
2018-10-31 14:00 | 246 | 246
2018-10-31 14:30 | 249 | 249
2018-10-31 15:00 | 261 | 261
2018-10-31 15:30 | 270 | 270
2018-10-31 16:00 | 277 | 277
2018-10-31 16:30 | 284 | 284
2018-10-31 17:00 | 282 | 282
2018-10-31 17:30 | 276 | 276
2018-10-31 18:00 | 277 | 277
2018-10-31 18:30 | 280 | 280
2018-10-31 19:00 | 277 | 276
2018-10-31 19:30 | 271 | 271
2018-10-31 20:00 | 261 | 261
2018-10-31 20:30 | 241 | 241
2018-10-31 21:00 | 227 | 227
2018-10-31 21:30 | 213 | 213
2018-10-31 22:00 | 204 | 204
2018-10-31 22:30 | 190 | 190
2018-10-31 23:00 | 185 | 185
2018-10-31 23:30 | 170 | 169
2018-11-01 | 154 | 153
2018-11-01 00:30 | 147 | 146
2018-11-01 01:00 | 148 | 147
2018-11-01 01:30 | 146 | 145
2018-11-01 02:00 | 144 | 143
2018-11-01 02:30 | 146 | 146
2018-11-01 03:00 | 144 | 143
2018-11-01 03:30 | 145 | 144
2018-11-01 04:00 | 152 | 151
2018-11-01 04:30 | 155 | 154
2018-11-01 05:00 | 162 | 162
2018-11-01 05:30 | 180 | 179
2018-11-01 06:00 | 194 | 194
2018-11-01 06:30 | 210 | 210
2018-11-01 07:00 | 217 | 217
2018-11-01 07:30 | 217 | 217
2018-11-01 08:00 | 219 | 219
2018-11-01 08:30 | 220 | 219
2018-11-01 09:00 | 216 | 215
2018-11-01 09:30 | 216 | 215
2018-11-01 10:00 | 206 | 206
2018-11-01 10:30 | 206 | 206
2018-11-01 11:00 | 212 | 212
2018-11-01 11:30 | 217 | 217
2018-11-01 12:00 | 216 | 216
2018-11-01 12:30 | 225 | 224
2018-11-01 13:00 | 231 | 231
2018-11-01 13:30 | 237 | 237
2018-11-01 14:00 | 240 | 240
2018-11-01 14:30 | 244 | 244
2018-11-01 15:00 | 256 | 256
2018-11-01 15:30 | 264 | 264
2018-11-01 16:00 | 274 | 274
2018-11-01 16:30 | 285 | 285
2018-11-01 17:00 | 289 | 288
2018-11-01 17:30 | 290 | 289
2018-11-01 18:00 | 291 | 291
2018-11-01 18:30 | 298 | 298
2018-11-01 19:00 | 298 | 297
2018-11-01 19:30 | 294 | 293
2018-11-01 20:00 | 279 | 278
2018-11-01 20:30 | 258 | 258
2018-11-01 21:00 | 236 | 236
2018-11-01 21:30 | 221 | 221
2018-11-01 22:00 | 210 | 210
2018-11-01 22:30 | 200 | 200
2018-11-01 23:00 | 191 | 190
2018-11-01 23:30 | 175 | 174
2018-11-02 | 164 | 163
2018-11-02 00:30 | 160 | 159
2018-11-02 01:00 | 157 | 156
2018-11-02 01:30 | 152 | 151
2018-11-02 02:00 | 144 | 144
2018-11-02 02:30 | 145 | 144
2018-11-02 03:00 | 145 | 144
2018-11-02 03:30 | 145 | 145
2018-11-02 04:00 | 148 | 147
2018-11-02 04:30 | 157 | 156
2018-11-02 05:00 | 169 | 168
2018-11-02 05:30 | 183 | 183
2018-11-02 06:00 | 199 | 199
2018-11-02 06:30 | 215 | 215
2018-11-02 07:00 | 230 | 230
2018-11-02 07:30 | 236 | 235
2018-11-02 08:00 | 234 | 234
2018-11-02 08:30 | 222 | 222
2018-11-02 09:00 | 218 | 218
2018-11-02 09:30 | 225 | 225
2018-11-02 10:00 | 224 | 224
2018-11-02 10:30 | 223 | 223
2018-11-02 11:00 | 202 | 202
2018-11-02 11:30 | 215 | 215
2018-11-02 12:00 | 218 | 218
2018-11-02 12:30 | 202 | 202
2018-11-02 13:00 | 233 | 233
2018-11-02 13:30 | 238 | 238
2018-11-02 14:00 | 242 | 242
2018-11-02 14:30 | 253 | 253
2018-11-02 15:00 | 261 | 261
2018-11-02 15:30 | 268 | 268
2018-11-02 16:00 | 279 | 279
2018-11-02 16:30 | 282 | 282
2018-11-02 17:00 | 276 | 276
2018-11-02 17:30 | 269 | 268
2018-11-02 18:00 | 265 | 265
2018-11-02 18:30 | 271 | 270
2018-11-02 19:00 | 264 | 264
2018-11-02 19:30 | 258 | 257
2018-11-02 20:00 | 250 | 249
2018-11-02 20:30 | 230 | 230
2018-11-02 21:00 | 221 | 221
2018-11-02 21:30 | 209 | 208
2018-11-02 22:00 | 204 | 204
2018-11-02 22:30 | 200 | 200
2018-11-02 23:00 | 189 | 189
2018-11-02 23:30 | 173 | 172
2018-11-03 | 154 | 152
2018-11-03 00:30 | 148 | 148
2018-11-03 01:00 | 147 | 147
2018-11-03 01:30 | 144 | 143
2018-11-03 02:00 | 127 | 127
2018-11-03 02:30 | 128 | 127
2018-11-03 03:00 | 130 | 130
2018-11-03 03:30 | 132 | 131
2018-11-03 04:00 | 131 | 131
2018-11-03 04:30 | 132 | 131
2018-11-03 05:00 | 135 | 135
2018-11-03 05:30 | 141 | 141
2018-11-03 06:00 | 153 | 153
2018-11-03 06:30 | 161 | 161
2018-11-03 07:00 | 176 | 176
2018-11-03 07:30 | 182 | 182
2018-11-03 08:00 | 184 | 184
2018-11-03 08:30 | 185 | 185
2018-11-03 09:00 | 188 | 188
2018-11-03 09:30 | 189 | 189
2018-11-03 10:00 | 185 | 185
2018-11-03 10:30 | 182 | 181
2018-11-03 11:00 | 180 | 180
2018-11-03 11:30 | 180 | 180
2018-11-03 12:00 | 183 | 183
2018-11-03 12:30 | 192 | 191
2018-11-03 13:00 | 194 | 193
2018-11-03 13:30 | 202 | 201
2018-11-03 14:00 | 211 | 211
2018-11-03 14:30 | 215 | 215
2018-11-03 15:00 | 227 | 227
2018-11-03 15:30 | 235 | 234
2018-11-03 16:00 | 243 | 242
2018-11-03 16:30 | 251 | 250
2018-11-03 17:00 | 251 | 249
2018-11-03 17:30 | 249 | 249
2018-11-03 18:00 | 254 | 254
2018-11-03 18:30 | 261 | 261
2018-11-03 19:00 | 255 | 255
2018-11-03 19:30 | 250 | 250
2018-11-03 20:00 | 245 | 245
2018-11-03 20:30 | 231 | 231
2018-11-03 21:00 | 218 | 218
2018-11-03 21:30 | 211 | 211
2018-11-03 22:00 | 205 | 205
2018-11-03 22:30 | 185 | 185
2018-11-03 23:00 | 182 | 182
2018-11-03 23:30 | 174 | 173
2018-11-04 | 162 | 160
2018-11-04 00:30 | 156 | 155
2018-11-04 01:00 | 155 | 154
2018-11-04 01:30 | 155 | 155
2018-11-04 02:00 | 156 | 156
2018-11-04 02:30 | 150 | 150
2018-11-04 03:00 | 150 | 149
2018-11-04 03:30 | 153 | 152
2018-11-04 04:00 | 144 | 143
2018-11-04 04:30 | 141 | 140
2018-11-04 05:00 | 141 | 140
2018-11-04 05:30 | 142 | 141
2018-11-04 06:00 | 152 | 152
2018-11-04 06:30 | 156 | 155
2018-11-04 07:00 | 165 | 165
2018-11-04 07:30 | 172 | 172
2018-11-04 08:00 | 178 | 178
2018-11-04 08:30 | 182 | 181
2018-11-04 09:00 | 186 | 186
2018-11-04 09:30 | 190 | 189
2018-11-04 10:00 | 195 | 194
2018-11-04 10:30 | 200 | 199
2018-11-04 11:00 | 199 | 198
2018-11-04 11:30 | 202 | 201
2018-11-04 12:00 | 205 | 204
2018-11-04 12:30 | 210 | 209
2018-11-04 13:00 | 216 | 216
2018-11-04 13:30 | 221 | 220
2018-11-04 14:00 | 228 | 228
2018-11-04 14:30 | 230 | 230
2018-11-04 15:00 | 239 | 239
2018-11-04 15:30 | 261 | 261
2018-11-04 16:00 | 264 | 263
2018-11-04 16:30 | 264 | 263
2018-11-04 17:00 | 279 | 278
2018-11-04 17:30 | 281 | 279
2018-11-04 18:00 | 284 | 283
2018-11-04 18:30 | 283 | 282
2018-11-04 19:00 | 276 | 275
2018-11-04 19:30 | 268 | 268
2018-11-04 20:00 | 258 | 258
2018-11-04 20:30 | 247 | 246
2018-11-04 21:00 | 226 | 226
2018-11-04 21:30 | 213 | 213
2018-11-04 22:00 | 193 | 193
2018-11-04 22:30 | 200 | 200
2018-11-04 23:00 | 193 | 192
2018-11-04 23:30 | 183 | 183
2018-11-05 | 164 | 163
2018-11-05 00:30 | 157 | 156
2018-11-05 01:00 | 157 | 157
2018-11-05 01:30 | 151 | 151
2018-11-05 02:00 | 150 | 150
2018-11-05 02:30 | 154 | 154
2018-11-05 03:00 | 154 | 153
2018-11-05 03:30 | 154 | 154
2018-11-05 04:00 | 164 | 163
2018-11-05 04:30 | 164 | 163
2018-11-05 05:00 | 169 | 169
2018-11-05 05:30 | 184 | 184
2018-11-05 06:00 | 206 | 206
2018-11-05 06:30 | 236 | 236
2018-11-05 07:00 | 252 | 252
2018-11-05 07:30 | 258 | 258
2018-11-05 08:00 | 257 | 257
2018-11-05 08:30 | 256 | 256
2018-11-05 09:00 | 257 | 257
2018-11-05 09:30 | 253 | 253
2018-11-05 10:00 | 249 | 248
2018-11-05 10:30 | 247 | 246
2018-11-05 11:00 | 250 | 249
2018-11-05 11:30 | 257 | 257
2018-11-05 12:00 | 260 | 260
2018-11-05 12:30 | 269 | 269
2018-11-05 13:00 | 274 | 274
2018-11-05 13:30 | 284 | 284
2018-11-05 14:00 | 296 | 296
2018-11-05 14:30 | 302 | 302
2018-11-05 15:00 | 292 | 292
2018-11-05 15:30 | 295 | 295
2018-11-05 16:00 | 321 | 321
2018-11-05 16:30 | 337 | 337
2018-11-05 17:00 | 334 | 334
2018-11-05 17:30 | 329 | 329
2018-11-05 18:00 | 329 | 329
2018-11-05 18:30 | 332 | 332
2018-11-05 19:00 | 327 | 326
2018-11-05 19:30 | 320 | 319
2018-11-05 20:00 | 301 | 299
2018-11-05 20:30 | 277 | 276
2018-11-05 21:00 | 258 | 257
2018-11-05 21:30 | 244 | 241
2018-11-05 22:00 | 222 | 221
2018-11-05 22:30 | 220 | 220
2018-11-05 23:00 | 203 | 202
2018-11-05 23:30 | 188 | 187
2018-11-06 | 165 | 164
2018-11-06 00:30 | 155 | 154
2018-11-06 01:00 | 154 | 153
2018-11-06 01:30 | 151 | 149
2018-11-06 02:00 | 152 | 151
2018-11-06 02:30 | 150 | 150
2018-11-06 03:00 | 150 | 150
2018-11-06 03:30 | 151 | 151
2018-11-06 04:00 | 154 | 154
2018-11-06 04:30 | 157 | 157
2018-11-06 05:00 | 170 | 169
2018-11-06 05:30 | 185 | 185
2018-11-06 06:00 | 210 | 210
2018-11-06 06:30 | 234 | 234
2018-11-06 07:00 | 257 | 257
2018-11-06 07:30 | 264 | 264
2018-11-06 08:00 | 273 | 273
2018-11-06 08:30 | 270 | 270
2018-11-06 09:00 | 276 | 275
2018-11-06 09:30 | 270 | 269
2018-11-06 10:00 | 269 | 268
2018-11-06 10:30 | 280 | 279
2018-11-06 11:00 | 279 | 278
2018-11-06 11:30 | 278 | 278
2018-11-06 12:00 | 281 | 281
2018-11-06 12:30 | 277 | 277
2018-11-06 13:00 | 278 | 278
2018-11-06 13:30 | 294 | 294
2018-11-06 14:00 | 308 | 308
2018-11-06 14:30 | 325 | 324
2018-11-06 15:00 | 350 | 350
2018-11-06 15:30 | 356 | 356
2018-11-06 16:00 | 362 | 362
2018-11-06 16:30 | 361 | 361
2018-11-06 17:00 | 358 | 357
2018-11-06 17:30 | 352 | 351
2018-11-06 18:00 | 344 | 343
2018-11-06 18:30 | 339 | 338
2018-11-06 19:00 | 318 | 317
2018-11-06 19:30 | 313 | 311
2018-11-06 20:00 | 307 | 305
2018-11-06 20:30 | 289 | 288
2018-11-06 21:00 | 266 | 265
2018-11-06 21:30 | 262 | 260
2018-11-06 22:00 | 234 | 233
2018-11-06 22:30 | 228 | 228
2018-11-06 23:00 | 221 | 220
2018-11-06 23:30 | 204 | 204
2018-11-07 | 184 | 184
2018-11-07 00:30 | 163 | 163
2018-11-07 01:00 | 148 | 147
2018-11-07 01:30 | 137 | 136
2018-11-07 02:00 | 137 | 136
2018-11-07 02:30 | 149 | 148
2018-11-07 03:00 | 150 | 149
2018-11-07 03:30 | 145 | 144
2018-11-07 04:00 | 137 | 136
2018-11-07 04:30 | 141 | 140
2018-11-07 05:00 | 165 | 164
2018-11-07 05:30 | 185 | 185
2018-11-07 06:00 | 219 | 219
2018-11-07 06:30 | 250 | 249
2018-11-07 07:00 | 264 | 264
2018-11-07 07:30 | 269 | 269
2018-11-07 08:00 | 273 | 272
2018-11-07 08:30 | 275 | 275
2018-11-07 09:00 | 271 | 271
2018-11-07 09:30 | 273 | 273
2018-11-07 10:00 | 269 | 269
2018-11-07 10:30 | 264 | 264
2018-11-07 11:00 | 268 | 268
2018-11-07 11:30 | 272 | 271
2018-11-07 12:00 | 272 | 271
2018-11-07 12:30 | 281 | 281
2018-11-07 13:00 | 281 | 281
2018-11-07 13:30 | 301 | 301
2018-11-07 14:00 | 325 | 324
2018-11-07 14:30 | 320 | 320
2018-11-07 15:00 | 337 | 336
2018-11-07 15:30 | 351 | 351
2018-11-07 16:00 | 355 | 355
2018-11-07 16:30 | 363 | 363
2018-11-07 17:00 | 363 | 363
2018-11-07 17:30 | 358 | 356
2018-11-07 18:00 | 352 | 351
2018-11-07 18:30 | 348 | 348
2018-11-07 19:00 | 315 | 314
2018-11-07 19:30 | 307 | 306
2018-11-07 20:00 | 291 | 289
2018-11-07 20:30 | 267 | 266
2018-11-07 21:00 | 248 | 247
2018-11-07 21:30 | 248 | 246
2018-11-07 22:00 | 229 | 229
2018-11-07 22:30 | 222 | 221
2018-11-07 23:00 | 207 | 206
2018-11-07 23:30 | 188 | 186
2018-11-08 | 150 | 149
2018-11-08 00:30 | 141 | 141
2018-11-08 01:00 | 147 | 146
2018-11-08 01:30 | 129 | 128
2018-11-08 02:00 | 127 | 126
2018-11-08 02:30 | 128 | 127
2018-11-08 03:00 | 139 | 138
2018-11-08 03:30 | 143 | 142
2018-11-08 04:00 | 143 | 142
2018-11-08 04:30 | 139 | 138
2018-11-08 05:00 | 152 | 151
2018-11-08 05:30 | 181 | 180
2018-11-08 06:00 | 215 | 215
2018-11-08 06:30 | 234 | 234
2018-11-08 07:00 | 252 | 251
2018-11-08 07:30 | 257 | 255
2018-11-08 08:00 | 258 | 256
2018-11-08 08:30 | 255 | 253
2018-11-08 09:00 | 257 | 256
2018-11-08 09:30 | 255 | 255
2018-11-08 10:00 | 257 | 256
2018-11-08 10:30 | 256 | 255
2018-11-08 11:00 | 256 | 255
2018-11-08 11:30 | 239 | 237
2018-11-08 12:00 | 236 | 234
2018-11-08 12:30 | 233 | 232
2018-11-08 13:00 | 233 | 233
2018-11-08 13:30 | 232 | 232
2018-11-08 14:00 | 219 | 219
2018-11-08 14:30 | 203 | 203
2018-11-08 15:00 | 217 | 216
2018-11-08 15:30 | 227 | 227
2018-11-08 16:00 | 235 | 235
2018-11-08 16:30 | 240 | 240
2018-11-08 17:00 | 245 | 244
2018-11-08 17:30 | 251 | 251
2018-11-08 18:00 | 259 | 259
2018-11-08 18:30 | 269 | 269
2018-11-08 19:00 | 266 | 266
2018-11-08 19:30 | 261 | 260
2018-11-08 20:00 | 253 | 252
2018-11-08 20:30 | 244 | 244
2018-11-08 21:00 | 239 | 239
2018-11-08 21:30 | 233 | 232
2018-11-08 22:00 | 225 | 224
2018-11-08 22:30 | 224 | 224
2018-11-08 23:00 | 211 | 211
2018-11-08 23:30 | 192 | 190
2018-11-09 | 177 | 175
2018-11-09 00:30 | 170 | 168
2018-11-09 01:00 | 169 | 166
2018-11-09 01:30 | 166 | 164
2018-11-09 02:00 | 168 | 166
2018-11-09 02:30 | 168 | 165
2018-11-09 03:00 | 168 | 165
2018-11-09 03:30 | 171 | 169
2018-11-09 04:00 | 168 | 166
2018-11-09 04:30 | 175 | 172
2018-11-09 05:00 | 189 | 187
2018-11-09 05:30 | 202 | 201
2018-11-09 06:00 | 210 | 209
2018-11-09 06:30 | 225 | 225
2018-11-09 07:00 | 237 | 237
2018-11-09 07:30 | 226 | 226
2018-11-09 08:00 | 219 | 219
2018-11-09 08:30 | 220 | 220
2018-11-09 09:00 | 230 | 230
2018-11-09 09:30 | 231 | 230
2018-11-09 10:00 | 227 | 227
2018-11-09 10:30 | 234 | 233
2018-11-09 11:00 | 222 | 222
2018-11-09 11:30 | 213 | 212
2018-11-09 12:00 | 215 | 215
2018-11-09 12:30 | 213 | 213
2018-11-09 13:00 | 210 | 210
2018-11-09 13:30 | 212 | 212
2018-11-09 14:00 | 210 | 210
2018-11-09 14:30 | 205 | 205
2018-11-09 15:00 | 216 | 215
2018-11-09 15:30 | 228 | 227
2018-11-09 16:00 | 237 | 236
2018-11-09 16:30 | 242 | 241
2018-11-09 17:00 | 246 | 245
2018-11-09 17:30 | 248 | 247
2018-11-09 18:00 | 249 | 248
2018-11-09 18:30 | 255 | 254
2018-11-09 19:00 | 254 | 253
2018-11-09 19:30 | 249 | 249
2018-11-09 20:00 | 240 | 240
2018-11-09 20:30 | 226 | 226
2018-11-09 21:00 | 215 | 215
2018-11-09 21:30 | 207 | 206
2018-11-09 22:00 | 204 | 203
2018-11-09 22:30 | 204 | 203
2018-11-09 23:00 | 197 | 196
2018-11-09 23:30 | 179 | 177
2018-11-10 | 162 | 160
2018-11-10 00:30 | 153 | 152
2018-11-10 01:00 | 151 | 150
2018-11-10 01:30 | 150 | 149
2018-11-10 02:00 | 148 | 147
2018-11-10 02:30 | 148 | 146
2018-11-10 03:00 | 151 | 149
2018-11-10 03:30 | 152 | 151
2018-11-10 04:00 | 152 | 151
2018-11-10 04:30 | 153 | 151
2018-11-10 05:00 | 157 | 155
2018-11-10 05:30 | 159 | 157
2018-11-10 06:00 | 167 | 166
2018-11-10 06:30 | 173 | 173
2018-11-10 07:00 | 180 | 180
2018-11-10 07:30 | 186 | 186
2018-11-10 08:00 | 193 | 192
2018-11-10 08:30 | 201 | 201
2018-11-10 09:00 | 202 | 202
2018-11-10 09:30 | 194 | 194
2018-11-10 10:00 | 186 | 186
2018-11-10 10:30 | 181 | 181
2018-11-10 11:00 | 178 | 178
2018-11-10 11:30 | 173 | 173
2018-11-10 12:00 | 171 | 171
2018-11-10 12:30 | 175 | 175
2018-11-10 13:00 | 179 | 179
2018-11-10 13:30 | 188 | 188
2018-11-10 14:00 | 189 | 189
2018-11-10 14:30 | 194 | 194
2018-11-10 15:00 | 199 | 199
2018-11-10 15:30 | 207 | 207
2018-11-10 16:00 | 218 | 218
2018-11-10 16:30 | 234 | 232
2018-11-10 17:00 | 234 | 232
2018-11-10 17:30 | 236 | 234
2018-11-10 18:00 | 243 | 241
2018-11-10 18:30 | 248 | 247
2018-11-10 19:00 | 244 | 243
2018-11-10 19:30 | 235 | 235
2018-11-10 20:00 | 231 | 231
2018-11-10 20:30 | 220 | 220
2018-11-10 21:00 | 209 | 209
2018-11-10 21:30 | 203 | 202
2018-11-10 22:00 | 199 | 198
2018-11-10 22:30 | 201 | 200
2018-11-10 23:00 | 191 | 190
2018-11-10 23:30 | 175 | 173
2018-11-11 | 162 | 159
2018-11-11 00:30 | 152 | 151
2018-11-11 01:00 | 144 | 143
2018-11-11 01:30 | 140 | 138
2018-11-11 02:00 | 138 | 137
2018-11-11 02:30 | 138 | 136
2018-11-11 03:00 | 140 | 139
2018-11-11 03:30 | 141 | 139
2018-11-11 04:00 | 145 | 143
2018-11-11 04:30 | 147 | 145
2018-11-11 05:00 | 145 | 143
2018-11-11 05:30 | 152 | 150
2018-11-11 06:00 | 157 | 156
2018-11-11 06:30 | 167 | 166
2018-11-11 07:00 | 178 | 178
2018-11-11 07:30 | 185 | 185
2018-11-11 08:00 | 187 | 187
2018-11-11 08:30 | 185 | 185
2018-11-11 09:00 | 188 | 188
2018-11-11 09:30 | 187 | 187
2018-11-11 10:00 | 183 | 182
2018-11-11 10:30 | 174 | 174
2018-11-11 11:00 | 169 | 168
2018-11-11 11:30 | 166 | 166
2018-11-11 12:00 | 169 | 168
2018-11-11 12:30 | 171 | 171
2018-11-11 13:00 | 174 | 174
2018-11-11 13:30 | 177 | 177
2018-11-11 14:00 | 185 | 185
2018-11-11 14:30 | 199 | 199
2018-11-11 15:00 | 203 | 203
2018-11-11 15:30 | 216 | 216
2018-11-11 16:00 | 230 | 230
2018-11-11 16:30 | 238 | 238
2018-11-11 17:00 | 239 | 239
2018-11-11 17:30 | 239 | 239
2018-11-11 18:00 | 240 | 240
2018-11-11 18:30 | 250 | 249
2018-11-11 19:00 | 247 | 244
2018-11-11 19:30 | 241 | 239
2018-11-11 20:00 | 231 | 229
2018-11-11 20:30 | 217 | 217
2018-11-11 21:00 | 208 | 208
2018-11-11 21:30 | 199 | 199
2018-11-11 22:00 | 194 | 194
2018-11-11 22:30 | 197 | 196
2018-11-11 23:00 | 186 | 184
2018-11-11 23:30 | 177 | 175
2018-11-12 | 165 | 163
2018-11-12 00:30 | 161 | 160
2018-11-12 01:00 | 158 | 157
2018-11-12 01:30 | 154 | 153
2018-11-12 02:00 | 155 | 154
2018-11-12 02:30 | 155 | 153
2018-11-12 03:00 | 156 | 154
2018-11-12 03:30 | 158 | 157
2018-11-12 04:00 | 157 | 156
2018-11-12 04:30 | 156 | 155
2018-11-12 05:00 | 161 | 160
2018-11-12 05:30 | 174 | 174
2018-11-12 06:00 | 190 | 190
2018-11-12 06:30 | 206 | 206
2018-11-12 07:00 | 218 | 216
2018-11-12 07:30 | 216 | 215
2018-11-12 08:00 | 219 | 218
2018-11-12 08:30 | 221 | 221
2018-11-12 09:00 | 225 | 224
2018-11-12 09:30 | 220 | 220
2018-11-12 10:00 | 217 | 217
2018-11-12 10:30 | 216 | 215
2018-11-12 11:00 | 210 | 210
2018-11-12 11:30 | 201 | 200
2018-11-12 12:00 | 204 | 204
2018-11-12 12:30 | 210 | 210
2018-11-12 13:00 | 216 | 216
2018-11-12 13:30 | 222 | 222
2018-11-12 14:00 | 223 | 223
2018-11-12 14:30 | 232 | 232
2018-11-12 15:00 | 245 | 245
2018-11-12 15:30 | 253 | 253
2018-11-12 16:00 | 267 | 267
2018-11-12 16:30 | 272 | 271
2018-11-12 17:00 | 273 | 273
2018-11-12 17:30 | 267 | 267
2018-11-12 18:00 | 263 | 262
2018-11-12 18:30 | 268 | 267
2018-11-12 19:00 | 259 | 258
2018-11-12 19:30 | 247 | 246
2018-11-12 20:00 | 243 | 241
2018-11-12 20:30 | 232 | 232
2018-11-12 21:00 | 221 | 221
2018-11-12 21:30 | 212 | 212
2018-11-12 22:00 | 208 | 208
2018-11-12 22:30 | 207 | 207
2018-11-12 23:00 | 188 | 188
2018-11-12 23:30 | 178 | 177
2018-11-13 | 162 | 162
2018-11-13 00:30 | 155 | 154
2018-11-13 01:00 | 152 | 151
2018-11-13 01:30 | 151 | 150
2018-11-13 02:00 | 151 | 150
2018-11-13 02:30 | 151 | 150
2018-11-13 03:00 | 155 | 153
2018-11-13 03:30 | 157 | 156
2018-11-13 04:00 | 165 | 164
2018-11-13 04:30 | 163 | 162
2018-11-13 05:00 | 170 | 169
2018-11-13 05:30 | 181 | 181
2018-11-13 06:00 | 196 | 196
2018-11-13 06:30 | 213 | 213
2018-11-13 07:00 | 225 | 225
2018-11-13 07:30 | 223 | 223
2018-11-13 08:00 | 222 | 222
2018-11-13 08:30 | 225 | 224
2018-11-13 09:00 | 223 | 223
2018-11-13 09:30 | 219 | 219
2018-11-13 10:00 | 220 | 220
2018-11-13 10:30 | 224 | 224
2018-11-13 11:00 | 222 | 222
2018-11-13 11:30 | 219 | 219
2018-11-13 12:00 | 218 | 217
2018-11-13 12:30 | 218 | 218
2018-11-13 13:00 | 215 | 215
2018-11-13 13:30 | 214 | 214
2018-11-13 14:00 | 218 | 218
2018-11-13 14:30 | 221 | 221
2018-11-13 15:00 | 230 | 230
2018-11-13 15:30 | 247 | 247
2018-11-13 16:00 | 261 | 261
2018-11-13 16:30 | 265 | 265
2018-11-13 17:00 | 264 | 263
2018-11-13 17:30 | 259 | 259
2018-11-13 18:00 | 260 | 260
2018-11-13 18:30 | 265 | 264
2018-11-13 19:00 | 261 | 261
2018-11-13 19:30 | 260 | 259
2018-11-13 20:00 | 250 | 250
2018-11-13 20:30 | 238 | 238
2018-11-13 21:00 | 224 | 224
2018-11-13 21:30 | 213 | 213
2018-11-13 22:00 | 203 | 203
2018-11-13 22:30 | 198 | 198
2018-11-13 23:00 | 187 | 187
2018-11-13 23:30 | 175 | 175
2018-11-14 | 164 | 163
2018-11-14 00:30 | 152 | 151
2018-11-14 01:00 | 150 | 149
2018-11-14 01:30 | 152 | 150
2018-11-14 02:00 | 158 | 157
2018-11-14 02:30 | 161 | 160
2018-11-14 03:00 | 160 | 159
2018-11-14 03:30 | 164 | 163
2018-11-14 04:00 | 168 | 167
2018-11-14 04:30 | 169 | 168
2018-11-14 05:00 | 179 | 178
2018-11-14 05:30 | 189 | 188
2018-11-14 06:00 | 205 | 205
2018-11-14 06:30 | 226 | 226
2018-11-14 07:00 | 238 | 238
2018-11-14 07:30 | 241 | 241
2018-11-14 08:00 | 247 | 247
2018-11-14 08:30 | 247 | 247
2018-11-14 09:00 | 242 | 242
2018-11-14 09:30 | 232 | 232
2018-11-14 10:00 | 230 | 229
2018-11-14 10:30 | 223 | 222
2018-11-14 11:00 | 218 | 217
2018-11-14 11:30 | 220 | 220
2018-11-14 12:00 | 221 | 221
2018-11-14 12:30 | 228 | 228
2018-11-14 13:00 | 233 | 233
2018-11-14 13:30 | 235 | 235
2018-11-14 14:00 | 239 | 239
2018-11-14 14:30 | 242 | 241
2018-11-14 15:00 | 250 | 249
2018-11-14 15:30 | 248 | 247
2018-11-14 16:00 | 252 | 252
2018-11-14 16:30 | 255 | 254
2018-11-14 17:00 | 263 | 262
2018-11-14 17:30 | 260 | 258
2018-11-14 18:00 | 267 | 265
2018-11-14 18:30 | 269 | 268
2018-11-14 19:00 | 265 | 263
2018-11-14 19:30 | 269 | 268
2018-11-14 20:00 | 264 | 263
2018-11-14 20:30 | 249 | 249
2018-11-14 21:00 | 232 | 232
2018-11-14 21:30 | 223 | 223
2018-11-14 22:00 | 218 | 218
2018-11-14 22:30 | 217 | 217
2018-11-14 23:00 | 205 | 205
2018-11-14 23:30 | 192 | 192
2018-11-15 | 174 | 174
2018-11-15 00:30 | 164 | 164
2018-11-15 01:00 | 157 | 156
2018-11-15 01:30 | 152 | 151
2018-11-15 02:00 | 151 | 151
2018-11-15 02:30 | 151 | 151
2018-11-15 03:00 | 152 | 151
2018-11-15 03:30 | 150 | 150
2018-11-15 04:00 | 159 | 158
2018-11-15 04:30 | 160 | 159
2018-11-15 05:00 | 172 | 171
2018-11-15 05:30 | 185 | 185
2018-11-15 06:00 | 204 | 204
2018-11-15 06:30 | 220 | 220
2018-11-15 07:00 | 233 | 233
2018-11-15 07:30 | 248 | 248
2018-11-15 08:00 | 252 | 252
2018-11-15 08:30 | 257 | 257
2018-11-15 09:00 | 255 | 255
2018-11-15 09:30 | 251 | 251
2018-11-15 10:00 | 250 | 250
2018-11-15 10:30 | 251 | 251
2018-11-15 11:00 | 249 | 249
2018-11-15 11:30 | 248 | 248
2018-11-15 12:00 | 261 | 261
2018-11-15 12:30 | 251 | 251
2018-11-15 13:00 | 249 | 249
2018-11-15 13:30 | 240 | 240
2018-11-15 14:00 | 248 | 248
2018-11-15 14:30 | 250 | 249
2018-11-15 15:00 | 251 | 251
2018-11-15 15:30 | 256 | 256
2018-11-15 16:00 | 261 | 261
2018-11-15 16:30 | 273 | 273
2018-11-15 17:00 | 275 | 274
2018-11-15 17:30 | 272 | 271
2018-11-15 18:00 | 274 | 273
2018-11-15 18:30 | 266 | 265
2018-11-15 19:00 | 265 | 264
2018-11-15 19:30 | 273 | 271
2018-11-15 20:00 | 267 | 265
2018-11-15 20:30 | 247 | 246
2018-11-15 21:00 | 233 | 233
2018-11-15 21:30 | 220 | 220
2018-11-15 22:00 | 215 | 215
2018-11-15 22:30 | 216 | 216
2018-11-15 23:00 | 207 | 207
2018-11-15 23:30 | 194 | 194
2018-11-16 | 179 | 178
2018-11-16 00:30 | 170 | 168
2018-11-16 01:00 | 166 | 164
2018-11-16 01:30 | 161 | 159
2018-11-16 02:00 | 160 | 158
2018-11-16 02:30 | 161 | 158
2018-11-16 03:00 | 160 | 158
2018-11-16 03:30 | 163 | 161
2018-11-16 04:00 | 166 | 164
2018-11-16 04:30 | 170 | 168
2018-11-16 05:00 | 182 | 180
2018-11-16 05:30 | 194 | 193
2018-11-16 06:00 | 209 | 209
2018-11-16 06:30 | 225 | 225
2018-11-16 07:00 | 241 | 241
2018-11-16 07:30 | 251 | 251
2018-11-16 08:00 | 252 | 252
2018-11-16 08:30 | 252 | 252
2018-11-16 09:00 | 252 | 252
2018-11-16 09:30 | 253 | 253
2018-11-16 10:00 | 252 | 252
2018-11-16 10:30 | 253 | 253
2018-11-16 11:00 | 252 | 252
2018-11-16 11:30 | 252 | 251
2018-11-16 12:00 | 251 | 250
2018-11-16 12:30 | 243 | 243
2018-11-16 13:00 | 243 | 242
2018-11-16 13:30 | 244 | 244
2018-11-16 14:00 | 248 | 247
2018-11-16 14:30 | 251 | 251
2018-11-16 15:00 | 265 | 264
2018-11-16 15:30 | 271 | 271
2018-11-16 16:00 | 276 | 275
2018-11-16 16:30 | 286 | 285
2018-11-16 17:00 | 282 | 281
2018-11-16 17:30 | 269 | 268
2018-11-16 18:00 | 263 | 262
2018-11-16 18:30 | 269 | 268
2018-11-16 19:00 | 266 | 265
2018-11-16 19:30 | 262 | 262
2018-11-16 20:00 | 256 | 256
2018-11-16 20:30 | 244 | 244
2018-11-16 21:00 | 236 | 236
2018-11-16 21:30 | 229 | 229
2018-11-16 22:00 | 229 | 229
2018-11-16 22:30 | 230 | 230
2018-11-16 23:00 | 216 | 216
2018-11-16 23:30 | 207 | 206
2018-11-17 | 190 | 190
2018-11-17 00:30 | 178 | 177
2018-11-17 01:00 | 173 | 171
2018-11-17 01:30 | 172 | 171
2018-11-17 02:00 | 173 | 171
2018-11-17 02:30 | 173 | 172
2018-11-17 03:00 | 173 | 171
2018-11-17 03:30 | 172 | 170
2018-11-17 04:00 | 167 | 165
2018-11-17 04:30 | 159 | 159
2018-11-17 05:00 | 156 | 156
2018-11-17 05:30 | 160 | 159
2018-11-17 06:00 | 170 | 169
2018-11-17 06:30 | 185 | 185
2018-11-17 07:00 | 207 | 207
2018-11-17 07:30 | 216 | 216
2018-11-17 08:00 | 213 | 213
2018-11-17 08:30 | 225 | 225
2018-11-17 09:00 | 236 | 236
2018-11-17 09:30 | 230 | 230
2018-11-17 10:00 | 232 | 232
2018-11-17 10:30 | 237 | 237
2018-11-17 11:00 | 231 | 230
2018-11-17 11:30 | 214 | 214
2018-11-17 12:00 | 220 | 220
2018-11-17 12:30 | 221 | 221
2018-11-17 13:00 | 221 | 221
2018-11-17 13:30 | 226 | 226
2018-11-17 14:00 | 230 | 230
2018-11-17 14:30 | 255 | 254
2018-11-17 15:00 | 265 | 265
2018-11-17 15:30 | 260 | 260
2018-11-17 16:00 | 259 | 259
2018-11-17 16:30 | 255 | 255
2018-11-17 17:00 | 248 | 248
2018-11-17 17:30 | 246 | 245
2018-11-17 18:00 | 250 | 249
2018-11-17 18:30 | 248 | 247
2018-11-17 19:00 | 240 | 240
2018-11-17 19:30 | 233 | 233
2018-11-17 20:00 | 225 | 225
2018-11-17 20:30 | 219 | 219
2018-11-17 21:00 | 216 | 216
2018-11-17 21:30 | 211 | 211
2018-11-17 22:00 | 207 | 207
2018-11-17 22:30 | 208 | 208
2018-11-17 23:00 | 201 | 200
2018-11-17 23:30 | 191 | 190
2018-11-18 | 178 | 177
2018-11-18 00:30 | 169 | 168
2018-11-18 01:00 | 160 | 160
2018-11-18 01:30 | 157 | 157
2018-11-18 02:00 | 158 | 157
2018-11-18 02:30 | 159 | 159
2018-11-18 03:00 | 157 | 156
2018-11-18 03:30 | 155 | 155
2018-11-18 04:00 | 155 | 154
2018-11-18 04:30 | 154 | 153
2018-11-18 05:00 | 156 | 155
2018-11-18 05:30 | 159 | 158
2018-11-18 06:00 | 167 | 167
2018-11-18 06:30 | 179 | 179
2018-11-18 07:00 | 190 | 190
2018-11-18 07:30 | 193 | 193
2018-11-18 08:00 | 197 | 197
2018-11-18 08:30 | 199 | 199
2018-11-18 09:00 | 205 | 204
2018-11-18 09:30 | 208 | 207
2018-11-18 10:00 | 222 | 222
2018-11-18 10:30 | 227 | 225
2018-11-18 11:00 | 220 | 218
2018-11-18 11:30 | 221 | 219
2018-11-18 12:00 | 230 | 228
2018-11-18 12:30 | 233 | 232
2018-11-18 13:00 | 226 | 224
2018-11-18 13:30 | 203 | 202
2018-11-18 14:00 | 212 | 211
2018-11-18 14:30 | 223 | 222
2018-11-18 15:00 | 226 | 225
2018-11-18 15:30 | 223 | 222
2018-11-18 16:00 | 220 | 219
2018-11-18 16:30 | 228 | 227
2018-11-18 17:00 | 233 | 233
2018-11-18 17:30 | 237 | 237
2018-11-18 18:00 | 242 | 241
2018-11-18 18:30 | 246 | 245
2018-11-18 19:00 | 243 | 242
2018-11-18 19:30 | 241 | 241
2018-11-18 20:00 | 238 | 237
2018-11-18 20:30 | 226 | 225
2018-11-18 21:00 | 210 | 210
2018-11-18 21:30 | 203 | 203
2018-11-18 22:00 | 199 | 199
2018-11-18 22:30 | 204 | 204
2018-11-18 23:00 | 193 | 193
2018-11-18 23:30 | 181 | 181
2018-11-19 | 167 | 166
2018-11-19 00:30 | 160 | 159
2018-11-19 01:00 | 152 | 151
2018-11-19 01:30 | 145 | 144
2018-11-19 02:00 | 144 | 143
2018-11-19 02:30 | 145 | 143
2018-11-19 03:00 | 147 | 146
2018-11-19 03:30 | 148 | 146
2018-11-19 04:00 | 153 | 152
2018-11-19 04:30 | 154 | 153
2018-11-19 05:00 | 159 | 158
2018-11-19 05:30 | 175 | 175
2018-11-19 06:00 | 196 | 196
2018-11-19 06:30 | 213 | 213
2018-11-19 07:00 | 216 | 216
2018-11-19 07:30 | 214 | 214
2018-11-19 08:00 | 215 | 215
2018-11-19 08:30 | 218 | 218
2018-11-19 09:00 | 223 | 223
2018-11-19 09:30 | 229 | 229
2018-11-19 10:00 | 225 | 224
2018-11-19 10:30 | 217 | 217
2018-11-19 11:00 | 204 | 204
2018-11-19 11:30 | 212 | 212
2018-11-19 12:00 | 222 | 222
2018-11-19 12:30 | 223 | 223
2018-11-19 13:00 | 226 | 226
2018-11-19 13:30 | 226 | 226
2018-11-19 14:00 | 227 | 227
2018-11-19 14:30 | 227 | 227
2018-11-19 15:00 | 236 | 236
2018-11-19 15:30 | 243 | 243
2018-11-19 16:00 | 250 | 250
2018-11-19 16:30 | 262 | 262
2018-11-19 17:00 | 264 | 264
2018-11-19 17:30 | 254 | 254
2018-11-19 18:00 | 253 | 252
2018-11-19 18:30 | 258 | 257
2018-11-19 19:00 | 250 | 250
2018-11-19 19:30 | 244 | 243
2018-11-19 20:00 | 233 | 233
2018-11-19 20:30 | 226 | 226
2018-11-19 21:00 | 215 | 215
2018-11-19 21:30 | 204 | 204
2018-11-19 22:00 | 204 | 204
2018-11-19 22:30 | 202 | 201
2018-11-19 23:00 | 193 | 192
2018-11-19 23:30 | 180 | 179
2018-11-20 | 165 | 164
2018-11-20 00:30 | 160 | 160
2018-11-20 01:00 | 151 | 150
2018-11-20 01:30 | 145 | 143
2018-11-20 02:00 | 142 | 141
2018-11-20 02:30 | 148 | 147
2018-11-20 03:00 | 152 | 151
2018-11-20 03:30 | 153 | 152
2018-11-20 04:00 | 156 | 155
2018-11-20 04:30 | 158 | 157
2018-11-20 05:00 | 169 | 168
2018-11-20 05:30 | 180 | 180
2018-11-20 06:00 | 190 | 190
2018-11-20 06:30 | 206 | 206
2018-11-20 07:00 | 219 | 218
2018-11-20 07:30 | 218 | 218
2018-11-20 08:00 | 220 | 219
2018-11-20 08:30 | 217 | 216
2018-11-20 09:00 | 223 | 223
2018-11-20 09:30 | 227 | 227
2018-11-20 10:00 | 221 | 221
2018-11-20 10:30 | 213 | 213
2018-11-20 11:00 | 214 | 214
2018-11-20 11:30 | 217 | 217
2018-11-20 12:00 | 219 | 219
2018-11-20 12:30 | 218 | 218
2018-11-20 13:00 | 220 | 220
2018-11-20 13:30 | 224 | 224
2018-11-20 14:00 | 233 | 233
2018-11-20 14:30 | 240 | 239
2018-11-20 15:00 | 242 | 241
2018-11-20 15:30 | 251 | 250
2018-11-20 16:00 | 267 | 266
2018-11-20 16:30 | 282 | 282
2018-11-20 17:00 | 287 | 286
2018-11-20 17:30 | 288 | 286
2018-11-20 18:00 | 291 | 289
2018-11-20 18:30 | 301 | 300
2018-11-20 19:00 | 294 | 293
2018-11-20 19:30 | 288 | 286
2018-11-20 20:00 | 271 | 269
2018-11-20 20:30 | 261 | 259
2018-11-20 21:00 | 246 | 246
2018-11-20 21:30 | 218 | 217
2018-11-20 22:00 | 215 | 213
2018-11-20 22:30 | 212 | 210
2018-11-20 23:00 | 200 | 197
2018-11-20 23:30 | 188 | 186
2018-11-21 | 166 | 166
2018-11-21 00:30 | 157 | 156
2018-11-21 01:00 | 149 | 148
2018-11-21 01:30 | 147 | 146
2018-11-21 02:00 | 147 | 146
2018-11-21 02:30 | 148 | 147
2018-11-21 03:00 | 151 | 150
2018-11-21 03:30 | 151 | 150
2018-11-21 04:00 | 155 | 155
2018-11-21 04:30 | 159 | 158
2018-11-21 05:00 | 161 | 160
2018-11-21 05:30 | 170 | 170
2018-11-21 06:00 | 182 | 182
2018-11-21 06:30 | 196 | 196
2018-11-21 07:00 | 212 | 212
2018-11-21 07:30 | 222 | 222
2018-11-21 08:00 | 227 | 227
2018-11-21 08:30 | 231 | 231
2018-11-21 09:00 | 232 | 232
2018-11-21 09:30 | 233 | 233
2018-11-21 10:00 | 233 | 233
2018-11-21 10:30 | 232 | 232
2018-11-21 11:00 | 232 | 232
2018-11-21 11:30 | 229 | 229
2018-11-21 12:00 | 230 | 230
2018-11-21 12:30 | 234 | 234
2018-11-21 13:00 | 237 | 237
2018-11-21 13:30 | 251 | 251
2018-11-21 14:00 | 268 | 268
2018-11-21 14:30 | 294 | 294
2018-11-21 15:00 | 306 | 306
2018-11-21 15:30 | 312 | 312
2018-11-21 16:00 | 319 | 319
2018-11-21 16:30 | 322 | 322
2018-11-21 17:00 | 322 | 321
2018-11-21 17:30 | 321 | 320
2018-11-21 18:00 | 321 | 321
2018-11-21 18:30 | 328 | 328
2018-11-21 19:00 | 323 | 322
2018-11-21 19:30 | 315 | 314
2018-11-21 20:00 | 306 | 304
2018-11-21 20:30 | 290 | 288
2018-11-21 21:00 | 272 | 272
2018-11-21 21:30 | 254 | 254
2018-11-21 22:00 | 242 | 241
2018-11-21 22:30 | 235 | 234
2018-11-21 23:00 | 224 | 224
2018-11-21 23:30 | 210 | 209
2018-11-22 | 195 | 194
2018-11-22 00:30 | 182 | 181
2018-11-22 01:00 | 164 | 162
2018-11-22 01:30 | 158 | 156
2018-11-22 02:00 | 159 | 158
2018-11-22 02:30 | 159 | 157
2018-11-22 03:00 | 159 | 157
2018-11-22 03:30 | 158 | 156
2018-11-22 04:00 | 158 | 156
2018-11-22 04:30 | 166 | 164
2018-11-22 05:00 | 177 | 176
2018-11-22 05:30 | 199 | 198
2018-11-22 06:00 | 223 | 222
2018-11-22 06:30 | 230 | 230
2018-11-22 07:00 | 228 | 228
2018-11-22 07:30 | 240 | 240
2018-11-22 08:00 | 244 | 242
2018-11-22 08:30 | 246 | 245
2018-11-22 09:00 | 249 | 249
2018-11-22 09:30 | 257 | 256
2018-11-22 10:00 | 262 | 262
2018-11-22 10:30 | 288 | 288
2018-11-22 11:00 | 257 | 255
2018-11-22 11:30 | 236 | 236
2018-11-22 12:00 | 210 | 209
2018-11-22 12:30 | 192 | 192
2018-11-22 13:00 | 178 | 178
2018-11-22 13:30 | 177 | 176
2018-11-22 14:00 | 190 | 190
2018-11-22 14:30 | 192 | 192
2018-11-22 15:00 | 214 | 214
2018-11-22 15:30 | 256 | 256
2018-11-22 16:00 | 280 | 280
2018-11-22 16:30 | 301 | 301
2018-11-22 17:00 | 317 | 316
2018-11-22 17:30 | 318 | 317
2018-11-22 18:00 | 317 | 316
2018-11-22 18:30 | 326 | 326
2018-11-22 19:00 | 320 | 319
2018-11-22 19:30 | 313 | 312
2018-11-22 20:00 | 303 | 302
2018-11-22 20:30 | 289 | 287
2018-11-22 21:00 | 268 | 268
2018-11-22 21:30 | 238 | 237
2018-11-22 22:00 | 231 | 231
2018-11-22 22:30 | 226 | 226
2018-11-22 23:00 | 209 | 209
2018-11-22 23:30 | 191 | 191
2018-11-23 | 174 | 173
2018-11-23 00:30 | 164 | 163
2018-11-23 01:00 | 153 | 151
2018-11-23 01:30 | 146 | 143
2018-11-23 02:00 | 139 | 136
2018-11-23 02:30 | 140 | 137
2018-11-23 03:00 | 140 | 137
2018-11-23 03:30 | 143 | 140
2018-11-23 04:00 | 144 | 142
2018-11-23 04:30 | 147 | 144
2018-11-23 05:00 | 160 | 158
2018-11-23 05:30 | 173 | 171
2018-11-23 06:00 | 187 | 186
2018-11-23 06:30 | 200 | 200
2018-11-23 07:00 | 212 | 212
2018-11-23 07:30 | 204 | 204
2018-11-23 08:00 | 206 | 206
2018-11-23 08:30 | 204 | 204
2018-11-23 09:00 | 201 | 201
2018-11-23 09:30 | 204 | 204
2018-11-23 10:00 | 203 | 203
2018-11-23 10:30 | 203 | 203
2018-11-23 11:00 | 205 | 205
2018-11-23 11:30 | 205 | 205
2018-11-23 12:00 | 208 | 208
2018-11-23 12:30 | 211 | 211
2018-11-23 13:00 | 211 | 211
2018-11-23 13:30 | 212 | 212
2018-11-23 14:00 | 222 | 222
2018-11-23 14:30 | 226 | 226
2018-11-23 15:00 | 237 | 237
2018-11-23 15:30 | 252 | 251
2018-11-23 16:00 | 266 | 266
2018-11-23 16:30 | 285 | 285
2018-11-23 17:00 | 290 | 290
2018-11-23 17:30 | 286 | 285
2018-11-23 18:00 | 284 | 282
2018-11-23 18:30 | 292 | 291
2018-11-23 19:00 | 289 | 287
2018-11-23 19:30 | 283 | 281
2018-11-23 20:00 | 263 | 260
2018-11-23 20:30 | 257 | 257
2018-11-23 21:00 | 237 | 236
2018-11-23 21:30 | 221 | 220
2018-11-23 22:00 | 217 | 216
2018-11-23 22:30 | 216 | 215
2018-11-23 23:00 | 200 | 198
2018-11-23 23:30 | 181 | 180
2018-11-24 | 168 | 166
2018-11-24 00:30 | 161 | 158
2018-11-24 01:00 | 158 | 155
2018-11-24 01:30 | 152 | 149
2018-11-24 02:00 | 151 | 147
2018-11-24 02:30 | 149 | 146
2018-11-24 03:00 | 144 | 140
2018-11-24 03:30 | 143 | 139
2018-11-24 04:00 | 150 | 146
2018-11-24 04:30 | 150 | 147
2018-11-24 05:00 | 154 | 153
2018-11-24 05:30 | 156 | 155
2018-11-24 06:00 | 165 | 165
2018-11-24 06:30 | 178 | 178
2018-11-24 07:00 | 188 | 188
2018-11-24 07:30 | 190 | 190
2018-11-24 08:00 | 194 | 194
2018-11-24 08:30 | 193 | 192
2018-11-24 09:00 | 194 | 194
2018-11-24 09:30 | 191 | 191
2018-11-24 10:00 | 187 | 187
2018-11-24 10:30 | 181 | 180
2018-11-24 11:00 | 187 | 187
2018-11-24 11:30 | 184 | 183
2018-11-24 12:00 | 185 | 185
2018-11-24 12:30 | 188 | 187
2018-11-24 13:00 | 188 | 188
2018-11-24 13:30 | 196 | 195
2018-11-24 14:00 | 204 | 204
2018-11-24 14:30 | 215 | 215
2018-11-24 15:00 | 223 | 223
2018-11-24 15:30 | 234 | 234
2018-11-24 16:00 | 245 | 245
2018-11-24 16:30 | 256 | 256
2018-11-24 17:00 | 270 | 270
2018-11-24 17:30 | 273 | 272
2018-11-24 18:00 | 273 | 272
2018-11-24 18:30 | 281 | 280
2018-11-24 19:00 | 277 | 276
2018-11-24 19:30 | 260 | 259
2018-11-24 20:00 | 246 | 245
2018-11-24 20:30 | 239 | 239
2018-11-24 21:00 | 224 | 224
2018-11-24 21:30 | 215 | 215
2018-11-24 22:00 | 210 | 210
2018-11-24 22:30 | 209 | 209
2018-11-24 23:00 | 198 | 198
2018-11-24 23:30 | 185 | 184
2018-11-25 | 174 | 172
2018-11-25 00:30 | 170 | 168
2018-11-25 01:00 | 164 | 162
2018-11-25 01:30 | 166 | 163
2018-11-25 02:00 | 166 | 164
2018-11-25 02:30 | 164 | 161
2018-11-25 03:00 | 163 | 160
2018-11-25 03:30 | 163 | 160
2018-11-25 04:00 | 158 | 155
2018-11-25 04:30 | 147 | 146
2018-11-25 05:00 | 146 | 145
2018-11-25 05:30 | 149 | 149
2018-11-25 06:00 | 156 | 156
2018-11-25 06:30 | 164 | 163
2018-11-25 07:00 | 174 | 174
2018-11-25 07:30 | 185 | 185
2018-11-25 08:00 | 182 | 181
2018-11-25 08:30 | 191 | 190
2018-11-25 09:00 | 212 | 212
2018-11-25 09:30 | 205 | 205
2018-11-25 10:00 | 206 | 206
2018-11-25 10:30 | 206 | 205
2018-11-25 11:00 | 222 | 221
2018-11-25 11:30 | 230 | 229
2018-11-25 12:00 | 198 | 197
2018-11-25 12:30 | 188 | 188
2018-11-25 13:00 | 203 | 202
2018-11-25 13:30 | 235 | 235
2018-11-25 14:00 | 232 | 230
2018-11-25 14:30 | 232 | 231
2018-11-25 15:00 | 233 | 231
2018-11-25 15:30 | 240 | 238
2018-11-25 16:00 | 239 | 237
2018-11-25 16:30 | 250 | 247
2018-11-25 17:00 | 256 | 253
2018-11-25 17:30 | 263 | 261
2018-11-25 18:00 | 266 | 263
2018-11-25 18:30 | 276 | 275
2018-11-25 19:00 | 272 | 271
2018-11-25 19:30 | 265 | 263
2018-11-25 20:00 | 253 | 251
2018-11-25 20:30 | 238 | 238
2018-11-25 21:00 | 225 | 225
2018-11-25 21:30 | 218 | 218
2018-11-25 22:00 | 214 | 214
2018-11-25 22:30 | 211 | 211
2018-11-25 23:00 | 195 | 194
2018-11-25 23:30 | 176 | 175
2018-11-26 | 163 | 162
2018-11-26 00:30 | 158 | 156
2018-11-26 01:00 | 156 | 155
2018-11-26 01:30 | 152 | 152
2018-11-26 02:00 | 147 | 147
2018-11-26 02:30 | 149 | 148
2018-11-26 03:00 | 149 | 148
2018-11-26 03:30 | 150 | 149
2018-11-26 04:00 | 153 | 152
2018-11-26 04:30 | 153 | 153
2018-11-26 05:00 | 165 | 164
2018-11-26 05:30 | 179 | 179
2018-11-26 06:00 | 195 | 195
2018-11-26 06:30 | 214 | 214
2018-11-26 07:00 | 228 | 228
2018-11-26 07:30 | 230 | 230
2018-11-26 08:00 | 233 | 233
2018-11-26 08:30 | 235 | 235
2018-11-26 09:00 | 237 | 237
2018-11-26 09:30 | 234 | 234
2018-11-26 10:00 | 234 | 233
2018-11-26 10:30 | 233 | 232
2018-11-26 11:00 | 233 | 232
2018-11-26 11:30 | 231 | 231
2018-11-26 12:00 | 227 | 227
2018-11-26 12:30 | 231 | 230
2018-11-26 13:00 | 232 | 232
2018-11-26 13:30 | 234 | 234
2018-11-26 14:00 | 239 | 238
2018-11-26 14:30 | 241 | 240
2018-11-26 15:00 | 250 | 250
2018-11-26 15:30 | 264 | 264
2018-11-26 16:00 | 277 | 277
2018-11-26 16:30 | 291 | 290
2018-11-26 17:00 | 295 | 295
2018-11-26 17:30 | 300 | 300
2018-11-26 18:00 | 292 | 292
2018-11-26 18:30 | 309 | 308
2018-11-26 19:00 | 295 | 295
2018-11-26 19:30 | 280 | 280
2018-11-26 20:00 | 267 | 267
2018-11-26 20:30 | 252 | 252
2018-11-26 21:00 | 236 | 235
2018-11-26 21:30 | 223 | 223
2018-11-26 22:00 | 218 | 218
2018-11-26 22:30 | 219 | 219
2018-11-26 23:00 | 208 | 207
2018-11-26 23:30 | 195 | 195
2018-11-27 | 181 | 181
2018-11-27 00:30 | 173 | 173
2018-11-27 01:00 | 171 | 170
2018-11-27 01:30 | 168 | 168
2018-11-27 02:00 | 165 | 165
2018-11-27 02:30 | 164 | 164
2018-11-27 03:00 | 164 | 164
2018-11-27 03:30 | 164 | 164
2018-11-27 04:00 | 165 | 164
2018-11-27 04:30 | 162 | 161
2018-11-27 05:00 | 174 | 173
2018-11-27 05:30 | 182 | 182
2018-11-27 06:00 | 201 | 201
2018-11-27 06:30 | 215 | 215
2018-11-27 07:00 | 248 | 247
2018-11-27 07:30 | 262 | 262
2018-11-27 08:00 | 268 | 267
2018-11-27 08:30 | 269 | 268
2018-11-27 09:00 | 271 | 270
2018-11-27 09:30 | 283 | 281
2018-11-27 10:00 | 266 | 264
2018-11-27 10:30 | 276 | 275
2018-11-27 11:00 | 277 | 275
2018-11-27 11:30 | 280 | 279
2018-11-27 12:00 | 274 | 273
2018-11-27 12:30 | 273 | 271
2018-11-27 13:00 | 269 | 268
2018-11-27 13:30 | 264 | 262
2018-11-27 14:00 | 267 | 265
2018-11-27 14:30 | 274 | 273
2018-11-27 15:00 | 289 | 288
2018-11-27 15:30 | 314 | 313
2018-11-27 16:00 | 332 | 331
2018-11-27 16:30 | 345 | 344
2018-11-27 17:00 | 348 | 347
2018-11-27 17:30 | 344 | 343
2018-11-27 18:00 | 341 | 341
2018-11-27 18:30 | 354 | 354
2018-11-27 19:00 | 349 | 349
2018-11-27 19:30 | 329 | 329
2018-11-27 20:00 | 316 | 315
2018-11-27 20:30 | 306 | 305
2018-11-27 21:00 | 286 | 285
2018-11-27 21:30 | 262 | 262
2018-11-27 22:00 | 255 | 255
2018-11-27 22:30 | 250 | 250
2018-11-27 23:00 | 234 | 234
2018-11-27 23:30 | 226 | 225
2018-11-28 | 220 | 220
2018-11-28 00:30 | 210 | 209
2018-11-28 01:00 | 197 | 197
2018-11-28 01:30 | 192 | 192
2018-11-28 02:00 | 189 | 189
2018-11-28 02:30 | 185 | 184
2018-11-28 03:00 | 186 | 186
2018-11-28 03:30 | 190 | 189
2018-11-28 04:00 | 195 | 194
2018-11-28 04:30 | 201 | 200
2018-11-28 05:00 | 205 | 205
2018-11-28 05:30 | 227 | 227
2018-11-28 06:00 | 253 | 252
2018-11-28 06:30 | 265 | 264
2018-11-28 07:00 | 289 | 288
2018-11-28 07:30 | 305 | 305
2018-11-28 08:00 | 312 | 312
2018-11-28 08:30 | 317 | 317
2018-11-28 09:00 | 307 | 307
2018-11-28 09:30 | 303 | 303
2018-11-28 10:00 | 304 | 304
2018-11-28 10:30 | 310 | 310
2018-11-28 11:00 | 317 | 317
2018-11-28 11:30 | 333 | 333
2018-11-28 12:00 | 375 | 374
2018-11-28 12:30 | 363 | 363
2018-11-28 13:00 | 331 | 330
2018-11-28 13:30 | 329 | 329
2018-11-28 14:00 | 339 | 339
2018-11-28 14:30 | 344 | 344
2018-11-28 15:00 | 353 | 353
2018-11-28 15:30 | 373 | 373
2018-11-28 16:00 | 394 | 394
2018-11-28 16:30 | 423 | 423
2018-11-28 17:00 | 425 | 425
2018-11-28 17:30 | 417 | 417
2018-11-28 18:00 | 407 | 407
2018-11-28 18:30 | 409 | 408
2018-11-28 19:00 | 399 | 398
2018-11-28 19:30 | 385 | 384
2018-11-28 20:00 | 365 | 364
2018-11-28 20:30 | 343 | 343
2018-11-28 21:00 | 321 | 321
2018-11-28 21:30 | 298 | 298
2018-11-28 22:00 | 287 | 287
2018-11-28 22:30 | 287 | 287
2018-11-28 23:00 | 271 | 271
2018-11-28 23:30 | 250 | 249
2018-11-29 | 231 | 231
2018-11-29 00:30 | 220 | 220
2018-11-29 01:00 | 204 | 204
2018-11-29 01:30 | 193 | 193
2018-11-29 02:00 | 191 | 191
2018-11-29 02:30 | 190 | 190
2018-11-29 03:00 | 193 | 193
2018-11-29 03:30 | 199 | 199
2018-11-29 04:00 | 202 | 202
2018-11-29 04:30 | 203 | 203
2018-11-29 05:00 | 214 | 214
2018-11-29 05:30 | 229 | 228
2018-11-29 06:00 | 243 | 242
2018-11-29 06:30 | 254 | 254
2018-11-29 07:00 | 261 | 261
2018-11-29 07:30 | 270 | 270
2018-11-29 08:00 | 282 | 282
2018-11-29 08:30 | 281 | 281
2018-11-29 09:00 | 286 | 285
2018-11-29 09:30 | 280 | 280
2018-11-29 10:00 | 279 | 279
2018-11-29 10:30 | 279 | 279
2018-11-29 11:00 | 276 | 276
2018-11-29 11:30 | 276 | 276
2018-11-29 12:00 | 276 | 276
2018-11-29 12:30 | 279 | 279
2018-11-29 13:00 | 287 | 286
2018-11-29 13:30 | 297 | 297
2018-11-29 14:00 | 318 | 318
2018-11-29 14:30 | 325 | 325
2018-11-29 15:00 | 332 | 332
2018-11-29 15:30 | 343 | 343
2018-11-29 16:00 | 351 | 350
2018-11-29 16:30 | 361 | 360
2018-11-29 17:00 | 361 | 360
2018-11-29 17:30 | 357 | 356
2018-11-29 18:00 | 356 | 355
2018-11-29 18:30 | 366 | 365
2018-11-29 19:00 | 360 | 360
2018-11-29 19:30 | 352 | 351
2018-11-29 20:00 | 338 | 338
2018-11-29 20:30 | 321 | 321
2018-11-29 21:00 | 304 | 303
2018-11-29 21:30 | 282 | 281
2018-11-29 22:00 | 275 | 274
2018-11-29 22:30 | 270 | 269
2018-11-29 23:00 | 255 | 254
2018-11-29 23:30 | 240 | 239
2018-11-30 | 221 | 220
2018-11-30 00:30 | 215 | 214
2018-11-30 01:00 | 207 | 206
2018-11-30 01:30 | 204 | 203
2018-11-30 02:00 | 201 | 200
2018-11-30 02:30 | 200 | 199
2018-11-30 03:00 | 200 | 199
2018-11-30 03:30 | 201 | 200
2018-11-30 04:00 | 204 | 202
2018-11-30 04:30 | 208 | 206
2018-11-30 05:00 | 214 | 212
2018-11-30 05:30 | 227 | 226
2018-11-30 06:00 | 244 | 244
2018-11-30 06:30 | 258 | 257
2018-11-30 07:00 | 276 | 274
2018-11-30 07:30 | 280 | 279
2018-11-30 08:00 | 281 | 280
2018-11-30 08:30 | 276 | 276
2018-11-30 09:00 | 282 | 281
2018-11-30 09:30 | 281 | 281
2018-11-30 10:00 | 273 | 272
2018-11-30 10:30 | 268 | 267
2018-11-30 11:00 | 285 | 284
2018-11-30 11:30 | 286 | 284
2018-11-30 12:00 | 282 | 280
2018-11-30 12:30 | 272 | 269
2018-11-30 13:00 | 305 | 303
2018-11-30 13:30 | 285 | 282
2018-11-30 14:00 | 281 | 278
2018-11-30 14:30 | 287 | 285
2018-11-30 15:00 | 309 | 307
2018-11-30 15:30 | 326 | 324
2018-11-30 16:00 | 340 | 338
2018-11-30 16:30 | 349 | 348
2018-11-30 17:00 | 348 | 345
2018-11-30 17:30 | 342 | 338
2018-11-30 18:00 | 337 | 333
2018-11-30 18:30 | 341 | 340
2018-11-30 19:00 | 338 | 338
2018-11-30 19:30 | 333 | 333
2018-11-30 20:00 | 323 | 323
2018-11-30 20:30 | 310 | 309
2018-11-30 21:00 | 298 | 297
2018-11-30 21:30 | 285 | 283
2018-11-30 22:00 | 280 | 278
2018-11-30 22:30 | 276 | 275
2018-11-30 23:00 | 258 | 257
2018-11-30 23:30 | 239 | 238
2018-12-01 | 223 | 221
2018-12-01 00:30 | 214 | 212
2018-12-01 01:00 | 205 | 203
2018-12-01 01:30 | 202 | 199
2018-12-01 02:00 | 200 | 197
2018-12-01 02:30 | 198 | 194
2018-12-01 03:00 | 188 | 186
2018-12-01 03:30 | 188 | 186
2018-12-01 04:00 | 192 | 190
2018-12-01 04:30 | 186 | 184
2018-12-01 05:00 | 188 | 186
2018-12-01 05:30 | 194 | 192
2018-12-01 06:00 | 206 | 205
2018-12-01 06:30 | 225 | 225
2018-12-01 07:00 | 236 | 236
2018-12-01 07:30 | 239 | 239
2018-12-01 08:00 | 247 | 246
2018-12-01 08:30 | 244 | 244
2018-12-01 09:00 | 242 | 242
2018-12-01 09:30 | 242 | 242
2018-12-01 10:00 | 246 | 246
2018-12-01 10:30 | 250 | 249
2018-12-01 11:00 | 256 | 254
2018-12-01 11:30 | 261 | 259
2018-12-01 12:00 | 266 | 265
2018-12-01 12:30 | 274 | 273
2018-12-01 13:00 | 285 | 284
2018-12-01 13:30 | 299 | 299
2018-12-01 14:00 | 315 | 314
2018-12-01 14:30 | 335 | 335
2018-12-01 15:00 | 352 | 352
2018-12-01 15:30 | 365 | 365
2018-12-01 16:00 | 378 | 378
2018-12-01 16:30 | 391 | 391
2018-12-01 17:00 | 393 | 392
2018-12-01 17:30 | 389 | 388
2018-12-01 18:00 | 382 | 380
2018-12-01 18:30 | 384 | 383
2018-12-01 19:00 | 380 | 378
2018-12-01 19:30 | 372 | 370
2018-12-01 20:00 | 360 | 357
2018-12-01 20:30 | 345 | 341
2018-12-01 21:00 | 330 | 326
2018-12-01 21:30 | 312 | 308
2018-12-01 22:00 | 300 | 299
2018-12-01 22:30 | 292 | 291
2018-12-01 23:00 | 264 | 262
2018-12-01 23:30 | 244 | 242
2018-12-02 | 221 | 220
2018-12-02 00:30 | 209 | 209
2018-12-02 01:00 | 204 | 203
2018-12-02 01:30 | 199 | 198
2018-12-02 02:00 | 190 | 189
2018-12-02 02:30 | 189 | 188
2018-12-02 03:00 | 190 | 188
2018-12-02 03:30 | 190 | 188
2018-12-02 04:00 | 188 | 187
2018-12-02 04:30 | 188 | 186
2018-12-02 05:00 | 195 | 193
2018-12-02 05:30 | 197 | 195
2018-12-02 06:00 | 211 | 210
2018-12-02 06:30 | 222 | 222
2018-12-02 07:00 | 233 | 233
2018-12-02 07:30 | 245 | 245
2018-12-02 08:00 | 258 | 257
2018-12-02 08:30 | 266 | 266
2018-12-02 09:00 | 258 | 257
2018-12-02 09:30 | 253 | 253
2018-12-02 10:00 | 267 | 267
2018-12-02 10:30 | 284 | 283
2018-12-02 11:00 | 296 | 295
2018-12-02 11:30 | 317 | 316
2018-12-02 12:00 | 337 | 337
2018-12-02 12:30 | 334 | 333
2018-12-02 13:00 | 351 | 350
2018-12-02 13:30 | 375 | 375
2018-12-02 14:00 | 391 | 391
2018-12-02 14:30 | 405 | 405
2018-12-02 15:00 | 424 | 424
2018-12-02 15:30 | 429 | 429
2018-12-02 16:00 | 441 | 441
2018-12-02 16:30 | 460 | 459
2018-12-02 17:00 | 463 | 462
2018-12-02 17:30 | 462 | 459
2018-12-02 18:00 | 458 | 455
2018-12-02 18:30 | 460 | 457
2018-12-02 19:00 | 445 | 444
2018-12-02 19:30 | 426 | 425
2018-12-02 20:00 | 406 | 404
2018-12-02 20:30 | 392 | 389
2018-12-02 21:00 | 365 | 363
2018-12-02 21:30 | 334 | 331
2018-12-02 22:00 | 318 | 317
2018-12-02 22:30 | 309 | 308
2018-12-02 23:00 | 285 | 284
2018-12-02 23:30 | 258 | 258
2018-12-03 | 241 | 241
2018-12-03 00:30 | 223 | 223
2018-12-03 01:00 | 202 | 202
2018-12-03 01:30 | 198 | 198
2018-12-03 02:00 | 194 | 194
2018-12-03 02:30 | 189 | 189
2018-12-03 03:00 | 190 | 190
2018-12-03 03:30 | 199 | 199
2018-12-03 04:00 | 200 | 200
2018-12-03 04:30 | 206 | 206
2018-12-03 05:00 | 220 | 220
2018-12-03 05:30 | 237 | 237
2018-12-03 06:00 | 259 | 259
2018-12-03 06:30 | 274 | 274
2018-12-03 07:00 | 290 | 290
2018-12-03 07:30 | 298 | 297
2018-12-03 08:00 | 305 | 305
2018-12-03 08:30 | 308 | 307
2018-12-03 09:00 | 311 | 310
2018-12-03 09:30 | 312 | 311
2018-12-03 10:00 | 311 | 310
2018-12-03 10:30 | 307 | 306
2018-12-03 11:00 | 299 | 297
2018-12-03 11:30 | 299 | 298
2018-12-03 12:00 | 315 | 314
2018-12-03 12:30 | 302 | 301
2018-12-03 13:00 | 316 | 315
2018-12-03 13:30 | 324 | 323
2018-12-03 14:00 | 335 | 334
2018-12-03 14:30 | 323 | 322
2018-12-03 15:00 | 324 | 322
2018-12-03 15:30 | 335 | 334
2018-12-03 16:00 | 341 | 340
2018-12-03 16:30 | 347 | 346
2018-12-03 17:00 | 345 | 342
2018-12-03 17:30 | 336 | 334
2018-12-03 18:00 | 331 | 329
2018-12-03 18:30 | 335 | 333
2018-12-03 19:00 | 326 | 325
2018-12-03 19:30 | 313 | 313
2018-12-03 20:00 | 303 | 303
2018-12-03 20:30 | 288 | 287
2018-12-03 21:00 | 269 | 269
2018-12-03 21:30 | 252 | 251
2018-12-03 22:00 | 245 | 244
2018-12-03 22:30 | 241 | 241
2018-12-03 23:00 | 227 | 227
2018-12-03 23:30 | 213 | 213
2018-12-04 | 196 | 196
2018-12-04 00:30 | 184 | 183
2018-12-04 01:00 | 179 | 178
2018-12-04 01:30 | 173 | 172
2018-12-04 02:00 | 164 | 162
2018-12-04 02:30 | 161 | 159
2018-12-04 03:00 | 165 | 163
2018-12-04 03:30 | 175 | 174
2018-12-04 04:00 | 180 | 178
2018-12-04 04:30 | 186 | 184
2018-12-04 05:00 | 194 | 193
2018-12-04 05:30 | 203 | 202
2018-12-04 06:00 | 215 | 215
2018-12-04 06:30 | 231 | 231
2018-12-04 07:00 | 252 | 251
2018-12-04 07:30 | 251 | 251
2018-12-04 08:00 | 261 | 261
2018-12-04 08:30 | 263 | 262
2018-12-04 09:00 | 279 | 279
2018-12-04 09:30 | 282 | 281
2018-12-04 10:00 | 286 | 286
2018-12-04 10:30 | 274 | 274
2018-12-04 11:00 | 282 | 281
2018-12-04 11:30 | 275 | 274
2018-12-04 12:00 | 260 | 259
2018-12-04 12:30 | 267 | 267
2018-12-04 13:00 | 281 | 280
2018-12-04 13:30 | 302 | 302
2018-12-04 14:00 | 319 | 319
2018-12-04 14:30 | 322 | 322
2018-12-04 15:00 | 321 | 320
2018-12-04 15:30 | 317 | 316
2018-12-04 16:00 | 320 | 318
2018-12-04 16:30 | 324 | 322
2018-12-04 17:00 | 323 | 321
2018-12-04 17:30 | 319 | 317
2018-12-04 18:00 | 318 | 316
2018-12-04 18:30 | 332 | 331
2018-12-04 19:00 | 325 | 324
2018-12-04 19:30 | 318 | 316
2018-12-04 20:00 | 308 | 306
2018-12-04 20:30 | 294 | 293
2018-12-04 21:00 | 278 | 277
2018-12-04 21:30 | 262 | 260
2018-12-04 22:00 | 257 | 254
2018-12-04 22:30 | 253 | 250
2018-12-04 23:00 | 233 | 231
2018-12-04 23:30 | 210 | 210
2018-12-05 | 196 | 196
2018-12-05 00:30 | 188 | 188
2018-12-05 01:00 | 172 | 172
2018-12-05 01:30 | 163 | 163
2018-12-05 02:00 | 157 | 157
2018-12-05 02:30 | 155 | 154
2018-12-05 03:00 | 155 | 154
2018-12-05 03:30 | 157 | 157
2018-12-05 04:00 | 165 | 165
2018-12-05 04:30 | 167 | 167
2018-12-05 05:00 | 189 | 188
2018-12-05 05:30 | 203 | 203
2018-12-05 06:00 | 212 | 212
2018-12-05 06:30 | 228 | 227
2018-12-05 07:00 | 245 | 245
2018-12-05 07:30 | 253 | 252
2018-12-05 08:00 | 252 | 252
2018-12-05 08:30 | 257 | 257
2018-12-05 09:00 | 261 | 260
2018-12-05 09:30 | 262 | 261
2018-12-05 10:00 | 272 | 271
2018-12-05 10:30 | 276 | 274
2018-12-05 11:00 | 257 | 256
2018-12-05 11:30 | 246 | 246
2018-12-05 12:00 | 251 | 251
2018-12-05 12:30 | 252 | 251
2018-12-05 13:00 | 247 | 246
2018-12-05 13:30 | 253 | 252
2018-12-05 14:00 | 249 | 248
2018-12-05 14:30 | 251 | 249
2018-12-05 15:00 | 255 | 253
2018-12-05 15:30 | 265 | 264
2018-12-05 16:00 | 276 | 274
2018-12-05 16:30 | 286 | 284
2018-12-05 17:00 | 288 | 286
2018-12-05 17:30 | 290 | 287
2018-12-05 18:00 | 290 | 288
2018-12-05 18:30 | 301 | 300
2018-12-05 19:00 | 299 | 298
2018-12-05 19:30 | 293 | 292
2018-12-05 20:00 | 284 | 284
2018-12-05 20:30 | 271 | 271
2018-12-05 21:00 | 257 | 257
2018-12-05 21:30 | 241 | 241
2018-12-05 22:00 | 236 | 236
2018-12-05 22:30 | 236 | 236
2018-12-05 23:00 | 222 | 222
2018-12-05 23:30 | 208 | 208
2018-12-06 | 187 | 187
2018-12-06 00:30 | 177 | 177
2018-12-06 01:00 | 166 | 166
2018-12-06 01:30 | 157 | 156
2018-12-06 02:00 | 155 | 154
2018-12-06 02:30 | 152 | 151
2018-12-06 03:00 | 152 | 151
2018-12-06 03:30 | 151 | 151
2018-12-06 04:00 | 153 | 153
2018-12-06 04:30 | 157 | 157
2018-12-06 05:00 | 173 | 172
2018-12-06 05:30 | 188 | 188
2018-12-06 06:00 | 206 | 206
2018-12-06 06:30 | 209 | 209
2018-12-06 07:00 | 226 | 226
2018-12-06 07:30 | 229 | 229
2018-12-06 08:00 | 239 | 239
2018-12-06 08:30 | 237 | 237
2018-12-06 09:00 | 237 | 236
2018-12-06 09:30 | 231 | 231
2018-12-06 10:00 | 231 | 230
2018-12-06 10:30 | 227 | 227
2018-12-06 11:00 | 224 | 224
2018-12-06 11:30 | 219 | 219
2018-12-06 12:00 | 223 | 222
2018-12-06 12:30 | 224 | 224
2018-12-06 13:00 | 237 | 237
2018-12-06 13:30 | 243 | 243
2018-12-06 14:00 | 239 | 239
2018-12-06 14:30 | 234 | 234
2018-12-06 15:00 | 239 | 239
2018-12-06 15:30 | 250 | 250
2018-12-06 16:00 | 258 | 258
2018-12-06 16:30 | 278 | 278
2018-12-06 17:00 | 282 | 281
2018-12-06 17:30 | 285 | 284
2018-12-06 18:00 | 287 | 286
2018-12-06 18:30 | 295 | 294
2018-12-06 19:00 | 295 | 295
2018-12-06 19:30 | 293 | 292
2018-12-06 20:00 | 288 | 286
2018-12-06 20:30 | 277 | 275
2018-12-06 21:00 | 263 | 261
2018-12-06 21:30 | 234 | 234
2018-12-06 22:00 | 227 | 226
2018-12-06 22:30 | 222 | 221
2018-12-06 23:00 | 205 | 204
2018-12-06 23:30 | 188 | 186
2018-12-07 | 175 | 173
2018-12-07 00:30 | 170 | 170
2018-12-07 01:00 | 168 | 167
2018-12-07 01:30 | 159 | 158
2018-12-07 02:00 | 156 | 155
2018-12-07 02:30 | 156 | 155
2018-12-07 03:00 | 154 | 154
2018-12-07 03:30 | 153 | 152
2018-12-07 04:00 | 154 | 153
2018-12-07 04:30 | 155 | 154
2018-12-07 05:00 | 167 | 166
2018-12-07 05:30 | 179 | 178
2018-12-07 06:00 | 197 | 197
2018-12-07 06:30 | 209 | 209
2018-12-07 07:00 | 221 | 220
2018-12-07 07:30 | 226 | 226
2018-12-07 08:00 | 229 | 228
2018-12-07 08:30 | 234 | 233
2018-12-07 09:00 | 243 | 243
2018-12-07 09:30 | 251 | 251
2018-12-07 10:00 | 250 | 249
2018-12-07 10:30 | 251 | 251
2018-12-07 11:00 | 241 | 240
2018-12-07 11:30 | 242 | 242
2018-12-07 12:00 | 253 | 253
2018-12-07 12:30 | 251 | 251
2018-12-07 13:00 | 256 | 255
2018-12-07 13:30 | 255 | 255
2018-12-07 14:00 | 259 | 258
2018-12-07 14:30 | 236 | 235
2018-12-07 15:00 | 234 | 233
2018-12-07 15:30 | 249 | 249
2018-12-07 16:00 | 240 | 239
2018-12-07 16:30 | 258 | 257
2018-12-07 17:00 | 271 | 270
2018-12-07 17:30 | 272 | 271
2018-12-07 18:00 | 264 | 264
2018-12-07 18:30 | 267 | 267
2018-12-07 19:00 | 268 | 268
2018-12-07 19:30 | 264 | 263
2018-12-07 20:00 | 249 | 249
2018-12-07 20:30 | 249 | 249
2018-12-07 21:00 | 248 | 248
2018-12-07 21:30 | 230 | 230
2018-12-07 22:00 | 227 | 227
2018-12-07 22:30 | 221 | 221
2018-12-07 23:00 | 206 | 206
2018-12-07 23:30 | 196 | 196
2018-12-08 | 182 | 181
2018-12-08 00:30 | 179 | 178
2018-12-08 01:00 | 172 | 172
2018-12-08 01:30 | 168 | 168
2018-12-08 02:00 | 164 | 164
2018-12-08 02:30 | 158 | 157
2018-12-08 03:00 | 158 | 155
2018-12-08 03:30 | 159 | 155
2018-12-08 04:00 | 157 | 154
2018-12-08 04:30 | 157 | 153
2018-12-08 05:00 | 163 | 159
2018-12-08 05:30 | 171 | 168
2018-12-08 06:00 | 181 | 178
2018-12-08 06:30 | 191 | 189
2018-12-08 07:00 | 209 | 208
2018-12-08 07:30 | 222 | 221
2018-12-08 08:00 | 228 | 227
2018-12-08 08:30 | 223 | 222
2018-12-08 09:00 | 227 | 227
2018-12-08 09:30 | 222 | 222
2018-12-08 10:00 | 243 | 242
2018-12-08 10:30 | 252 | 251
2018-12-08 11:00 | 256 | 253
2018-12-08 11:30 | 253 | 249
2018-12-08 12:00 | 249 | 245
2018-12-08 12:30 | 252 | 248
2018-12-08 13:00 | 253 | 249
2018-12-08 13:30 | 242 | 239
2018-12-08 14:00 | 238 | 235
2018-12-08 14:30 | 237 | 234
2018-12-08 15:00 | 226 | 222
2018-12-08 15:30 | 230 | 227
2018-12-08 16:00 | 243 | 240
2018-12-08 16:30 | 248 | 245
2018-12-08 17:00 | 247 | 243
2018-12-08 17:30 | 249 | 246
2018-12-08 18:00 | 247 | 244
2018-12-08 18:30 | 254 | 252
2018-12-08 19:00 | 255 | 252
2018-12-08 19:30 | 246 | 244
2018-12-08 20:00 | 238 | 237
2018-12-08 20:30 | 240 | 239
2018-12-08 21:00 | 234 | 233
2018-12-08 21:30 | 223 | 221
2018-12-08 22:00 | 218 | 216
2018-12-08 22:30 | 218 | 217
2018-12-08 23:00 | 208 | 205
2018-12-08 23:30 | 193 | 189
2018-12-09 | 177 | 172
2018-12-09 00:30 | 175 | 169
2018-12-09 01:00 | 169 | 165
2018-12-09 01:30 | 159 | 156
2018-12-09 02:00 | 160 | 157
2018-12-09 02:30 | 159 | 155
2018-12-09 03:00 | 159 | 156
2018-12-09 03:30 | 158 | 155
2018-12-09 04:00 | 159 | 156
2018-12-09 04:30 | 156 | 152
2018-12-09 05:00 | 158 | 154
2018-12-09 05:30 | 161 | 157
2018-12-09 06:00 | 165 | 162
2018-12-09 06:30 | 168 | 165
2018-12-09 07:00 | 176 | 175
2018-12-09 07:30 | 182 | 182
2018-12-09 08:00 | 200 | 200
2018-12-09 08:30 | 204 | 203
2018-12-09 09:00 | 198 | 197
2018-12-09 09:30 | 202 | 202
2018-12-09 10:00 | 203 | 203
2018-12-09 10:30 | 204 | 203
2018-12-09 11:00 | 202 | 201
2018-12-09 11:30 | 204 | 204
2018-12-09 12:00 | 204 | 204
2018-12-09 12:30 | 216 | 216
2018-12-09 13:00 | 227 | 227
2018-12-09 13:30 | 235 | 234
2018-12-09 14:00 | 238 | 238
2018-12-09 14:30 | 241 | 241
2018-12-09 15:00 | 242 | 242
2018-12-09 15:30 | 239 | 239
2018-12-09 16:00 | 246 | 246
2018-12-09 16:30 | 258 | 258
2018-12-09 17:00 | 265 | 265
2018-12-09 17:30 | 273 | 273
2018-12-09 18:00 | 276 | 276
2018-12-09 18:30 | 286 | 286
2018-12-09 19:00 | 287 | 287
2018-12-09 19:30 | 280 | 280
2018-12-09 20:00 | 272 | 272
2018-12-09 20:30 | 263 | 263
2018-12-09 21:00 | 251 | 251
2018-12-09 21:30 | 235 | 234
2018-12-09 22:00 | 230 | 229
2018-12-09 22:30 | 228 | 227
2018-12-09 23:00 | 213 | 212
2018-12-09 23:30 | 202 | 202
2018-12-10 | 189 | 188
2018-12-10 00:30 | 183 | 183
2018-12-10 01:00 | 179 | 179
2018-12-10 01:30 | 172 | 171
2018-12-10 02:00 | 165 | 165
2018-12-10 02:30 | 163 | 163
2018-12-10 03:00 | 164 | 164
2018-12-10 03:30 | 164 | 164
2018-12-10 04:00 | 172 | 172
2018-12-10 04:30 | 173 | 173
2018-12-10 05:00 | 183 | 183
2018-12-10 05:30 | 197 | 197
2018-12-10 06:00 | 210 | 209
2018-12-10 06:30 | 227 | 227
2018-12-10 07:00 | 247 | 247
2018-12-10 07:30 | 255 | 254
2018-12-10 08:00 | 257 | 257
2018-12-10 08:30 | 255 | 255
2018-12-10 09:00 | 254 | 254
2018-12-10 09:30 | 260 | 260
2018-12-10 10:00 | 262 | 261
2018-12-10 10:30 | 270 | 269
2018-12-10 11:00 | 267 | 265
2018-12-10 11:30 | 262 | 261
2018-12-10 12:00 | 263 | 262
2018-12-10 12:30 | 266 | 265
2018-12-10 13:00 | 272 | 271
2018-12-10 13:30 | 274 | 273
2018-12-10 14:00 | 282 | 281
2018-12-10 14:30 | 288 | 287
2018-12-10 15:00 | 318 | 317
2018-12-10 15:30 | 325 | 325
2018-12-10 16:00 | 320 | 318
2018-12-10 16:30 | 334 | 333
2018-12-10 17:00 | 339 | 337
2018-12-10 17:30 | 341 | 339
2018-12-10 18:00 | 336 | 334
2018-12-10 18:30 | 338 | 336
2018-12-10 19:00 | 335 | 334
2018-12-10 19:30 | 327 | 325
2018-12-10 20:00 | 313 | 310
2018-12-10 20:30 | 297 | 296
2018-12-10 21:00 | 277 | 277
2018-12-10 21:30 | 257 | 256
2018-12-10 22:00 | 250 | 249
2018-12-10 22:30 | 246 | 245
2018-12-10 23:00 | 230 | 229
2018-12-10 23:30 | 211 | 209
2018-12-11 | 191 | 190
2018-12-11 00:30 | 182 | 182
2018-12-11 01:00 | 174 | 174
2018-12-11 01:30 | 170 | 169
2018-12-11 02:00 | 169 | 169
2018-12-11 02:30 | 169 | 168
2018-12-11 03:00 | 168 | 167
2018-12-11 03:30 | 172 | 171
2018-12-11 04:00 | 178 | 178
2018-12-11 04:30 | 175 | 174
2018-12-11 05:00 | 181 | 181
2018-12-11 05:30 | 193 | 193
2018-12-11 06:00 | 211 | 211
2018-12-11 06:30 | 221 | 221
2018-12-11 07:00 | 236 | 236
2018-12-11 07:30 | 242 | 242
2018-12-11 08:00 | 251 | 251
2018-12-11 08:30 | 249 | 249
2018-12-11 09:00 | 250 | 250
2018-12-11 09:30 | 248 | 248
2018-12-11 10:00 | 250 | 250
2018-12-11 10:30 | 257 | 257
2018-12-11 11:00 | 261 | 261
2018-12-11 11:30 | 254 | 254
2018-12-11 12:00 | 260 | 259
2018-12-11 12:30 | 259 | 259
2018-12-11 13:00 | 267 | 267
2018-12-11 13:30 | 270 | 270
2018-12-11 14:00 | 280 | 280
2018-12-11 14:30 | 289 | 289
2018-12-11 15:00 | 310 | 309
2018-12-11 15:30 | 328 | 327
2018-12-11 16:00 | 344 | 343
2018-12-11 16:30 | 338 | 337
2018-12-11 17:00 | 331 | 330
2018-12-11 17:30 | 338 | 336
2018-12-11 18:00 | 333 | 332
2018-12-11 18:30 | 337 | 336
2018-12-11 19:00 | 335 | 334
2018-12-11 19:30 | 327 | 326
2018-12-11 20:00 | 315 | 313
2018-12-11 20:30 | 299 | 298
2018-12-11 21:00 | 278 | 278
2018-12-11 21:30 | 257 | 257
2018-12-11 22:00 | 250 | 250
2018-12-11 22:30 | 245 | 245
2018-12-11 23:00 | 229 | 229
2018-12-11 23:30 | 210 | 210
2018-12-12 | 195 | 194
2018-12-12 00:30 | 186 | 185
2018-12-12 01:00 | 180 | 179
2018-12-12 01:30 | 177 | 176
2018-12-12 02:00 | 177 | 175
2018-12-12 02:30 | 181 | 179
2018-12-12 03:00 | 185 | 183
2018-12-12 03:30 | 185 | 184
2018-12-12 04:00 | 183 | 182
2018-12-12 04:30 | 181 | 180
2018-12-12 05:00 | 190 | 190
2018-12-12 05:30 | 198 | 198
2018-12-12 06:00 | 211 | 211
2018-12-12 06:30 | 223 | 222
2018-12-12 07:00 | 243 | 243
2018-12-12 07:30 | 247 | 247
2018-12-12 08:00 | 254 | 254
2018-12-12 08:30 | 251 | 251
2018-12-12 09:00 | 252 | 252
2018-12-12 09:30 | 253 | 253
2018-12-12 10:00 | 253 | 253
2018-12-12 10:30 | 250 | 250
2018-12-12 11:00 | 248 | 248
2018-12-12 11:30 | 248 | 248
2018-12-12 12:00 | 249 | 248
2018-12-12 12:30 | 254 | 253
2018-12-12 13:00 | 258 | 258
2018-12-12 13:30 | 264 | 264
2018-12-12 14:00 | 267 | 267
2018-12-12 14:30 | 278 | 278
2018-12-12 15:00 | 294 | 294
2018-12-12 15:30 | 310 | 310
2018-12-12 16:00 | 323 | 323
2018-12-12 16:30 | 333 | 333
2018-12-12 17:00 | 337 | 336
2018-12-12 17:30 | 336 | 335
2018-12-12 18:00 | 331 | 330
2018-12-12 18:30 | 335 | 334
2018-12-12 19:00 | 329 | 328
2018-12-12 19:30 | 322 | 320
2018-12-12 20:00 | 310 | 308
2018-12-12 20:30 | 296 | 295
2018-12-12 21:00 | 280 | 278
2018-12-12 21:30 | 260 | 258
2018-12-12 22:00 | 250 | 250
2018-12-12 22:30 | 246 | 246
2018-12-12 23:00 | 230 | 230
2018-12-12 23:30 | 211 | 210
2018-12-13 | 197 | 196
2018-12-13 00:30 | 186 | 185
2018-12-13 01:00 | 179 | 177
2018-12-13 01:30 | 174 | 173
2018-12-13 02:00 | 174 | 174
2018-12-13 02:30 | 176 | 176
2018-12-13 03:00 | 177 | 176
2018-12-13 03:30 | 178 | 177
2018-12-13 04:00 | 182 | 182
2018-12-13 04:30 | 182 | 182
2018-12-13 05:00 | 187 | 186
2018-12-13 05:30 | 200 | 199
2018-12-13 06:00 | 212 | 212
2018-12-13 06:30 | 223 | 223
2018-12-13 07:00 | 242 | 240
2018-12-13 07:30 | 257 | 255
2018-12-13 08:00 | 278 | 275
2018-12-13 08:30 | 266 | 262
2018-12-13 09:00 | 267 | 264
2018-12-13 09:30 | 272 | 269
2018-12-13 10:00 | 271 | 266
2018-12-13 10:30 | 263 | 258
2018-12-13 11:00 | 263 | 259
2018-12-13 11:30 | 263 | 259
2018-12-13 12:00 | 263 | 259
2018-12-13 12:30 | 268 | 263
2018-12-13 13:00 | 279 | 275
2018-12-13 13:30 | 289 | 286
2018-12-13 14:00 | 299 | 296
2018-12-13 14:30 | 311 | 308
2018-12-13 15:00 | 327 | 324
2018-12-13 15:30 | 336 | 333
2018-12-13 16:00 | 344 | 341
2018-12-13 16:30 | 350 | 347
2018-12-13 17:00 | 347 | 343
2018-12-13 17:30 | 356 | 353
2018-12-13 18:00 | 354 | 349
2018-12-13 18:30 | 359 | 355
2018-12-13 19:00 | 353 | 349
2018-12-13 19:30 | 347 | 342
2018-12-13 20:00 | 336 | 330
2018-12-13 20:30 | 323 | 318
2018-12-13 21:00 | 305 | 298
2018-12-13 21:30 | 280 | 274
2018-12-13 22:00 | 269 | 266
2018-12-13 22:30 | 262 | 261
2018-12-13 23:00 | 246 | 243
2018-12-13 23:30 | 227 | 224
2018-12-14 | 214 | 209
2018-12-14 00:30 | 203 | 198
2018-12-14 01:00 | 190 | 188
2018-12-14 01:30 | 186 | 184
2018-12-14 02:00 | 184 | 182
2018-12-14 02:30 | 182 | 180
2018-12-14 03:00 | 182 | 180
2018-12-14 03:30 | 183 | 180
2018-12-14 04:00 | 185 | 183
2018-12-14 04:30 | 189 | 187
2018-12-14 05:00 | 199 | 197
2018-12-14 05:30 | 212 | 211
2018-12-14 06:00 | 230 | 229
2018-12-14 06:30 | 248 | 247
2018-12-14 07:00 | 280 | 279
2018-12-14 07:30 | 302 | 302
2018-12-14 08:00 | 326 | 325
2018-12-14 08:30 | 332 | 332
2018-12-14 09:00 | 334 | 334
2018-12-14 09:30 | 330 | 330
2018-12-14 10:00 | 314 | 314
2018-12-14 10:30 | 291 | 291
2018-12-14 11:00 | 290 | 290
2018-12-14 11:30 | 287 | 287
2018-12-14 12:00 | 296 | 296
2018-12-14 12:30 | 293 | 293
2018-12-14 13:00 | 296 | 295
2018-12-14 13:30 | 309 | 309
2018-12-14 14:00 | 315 | 314
2018-12-14 14:30 | 305 | 305
2018-12-14 15:00 | 312 | 312
2018-12-14 15:30 | 352 | 352
2018-12-14 16:00 | 360 | 359
2018-12-14 16:30 | 354 | 353
2018-12-14 17:00 | 337 | 336
2018-12-14 17:30 | 322 | 322
2018-12-14 18:00 | 315 | 314
2018-12-14 18:30 | 317 | 317
2018-12-14 19:00 | 313 | 313
2018-12-14 19:30 | 309 | 309
2018-12-14 20:00 | 298 | 298
2018-12-14 20:30 | 289 | 289
2018-12-14 21:00 | 278 | 278
2018-12-14 21:30 | 272 | 271
2018-12-14 22:00 | 267 | 267
2018-12-14 22:30 | 264 | 264
2018-12-14 23:00 | 248 | 248
2018-12-14 23:30 | 230 | 230
2018-12-15 | 217 | 216
2018-12-15 00:30 | 211 | 210
2018-12-15 01:00 | 205 | 205
2018-12-15 01:30 | 201 | 201
2018-12-15 02:00 | 201 | 201
2018-12-15 02:30 | 199 | 199
2018-12-15 03:00 | 202 | 202
2018-12-15 03:30 | 201 | 201
2018-12-15 04:00 | 201 | 201
2018-12-15 04:30 | 198 | 198
2018-12-15 05:00 | 200 | 200
2018-12-15 05:30 | 207 | 207
2018-12-15 06:00 | 221 | 221
2018-12-15 06:30 | 222 | 222
2018-12-15 07:00 | 236 | 236
2018-12-15 07:30 | 250 | 250
2018-12-15 08:00 | 269 | 269
2018-12-15 08:30 | 270 | 270
2018-12-15 09:00 | 273 | 272
2018-12-15 09:30 | 273 | 273
2018-12-15 10:00 | 279 | 279
2018-12-15 10:30 | 293 | 292
2018-12-15 11:00 | 289 | 288
2018-12-15 11:30 | 286 | 285
2018-12-15 12:00 | 285 | 284
2018-12-15 12:30 | 290 | 290
2018-12-15 13:00 | 297 | 297
2018-12-15 13:30 | 288 | 288
2018-12-15 14:00 | 288 | 287
2018-12-15 14:30 | 296 | 295
2018-12-15 15:00 | 306 | 305
2018-12-15 15:30 | 307 | 306
2018-12-15 16:00 | 306 | 305
2018-12-15 16:30 | 318 | 317
2018-12-15 17:00 | 321 | 320
2018-12-15 17:30 | 317 | 316
2018-12-15 18:00 | 312 | 311
2018-12-15 18:30 | 308 | 308
2018-12-15 19:00 | 298 | 298
2018-12-15 19:30 | 292 | 292
2018-12-15 20:00 | 287 | 287
2018-12-15 20:30 | 279 | 279
2018-12-15 21:00 | 270 | 270
2018-12-15 21:30 | 262 | 261
2018-12-15 22:00 | 257 | 257
2018-12-15 22:30 | 253 | 252
2018-12-15 23:00 | 241 | 241
2018-12-15 23:30 | 229 | 228
2018-12-16 | 219 | 218
2018-12-16 00:30 | 215 | 213
2018-12-16 01:00 | 205 | 205
2018-12-16 01:30 | 202 | 202
2018-12-16 02:00 | 199 | 199
2018-12-16 02:30 | 195 | 195
2018-12-16 03:00 | 197 | 197
2018-12-16 03:30 | 195 | 195
2018-12-16 04:00 | 194 | 194
2018-12-16 04:30 | 189 | 189
2018-12-16 05:00 | 190 | 190
2018-12-16 05:30 | 197 | 197
2018-12-16 06:00 | 207 | 207
2018-12-16 06:30 | 214 | 214
2018-12-16 07:00 | 228 | 227
2018-12-16 07:30 | 240 | 240
2018-12-16 08:00 | 254 | 254
2018-12-16 08:30 | 259 | 258
2018-12-16 09:00 | 262 | 261
2018-12-16 09:30 | 273 | 273
2018-12-16 10:00 | 277 | 277
2018-12-16 10:30 | 280 | 280
2018-12-16 11:00 | 276 | 276
2018-12-16 11:30 | 276 | 276
2018-12-16 12:00 | 279 | 279
2018-12-16 12:30 | 276 | 276
2018-12-16 13:00 | 277 | 277
2018-12-16 13:30 | 277 | 277
2018-12-16 14:00 | 277 | 277
2018-12-16 14:30 | 283 | 283
2018-12-16 15:00 | 282 | 282
2018-12-16 15:30 | 291 | 291
2018-12-16 16:00 | 288 | 288
2018-12-16 16:30 | 293 | 293
2018-12-16 17:00 | 290 | 290
2018-12-16 17:30 | 294 | 293
2018-12-16 18:00 | 291 | 291
2018-12-16 18:30 | 292 | 292
2018-12-16 19:00 | 285 | 285
2018-12-16 19:30 | 284 | 284
2018-12-16 20:00 | 278 | 278
2018-12-16 20:30 | 269 | 268
2018-12-16 21:00 | 259 | 259
2018-12-16 21:30 | 249 | 249
2018-12-16 22:00 | 242 | 242
2018-12-16 22:30 | 240 | 240
2018-12-16 23:00 | 224 | 224
2018-12-16 23:30 | 209 | 209
2018-12-17 | 197 | 197
2018-12-17 00:30 | 193 | 193
2018-12-17 01:00 | 191 | 191
2018-12-17 01:30 | 191 | 191
2018-12-17 02:00 | 184 | 184
2018-12-17 02:30 | 184 | 184
2018-12-17 03:00 | 186 | 186
2018-12-17 03:30 | 184 | 184
2018-12-17 04:00 | 186 | 186
2018-12-17 04:30 | 184 | 184
2018-12-17 05:00 | 196 | 196
2018-12-17 05:30 | 209 | 208
2018-12-17 06:00 | 229 | 229
2018-12-17 06:30 | 237 | 236
2018-12-17 07:00 | 260 | 260
2018-12-17 07:30 | 281 | 280
2018-12-17 08:00 | 286 | 284
2018-12-17 08:30 | 290 | 289
2018-12-17 09:00 | 287 | 286
2018-12-17 09:30 | 290 | 289
2018-12-17 10:00 | 274 | 273
2018-12-17 10:30 | 275 | 274
2018-12-17 11:00 | 286 | 286
2018-12-17 11:30 | 285 | 285
2018-12-17 12:00 | 284 | 283
2018-12-17 12:30 | 282 | 282
2018-12-17 13:00 | 280 | 279
2018-12-17 13:30 | 284 | 284
2018-12-17 14:00 | 290 | 290
2018-12-17 14:30 | 304 | 304
2018-12-17 15:00 | 303 | 303
2018-12-17 15:30 | 311 | 311
2018-12-17 16:00 | 314 | 314
2018-12-17 16:30 | 313 | 312
2018-12-17 17:00 | 313 | 311
2018-12-17 17:30 | 305 | 304
2018-12-17 18:00 | 299 | 299
2018-12-17 18:30 | 296 | 296
2018-12-17 19:00 | 294 | 293
2018-12-17 19:30 | 292 | 292
2018-12-17 20:00 | 285 | 284
2018-12-17 20:30 | 276 | 275
2018-12-17 21:00 | 263 | 261
2018-12-17 21:30 | 251 | 251
2018-12-17 22:00 | 245 | 244
2018-12-17 22:30 | 236 | 236
2018-12-17 23:00 | 224 | 223
2018-12-17 23:30 | 212 | 211
2018-12-18 | 196 | 194
2018-12-18 00:30 | 192 | 191
2018-12-18 01:00 | 190 | 189
2018-12-18 01:30 | 186 | 185
2018-12-18 02:00 | 184 | 183
2018-12-18 02:30 | 184 | 183
2018-12-18 03:00 | 186 | 185
2018-12-18 03:30 | 187 | 186
2018-12-18 04:00 | 190 | 189
2018-12-18 04:30 | 193 | 192
2018-12-18 05:00 | 206 | 205
2018-12-18 05:30 | 211 | 211
2018-12-18 06:00 | 220 | 220
2018-12-18 06:30 | 236 | 236
2018-12-18 07:00 | 250 | 250
2018-12-18 07:30 | 259 | 259
2018-12-18 08:00 | 260 | 260
2018-12-18 08:30 | 270 | 270
2018-12-18 09:00 | 264 | 264
2018-12-18 09:30 | 267 | 267
2018-12-18 10:00 | 271 | 270
2018-12-18 10:30 | 276 | 276
2018-12-18 11:00 | 283 | 283
2018-12-18 11:30 | 279 | 278
2018-12-18 12:00 | 282 | 281
2018-12-18 12:30 | 292 | 292
2018-12-18 13:00 | 296 | 296
2018-12-18 13:30 | 302 | 302
2018-12-18 14:00 | 308 | 307
2018-12-18 14:30 | 307 | 307
2018-12-18 15:00 | 311 | 311
2018-12-18 15:30 | 306 | 305
2018-12-18 16:00 | 313 | 312
2018-12-18 16:30 | 330 | 330
2018-12-18 17:00 | 333 | 333
2018-12-18 17:30 | 329 | 328
2018-12-18 18:00 | 323 | 322
2018-12-18 18:30 | 328 | 328
2018-12-18 19:00 | 332 | 331
2018-12-18 19:30 | 317 | 316
2018-12-18 20:00 | 303 | 302
2018-12-18 20:30 | 293 | 292
2018-12-18 21:00 | 272 | 272
2018-12-18 21:30 | 259 | 258
2018-12-18 22:00 | 249 | 248
2018-12-18 22:30 | 252 | 251
2018-12-18 23:00 | 237 | 235
2018-12-18 23:30 | 220 | 218
2018-12-19 | 205 | 202
2018-12-19 00:30 | 201 | 197
2018-12-19 01:00 | 197 | 192
2018-12-19 01:30 | 192 | 187
2018-12-19 02:00 | 192 | 186
2018-12-19 02:30 | 191 | 185
2018-12-19 03:00 | 191 | 185
2018-12-19 03:30 | 185 | 179
2018-12-19 04:00 | 192 | 186
2018-12-19 04:30 | 198 | 191
2018-12-19 05:00 | 208 | 203
2018-12-19 05:30 | 215 | 211
2018-12-19 06:00 | 231 | 229
2018-12-19 06:30 | 247 | 245
2018-12-19 07:00 | 259 | 259
2018-12-19 07:30 | 270 | 270
2018-12-19 08:00 | 276 | 276
2018-12-19 08:30 | 277 | 277
2018-12-19 09:00 | 284 | 284
2018-12-19 09:30 | 287 | 287
2018-12-19 10:00 | 289 | 289
2018-12-19 10:30 | 288 | 287
2018-12-19 11:00 | 291 | 291
2018-12-19 11:30 | 289 | 289
2018-12-19 12:00 | 290 | 290
2018-12-19 12:30 | 293 | 293
2018-12-19 13:00 | 300 | 300
2018-12-19 13:30 | 304 | 304
2018-12-19 14:00 | 318 | 318
2018-12-19 14:30 | 336 | 336
2018-12-19 15:00 | 348 | 348
2018-12-19 15:30 | 345 | 345
2018-12-19 16:00 | 349 | 349
2018-12-19 16:30 | 353 | 353
2018-12-19 17:00 | 352 | 351
2018-12-19 17:30 | 348 | 348
2018-12-19 18:00 | 345 | 343
2018-12-19 18:30 | 347 | 346
2018-12-19 19:00 | 345 | 344
2018-12-19 19:30 | 333 | 332
2018-12-19 20:00 | 320 | 319
2018-12-19 20:30 | 309 | 306
2018-12-19 21:00 | 294 | 291
2018-12-19 21:30 | 275 | 274
2018-12-19 22:00 | 258 | 256
2018-12-19 22:30 | 252 | 250
2018-12-19 23:00 | 238 | 235
2018-12-19 23:30 | 220 | 217
2018-12-20 | 203 | 200
2018-12-20 00:30 | 199 | 195
2018-12-20 01:00 | 193 | 188
2018-12-20 01:30 | 186 | 181
2018-12-20 02:00 | 184 | 179
2018-12-20 02:30 | 184 | 178
2018-12-20 03:00 | 184 | 178
2018-12-20 03:30 | 184 | 178
2018-12-20 04:00 | 189 | 184
2018-12-20 04:30 | 189 | 184
2018-12-20 05:00 | 201 | 196
2018-12-20 05:30 | 214 | 210
2018-12-20 06:00 | 229 | 228
2018-12-20 06:30 | 248 | 248
2018-12-20 07:00 | 255 | 254
2018-12-20 07:30 | 270 | 270
2018-12-20 08:00 | 289 | 289
2018-12-20 08:30 | 287 | 287
2018-12-20 09:00 | 283 | 283
2018-12-20 09:30 | 289 | 289
2018-12-20 10:00 | 295 | 295
2018-12-20 10:30 | 303 | 303
2018-12-20 11:00 | 308 | 308
2018-12-20 11:30 | 305 | 305
2018-12-20 12:00 | 313 | 313
2018-12-20 12:30 | 306 | 306
2018-12-20 13:00 | 322 | 322
2018-12-20 13:30 | 335 | 335
2018-12-20 14:00 | 346 | 346
2018-12-20 14:30 | 357 | 357
2018-12-20 15:00 | 385 | 385
2018-12-20 15:30 | 408 | 408
2018-12-20 16:00 | 418 | 418
2018-12-20 16:30 | 427 | 427
2018-12-20 17:00 | 423 | 423
2018-12-20 17:30 | 419 | 419
2018-12-20 18:00 | 412 | 411
2018-12-20 18:30 | 409 | 408
2018-12-20 19:00 | 403 | 402
2018-12-20 19:30 | 392 | 391
2018-12-20 20:00 | 376 | 375
2018-12-20 20:30 | 360 | 357
2018-12-20 21:00 | 335 | 333
2018-12-20 21:30 | 314 | 312
2018-12-20 22:00 | 305 | 304
2018-12-20 22:30 | 298 | 297
2018-12-20 23:00 | 272 | 272
2018-12-20 23:30 | 249 | 249
2018-12-21 | 224 | 223
2018-12-21 00:30 | 214 | 213
2018-12-21 01:00 | 207 | 206
2018-12-21 01:30 | 199 | 198
2018-12-21 02:00 | 195 | 194
2018-12-21 02:30 | 197 | 196
2018-12-21 03:00 | 198 | 197
2018-12-21 03:30 | 197 | 197
2018-12-21 04:00 | 198 | 197
2018-12-21 04:30 | 198 | 197
2018-12-21 05:00 | 208 | 207
2018-12-21 05:30 | 221 | 220
2018-12-21 06:00 | 231 | 231
2018-12-21 06:30 | 251 | 251
2018-12-21 07:00 | 268 | 267
2018-12-21 07:30 | 294 | 294
2018-12-21 08:00 | 301 | 301
2018-12-21 08:30 | 319 | 319
2018-12-21 09:00 | 333 | 333
2018-12-21 09:30 | 323 | 323
2018-12-21 10:00 | 318 | 318
2018-12-21 10:30 | 321 | 321
2018-12-21 11:00 | 319 | 319
2018-12-21 11:30 | 323 | 323
2018-12-21 12:00 | 329 | 329
2018-12-21 12:30 | 337 | 337
2018-12-21 13:00 | 359 | 359
2018-12-21 13:30 | 376 | 376
2018-12-21 14:00 | 391 | 391
2018-12-21 14:30 | 405 | 405
2018-12-21 15:00 | 426 | 426
2018-12-21 15:30 | 457 | 457
2018-12-21 16:00 | 459 | 459
2018-12-21 16:30 | 449 | 449
2018-12-21 17:00 | 435 | 434
2018-12-21 17:30 | 397 | 396
2018-12-21 18:00 | 352 | 352
2018-12-21 18:30 | 334 | 334
2018-12-21 19:00 | 321 | 321
2018-12-21 19:30 | 310 | 310
2018-12-21 20:00 | 311 | 310
2018-12-21 20:30 | 302 | 302
2018-12-21 21:00 | 283 | 282
2018-12-21 21:30 | 273 | 272
2018-12-21 22:00 | 255 | 253
2018-12-21 22:30 | 259 | 257
2018-12-21 23:00 | 246 | 246
2018-12-21 23:30 | 225 | 224
2018-12-22 | 208 | 208
2018-12-22 00:30 | 207 | 206
2018-12-22 01:00 | 195 | 195
2018-12-22 01:30 | 186 | 185
2018-12-22 02:00 | 185 | 184
2018-12-22 02:30 | 189 | 189
2018-12-22 03:00 | 184 | 183
2018-12-22 03:30 | 186 | 185
2018-12-22 04:00 | 184 | 183
2018-12-22 04:30 | 182 | 180
2018-12-22 05:00 | 185 | 185
2018-12-22 05:30 | 191 | 191
2018-12-22 06:00 | 205 | 205
2018-12-22 06:30 | 216 | 216
2018-12-22 07:00 | 228 | 228
2018-12-22 07:30 | 227 | 227
2018-12-22 08:00 | 236 | 236
2018-12-22 08:30 | 255 | 255
2018-12-22 09:00 | 273 | 272
2018-12-22 09:30 | 270 | 269
2018-12-22 10:00 | 265 | 264
2018-12-22 10:30 | 253 | 253
2018-12-22 11:00 | 267 | 266
2018-12-22 11:30 | 268 | 268
2018-12-22 12:00 | 269 | 269
2018-12-22 12:30 | 273 | 273
2018-12-22 13:00 | 285 | 284
2018-12-22 13:30 | 300 | 299
2018-12-22 14:00 | 343 | 342
2018-12-22 14:30 | 345 | 345
2018-12-22 15:00 | 357 | 357
2018-12-22 15:30 | 358 | 358
2018-12-22 16:00 | 343 | 343
2018-12-22 16:30 | 324 | 323
2018-12-22 17:00 | 306 | 305
2018-12-22 17:30 | 292 | 292
2018-12-22 18:00 | 288 | 288
2018-12-22 18:30 | 290 | 290
2018-12-22 19:00 | 289 | 289
2018-12-22 19:30 | 285 | 285
2018-12-22 20:00 | 277 | 277
2018-12-22 20:30 | 265 | 265
2018-12-22 21:00 | 255 | 255
2018-12-22 21:30 | 241 | 240
2018-12-22 22:00 | 233 | 232
2018-12-22 22:30 | 229 | 228
2018-12-22 23:00 | 212 | 211
2018-12-22 23:30 | 188 | 188
2018-12-23 | 174 | 174
2018-12-23 00:30 | 168 | 168
2018-12-23 01:00 | 161 | 161
2018-12-23 01:30 | 156 | 155
2018-12-23 02:00 | 153 | 153
2018-12-23 02:30 | 152 | 152
2018-12-23 03:00 | 151 | 151
2018-12-23 03:30 | 150 | 149
2018-12-23 04:00 | 149 | 149
2018-12-23 04:30 | 148 | 147
2018-12-23 05:00 | 149 | 148
2018-12-23 05:30 | 151 | 151
2018-12-23 06:00 | 156 | 155
2018-12-23 06:30 | 158 | 158
2018-12-23 07:00 | 164 | 164
2018-12-23 07:30 | 165 | 165
2018-12-23 08:00 | 172 | 172
2018-12-23 08:30 | 177 | 176
2018-12-23 09:00 | 180 | 179
2018-12-23 09:30 | 185 | 184
2018-12-23 10:00 | 187 | 186
2018-12-23 10:30 | 186 | 185
2018-12-23 11:00 | 186 | 186
2018-12-23 11:30 | 183 | 183
2018-12-23 12:00 | 186 | 186
2018-12-23 12:30 | 186 | 186
2018-12-23 13:00 | 187 | 186
2018-12-23 13:30 | 192 | 191
2018-12-23 14:00 | 197 | 197
2018-12-23 14:30 | 200 | 200
2018-12-23 15:00 | 203 | 203
2018-12-23 15:30 | 210 | 210
2018-12-23 16:00 | 222 | 222
2018-12-23 16:30 | 235 | 235
2018-12-23 17:00 | 242 | 241
2018-12-23 17:30 | 246 | 245
2018-12-23 18:00 | 250 | 249
2018-12-23 18:30 | 256 | 255
2018-12-23 19:00 | 259 | 259
2018-12-23 19:30 | 258 | 257
2018-12-23 20:00 | 253 | 252
2018-12-23 20:30 | 242 | 241
2018-12-23 21:00 | 235 | 233
2018-12-23 21:30 | 226 | 224
2018-12-23 22:00 | 226 | 223
2018-12-23 22:30 | 224 | 222
2018-12-23 23:00 | 205 | 205
2018-12-23 23:30 | 188 | 188
2018-12-24 | 175 | 174
2018-12-24 00:30 | 165 | 164
2018-12-24 01:00 | 160 | 158
2018-12-24 01:30 | 155 | 153
2018-12-24 02:00 | 151 | 150
2018-12-24 02:30 | 148 | 148
2018-12-24 03:00 | 149 | 148
2018-12-24 03:30 | 148 | 148
2018-12-24 04:00 | 150 | 149
2018-12-24 04:30 | 151 | 150
2018-12-24 05:00 | 157 | 156
2018-12-24 05:30 | 161 | 161
2018-12-24 06:00 | 169 | 169
2018-12-24 06:30 | 179 | 179
2018-12-24 07:00 | 192 | 192
2018-12-24 07:30 | 200 | 200
2018-12-24 08:00 | 201 | 201
2018-12-24 08:30 | 218 | 217
2018-12-24 09:00 | 234 | 233
2018-12-24 09:30 | 222 | 221
2018-12-24 10:00 | 224 | 223
2018-12-24 10:30 | 217 | 216
2018-12-24 11:00 | 216 | 215
2018-12-24 11:30 | 205 | 204
2018-12-24 12:00 | 201 | 200
2018-12-24 12:30 | 214 | 213
2018-12-24 13:00 | 215 | 215
2018-12-24 13:30 | 221 | 220
2018-12-24 14:00 | 228 | 227
2018-12-24 14:30 | 237 | 236
2018-12-24 15:00 | 247 | 247
2018-12-24 15:30 | 256 | 256
2018-12-24 16:00 | 269 | 269
2018-12-24 16:30 | 277 | 276
2018-12-24 17:00 | 276 | 276
2018-12-24 17:30 | 270 | 269
2018-12-24 18:00 | 262 | 262
2018-12-24 18:30 | 263 | 263
2018-12-24 19:00 | 264 | 263
2018-12-24 19:30 | 263 | 263
2018-12-24 20:00 | 258 | 258
2018-12-24 20:30 | 247 | 247
2018-12-24 21:00 | 238 | 238
2018-12-24 21:30 | 231 | 231
2018-12-24 22:00 | 226 | 225
2018-12-24 22:30 | 221 | 221
2018-12-24 23:00 | 212 | 212
2018-12-24 23:30 | 200 | 200
2018-12-25 | 188 | 188
2018-12-25 00:30 | 181 | 181
2018-12-25 01:00 | 173 | 172
2018-12-25 01:30 | 168 | 167
2018-12-25 02:00 | 165 | 164
2018-12-25 02:30 | 164 | 161
2018-12-25 03:00 | 163 | 160
2018-12-25 03:30 | 162 | 159
2018-12-25 04:00 | 162 | 160
2018-12-25 04:30 | 163 | 159
2018-12-25 05:00 | 171 | 168
2018-12-25 05:30 | 174 | 171
2018-12-25 06:00 | 178 | 176
2018-12-25 06:30 | 182 | 180
2018-12-25 07:00 | 190 | 189
2018-12-25 07:30 | 190 | 189
2018-12-25 08:00 | 196 | 196
2018-12-25 08:30 | 198 | 198
2018-12-25 09:00 | 202 | 202
2018-12-25 09:30 | 201 | 201
2018-12-25 10:00 | 200 | 199
2018-12-25 10:30 | 197 | 197
2018-12-25 11:00 | 193 | 192
2018-12-25 11:30 | 191 | 190
2018-12-25 12:00 | 187 | 187
2018-12-25 12:30 | 183 | 182
2018-12-25 13:00 | 182 | 182
2018-12-25 13:30 | 185 | 185
2018-12-25 14:00 | 190 | 190
2018-12-25 14:30 | 197 | 197
2018-12-25 15:00 | 206 | 206
2018-12-25 15:30 | 218 | 218
2018-12-25 16:00 | 231 | 231
2018-12-25 16:30 | 243 | 243
2018-12-25 17:00 | 250 | 250
2018-12-25 17:30 | 249 | 249
2018-12-25 18:00 | 242 | 242
2018-12-25 18:30 | 240 | 240
2018-12-25 19:00 | 246 | 246
2018-12-25 19:30 | 247 | 246
2018-12-25 20:00 | 246 | 245
2018-12-25 20:30 | 239 | 238
2018-12-25 21:00 | 233 | 232
2018-12-25 21:30 | 227 | 226
2018-12-25 22:00 | 223 | 221
2018-12-25 22:30 | 224 | 222
2018-12-25 23:00 | 211 | 209
2018-12-25 23:30 | 200 | 197
2018-12-26 | 190 | 186
2018-12-26 00:30 | 186 | 181
2018-12-26 01:00 | 183 | 178
2018-12-26 01:30 | 177 | 173
2018-12-26 02:00 | 174 | 171
2018-12-26 02:30 | 172 | 170
2018-12-26 03:00 | 172 | 169
2018-12-26 03:30 | 171 | 169
2018-12-26 04:00 | 172 | 170
2018-12-26 04:30 | 172 | 169
2018-12-26 05:00 | 175 | 171
2018-12-26 05:30 | 172 | 169
2018-12-26 06:00 | 178 | 176
2018-12-26 06:30 | 182 | 180
2018-12-26 07:00 | 189 | 188
2018-12-26 07:30 | 192 | 192
2018-12-26 08:00 | 202 | 202
2018-12-26 08:30 | 208 | 208
2018-12-26 09:00 | 211 | 211
2018-12-26 09:30 | 206 | 206
2018-12-26 10:00 | 206 | 206
2018-12-26 10:30 | 205 | 204
2018-12-26 11:00 | 201 | 201
2018-12-26 11:30 | 201 | 199
2018-12-26 12:00 | 196 | 195
2018-12-26 12:30 | 193 | 192
2018-12-26 13:00 | 194 | 193
2018-12-26 13:30 | 198 | 197
2018-12-26 14:00 | 206 | 206
2018-12-26 14:30 | 215 | 215
2018-12-26 15:00 | 227 | 227
2018-12-26 15:30 | 241 | 240
2018-12-26 16:00 | 259 | 258
2018-12-26 16:30 | 278 | 275
2018-12-26 17:00 | 285 | 282
2018-12-26 17:30 | 286 | 282
2018-12-26 18:00 | 284 | 279
2018-12-26 18:30 | 278 | 277
2018-12-26 19:00 | 276 | 276
2018-12-26 19:30 | 274 | 274
2018-12-26 20:00 | 267 | 267
2018-12-26 20:30 | 250 | 250
2018-12-26 21:00 | 242 | 241
2018-12-26 21:30 | 232 | 232
2018-12-26 22:00 | 225 | 224
2018-12-26 22:30 | 222 | 221
2018-12-26 23:00 | 210 | 209
2018-12-26 23:30 | 204 | 202
2018-12-27 | 194 | 192
2018-12-27 00:30 | 184 | 182
2018-12-27 01:00 | 177 | 176
2018-12-27 01:30 | 173 | 171
2018-12-27 02:00 | 171 | 169
2018-12-27 02:30 | 170 | 168
2018-12-27 03:00 | 170 | 169
2018-12-27 03:30 | 167 | 165
2018-12-27 04:00 | 169 | 167
2018-12-27 04:30 | 168 | 165
2018-12-27 05:00 | 171 | 169
2018-12-27 05:30 | 175 | 173
2018-12-27 06:00 | 182 | 180
2018-12-27 06:30 | 192 | 191
2018-12-27 07:00 | 203 | 203
2018-12-27 07:30 | 206 | 206
2018-12-27 08:00 | 215 | 215
2018-12-27 08:30 | 223 | 223
2018-12-27 09:00 | 226 | 226
2018-12-27 09:30 | 223 | 223
2018-12-27 10:00 | 221 | 220
2018-12-27 10:30 | 219 | 219
2018-12-27 11:00 | 219 | 218
2018-12-27 11:30 | 219 | 218
2018-12-27 12:00 | 218 | 218
2018-12-27 12:30 | 220 | 220
2018-12-27 13:00 | 223 | 223
2018-12-27 13:30 | 249 | 249
2018-12-27 14:00 | 254 | 254
2018-12-27 14:30 | 263 | 263
2018-12-27 15:00 | 275 | 275
2018-12-27 15:30 | 279 | 279
2018-12-27 16:00 | 297 | 296
2018-12-27 16:30 | 306 | 304
2018-12-27 17:00 | 311 | 309
2018-12-27 17:30 | 305 | 303
2018-12-27 18:00 | 299 | 297
2018-12-27 18:30 | 291 | 289
2018-12-27 19:00 | 290 | 289
2018-12-27 19:30 | 284 | 282
2018-12-27 20:00 | 273 | 271
2018-12-27 20:30 | 261 | 260
2018-12-27 21:00 | 247 | 247
2018-12-27 21:30 | 231 | 231
2018-12-27 22:00 | 231 | 231
2018-12-27 22:30 | 231 | 230
2018-12-27 23:00 | 219 | 218
2018-12-27 23:30 | 204 | 203
2018-12-28 | 193 | 192
2018-12-28 00:30 | 190 | 188
2018-12-28 01:00 | 186 | 185
2018-12-28 01:30 | 183 | 181
2018-12-28 02:00 | 177 | 175
2018-12-28 02:30 | 171 | 169
2018-12-28 03:00 | 166 | 164
2018-12-28 03:30 | 166 | 164
2018-12-28 04:00 | 171 | 168
2018-12-28 04:30 | 174 | 172
2018-12-28 05:00 | 181 | 178
2018-12-28 05:30 | 190 | 188
2018-12-28 06:00 | 201 | 200
2018-12-28 06:30 | 209 | 209
2018-12-28 07:00 | 229 | 229
2018-12-28 07:30 | 242 | 241
2018-12-28 08:00 | 249 | 248
2018-12-28 08:30 | 251 | 250
2018-12-28 09:00 | 255 | 255
2018-12-28 09:30 | 257 | 257
2018-12-28 10:00 | 256 | 256
2018-12-28 10:30 | 252 | 252
2018-12-28 11:00 | 252 | 252
2018-12-28 11:30 | 253 | 253
2018-12-28 12:00 | 251 | 251
2018-12-28 12:30 | 254 | 254
2018-12-28 13:00 | 253 | 253
2018-12-28 13:30 | 270 | 268
2018-12-28 14:00 | 280 | 278
2018-12-28 14:30 | 291 | 290
2018-12-28 15:00 | 300 | 299
2018-12-28 15:30 | 298 | 296
2018-12-28 16:00 | 310 | 308
2018-12-28 16:30 | 319 | 317
2018-12-28 17:00 | 320 | 318
2018-12-28 17:30 | 311 | 309
2018-12-28 18:00 | 302 | 300
2018-12-28 18:30 | 300 | 297
2018-12-28 19:00 | 299 | 297
2018-12-28 19:30 | 287 | 287
2018-12-28 20:00 | 274 | 274
2018-12-28 20:30 | 262 | 262
2018-12-28 21:00 | 255 | 255
2018-12-28 21:30 | 246 | 246
2018-12-28 22:00 | 238 | 237
2018-12-28 22:30 | 230 | 229
2018-12-28 23:00 | 219 | 217
2018-12-28 23:30 | 210 | 207
2018-12-29 | 201 | 199
2018-12-29 00:30 | 192 | 190
2018-12-29 01:00 | 186 | 184
2018-12-29 01:30 | 179 | 177
2018-12-29 02:00 | 176 | 174
2018-12-29 02:30 | 171 | 168
2018-12-29 03:00 | 173 | 170
2018-12-29 03:30 | 175 | 172
2018-12-29 04:00 | 172 | 169
2018-12-29 04:30 | 169 | 167
2018-12-29 05:00 | 165 | 164
2018-12-29 05:30 | 179 | 178
2018-12-29 06:00 | 190 | 189
2018-12-29 06:30 | 196 | 196
2018-12-29 07:00 | 209 | 209
2018-12-29 07:30 | 219 | 219
2018-12-29 08:00 | 230 | 229
2018-12-29 08:30 | 236 | 236
2018-12-29 09:00 | 245 | 245
2018-12-29 09:30 | 242 | 242
2018-12-29 10:00 | 244 | 244
2018-12-29 10:30 | 233 | 233
2018-12-29 11:00 | 224 | 223
2018-12-29 11:30 | 224 | 224
2018-12-29 12:00 | 224 | 224
2018-12-29 12:30 | 229 | 229
2018-12-29 13:00 | 235 | 235
2018-12-29 13:30 | 240 | 240
2018-12-29 14:00 | 250 | 250
2018-12-29 14:30 | 259 | 259
2018-12-29 15:00 | 268 | 268
2018-12-29 15:30 | 279 | 279
2018-12-29 16:00 | 299 | 298
2018-12-29 16:30 | 302 | 300
2018-12-29 17:00 | 303 | 301
2018-12-29 17:30 | 300 | 298
2018-12-29 18:00 | 296 | 293
2018-12-29 18:30 | 298 | 296
2018-12-29 19:00 | 299 | 297
2018-12-29 19:30 | 297 | 294
2018-12-29 20:00 | 286 | 283
2018-12-29 20:30 | 277 | 275
2018-12-29 21:00 | 265 | 264
2018-12-29 21:30 | 258 | 258
2018-12-29 22:00 | 255 | 254
2018-12-29 22:30 | 249 | 248
2018-12-29 23:00 | 228 | 227
2018-12-29 23:30 | 214 | 214
2018-12-30 | 201 | 200
2018-12-30 00:30 | 200 | 200
2018-12-30 01:00 | 194 | 194
2018-12-30 01:30 | 189 | 188
2018-12-30 02:00 | 184 | 183
2018-12-30 02:30 | 184 | 183
2018-12-30 03:00 | 181 | 180
2018-12-30 03:30 | 178 | 176
2018-12-30 04:00 | 175 | 174
2018-12-30 04:30 | 173 | 172
2018-12-30 05:00 | 174 | 173
2018-12-30 05:30 | 177 | 175
2018-12-30 06:00 | 185 | 184
2018-12-30 06:30 | 197 | 197
2018-12-30 07:00 | 207 | 207
2018-12-30 07:30 | 213 | 213
2018-12-30 08:00 | 222 | 222
2018-12-30 08:30 | 227 | 227
2018-12-30 09:00 | 232 | 232
2018-12-30 09:30 | 237 | 237
2018-12-30 10:00 | 240 | 240
2018-12-30 10:30 | 240 | 240
2018-12-30 11:00 | 239 | 239
2018-12-30 11:30 | 239 | 239
2018-12-30 12:00 | 239 | 239
2018-12-30 12:30 | 241 | 241
2018-12-30 13:00 | 246 | 245
2018-12-30 13:30 | 251 | 251
2018-12-30 14:00 | 261 | 261
2018-12-30 14:30 | 270 | 270
2018-12-30 15:00 | 283 | 283
2018-12-30 15:30 | 290 | 289
2018-12-30 16:00 | 300 | 299
2018-12-30 16:30 | 318 | 317
2018-12-30 17:00 | 329 | 328
2018-12-30 17:30 | 334 | 332
2018-12-30 18:00 | 331 | 329
2018-12-30 18:30 | 328 | 326
2018-12-30 19:00 | 326 | 325
2018-12-30 19:30 | 322 | 320
2018-12-30 20:00 | 305 | 305
2018-12-30 20:30 | 295 | 295
2018-12-30 21:00 | 279 | 279
2018-12-30 21:30 | 263 | 263
2018-12-30 22:00 | 262 | 262
2018-12-30 22:30 | 261 | 260
2018-12-30 23:00 | 238 | 238
2018-12-30 23:30 | 216 | 216
2018-12-31 | 200 | 200
2018-12-31 00:30 | 194 | 194
2018-12-31 01:00 | 188 | 188
2018-12-31 01:30 | 184 | 184
2018-12-31 02:00 | 184 | 184
2018-12-31 02:30 | 179 | 179
2018-12-31 03:00 | 179 | 179
2018-12-31 03:30 | 177 | 177
2018-12-31 04:00 | 179 | 179
2018-12-31 04:30 | 181 | 181
2018-12-31 05:00 | 186 | 186
2018-12-31 05:30 | 191 | 191
2018-12-31 06:00 | 201 | 201
2018-12-31 06:30 | 213 | 213
2018-12-31 07:00 | 228 | 228
2018-12-31 07:30 | 239 | 239
2018-12-31 08:00 | 248 | 248
2018-12-31 08:30 | 253 | 253
2018-12-31 09:00 | 257 | 257
2018-12-31 09:30 | 255 | 255
2018-12-31 10:00 | 258 | 258
2018-12-31 10:30 | 258 | 258
2018-12-31 11:00 | 261 | 261
2018-12-31 11:30 | 257 | 257
2018-12-31 12:00 | 257 | 257
2018-12-31 12:30 | 260 | 260
2018-12-31 13:00 | 265 | 265
2018-12-31 13:30 | 272 | 272
2018-12-31 14:00 | 283 | 283
2018-12-31 14:30 | 293 | 293
2018-12-31 15:00 | 301 | 301
2018-12-31 15:30 | 307 | 306
2018-12-31 16:00 | 323 | 323
2018-12-31 16:30 | 337 | 337
2018-12-31 17:00 | 342 | 341
2018-12-31 17:30 | 337 | 337
2018-12-31 18:00 | 325 | 325
2018-12-31 18:30 | 320 | 320
2018-12-31 19:00 | 313 | 313
2018-12-31 19:30 | 305 | 305
2018-12-31 20:00 | 290 | 290
2018-12-31 20:30 | 281 | 281
2018-12-31 21:00 | 271 | 271
2018-12-31 21:30 | 263 | 263
2018-12-31 22:00 | 256 | 256
2018-12-31 22:30 | 250 | 250
2018-12-31 23:00 | 235 | 235
2018-12-31 23:30 | 223 | 223
2019-01-01 | 208 | 208
2019-01-01 00:30 | 207 | 207
2019-01-01 01:00 | 204 | 204
2019-01-01 01:30 | 199 | 199
2019-01-01 02:00 | 193 | 193
2019-01-01 02:30 | 193 | 193
2019-01-01 03:00 | 188 | 188
2019-01-01 03:30 | 184 | 184
2019-01-01 04:00 | 180 | 180
2019-01-01 04:30 | 178 | 178
2019-01-01 05:00 | 177 | 177
2019-01-01 05:30 | 180 | 180
2019-01-01 06:00 | 183 | 183
2019-01-01 06:30 | 192 | 192
2019-01-01 07:00 | 204 | 204
2019-01-01 07:30 | 214 | 213
2019-01-01 08:00 | 224 | 223
2019-01-01 08:30 | 228 | 228
2019-01-01 09:00 | 233 | 233
2019-01-01 09:30 | 236 | 236
2019-01-01 10:00 | 240 | 240
2019-01-01 10:30 | 241 | 241
2019-01-01 11:00 | 241 | 241
2019-01-01 11:30 | 244 | 244
2019-01-01 12:00 | 249 | 249
2019-01-01 12:30 | 257 | 257
2019-01-01 13:00 | 265 | 265
2019-01-01 13:30 | 272 | 272
2019-01-01 14:00 | 272 | 272
2019-01-01 14:30 | 283 | 283
2019-01-01 15:00 | 285 | 285
2019-01-01 15:30 | 297 | 297
2019-01-01 16:00 | 302 | 302
2019-01-01 16:30 | 301 | 300
2019-01-01 17:00 | 298 | 298
2019-01-01 17:30 | 298 | 298
2019-01-01 18:00 | 291 | 290
2019-01-01 18:30 | 293 | 293
2019-01-01 19:00 | 292 | 292
2019-01-01 19:30 | 288 | 288
2019-01-01 20:00 | 284 | 284
2019-01-01 20:30 | 272 | 271
2019-01-01 21:00 | 263 | 263
2019-01-01 21:30 | 253 | 253
2019-01-01 22:00 | 247 | 247
2019-01-01 22:30 | 237 | 236
2019-01-01 23:00 | 223 | 222
2019-01-01 23:30 | 213 | 212
2019-01-02 | 199 | 199
2019-01-02 00:30 | 191 | 191
2019-01-02 01:00 | 184 | 184
2019-01-02 01:30 | 180 | 180
2019-01-02 02:00 | 180 | 180
2019-01-02 02:30 | 179 | 178
2019-01-02 03:00 | 178 | 178
2019-01-02 03:30 | 176 | 176
2019-01-02 04:00 | 179 | 179
2019-01-02 04:30 | 178 | 178
2019-01-02 05:00 | 187 | 187
2019-01-02 05:30 | 197 | 196
2019-01-02 06:00 | 203 | 203
2019-01-02 06:30 | 198 | 197
2019-01-02 07:00 | 214 | 214
2019-01-02 07:30 | 226 | 225
2019-01-02 08:00 | 241 | 240
2019-01-02 08:30 | 271 | 268
2019-01-02 09:00 | 274 | 272
2019-01-02 09:30 | 273 | 271
2019-01-02 10:00 | 279 | 277
2019-01-02 10:30 | 283 | 281
2019-01-02 11:00 | 277 | 275
2019-01-02 11:30 | 279 | 277
2019-01-02 12:00 | 283 | 282
2019-01-02 12:30 | 292 | 291
2019-01-02 13:00 | 291 | 290
2019-01-02 13:30 | 294 | 293
2019-01-02 14:00 | 298 | 297
2019-01-02 14:30 | 304 | 303
2019-01-02 15:00 | 310 | 309
2019-01-02 15:30 | 313 | 312
2019-01-02 16:00 | 319 | 318
2019-01-02 16:30 | 327 | 326
2019-01-02 17:00 | 328 | 326
2019-01-02 17:30 | 324 | 322
2019-01-02 18:00 | 320 | 317
2019-01-02 18:30 | 317 | 314
2019-01-02 19:00 | 312 | 309
2019-01-02 19:30 | 308 | 304
2019-01-02 20:00 | 305 | 301
2019-01-02 20:30 | 289 | 287
2019-01-02 21:00 | 279 | 277
2019-01-02 21:30 | 267 | 264
2019-01-02 22:00 | 253 | 250
2019-01-02 22:30 | 246 | 244
2019-01-02 23:00 | 229 | 228
2019-01-02 23:30 | 215 | 214
2019-01-03 | 198 | 196
2019-01-03 00:30 | 195 | 193
2019-01-03 01:00 | 191 | 188
2019-01-03 01:30 | 186 | 183
2019-01-03 02:00 | 186 | 183
2019-01-03 02:30 | 185 | 182
2019-01-03 03:00 | 183 | 180
2019-01-03 03:30 | 182 | 179
2019-01-03 04:00 | 181 | 178
2019-01-03 04:30 | 182 | 179
2019-01-03 05:00 | 189 | 186
2019-01-03 05:30 | 199 | 197
2019-01-03 06:00 | 207 | 205
2019-01-03 06:30 | 221 | 221
2019-01-03 07:00 | 242 | 242
2019-01-03 07:30 | 258 | 257
2019-01-03 08:00 | 269 | 269
2019-01-03 08:30 | 269 | 269
2019-01-03 09:00 | 278 | 278
2019-01-03 09:30 | 291 | 291
2019-01-03 10:00 | 294 | 294
2019-01-03 10:30 | 285 | 284
2019-01-03 11:00 | 278 | 278
2019-01-03 11:30 | 283 | 283
2019-01-03 12:00 | 283 | 283
2019-01-03 12:30 | 287 | 287
2019-01-03 13:00 | 292 | 292
2019-01-03 13:30 | 296 | 295
2019-01-03 14:00 | 296 | 296
2019-01-03 14:30 | 303 | 303
2019-01-03 15:00 | 304 | 304
2019-01-03 15:30 | 312 | 312
2019-01-03 16:00 | 316 | 315
2019-01-03 16:30 | 317 | 316
2019-01-03 17:00 | 317 | 316
2019-01-03 17:30 | 314 | 313
2019-01-03 18:00 | 308 | 307
2019-01-03 18:30 | 304 | 302
2019-01-03 19:00 | 311 | 309
2019-01-03 19:30 | 314 | 313
2019-01-03 20:00 | 307 | 304
2019-01-03 20:30 | 290 | 290
2019-01-03 21:00 | 283 | 283
2019-01-03 21:30 | 270 | 269
2019-01-03 22:00 | 258 | 257
2019-01-03 22:30 | 253 | 253
2019-01-03 23:00 | 235 | 234
2019-01-03 23:30 | 218 | 218
2019-01-04 | 203 | 203
2019-01-04 00:30 | 200 | 200
2019-01-04 01:00 | 196 | 196
2019-01-04 01:30 | 188 | 188
2019-01-04 02:00 | 186 | 186
2019-01-04 02:30 | 186 | 185
2019-01-04 03:00 | 181 | 181
2019-01-04 03:30 | 183 | 182
2019-01-04 04:00 | 185 | 185
2019-01-04 04:30 | 184 | 184
2019-01-04 05:00 | 196 | 195
2019-01-04 05:30 | 200 | 200
2019-01-04 06:00 | 221 | 221
2019-01-04 06:30 | 232 | 232
2019-01-04 07:00 | 254 | 253
2019-01-04 07:30 | 273 | 273
2019-01-04 08:00 | 279 | 279
2019-01-04 08:30 | 286 | 286
2019-01-04 09:00 | 292 | 292
2019-01-04 09:30 | 291 | 291
2019-01-04 10:00 | 289 | 289
2019-01-04 10:30 | 287 | 287
2019-01-04 11:00 | 286 | 286
2019-01-04 11:30 | 295 | 295
2019-01-04 12:00 | 302 | 300
2019-01-04 12:30 | 305 | 303
2019-01-04 13:00 | 293 | 293
2019-01-04 13:30 | 292 | 292
2019-01-04 14:00 | 318 | 318
2019-01-04 14:30 | 324 | 324
2019-01-04 15:00 | 302 | 302
2019-01-04 15:30 | 306 | 306
2019-01-04 16:00 | 345 | 345
2019-01-04 16:30 | 343 | 343
2019-01-04 17:00 | 343 | 343
2019-01-04 17:30 | 336 | 335
2019-01-04 18:00 | 324 | 323
2019-01-04 18:30 | 327 | 326
2019-01-04 19:00 | 328 | 327
2019-01-04 19:30 | 328 | 327
2019-01-04 20:00 | 316 | 315
2019-01-04 20:30 | 301 | 301
2019-01-04 21:00 | 291 | 291
2019-01-04 21:30 | 283 | 283
2019-01-04 22:00 | 274 | 274
2019-01-04 22:30 | 267 | 267
2019-01-04 23:00 | 256 | 255
2019-01-04 23:30 | 240 | 240
2019-01-05 | 220 | 220
2019-01-05 00:30 | 207 | 207
2019-01-05 01:00 | 196 | 196
2019-01-05 01:30 | 193 | 193
2019-01-05 02:00 | 192 | 192
2019-01-05 02:30 | 189 | 189
2019-01-05 03:00 | 189 | 189
2019-01-05 03:30 | 186 | 186
2019-01-05 04:00 | 185 | 185
2019-01-05 04:30 | 186 | 186
2019-01-05 05:00 | 195 | 195
2019-01-05 05:30 | 196 | 196
2019-01-05 06:00 | 207 | 207
2019-01-05 06:30 | 220 | 220
2019-01-05 07:00 | 238 | 238
2019-01-05 07:30 | 255 | 255
2019-01-05 08:00 | 267 | 267
2019-01-05 08:30 | 274 | 274
2019-01-05 09:00 | 280 | 280
2019-01-05 09:30 | 282 | 282
2019-01-05 10:00 | 282 | 282
2019-01-05 10:30 | 277 | 277
2019-01-05 11:00 | 282 | 282
2019-01-05 11:30 | 289 | 288
2019-01-05 12:00 | 289 | 288
2019-01-05 12:30 | 285 | 284
2019-01-05 13:00 | 286 | 285
2019-01-05 13:30 | 291 | 290
2019-01-05 14:00 | 292 | 291
2019-01-05 14:30 | 295 | 294
2019-01-05 15:00 | 308 | 306
2019-01-05 15:30 | 315 | 313
2019-01-05 16:00 | 321 | 320
2019-01-05 16:30 | 323 | 321
2019-01-05 17:00 | 324 | 322
2019-01-05 17:30 | 312 | 311
2019-01-05 18:00 | 307 | 306
2019-01-05 18:30 | 309 | 308
2019-01-05 19:00 | 308 | 306
2019-01-05 19:30 | 305 | 303
2019-01-05 20:00 | 300 | 299
2019-01-05 20:30 | 284 | 284
2019-01-05 21:00 | 280 | 280
2019-01-05 21:30 | 277 | 277
2019-01-05 22:00 | 269 | 268
2019-01-05 22:30 | 263 | 261
2019-01-05 23:00 | 245 | 245
2019-01-05 23:30 | 229 | 229
2019-01-06 | 209 | 209
2019-01-06 00:30 | 203 | 203
2019-01-06 01:00 | 199 | 198
2019-01-06 01:30 | 192 | 191
2019-01-06 02:00 | 190 | 189
2019-01-06 02:30 | 186 | 184
2019-01-06 03:00 | 188 | 186
2019-01-06 03:30 | 188 | 186
2019-01-06 04:00 | 190 | 188
2019-01-06 04:30 | 187 | 185
2019-01-06 05:00 | 187 | 185
2019-01-06 05:30 | 187 | 186
2019-01-06 06:00 | 194 | 193
2019-01-06 06:30 | 200 | 200
2019-01-06 07:00 | 212 | 212
2019-01-06 07:30 | 225 | 225
2019-01-06 08:00 | 238 | 238
2019-01-06 08:30 | 241 | 241
2019-01-06 09:00 | 244 | 244
2019-01-06 09:30 | 253 | 252
2019-01-06 10:00 | 256 | 256
2019-01-06 10:30 | 262 | 261
2019-01-06 11:00 | 272 | 272
2019-01-06 11:30 | 274 | 273
2019-01-06 12:00 | 269 | 267
2019-01-06 12:30 | 273 | 271
2019-01-06 13:00 | 273 | 272
2019-01-06 13:30 | 274 | 272
2019-01-06 14:00 | 279 | 278
2019-01-06 14:30 | 284 | 283
2019-01-06 15:00 | 285 | 284
2019-01-06 15:30 | 293 | 293
2019-01-06 16:00 | 292 | 291
2019-01-06 16:30 | 298 | 297
2019-01-06 17:00 | 301 | 300
2019-01-06 17:30 | 297 | 296
2019-01-06 18:00 | 298 | 297
2019-01-06 18:30 | 300 | 299
2019-01-06 19:00 | 302 | 301
2019-01-06 19:30 | 304 | 302
2019-01-06 20:00 | 300 | 298
2019-01-06 20:30 | 285 | 284
2019-01-06 21:00 | 277 | 276
2019-01-06 21:30 | 266 | 264
2019-01-06 22:00 | 257 | 257
2019-01-06 22:30 | 250 | 250
2019-01-06 23:00 | 233 | 232
2019-01-06 23:30 | 218 | 216
2019-01-07 | 204 | 203
2019-01-07 00:30 | 200 | 198
2019-01-07 01:00 | 194 | 192
2019-01-07 01:30 | 189 | 188
2019-01-07 02:00 | 187 | 187
2019-01-07 02:30 | 185 | 185
2019-01-07 03:00 | 185 | 185
2019-01-07 03:30 | 185 | 185
2019-01-07 04:00 | 190 | 190
2019-01-07 04:30 | 195 | 195
2019-01-07 05:00 | 199 | 199
2019-01-07 05:30 | 207 | 207
2019-01-07 06:00 | 222 | 222
2019-01-07 06:30 | 231 | 231
2019-01-07 07:00 | 252 | 251
2019-01-07 07:30 | 265 | 265
2019-01-07 08:00 | 282 | 281
2019-01-07 08:30 | 288 | 288
2019-01-07 09:00 | 293 | 293
2019-01-07 09:30 | 301 | 301
2019-01-07 10:00 | 299 | 298
2019-01-07 10:30 | 293 | 292
2019-01-07 11:00 | 293 | 292
2019-01-07 11:30 | 294 | 293
2019-01-07 12:00 | 293 | 292
2019-01-07 12:30 | 307 | 306
2019-01-07 13:00 | 317 | 316
2019-01-07 13:30 | 321 | 320
2019-01-07 14:00 | 321 | 320
2019-01-07 14:30 | 321 | 320
2019-01-07 15:00 | 315 | 314
2019-01-07 15:30 | 319 | 317
2019-01-07 16:00 | 321 | 319
2019-01-07 16:30 | 318 | 317
2019-01-07 17:00 | 311 | 311
2019-01-07 17:30 | 309 | 307
2019-01-07 18:00 | 305 | 304
2019-01-07 18:30 | 303 | 303
2019-01-07 19:00 | 301 | 300
2019-01-07 19:30 | 303 | 303
2019-01-07 20:00 | 293 | 292
2019-01-07 20:30 | 284 | 283
2019-01-07 21:00 | 275 | 274
2019-01-07 21:30 | 263 | 261
2019-01-07 22:00 | 251 | 248
2019-01-07 22:30 | 248 | 245
2019-01-07 23:00 | 230 | 229
2019-01-07 23:30 | 214 | 213
2019-01-08 | 200 | 199
2019-01-08 00:30 | 199 | 198
2019-01-08 01:00 | 197 | 195
2019-01-08 01:30 | 191 | 189
2019-01-08 02:00 | 188 | 185
2019-01-08 02:30 | 184 | 183
2019-01-08 03:00 | 184 | 184
2019-01-08 03:30 | 185 | 185
2019-01-08 04:00 | 185 | 185
2019-01-08 04:30 | 184 | 183
2019-01-08 05:00 | 188 | 188
2019-01-08 05:30 | 199 | 199
2019-01-08 06:00 | 215 | 215
2019-01-08 06:30 | 233 | 233
2019-01-08 07:00 | 258 | 258
2019-01-08 07:30 | 274 | 274
2019-01-08 08:00 | 284 | 284
2019-01-08 08:30 | 285 | 285
2019-01-08 09:00 | 294 | 294
2019-01-08 09:30 | 288 | 288
2019-01-08 10:00 | 264 | 264
2019-01-08 10:30 | 252 | 252
2019-01-08 11:00 | 257 | 257
2019-01-08 11:30 | 276 | 276
2019-01-08 12:00 | 279 | 279
2019-01-08 12:30 | 290 | 290
2019-01-08 13:00 | 301 | 301
2019-01-08 13:30 | 307 | 306
2019-01-08 14:00 | 311 | 310
2019-01-08 14:30 | 316 | 315
2019-01-08 15:00 | 309 | 307
2019-01-08 15:30 | 313 | 313
2019-01-08 16:00 | 318 | 318
2019-01-08 16:30 | 320 | 319
2019-01-08 17:00 | 325 | 324
2019-01-08 17:30 | 321 | 320
2019-01-08 18:00 | 317 | 316
2019-01-08 18:30 | 319 | 317
2019-01-08 19:00 | 320 | 319
2019-01-08 19:30 | 319 | 318
2019-01-08 20:00 | 309 | 308
2019-01-08 20:30 | 290 | 290
2019-01-08 21:00 | 280 | 280
2019-01-08 21:30 | 267 | 267
2019-01-08 22:00 | 256 | 256
2019-01-08 22:30 | 251 | 250
2019-01-08 23:00 | 232 | 232
2019-01-08 23:30 | 217 | 215
2019-01-09 | 202 | 199
2019-01-09 00:30 | 198 | 195
2019-01-09 01:00 | 189 | 185
2019-01-09 01:30 | 183 | 179
2019-01-09 02:00 | 185 | 180
2019-01-09 02:30 | 182 | 177
2019-01-09 03:00 | 182 | 178
2019-01-09 03:30 | 187 | 182
2019-01-09 04:00 | 192 | 187
2019-01-09 04:30 | 193 | 189
2019-01-09 05:00 | 197 | 192
2019-01-09 05:30 | 203 | 200
2019-01-09 06:00 | 214 | 212
2019-01-09 06:30 | 225 | 224
2019-01-09 07:00 | 255 | 252
2019-01-09 07:30 | 278 | 275
2019-01-09 08:00 | 297 | 294
2019-01-09 08:30 | 300 | 298
2019-01-09 09:00 | 305 | 304
2019-01-09 09:30 | 310 | 306
2019-01-09 10:00 | 312 | 308
2019-01-09 10:30 | 306 | 301
2019-01-09 11:00 | 311 | 307
2019-01-09 11:30 | 307 | 302
2019-01-09 12:00 | 296 | 291
2019-01-09 12:30 | 307 | 303
2019-01-09 13:00 | 314 | 311
2019-01-09 13:30 | 314 | 311
2019-01-09 14:00 | 317 | 314
2019-01-09 14:30 | 322 | 319
2019-01-09 15:00 | 328 | 325
2019-01-09 15:30 | 332 | 329
2019-01-09 16:00 | 329 | 326
2019-01-09 16:30 | 333 | 330
2019-01-09 17:00 | 333 | 330
2019-01-09 17:30 | 318 | 315
2019-01-09 18:00 | 311 | 309
2019-01-09 18:30 | 319 | 318
2019-01-09 19:00 | 315 | 314
2019-01-09 19:30 | 318 | 317
2019-01-09 20:00 | 303 | 301
2019-01-09 20:30 | 287 | 284
2019-01-09 21:00 | 280 | 276
2019-01-09 21:30 | 266 | 261
2019-01-09 22:00 | 244 | 241
2019-01-09 22:30 | 250 | 247
2019-01-09 23:00 | 239 | 234
2019-01-09 23:30 | 225 | 219
2019-01-10 | 210 | 204
2019-01-10 00:30 | 204 | 197
2019-01-10 01:00 | 197 | 189
2019-01-10 01:30 | 190 | 183
2019-01-10 02:00 | 187 | 181
2019-01-10 02:30 | 188 | 182
2019-01-10 03:00 | 186 | 180
2019-01-10 03:30 | 185 | 179
2019-01-10 04:00 | 184 | 178
2019-01-10 04:30 | 191 | 185
2019-01-10 05:00 | 193 | 188
2019-01-10 05:30 | 201 | 196
2019-01-10 06:00 | 216 | 214
2019-01-10 06:30 | 234 | 232
2019-01-10 07:00 | 258 | 258
2019-01-10 07:30 | 271 | 271
2019-01-10 08:00 | 276 | 276
2019-01-10 08:30 | 282 | 281
2019-01-10 09:00 | 288 | 287
2019-01-10 09:30 | 289 | 289
2019-01-10 10:00 | 298 | 298
2019-01-10 10:30 | 299 | 299
2019-01-10 11:00 | 293 | 293
2019-01-10 11:30 | 297 | 297
2019-01-10 12:00 | 286 | 286
2019-01-10 12:30 | 290 | 290
2019-01-10 13:00 | 297 | 296
2019-01-10 13:30 | 310 | 310
2019-01-10 14:00 | 315 | 315
2019-01-10 14:30 | 309 | 309
2019-01-10 15:00 | 309 | 309
2019-01-10 15:30 | 311 | 311
2019-01-10 16:00 | 324 | 324
2019-01-10 16:30 | 331 | 331
2019-01-10 17:00 | 333 | 333
2019-01-10 17:30 | 336 | 336
2019-01-10 18:00 | 339 | 338
2019-01-10 18:30 | 347 | 347
2019-01-10 19:00 | 365 | 364
2019-01-10 19:30 | 364 | 363
2019-01-10 20:00 | 352 | 351
2019-01-10 20:30 | 333 | 333
2019-01-10 21:00 | 315 | 314
2019-01-10 21:30 | 295 | 294
2019-01-10 22:00 | 287 | 286
2019-01-10 22:30 | 279 | 278
2019-01-10 23:00 | 256 | 255
2019-01-10 23:30 | 232 | 232
2019-01-11 | 200 | 200
2019-01-11 00:30 | 195 | 195
2019-01-11 01:00 | 192 | 192
2019-01-11 01:30 | 187 | 187
2019-01-11 02:00 | 185 | 185
2019-01-11 02:30 | 184 | 184
2019-01-11 03:00 | 178 | 177
2019-01-11 03:30 | 178 | 177
2019-01-11 04:00 | 179 | 178
2019-01-11 04:30 | 185 | 184
2019-01-11 05:00 | 192 | 192
2019-01-11 05:30 | 198 | 198
2019-01-11 06:00 | 212 | 212
2019-01-11 06:30 | 221 | 221
2019-01-11 07:00 | 246 | 246
2019-01-11 07:30 | 258 | 258
2019-01-11 08:00 | 272 | 272
2019-01-11 08:30 | 277 | 277
2019-01-11 09:00 | 286 | 286
2019-01-11 09:30 | 289 | 289
2019-01-11 10:00 | 291 | 291
2019-01-11 10:30 | 289 | 289
2019-01-11 11:00 | 294 | 294
2019-01-11 11:30 | 295 | 295
2019-01-11 12:00 | 293 | 293
2019-01-11 12:30 | 294 | 294
2019-01-11 13:00 | 312 | 311
2019-01-11 13:30 | 318 | 317
2019-01-11 14:00 | 322 | 321
2019-01-11 14:30 | 332 | 330
2019-01-11 15:00 | 332 | 331
2019-01-11 15:30 | 327 | 326
2019-01-11 16:00 | 326 | 325
2019-01-11 16:30 | 327 | 326
2019-01-11 17:00 | 325 | 324
2019-01-11 17:30 | 318 | 317
2019-01-11 18:00 | 307 | 307
2019-01-11 18:30 | 305 | 304
2019-01-11 19:00 | 305 | 305
2019-01-11 19:30 | 301 | 301
2019-01-11 20:00 | 291 | 291
2019-01-11 20:30 | 285 | 284
2019-01-11 21:00 | 282 | 281
2019-01-11 21:30 | 266 | 265
2019-01-11 22:00 | 256 | 255
2019-01-11 22:30 | 246 | 246
2019-01-11 23:00 | 226 | 226
2019-01-11 23:30 | 212 | 212
2019-01-12 | 198 | 198
2019-01-12 00:30 | 194 | 194
2019-01-12 01:00 | 189 | 189
2019-01-12 01:30 | 186 | 185
2019-01-12 02:00 | 175 | 175
2019-01-12 02:30 | 168 | 167
2019-01-12 03:00 | 174 | 173
2019-01-12 03:30 | 177 | 176
2019-01-12 04:00 | 176 | 176
2019-01-12 04:30 | 175 | 174
2019-01-12 05:00 | 177 | 175
2019-01-12 05:30 | 180 | 179
2019-01-12 06:00 | 186 | 186
2019-01-12 06:30 | 202 | 202
2019-01-12 07:00 | 216 | 216
2019-01-12 07:30 | 227 | 227
2019-01-12 08:00 | 237 | 237
2019-01-12 08:30 | 241 | 241
2019-01-12 09:00 | 247 | 247
2019-01-12 09:30 | 245 | 245
2019-01-12 10:00 | 248 | 248
2019-01-12 10:30 | 250 | 250
2019-01-12 11:00 | 249 | 249
2019-01-12 11:30 | 249 | 248
2019-01-12 12:00 | 250 | 250
2019-01-12 12:30 | 257 | 257
2019-01-12 13:00 | 260 | 260
2019-01-12 13:30 | 264 | 264
2019-01-12 14:00 | 272 | 272
2019-01-12 14:30 | 283 | 283
2019-01-12 15:00 | 290 | 290
2019-01-12 15:30 | 299 | 299
2019-01-12 16:00 | 304 | 302
2019-01-12 16:30 | 320 | 318
2019-01-12 17:00 | 315 | 314
2019-01-12 17:30 | 317 | 316
2019-01-12 18:00 | 304 | 304
2019-01-12 18:30 | 311 | 310
2019-01-12 19:00 | 311 | 311
2019-01-12 19:30 | 309 | 308
2019-01-12 20:00 | 298 | 298
2019-01-12 20:30 | 286 | 285
2019-01-12 21:00 | 272 | 271
2019-01-12 21:30 | 259 | 257
2019-01-12 22:00 | 248 | 246
2019-01-12 22:30 | 246 | 244
2019-01-12 23:00 | 228 | 227
2019-01-12 23:30 | 212 | 211
2019-01-13 | 200 | 199
2019-01-13 00:30 | 196 | 194
2019-01-13 01:00 | 191 | 189
2019-01-13 01:30 | 189 | 187
2019-01-13 02:00 | 186 | 183
2019-01-13 02:30 | 183 | 181
2019-01-13 03:00 | 178 | 177
2019-01-13 03:30 | 177 | 176
2019-01-13 04:00 | 174 | 173
2019-01-13 04:30 | 171 | 170
2019-01-13 05:00 | 175 | 174
2019-01-13 05:30 | 179 | 178
2019-01-13 06:00 | 185 | 185
2019-01-13 06:30 | 195 | 194
2019-01-13 07:00 | 205 | 205
2019-01-13 07:30 | 215 | 215
2019-01-13 08:00 | 226 | 226
2019-01-13 08:30 | 233 | 233
2019-01-13 09:00 | 237 | 237
2019-01-13 09:30 | 241 | 241
2019-01-13 10:00 | 244 | 244
2019-01-13 10:30 | 245 | 245
2019-01-13 11:00 | 244 | 244
2019-01-13 11:30 | 246 | 246
2019-01-13 12:00 | 242 | 242
2019-01-13 12:30 | 247 | 246
2019-01-13 13:00 | 251 | 251
2019-01-13 13:30 | 257 | 256
2019-01-13 14:00 | 261 | 261
2019-01-13 14:30 | 264 | 264
2019-01-13 15:00 | 279 | 279
2019-01-13 15:30 | 287 | 287
2019-01-13 16:00 | 294 | 294
2019-01-13 16:30 | 297 | 297
2019-01-13 17:00 | 299 | 299
2019-01-13 17:30 | 296 | 296
2019-01-13 18:00 | 295 | 295
2019-01-13 18:30 | 290 | 290
2019-01-13 19:00 | 292 | 292
2019-01-13 19:30 | 294 | 293
2019-01-13 20:00 | 282 | 282
2019-01-13 20:30 | 262 | 262
2019-01-13 21:00 | 252 | 252
2019-01-13 21:30 | 243 | 243
2019-01-13 22:00 | 235 | 235
2019-01-13 22:30 | 233 | 233
2019-01-13 23:00 | 220 | 219
2019-01-13 23:30 | 209 | 209
2019-01-14 | 200 | 199
2019-01-14 00:30 | 196 | 194
2019-01-14 01:00 | 189 | 187
2019-01-14 01:30 | 184 | 181
2019-01-14 02:00 | 185 | 183
2019-01-14 02:30 | 185 | 183
2019-01-14 03:00 | 185 | 183
2019-01-14 03:30 | 188 | 186
2019-01-14 04:00 | 194 | 192
2019-01-14 04:30 | 192 | 190
2019-01-14 05:00 | 194 | 192
2019-01-14 05:30 | 199 | 197
2019-01-14 06:00 | 219 | 219
2019-01-14 06:30 | 234 | 234
2019-01-14 07:00 | 255 | 255
2019-01-14 07:30 | 265 | 265
2019-01-14 08:00 | 273 | 273
2019-01-14 08:30 | 290 | 290
2019-01-14 09:00 | 296 | 296
2019-01-14 09:30 | 302 | 302
2019-01-14 10:00 | 311 | 310
2019-01-14 10:30 | 304 | 302
2019-01-14 11:00 | 303 | 301
2019-01-14 11:30 | 305 | 304
2019-01-14 12:00 | 312 | 310
2019-01-14 12:30 | 317 | 315
2019-01-14 13:00 | 323 | 322
2019-01-14 13:30 | 330 | 329
2019-01-14 14:00 | 340 | 339
2019-01-14 14:30 | 348 | 347
2019-01-14 15:00 | 358 | 357
2019-01-14 15:30 | 367 | 367
2019-01-14 16:00 | 376 | 375
2019-01-14 16:30 | 382 | 381
2019-01-14 17:00 | 374 | 372
2019-01-14 17:30 | 366 | 365
2019-01-14 18:00 | 362 | 361
2019-01-14 18:30 | 365 | 364
2019-01-14 19:00 | 374 | 373
2019-01-14 19:30 | 370 | 369
2019-01-14 20:00 | 357 | 355
2019-01-14 20:30 | 332 | 330
2019-01-14 21:00 | 307 | 307
2019-01-14 21:30 | 285 | 284
2019-01-14 22:00 | 285 | 284
2019-01-14 22:30 | 272 | 270
2019-01-14 23:00 | 250 | 248
2019-01-14 23:30 | 229 | 228
2019-01-15 | 215 | 214
2019-01-15 00:30 | 207 | 206
2019-01-15 01:00 | 199 | 197
2019-01-15 01:30 | 193 | 191
2019-01-15 02:00 | 193 | 191
2019-01-15 02:30 | 189 | 187
2019-01-15 03:00 | 187 | 186
2019-01-15 03:30 | 188 | 188
2019-01-15 04:00 | 190 | 190
2019-01-15 04:30 | 193 | 193
2019-01-15 05:00 | 201 | 200
2019-01-15 05:30 | 210 | 209
2019-01-15 06:00 | 227 | 227
2019-01-15 06:30 | 241 | 241
2019-01-15 07:00 | 259 | 259
2019-01-15 07:30 | 278 | 278
2019-01-15 08:00 | 297 | 297
2019-01-15 08:30 | 306 | 306
2019-01-15 09:00 | 315 | 315
2019-01-15 09:30 | 317 | 317
2019-01-15 10:00 | 318 | 318
2019-01-15 10:30 | 317 | 317
2019-01-15 11:00 | 317 | 317
2019-01-15 11:30 | 322 | 322
2019-01-15 12:00 | 323 | 323
2019-01-15 12:30 | 330 | 329
2019-01-15 13:00 | 336 | 336
2019-01-15 13:30 | 343 | 343
2019-01-15 14:00 | 350 | 350
2019-01-15 14:30 | 357 | 356
2019-01-15 15:00 | 366 | 365
2019-01-15 15:30 | 392 | 392
2019-01-15 16:00 | 413 | 413
2019-01-15 16:30 | 421 | 421
2019-01-15 17:00 | 425 | 425
2019-01-15 17:30 | 419 | 419
2019-01-15 18:00 | 404 | 403
2019-01-15 18:30 | 385 | 384
2019-01-15 19:00 | 386 | 384
2019-01-15 19:30 | 395 | 393
2019-01-15 20:00 | 381 | 379
2019-01-15 20:30 | 331 | 330
2019-01-15 21:00 | 314 | 313
2019-01-15 21:30 | 297 | 295
2019-01-15 22:00 | 290 | 287
2019-01-15 22:30 | 276 | 273
2019-01-15 23:00 | 252 | 249
2019-01-15 23:30 | 227 | 227
2019-01-16 | 212 | 212
2019-01-16 00:30 | 207 | 206
2019-01-16 01:00 | 206 | 205
2019-01-16 01:30 | 203 | 202
2019-01-16 02:00 | 200 | 199
2019-01-16 02:30 | 198 | 196
2019-01-16 03:00 | 200 | 199
2019-01-16 03:30 | 202 | 201
2019-01-16 04:00 | 204 | 203
2019-01-16 04:30 | 205 | 203
2019-01-16 05:00 | 212 | 210
2019-01-16 05:30 | 218 | 217
2019-01-16 06:00 | 238 | 238
2019-01-16 06:30 | 251 | 251
2019-01-16 07:00 | 277 | 277
2019-01-16 07:30 | 287 | 287
2019-01-16 08:00 | 309 | 308
2019-01-16 08:30 | 329 | 328
2019-01-16 09:00 | 319 | 319
2019-01-16 09:30 | 316 | 316
2019-01-16 10:00 | 324 | 324
2019-01-16 10:30 | 334 | 334
2019-01-16 11:00 | 322 | 322
2019-01-16 11:30 | 329 | 329
2019-01-16 12:00 | 335 | 335
2019-01-16 12:30 | 342 | 342
2019-01-16 13:00 | 355 | 355
2019-01-16 13:30 | 376 | 376
2019-01-16 14:00 | 375 | 374
2019-01-16 14:30 | 395 | 395
2019-01-16 15:00 | 400 | 400
2019-01-16 15:30 | 401 | 401
2019-01-16 16:00 | 415 | 415
2019-01-16 16:30 | 437 | 436
2019-01-16 17:00 | 407 | 406
2019-01-16 17:30 | 394 | 393
2019-01-16 18:00 | 377 | 377
2019-01-16 18:30 | 375 | 375
2019-01-16 19:00 | 373 | 373
2019-01-16 19:30 | 375 | 374
2019-01-16 20:00 | 387 | 387
2019-01-16 20:30 | 352 | 351
2019-01-16 21:00 | 313 | 313
2019-01-16 21:30 | 285 | 285
2019-01-16 22:00 | 278 | 277
2019-01-16 22:30 | 266 | 266
2019-01-16 23:00 | 243 | 243
2019-01-16 23:30 | 229 | 229
2019-01-17 | 221 | 221
2019-01-17 00:30 | 214 | 214
2019-01-17 01:00 | 206 | 206
2019-01-17 01:30 | 205 | 205
2019-01-17 02:00 | 199 | 199
2019-01-17 02:30 | 197 | 197
2019-01-17 03:00 | 200 | 200
2019-01-17 03:30 | 197 | 197
2019-01-17 04:00 | 200 | 200
2019-01-17 04:30 | 206 | 206
2019-01-17 05:00 | 215 | 215
2019-01-17 05:30 | 230 | 230
2019-01-17 06:00 | 244 | 244
2019-01-17 06:30 | 264 | 263
2019-01-17 07:00 | 285 | 285
2019-01-17 07:30 | 298 | 297
2019-01-17 08:00 | 303 | 303
2019-01-17 08:30 | 313 | 312
2019-01-17 09:00 | 307 | 306
2019-01-17 09:30 | 301 | 301
2019-01-17 10:00 | 304 | 303
2019-01-17 10:30 | 306 | 306
2019-01-17 11:00 | 304 | 304
2019-01-17 11:30 | 310 | 309
2019-01-17 12:00 | 341 | 341
2019-01-17 12:30 | 332 | 332
2019-01-17 13:00 | 350 | 350
2019-01-17 13:30 | 367 | 366
2019-01-17 14:00 | 366 | 366
2019-01-17 14:30 | 383 | 383
2019-01-17 15:00 | 377 | 377
2019-01-17 15:30 | 402 | 402
2019-01-17 16:00 | 412 | 411
2019-01-17 16:30 | 417 | 416
2019-01-17 17:00 | 423 | 422
2019-01-17 17:30 | 396 | 394
2019-01-17 18:00 | 391 | 389
2019-01-17 18:30 | 374 | 371
2019-01-17 19:00 | 372 | 370
2019-01-17 19:30 | 370 | 369
2019-01-17 20:00 | 357 | 356
2019-01-17 20:30 | 341 | 341
2019-01-17 21:00 | 318 | 316
2019-01-17 21:30 | 295 | 294
2019-01-17 22:00 | 285 | 284
2019-01-17 22:30 | 274 | 274
2019-01-17 23:00 | 247 | 247
2019-01-17 23:30 | 227 | 227
2019-01-18 | 209 | 209
2019-01-18 00:30 | 205 | 204
2019-01-18 01:00 | 199 | 197
2019-01-18 01:30 | 198 | 197
2019-01-18 02:00 | 198 | 196
2019-01-18 02:30 | 201 | 200
2019-01-18 03:00 | 203 | 201
2019-01-18 03:30 | 203 | 201
2019-01-18 04:00 | 201 | 199
2019-01-18 04:30 | 202 | 201
2019-01-18 05:00 | 207 | 205
2019-01-18 05:30 | 219 | 218
2019-01-18 06:00 | 231 | 230
2019-01-18 06:30 | 238 | 238
2019-01-18 07:00 | 263 | 263
2019-01-18 07:30 | 276 | 276
2019-01-18 08:00 | 291 | 291
2019-01-18 08:30 | 296 | 296
2019-01-18 09:00 | 301 | 300
2019-01-18 09:30 | 310 | 310
2019-01-18 10:00 | 310 | 310
2019-01-18 10:30 | 306 | 306
2019-01-18 11:00 | 304 | 304
2019-01-18 11:30 | 300 | 300
2019-01-18 12:00 | 294 | 294
2019-01-18 12:30 | 296 | 295
2019-01-18 13:00 | 302 | 302
2019-01-18 13:30 | 311 | 311
2019-01-18 14:00 | 321 | 321
2019-01-18 14:30 | 327 | 327
2019-01-18 15:00 | 343 | 343
2019-01-18 15:30 | 353 | 353
2019-01-18 16:00 | 364 | 364
2019-01-18 16:30 | 380 | 380
2019-01-18 17:00 | 378 | 378
2019-01-18 17:30 | 372 | 371
2019-01-18 18:00 | 360 | 359
2019-01-18 18:30 | 353 | 351
2019-01-18 19:00 | 351 | 351
2019-01-18 19:30 | 351 | 351
2019-01-18 20:00 | 340 | 339
2019-01-18 20:30 | 332 | 330
2019-01-18 21:00 | 314 | 314
2019-01-18 21:30 | 300 | 300
2019-01-18 22:00 | 285 | 285
2019-01-18 22:30 | 273 | 273
2019-01-18 23:00 | 251 | 250
2019-01-18 23:30 | 231 | 230
2019-01-19 | 216 | 214
2019-01-19 00:30 | 206 | 205
2019-01-19 01:00 | 200 | 200
2019-01-19 01:30 | 198 | 197
2019-01-19 02:00 | 195 | 194
2019-01-19 02:30 | 191 | 190
2019-01-19 03:00 | 189 | 188
2019-01-19 03:30 | 194 | 192
2019-01-19 04:00 | 193 | 191
2019-01-19 04:30 | 194 | 192
2019-01-19 05:00 | 197 | 195
2019-01-19 05:30 | 202 | 200
2019-01-19 06:00 | 209 | 208
2019-01-19 06:30 | 216 | 216
2019-01-19 07:00 | 228 | 228
2019-01-19 07:30 | 239 | 239
2019-01-19 08:00 | 251 | 251
2019-01-19 08:30 | 261 | 260
2019-01-19 09:00 | 273 | 273
2019-01-19 09:30 | 273 | 273
2019-01-19 10:00 | 292 | 291
2019-01-19 10:30 | 290 | 289
2019-01-19 11:00 | 285 | 284
2019-01-19 11:30 | 290 | 288
2019-01-19 12:00 | 292 | 290
2019-01-19 12:30 | 293 | 291
2019-01-19 13:00 | 294 | 293
2019-01-19 13:30 | 297 | 296
2019-01-19 14:00 | 303 | 302
2019-01-19 14:30 | 314 | 313
2019-01-19 15:00 | 320 | 319
2019-01-19 15:30 | 332 | 331
2019-01-19 16:00 | 332 | 332
2019-01-19 16:30 | 333 | 333
2019-01-19 17:00 | 337 | 337
2019-01-19 17:30 | 334 | 334
2019-01-19 18:00 | 333 | 332
2019-01-19 18:30 | 326 | 325
2019-01-19 19:00 | 321 | 321
2019-01-19 19:30 | 317 | 316
2019-01-19 20:00 | 307 | 306
2019-01-19 20:30 | 296 | 296
2019-01-19 21:00 | 284 | 283
2019-01-19 21:30 | 274 | 274
2019-01-19 22:00 | 263 | 263
2019-01-19 22:30 | 258 | 258
2019-01-19 23:00 | 244 | 244
2019-01-19 23:30 | 224 | 224
2019-01-20 | 209 | 209
2019-01-20 00:30 | 200 | 200
2019-01-20 01:00 | 185 | 185
2019-01-20 01:30 | 179 | 179
2019-01-20 02:00 | 178 | 177
2019-01-20 02:30 | 179 | 179
2019-01-20 03:00 | 177 | 177
2019-01-20 03:30 | 180 | 180
2019-01-20 04:00 | 181 | 181
2019-01-20 04:30 | 182 | 182
2019-01-20 05:00 | 182 | 182
2019-01-20 05:30 | 187 | 187
2019-01-20 06:00 | 197 | 197
2019-01-20 06:30 | 208 | 207
2019-01-20 07:00 | 217 | 216
2019-01-20 07:30 | 225 | 225
2019-01-20 08:00 | 231 | 231
2019-01-20 08:30 | 239 | 239
2019-01-20 09:00 | 245 | 245
2019-01-20 09:30 | 249 | 249
2019-01-20 10:00 | 256 | 256
2019-01-20 10:30 | 259 | 258
2019-01-20 11:00 | 265 | 264
2019-01-20 11:30 | 268 | 267
2019-01-20 12:00 | 275 | 274
2019-01-20 12:30 | 287 | 285
2019-01-20 13:00 | 298 | 296
2019-01-20 13:30 | 306 | 304
2019-01-20 14:00 | 298 | 296
2019-01-20 14:30 | 309 | 308
2019-01-20 15:00 | 310 | 309
2019-01-20 15:30 | 317 | 315
2019-01-20 16:00 | 332 | 331
2019-01-20 16:30 | 344 | 343
2019-01-20 17:00 | 338 | 337
2019-01-20 17:30 | 343 | 342
2019-01-20 18:00 | 342 | 340
2019-01-20 18:30 | 341 | 339
2019-01-20 19:00 | 337 | 337
2019-01-20 19:30 | 333 | 333
2019-01-20 20:00 | 322 | 322
2019-01-20 20:30 | 291 | 290
2019-01-20 21:00 | 281 | 280
2019-01-20 21:30 | 269 | 268
2019-01-20 22:00 | 264 | 263
2019-01-20 22:30 | 258 | 258
2019-01-20 23:00 | 239 | 238
2019-01-20 23:30 | 221 | 220
2019-01-21 | 211 | 209
2019-01-21 00:30 | 210 | 208
2019-01-21 01:00 | 202 | 200
2019-01-21 01:30 | 198 | 195
2019-01-21 02:00 | 198 | 195
2019-01-21 02:30 | 197 | 194
2019-01-21 03:00 | 199 | 196
2019-01-21 03:30 | 202 | 200
2019-01-21 04:00 | 202 | 199
2019-01-21 04:30 | 205 | 202
2019-01-21 05:00 | 213 | 210
2019-01-21 05:30 | 221 | 219
2019-01-21 06:00 | 233 | 232
2019-01-21 06:30 | 247 | 247
2019-01-21 07:00 | 277 | 277
2019-01-21 07:30 | 303 | 302
2019-01-21 08:00 | 316 | 315
2019-01-21 08:30 | 319 | 318
2019-01-21 09:00 | 322 | 322
2019-01-21 09:30 | 323 | 322
2019-01-21 10:00 | 324 | 323
2019-01-21 10:30 | 324 | 324
2019-01-21 11:00 | 325 | 325
2019-01-21 11:30 | 328 | 327
2019-01-21 12:00 | 329 | 329
2019-01-21 12:30 | 338 | 337
2019-01-21 13:00 | 351 | 351
2019-01-21 13:30 | 355 | 355
2019-01-21 14:00 | 363 | 363
2019-01-21 14:30 | 367 | 367
2019-01-21 15:00 | 370 | 370
2019-01-21 15:30 | 379 | 379
2019-01-21 16:00 | 381 | 381
2019-01-21 16:30 | 385 | 385
2019-01-21 17:00 | 379 | 379
2019-01-21 17:30 | 375 | 374
2019-01-21 18:00 | 361 | 360
2019-01-21 18:30 | 371 | 369
2019-01-21 19:00 | 369 | 367
2019-01-21 19:30 | 365 | 363
2019-01-21 20:00 | 348 | 345
2019-01-21 20:30 | 322 | 321
2019-01-21 21:00 | 302 | 301
2019-01-21 21:30 | 288 | 287
2019-01-21 22:00 | 274 | 273
2019-01-21 22:30 | 261 | 259
2019-01-21 23:00 | 235 | 233
2019-01-21 23:30 | 216 | 215
2019-01-22 | 203 | 203
2019-01-22 00:30 | 197 | 196
2019-01-22 01:00 | 191 | 191
2019-01-22 01:30 | 194 | 193
2019-01-22 02:00 | 195 | 194
2019-01-22 02:30 | 196 | 195
2019-01-22 03:00 | 197 | 196
2019-01-22 03:30 | 197 | 196
2019-01-22 04:00 | 198 | 197
2019-01-22 04:30 | 197 | 196
2019-01-22 05:00 | 204 | 204
2019-01-22 05:30 | 215 | 214
2019-01-22 06:00 | 225 | 225
2019-01-22 06:30 | 238 | 238
2019-01-22 07:00 | 263 | 263
2019-01-22 07:30 | 283 | 283
2019-01-22 08:00 | 297 | 297
2019-01-22 08:30 | 305 | 305
2019-01-22 09:00 | 315 | 315
2019-01-22 09:30 | 317 | 317
2019-01-22 10:00 | 324 | 324
2019-01-22 10:30 | 331 | 330
2019-01-22 11:00 | 330 | 329
2019-01-22 11:30 | 338 | 337
2019-01-22 12:00 | 345 | 344
2019-01-22 12:30 | 346 | 345
2019-01-22 13:00 | 354 | 354
2019-01-22 13:30 | 361 | 361
2019-01-22 14:00 | 379 | 379
2019-01-22 14:30 | 394 | 394
2019-01-22 15:00 | 394 | 394
2019-01-22 15:30 | 416 | 416
2019-01-22 16:00 | 431 | 430
2019-01-22 16:30 | 421 | 420
2019-01-22 17:00 | 410 | 407
2019-01-22 17:30 | 402 | 400
2019-01-22 18:00 | 390 | 388
2019-01-22 18:30 | 400 | 398
2019-01-22 19:00 | 394 | 392
2019-01-22 19:30 | 378 | 376
2019-01-22 20:00 | 355 | 353
2019-01-22 20:30 | 339 | 336
2019-01-22 21:00 | 326 | 322
2019-01-22 21:30 | 306 | 302
2019-01-22 22:00 | 284 | 284
2019-01-22 22:30 | 267 | 267
2019-01-22 23:00 | 248 | 248
2019-01-22 23:30 | 234 | 234
2019-01-23 | 217 | 217
2019-01-23 00:30 | 206 | 205
2019-01-23 01:00 | 200 | 200
2019-01-23 01:30 | 200 | 199
2019-01-23 02:00 | 200 | 199
2019-01-23 02:30 | 201 | 200
2019-01-23 03:00 | 199 | 199
2019-01-23 03:30 | 199 | 198
2019-01-23 04:00 | 196 | 195
2019-01-23 04:30 | 199 | 198
2019-01-23 05:00 | 205 | 205
2019-01-23 05:30 | 217 | 217
2019-01-23 06:00 | 227 | 227
2019-01-23 06:30 | 240 | 240
2019-01-23 07:00 | 264 | 264
2019-01-23 07:30 | 283 | 283
2019-01-23 08:00 | 297 | 297
2019-01-23 08:30 | 309 | 309
2019-01-23 09:00 | 311 | 311
2019-01-23 09:30 | 318 | 318
2019-01-23 10:00 | 330 | 330
2019-01-23 10:30 | 341 | 341
2019-01-23 11:00 | 349 | 348
2019-01-23 11:30 | 361 | 361
2019-01-23 12:00 | 358 | 358
2019-01-23 12:30 | 359 | 359
2019-01-23 13:00 | 361 | 361
2019-01-23 13:30 | 371 | 371
2019-01-23 14:00 | 375 | 374
2019-01-23 14:30 | 378 | 377
2019-01-23 15:00 | 391 | 391
2019-01-23 15:30 | 415 | 415
2019-01-23 16:00 | 422 | 422
2019-01-23 16:30 | 415 | 415
2019-01-23 17:00 | 401 | 400
2019-01-23 17:30 | 393 | 392
2019-01-23 18:00 | 377 | 376
2019-01-23 18:30 | 366 | 365
2019-01-23 19:00 | 356 | 355
2019-01-23 19:30 | 348 | 347
2019-01-23 20:00 | 339 | 339
2019-01-23 20:30 | 318 | 318
2019-01-23 21:00 | 302 | 302
2019-01-23 21:30 | 288 | 288
2019-01-23 22:00 | 274 | 274
2019-01-23 22:30 | 262 | 262
2019-01-23 23:00 | 239 | 238
2019-01-23 23:30 | 220 | 220
2019-01-24 | 207 | 207
2019-01-24 00:30 | 202 | 202
2019-01-24 01:00 | 197 | 197
2019-01-24 01:30 | 196 | 196
2019-01-24 02:00 | 193 | 193
2019-01-24 02:30 | 190 | 190
2019-01-24 03:00 | 192 | 192
2019-01-24 03:30 | 190 | 190
2019-01-24 04:00 | 191 | 191
2019-01-24 04:30 | 191 | 191
2019-01-24 05:00 | 198 | 198
2019-01-24 05:30 | 210 | 210
2019-01-24 06:00 | 228 | 228
2019-01-24 06:30 | 247 | 247
2019-01-24 07:00 | 272 | 272
2019-01-24 07:30 | 290 | 290
2019-01-24 08:00 | 307 | 307
2019-01-24 08:30 | 321 | 321
2019-01-24 09:00 | 333 | 333
2019-01-24 09:30 | 333 | 333
2019-01-24 10:00 | 322 | 322
2019-01-24 10:30 | 316 | 316
2019-01-24 11:00 | 323 | 323
2019-01-24 11:30 | 329 | 329
2019-01-24 12:00 | 322 | 322
2019-01-24 12:30 | 314 | 314
2019-01-24 13:00 | 320 | 320
2019-01-24 13:30 | 329 | 329
2019-01-24 14:00 | 360 | 360
2019-01-24 14:30 | 368 | 368
2019-01-24 15:00 | 365 | 365
2019-01-24 15:30 | 387 | 387
2019-01-24 16:00 | 395 | 395
2019-01-24 16:30 | 402 | 402
2019-01-24 17:00 | 396 | 396
2019-01-24 17:30 | 377 | 376
2019-01-24 18:00 | 367 | 366
2019-01-24 18:30 | 370 | 370
2019-01-24 19:00 | 376 | 376
2019-01-24 19:30 | 374 | 373
2019-01-24 20:00 | 351 | 351
2019-01-24 20:30 | 332 | 332
2019-01-24 21:00 | 323 | 322
2019-01-24 21:30 | 306 | 305
2019-01-24 22:00 | 286 | 284
2019-01-24 22:30 | 269 | 268
2019-01-24 23:00 | 245 | 245
2019-01-24 23:30 | 231 | 231
2019-01-25 | 220 | 220
2019-01-25 00:30 | 217 | 216
2019-01-25 01:00 | 212 | 211
2019-01-25 01:30 | 210 | 210
2019-01-25 02:00 | 210 | 209
2019-01-25 02:30 | 207 | 206
2019-01-25 03:00 | 210 | 209
2019-01-25 03:30 | 208 | 207
2019-01-25 04:00 | 205 | 204
2019-01-25 04:30 | 210 | 209
2019-01-25 05:00 | 215 | 214
2019-01-25 05:30 | 227 | 226
2019-01-25 06:00 | 237 | 237
2019-01-25 06:30 | 256 | 256
2019-01-25 07:00 | 287 | 287
2019-01-25 07:30 | 308 | 308
2019-01-25 08:00 | 324 | 324
2019-01-25 08:30 | 336 | 335
2019-01-25 09:00 | 335 | 334
2019-01-25 09:30 | 335 | 334
2019-01-25 10:00 | 332 | 331
2019-01-25 10:30 | 340 | 340
2019-01-25 11:00 | 339 | 338
2019-01-25 11:30 | 369 | 368
2019-01-25 12:00 | 372 | 372
2019-01-25 12:30 | 356 | 355
2019-01-25 13:00 | 360 | 359
2019-01-25 13:30 | 372 | 371
2019-01-25 14:00 | 413 | 413
2019-01-25 14:30 | 414 | 414
2019-01-25 15:00 | 415 | 415
2019-01-25 15:30 | 409 | 409
2019-01-25 16:00 | 413 | 413
2019-01-25 16:30 | 423 | 423
2019-01-25 17:00 | 421 | 420
2019-01-25 17:30 | 414 | 412
2019-01-25 18:00 | 426 | 424
2019-01-25 18:30 | 431 | 428
2019-01-25 19:00 | 439 | 437
2019-01-25 19:30 | 434 | 432
2019-01-25 20:00 | 381 | 378
2019-01-25 20:30 | 376 | 373
2019-01-25 21:00 | 350 | 347
2019-01-25 21:30 | 326 | 324
2019-01-25 22:00 | 311 | 309
2019-01-25 22:30 | 291 | 291
2019-01-25 23:00 | 265 | 264
2019-01-25 23:30 | 244 | 243
2019-01-26 | 221 | 221
2019-01-26 00:30 | 213 | 213
2019-01-26 01:00 | 207 | 207
2019-01-26 01:30 | 203 | 202
2019-01-26 02:00 | 200 | 199
2019-01-26 02:30 | 199 | 199
2019-01-26 03:00 | 196 | 196
2019-01-26 03:30 | 195 | 194
2019-01-26 04:00 | 196 | 195
2019-01-26 04:30 | 195 | 195
2019-01-26 05:00 | 198 | 197
2019-01-26 05:30 | 205 | 204
2019-01-26 06:00 | 213 | 212
2019-01-26 06:30 | 222 | 222
2019-01-26 07:00 | 234 | 234
2019-01-26 07:30 | 248 | 248
2019-01-26 08:00 | 261 | 261
2019-01-26 08:30 | 274 | 274
2019-01-26 09:00 | 282 | 281
2019-01-26 09:30 | 286 | 285
2019-01-26 10:00 | 313 | 313
2019-01-26 10:30 | 327 | 326
2019-01-26 11:00 | 322 | 320
2019-01-26 11:30 | 329 | 328
2019-01-26 12:00 | 327 | 326
2019-01-26 12:30 | 332 | 331
2019-01-26 13:00 | 339 | 338
2019-01-26 13:30 | 339 | 338
2019-01-26 14:00 | 337 | 336
2019-01-26 14:30 | 355 | 355
2019-01-26 15:00 | 365 | 364
2019-01-26 15:30 | 372 | 372
2019-01-26 16:00 | 374 | 374
2019-01-26 16:30 | 398 | 398
2019-01-26 17:00 | 392 | 392
2019-01-26 17:30 | 363 | 361
2019-01-26 18:00 | 351 | 350
2019-01-26 18:30 | 351 | 350
2019-01-26 19:00 | 349 | 349
2019-01-26 19:30 | 342 | 341
2019-01-26 20:00 | 328 | 328
2019-01-26 20:30 | 314 | 314
2019-01-26 21:00 | 304 | 304
2019-01-26 21:30 | 290 | 290
2019-01-26 22:00 | 278 | 278
2019-01-26 22:30 | 271 | 271
2019-01-26 23:00 | 252 | 251
2019-01-26 23:30 | 236 | 235
2019-01-27 | 222 | 222
2019-01-27 00:30 | 217 | 217
2019-01-27 01:00 | 213 | 212
2019-01-27 01:30 | 208 | 207
2019-01-27 02:00 | 206 | 205
2019-01-27 02:30 | 204 | 203
2019-01-27 03:00 | 204 | 203
2019-01-27 03:30 | 203 | 202
2019-01-27 04:00 | 204 | 203
2019-01-27 04:30 | 200 | 199
2019-01-27 05:00 | 203 | 201
2019-01-27 05:30 | 207 | 205
2019-01-27 06:00 | 215 | 215
2019-01-27 06:30 | 233 | 233
2019-01-27 07:00 | 243 | 243
2019-01-27 07:30 | 253 | 253
2019-01-27 08:00 | 261 | 261
2019-01-27 08:30 | 267 | 267
2019-01-27 09:00 | 268 | 268
2019-01-27 09:30 | 273 | 273
2019-01-27 10:00 | 273 | 273
2019-01-27 10:30 | 274 | 274
2019-01-27 11:00 | 279 | 279
2019-01-27 11:30 | 287 | 287
2019-01-27 12:00 | 284 | 283
2019-01-27 12:30 | 289 | 288
2019-01-27 13:00 | 294 | 294
2019-01-27 13:30 | 299 | 298
2019-01-27 14:00 | 306 | 306
2019-01-27 14:30 | 316 | 316
2019-01-27 15:00 | 327 | 326
2019-01-27 15:30 | 328 | 328
2019-01-27 16:00 | 333 | 333
2019-01-27 16:30 | 339 | 339
2019-01-27 17:00 | 342 | 341
2019-01-27 17:30 | 338 | 337
2019-01-27 18:00 | 334 | 333
2019-01-27 18:30 | 335 | 333
2019-01-27 19:00 | 336 | 335
2019-01-27 19:30 | 337 | 335
2019-01-27 20:00 | 324 | 323
2019-01-27 20:30 | 312 | 312
2019-01-27 21:00 | 301 | 301
2019-01-27 21:30 | 288 | 288
2019-01-27 22:00 | 278 | 278
2019-01-27 22:30 | 269 | 269
2019-01-27 23:00 | 251 | 251
2019-01-27 23:30 | 239 | 239
2019-01-28 | 224 | 223
2019-01-28 00:30 | 216 | 215
2019-01-28 01:00 | 209 | 208
2019-01-28 01:30 | 201 | 200
2019-01-28 02:00 | 200 | 199
2019-01-28 02:30 | 200 | 198
2019-01-28 03:00 | 200 | 199
2019-01-28 03:30 | 206 | 205
2019-01-28 04:00 | 204 | 203
2019-01-28 04:30 | 206 | 205
2019-01-28 05:00 | 229 | 228
2019-01-28 05:30 | 235 | 234
2019-01-28 06:00 | 218 | 218
2019-01-28 06:30 | 226 | 225
2019-01-28 07:00 | 238 | 238
2019-01-28 07:30 | 246 | 246
2019-01-28 08:00 | 255 | 254
2019-01-28 08:30 | 263 | 263
2019-01-28 09:00 | 263 | 262
2019-01-28 09:30 | 264 | 264
2019-01-28 10:00 | 271 | 271
2019-01-28 10:30 | 273 | 273
2019-01-28 11:00 | 279 | 279
2019-01-28 11:30 | 287 | 287
2019-01-28 12:00 | 286 | 286
2019-01-28 12:30 | 296 | 296
2019-01-28 13:00 | 304 | 302
2019-01-28 13:30 | 313 | 311
2019-01-28 14:00 | 320 | 318
2019-01-28 14:30 | 334 | 333
2019-01-28 15:00 | 347 | 346
2019-01-28 15:30 | 358 | 357
2019-01-28 16:00 | 381 | 381
2019-01-28 16:30 | 375 | 375
2019-01-28 17:00 | 377 | 376
2019-01-28 17:30 | 376 | 376
2019-01-28 18:00 | 371 | 370
2019-01-28 18:30 | 368 | 368
2019-01-28 19:00 | 367 | 366
2019-01-28 19:30 | 355 | 355
2019-01-28 20:00 | 333 | 332
2019-01-28 20:30 | 315 | 314
2019-01-28 21:00 | 306 | 305
2019-01-28 21:30 | 291 | 289
2019-01-28 22:00 | 274 | 274
2019-01-28 22:30 | 264 | 264
2019-01-28 23:00 | 244 | 244
2019-01-28 23:30 | 229 | 229
2019-01-29 | 217 | 217
2019-01-29 00:30 | 212 | 212
2019-01-29 01:00 | 207 | 207
2019-01-29 01:30 | 200 | 199
2019-01-29 02:00 | 199 | 198
2019-01-29 02:30 | 198 | 198
2019-01-29 03:00 | 194 | 194
2019-01-29 03:30 | 194 | 194
2019-01-29 04:00 | 197 | 197
2019-01-29 04:30 | 198 | 198
2019-01-29 05:00 | 205 | 204
2019-01-29 05:30 | 215 | 215
2019-01-29 06:00 | 238 | 238
2019-01-29 06:30 | 266 | 265
2019-01-29 07:00 | 288 | 288
2019-01-29 07:30 | 307 | 307
2019-01-29 08:00 | 309 | 308
2019-01-29 08:30 | 315 | 315
2019-01-29 09:00 | 327 | 327
2019-01-29 09:30 | 323 | 323
2019-01-29 10:00 | 325 | 325
2019-01-29 10:30 | 333 | 333
2019-01-29 11:00 | 342 | 342
2019-01-29 11:30 | 343 | 343
2019-01-29 12:00 | 336 | 336
2019-01-29 12:30 | 344 | 344
2019-01-29 13:00 | 358 | 357
2019-01-29 13:30 | 367 | 367
2019-01-29 14:00 | 376 | 376
2019-01-29 14:30 | 382 | 382
2019-01-29 15:00 | 391 | 391
2019-01-29 15:30 | 388 | 388
2019-01-29 16:00 | 402 | 402
2019-01-29 16:30 | 415 | 415
2019-01-29 17:00 | 416 | 416
2019-01-29 17:30 | 400 | 399
2019-01-29 18:00 | 399 | 398
2019-01-29 18:30 | 408 | 408
2019-01-29 19:00 | 391 | 390
2019-01-29 19:30 | 377 | 376
2019-01-29 20:00 | 362 | 360
2019-01-29 20:30 | 339 | 339
2019-01-29 21:00 | 310 | 310
2019-01-29 21:30 | 297 | 296
2019-01-29 22:00 | 282 | 281
2019-01-29 22:30 | 272 | 272
2019-01-29 23:00 | 255 | 254
2019-01-29 23:30 | 240 | 240
2019-01-30 | 227 | 226
2019-01-30 00:30 | 223 | 223
2019-01-30 01:00 | 214 | 214
2019-01-30 01:30 | 209 | 209
2019-01-30 02:00 | 205 | 205
2019-01-30 02:30 | 204 | 204
2019-01-30 03:00 | 204 | 203
2019-01-30 03:30 | 206 | 206
2019-01-30 04:00 | 206 | 206
2019-01-30 04:30 | 206 | 206
2019-01-30 05:00 | 214 | 214
2019-01-30 05:30 | 227 | 227
2019-01-30 06:00 | 246 | 246
2019-01-30 06:30 | 265 | 265
2019-01-30 07:00 | 292 | 291
2019-01-30 07:30 | 311 | 311
2019-01-30 08:00 | 328 | 328
2019-01-30 08:30 | 322 | 322
2019-01-30 09:00 | 333 | 333
2019-01-30 09:30 | 332 | 332
2019-01-30 10:00 | 333 | 333
2019-01-30 10:30 | 334 | 334
2019-01-30 11:00 | 334 | 333
2019-01-30 11:30 | 340 | 340
2019-01-30 12:00 | 353 | 352
2019-01-30 12:30 | 357 | 357
2019-01-30 13:00 | 368 | 368
2019-01-30 13:30 | 382 | 381
2019-01-30 14:00 | 376 | 376
2019-01-30 14:30 | 395 | 395
2019-01-30 15:00 | 397 | 397
2019-01-30 15:30 | 385 | 385
2019-01-30 16:00 | 383 | 382
2019-01-30 16:30 | 390 | 390
2019-01-30 17:00 | 394 | 394
2019-01-30 17:30 | 382 | 382
2019-01-30 18:00 | 366 | 366
2019-01-30 18:30 | 378 | 378
2019-01-30 19:00 | 376 | 376
2019-01-30 19:30 | 369 | 369
2019-01-30 20:00 | 352 | 352
2019-01-30 20:30 | 335 | 335
2019-01-30 21:00 | 316 | 315
2019-01-30 21:30 | 294 | 293
2019-01-30 22:00 | 274 | 274
2019-01-30 22:30 | 252 | 252
2019-01-30 23:00 | 225 | 225
2019-01-30 23:30 | 209 | 209
2019-01-31 | 197 | 197
2019-01-31 00:30 | 192 | 192
2019-01-31 01:00 | 182 | 182
2019-01-31 01:30 | 181 | 181
2019-01-31 02:00 | 182 | 182
2019-01-31 02:30 | 183 | 183
2019-01-31 03:00 | 186 | 186
2019-01-31 03:30 | 185 | 185
2019-01-31 04:00 | 186 | 186
2019-01-31 04:30 | 188 | 188
2019-01-31 05:00 | 199 | 199
2019-01-31 05:30 | 209 | 209
2019-01-31 06:00 | 232 | 232
2019-01-31 06:30 | 255 | 255
2019-01-31 07:00 | 269 | 269
2019-01-31 07:30 | 280 | 280
2019-01-31 08:00 | 287 | 287
2019-01-31 08:30 | 297 | 297
2019-01-31 09:00 | 297 | 296
2019-01-31 09:30 | 304 | 303
2019-01-31 10:00 | 314 | 314
2019-01-31 10:30 | 321 | 321
2019-01-31 11:00 | 327 | 327
2019-01-31 11:30 | 324 | 323
2019-01-31 12:00 | 324 | 324
2019-01-31 12:30 | 340 | 340
2019-01-31 13:00 | 361 | 361
2019-01-31 13:30 | 362 | 361
2019-01-31 14:00 | 352 | 352
2019-01-31 14:30 | 362 | 361
2019-01-31 15:00 | 375 | 375
2019-01-31 15:30 | 383 | 382
2019-01-31 16:00 | 397 | 396
2019-01-31 16:30 | 415 | 415
2019-01-31 17:00 | 396 | 395
2019-01-31 17:30 | 387 | 386
2019-01-31 18:00 | 381 | 379
2019-01-31 18:30 | 385 | 384
2019-01-31 19:00 | 379 | 378
2019-01-31 19:30 | 376 | 374
2019-01-31 20:00 | 354 | 353
2019-01-31 20:30 | 334 | 334
2019-01-31 21:00 | 312 | 312
2019-01-31 21:30 | 290 | 289
2019-01-31 22:00 | 273 | 271
2019-01-31 22:30 | 260 | 259
2019-01-31 23:00 | 237 | 237
2019-01-31 23:30 | 219 | 219
2019-02-01 | 205 | 205
2019-02-01 00:30 | 199 | 199
2019-02-01 01:00 | 197 | 197
2019-02-01 01:30 | 192 | 191
2019-02-01 02:00 | 188 | 188
2019-02-01 02:30 | 188 | 188
2019-02-01 03:00 | 186 | 185
2019-02-01 03:30 | 185 | 185
2019-02-01 04:00 | 186 | 185
2019-02-01 04:30 | 189 | 188
2019-02-01 05:00 | 201 | 201
2019-02-01 05:30 | 205 | 205
2019-02-01 06:00 | 222 | 222
2019-02-01 06:30 | 241 | 240
2019-02-01 07:00 | 261 | 261
2019-02-01 07:30 | 273 | 273
2019-02-01 08:00 | 283 | 282
2019-02-01 08:30 | 284 | 283
2019-02-01 09:00 | 290 | 289
2019-02-01 09:30 | 287 | 287
2019-02-01 10:00 | 287 | 286
2019-02-01 10:30 | 289 | 288
2019-02-01 11:00 | 288 | 288
2019-02-01 11:30 | 291 | 291
2019-02-01 12:00 | 296 | 296
2019-02-01 12:30 | 305 | 304
2019-02-01 13:00 | 320 | 320
2019-02-01 13:30 | 334 | 334
2019-02-01 14:00 | 358 | 358
2019-02-01 14:30 | 357 | 357
2019-02-01 15:00 | 342 | 342
2019-02-01 15:30 | 331 | 331
2019-02-01 16:00 | 336 | 336
2019-02-01 16:30 | 337 | 337
2019-02-01 17:00 | 328 | 328
2019-02-01 17:30 | 325 | 325
2019-02-01 18:00 | 319 | 319
2019-02-01 18:30 | 326 | 326
2019-02-01 19:00 | 325 | 325
2019-02-01 19:30 | 325 | 325
2019-02-01 20:00 | 311 | 311
2019-02-01 20:30 | 296 | 294
2019-02-01 21:00 | 298 | 297
2019-02-01 21:30 | 275 | 274
2019-02-01 22:00 | 259 | 259
2019-02-01 22:30 | 251 | 251
2019-02-01 23:00 | 233 | 233
2019-02-01 23:30 | 216 | 215
2019-02-02 | 204 | 203
2019-02-02 00:30 | 200 | 200
2019-02-02 01:00 | 200 | 200
2019-02-02 01:30 | 196 | 196
2019-02-02 02:00 | 196 | 196
2019-02-02 02:30 | 198 | 198
2019-02-02 03:00 | 195 | 195
2019-02-02 03:30 | 196 | 196
2019-02-02 04:00 | 188 | 188
2019-02-02 04:30 | 186 | 186
2019-02-02 05:00 | 186 | 186
2019-02-02 05:30 | 187 | 187
2019-02-02 06:00 | 200 | 200
2019-02-02 06:30 | 210 | 209
2019-02-02 07:00 | 221 | 220
2019-02-02 07:30 | 230 | 230
2019-02-02 08:00 | 239 | 239
2019-02-02 08:30 | 244 | 244
2019-02-02 09:00 | 255 | 255
2019-02-02 09:30 | 259 | 258
2019-02-02 10:00 | 252 | 252
2019-02-02 10:30 | 259 | 258
2019-02-02 11:00 | 254 | 252
2019-02-02 11:30 | 258 | 256
2019-02-02 12:00 | 258 | 256
2019-02-02 12:30 | 264 | 262
2019-02-02 13:00 | 273 | 271
2019-02-02 13:30 | 278 | 276
2019-02-02 14:00 | 284 | 283
2019-02-02 14:30 | 286 | 285
2019-02-02 15:00 | 290 | 289
2019-02-02 15:30 | 289 | 288
2019-02-02 16:00 | 295 | 293
2019-02-02 16:30 | 302 | 301
2019-02-02 17:00 | 311 | 309
2019-02-02 17:30 | 309 | 307
2019-02-02 18:00 | 304 | 302
2019-02-02 18:30 | 304 | 302
2019-02-02 19:00 | 307 | 305
2019-02-02 19:30 | 309 | 307
2019-02-02 20:00 | 292 | 291
2019-02-02 20:30 | 277 | 276
2019-02-02 21:00 | 275 | 274
2019-02-02 21:30 | 254 | 254
2019-02-02 22:00 | 251 | 251
2019-02-02 22:30 | 245 | 245
2019-02-02 23:00 | 232 | 232
2019-02-02 23:30 | 214 | 214
2019-02-03 | 200 | 199
2019-02-03 00:30 | 195 | 194
2019-02-03 01:00 | 189 | 188
2019-02-03 01:30 | 185 | 184
2019-02-03 02:00 | 184 | 183
2019-02-03 02:30 | 186 | 184
2019-02-03 03:00 | 185 | 184
2019-02-03 03:30 | 187 | 185
2019-02-03 04:00 | 183 | 181
2019-02-03 04:30 | 182 | 180
2019-02-03 05:00 | 185 | 183
2019-02-03 05:30 | 177 | 175
2019-02-03 06:00 | 186 | 185
2019-02-03 06:30 | 197 | 196
2019-02-03 07:00 | 205 | 204
2019-02-03 07:30 | 221 | 220
2019-02-03 08:00 | 233 | 233
2019-02-03 08:30 | 235 | 235
2019-02-03 09:00 | 227 | 227
2019-02-03 09:30 | 228 | 228
2019-02-03 10:00 | 235 | 235
2019-02-03 10:30 | 235 | 235
2019-02-03 11:00 | 235 | 235
2019-02-03 11:30 | 242 | 242
2019-02-03 12:00 | 244 | 244
2019-02-03 12:30 | 249 | 249
2019-02-03 13:00 | 259 | 258
2019-02-03 13:30 | 278 | 278
2019-02-03 14:00 | 276 | 276
2019-02-03 14:30 | 283 | 283
2019-02-03 15:00 | 293 | 293
2019-02-03 15:30 | 309 | 308
2019-02-03 16:00 | 321 | 321
2019-02-03 16:30 | 333 | 332
2019-02-03 17:00 | 338 | 337
2019-02-03 17:30 | 339 | 337
2019-02-03 18:00 | 334 | 332
2019-02-03 18:30 | 340 | 339
2019-02-03 19:00 | 342 | 341
2019-02-03 19:30 | 341 | 339
2019-02-03 20:00 | 331 | 328
2019-02-03 20:30 | 312 | 311
2019-02-03 21:00 | 298 | 298
2019-02-03 21:30 | 284 | 284
2019-02-03 22:00 | 274 | 273
2019-02-03 22:30 | 266 | 266
2019-02-03 23:00 | 250 | 250
2019-02-03 23:30 | 234 | 233
2019-02-04 | 217 | 217
2019-02-04 00:30 | 210 | 210
2019-02-04 01:00 | 207 | 206
2019-02-04 01:30 | 202 | 201
2019-02-04 02:00 | 201 | 200
2019-02-04 02:30 | 199 | 198
2019-02-04 03:00 | 200 | 199
2019-02-04 03:30 | 201 | 200
2019-02-04 04:00 | 206 | 205
2019-02-04 04:30 | 206 | 206
2019-02-04 05:00 | 215 | 214
2019-02-04 05:30 | 232 | 232
2019-02-04 06:00 | 247 | 247
2019-02-04 06:30 | 267 | 267
2019-02-04 07:00 | 285 | 284
2019-02-04 07:30 | 297 | 297
2019-02-04 08:00 | 312 | 312
2019-02-04 08:30 | 312 | 312
2019-02-04 09:00 | 310 | 310
2019-02-04 09:30 | 302 | 302
2019-02-04 10:00 | 298 | 298
2019-02-04 10:30 | 299 | 298
2019-02-04 11:00 | 297 | 297
2019-02-04 11:30 | 302 | 302
2019-02-04 12:00 | 308 | 308
2019-02-04 12:30 | 312 | 312
2019-02-04 13:00 | 316 | 316
2019-02-04 13:30 | 323 | 323
2019-02-04 14:00 | 332 | 332
2019-02-04 14:30 | 339 | 337
2019-02-04 15:00 | 345 | 343
2019-02-04 15:30 | 368 | 366
2019-02-04 16:00 | 379 | 377
2019-02-04 16:30 | 395 | 394
2019-02-04 17:00 | 399 | 397
2019-02-04 17:30 | 400 | 398
2019-02-04 18:00 | 379 | 376
2019-02-04 18:30 | 367 | 365
2019-02-04 19:00 | 361 | 360
2019-02-04 19:30 | 359 | 358
2019-02-04 20:00 | 343 | 341
2019-02-04 20:30 | 316 | 316
2019-02-04 21:00 | 301 | 301
2019-02-04 21:30 | 290 | 290
2019-02-04 22:00 | 278 | 277
2019-02-04 22:30 | 268 | 267
2019-02-04 23:00 | 247 | 246
2019-02-04 23:30 | 232 | 231
2019-02-05 | 217 | 215
2019-02-05 00:30 | 209 | 208
2019-02-05 01:00 | 204 | 203
2019-02-05 01:30 | 195 | 194
2019-02-05 02:00 | 192 | 191
2019-02-05 02:30 | 189 | 188
2019-02-05 03:00 | 190 | 189
2019-02-05 03:30 | 193 | 192
2019-02-05 04:00 | 200 | 199
2019-02-05 04:30 | 204 | 203
2019-02-05 05:00 | 213 | 213
2019-02-05 05:30 | 225 | 225
2019-02-05 06:00 | 244 | 244
2019-02-05 06:30 | 258 | 257
2019-02-05 07:00 | 281 | 280
2019-02-05 07:30 | 292 | 292
2019-02-05 08:00 | 297 | 297
2019-02-05 08:30 | 298 | 298
2019-02-05 09:00 | 299 | 299
2019-02-05 09:30 | 300 | 300
2019-02-05 10:00 | 297 | 297
2019-02-05 10:30 | 295 | 295
2019-02-05 11:00 | 297 | 297
2019-02-05 11:30 | 303 | 302
2019-02-05 12:00 | 302 | 302
2019-02-05 12:30 | 303 | 303
2019-02-05 13:00 | 314 | 313
2019-02-05 13:30 | 322 | 322
2019-02-05 14:00 | 327 | 327
2019-02-05 14:30 | 327 | 327
2019-02-05 15:00 | 335 | 335
2019-02-05 15:30 | 345 | 344
2019-02-05 16:00 | 353 | 353
2019-02-05 16:30 | 368 | 368
2019-02-05 17:00 | 368 | 368
2019-02-05 17:30 | 355 | 354
2019-02-05 18:00 | 346 | 345
2019-02-05 18:30 | 349 | 348
2019-02-05 19:00 | 341 | 340
2019-02-05 19:30 | 329 | 329
2019-02-05 20:00 | 318 | 318
2019-02-05 20:30 | 299 | 299
2019-02-05 21:00 | 294 | 294
2019-02-05 21:30 | 283 | 282
2019-02-05 22:00 | 275 | 275
2019-02-05 22:30 | 270 | 269
2019-02-05 23:00 | 254 | 254
2019-02-05 23:30 | 232 | 231
2019-02-06 | 216 | 215
2019-02-06 00:30 | 209 | 207
2019-02-06 01:00 | 203 | 201
2019-02-06 01:30 | 198 | 196
2019-02-06 02:00 | 197 | 195
2019-02-06 02:30 | 198 | 196
2019-02-06 03:00 | 198 | 196
2019-02-06 03:30 | 197 | 194
2019-02-06 04:00 | 196 | 194
2019-02-06 04:30 | 201 | 198
2019-02-06 05:00 | 212 | 210
2019-02-06 05:30 | 221 | 219
2019-02-06 06:00 | 233 | 232
2019-02-06 06:30 | 245 | 245
2019-02-06 07:00 | 262 | 262
2019-02-06 07:30 | 275 | 275
2019-02-06 08:00 | 284 | 284
2019-02-06 08:30 | 281 | 281
2019-02-06 09:00 | 290 | 290
2019-02-06 09:30 | 303 | 302
2019-02-06 10:00 | 314 | 313
2019-02-06 10:30 | 306 | 304
2019-02-06 11:00 | 306 | 304
2019-02-06 11:30 | 307 | 305
2019-02-06 12:00 | 315 | 313
2019-02-06 12:30 | 321 | 319
2019-02-06 13:00 | 313 | 312
2019-02-06 13:30 | 324 | 323
2019-02-06 14:00 | 316 | 315
2019-02-06 14:30 | 326 | 325
2019-02-06 15:00 | 328 | 327
2019-02-06 15:30 | 355 | 355
2019-02-06 16:00 | 370 | 370
2019-02-06 16:30 | 350 | 349
2019-02-06 17:00 | 343 | 340
2019-02-06 17:30 | 343 | 341
2019-02-06 18:00 | 337 | 335
2019-02-06 18:30 | 339 | 338
2019-02-06 19:00 | 338 | 336
2019-02-06 19:30 | 336 | 334
2019-02-06 20:00 | 322 | 321
2019-02-06 20:30 | 307 | 307
2019-02-06 21:00 | 294 | 294
2019-02-06 21:30 | 283 | 282
2019-02-06 22:00 | 273 | 273
2019-02-06 22:30 | 265 | 265
2019-02-06 23:00 | 246 | 245
2019-02-06 23:30 | 225 | 225
2019-02-07 | 210 | 209
2019-02-07 00:30 | 204 | 204
2019-02-07 01:00 | 198 | 197
2019-02-07 01:30 | 190 | 189
2019-02-07 02:00 | 191 | 189
2019-02-07 02:30 | 193 | 191
2019-02-07 03:00 | 191 | 189
2019-02-07 03:30 | 190 | 188
2019-02-07 04:00 | 198 | 197
2019-02-07 04:30 | 200 | 199
2019-02-07 05:00 | 207 | 206
2019-02-07 05:30 | 219 | 219
2019-02-07 06:00 | 231 | 231
2019-02-07 06:30 | 256 | 256
2019-02-07 07:00 | 273 | 272
2019-02-07 07:30 | 285 | 285
2019-02-07 08:00 | 290 | 290
2019-02-07 08:30 | 301 | 301
2019-02-07 09:00 | 302 | 302
2019-02-07 09:30 | 305 | 305
2019-02-07 10:00 | 313 | 313
2019-02-07 10:30 | 320 | 320
2019-02-07 11:00 | 331 | 331
2019-02-07 11:30 | 316 | 316
2019-02-07 12:00 | 308 | 308
2019-02-07 12:30 | 323 | 323
2019-02-07 13:00 | 333 | 333
2019-02-07 13:30 | 335 | 335
2019-02-07 14:00 | 338 | 338
2019-02-07 14:30 | 350 | 350
2019-02-07 15:00 | 361 | 361
2019-02-07 15:30 | 368 | 368
2019-02-07 16:00 | 355 | 355
2019-02-07 16:30 | 354 | 353
2019-02-07 17:00 | 342 | 341
2019-02-07 17:30 | 342 | 340
2019-02-07 18:00 | 336 | 334
2019-02-07 18:30 | 340 | 340
2019-02-07 19:00 | 341 | 340
2019-02-07 19:30 | 343 | 343
2019-02-07 20:00 | 329 | 329
2019-02-07 20:30 | 312 | 311
2019-02-07 21:00 | 294 | 294
2019-02-07 21:30 | 279 | 279
2019-02-07 22:00 | 270 | 269
2019-02-07 22:30 | 264 | 264
2019-02-07 23:00 | 246 | 246
2019-02-07 23:30 | 228 | 228
2019-02-08 | 213 | 212
2019-02-08 00:30 | 206 | 205
2019-02-08 01:00 | 203 | 202
2019-02-08 01:30 | 202 | 201
2019-02-08 02:00 | 200 | 199
2019-02-08 02:30 | 199 | 197
2019-02-08 03:00 | 199 | 197
2019-02-08 03:30 | 197 | 196
2019-02-08 04:00 | 198 | 197
2019-02-08 04:30 | 200 | 199
2019-02-08 05:00 | 208 | 207
2019-02-08 05:30 | 217 | 216
2019-02-08 06:00 | 232 | 232
2019-02-08 06:30 | 249 | 249
2019-02-08 07:00 | 274 | 274
2019-02-08 07:30 | 290 | 290
2019-02-08 08:00 | 295 | 295
2019-02-08 08:30 | 298 | 298
2019-02-08 09:00 | 304 | 303
2019-02-08 09:30 | 298 | 297
2019-02-08 10:00 | 308 | 307
2019-02-08 10:30 | 302 | 302
2019-02-08 11:00 | 302 | 302
2019-02-08 11:30 | 310 | 309
2019-02-08 12:00 | 309 | 309
2019-02-08 12:30 | 305 | 304
2019-02-08 13:00 | 311 | 311
2019-02-08 13:30 | 321 | 321
2019-02-08 14:00 | 319 | 319
2019-02-08 14:30 | 330 | 330
2019-02-08 15:00 | 332 | 332
2019-02-08 15:30 | 343 | 343
2019-02-08 16:00 | 356 | 356
2019-02-08 16:30 | 352 | 352
2019-02-08 17:00 | 343 | 343
2019-02-08 17:30 | 331 | 330
2019-02-08 18:00 | 320 | 319
2019-02-08 18:30 | 322 | 322
2019-02-08 19:00 | 321 | 321
2019-02-08 19:30 | 322 | 321
2019-02-08 20:00 | 306 | 306
2019-02-08 20:30 | 303 | 301
2019-02-08 21:00 | 298 | 296
2019-02-08 21:30 | 287 | 285
2019-02-08 22:00 | 279 | 279
2019-02-08 22:30 | 275 | 275
2019-02-08 23:00 | 256 | 255
2019-02-08 23:30 | 235 | 234
2019-02-09 | 212 | 212
2019-02-09 00:30 | 205 | 205
2019-02-09 01:00 | 193 | 193
2019-02-09 01:30 | 187 | 187
2019-02-09 02:00 | 183 | 183
2019-02-09 02:30 | 179 | 179
2019-02-09 03:00 | 177 | 177
2019-02-09 03:30 | 176 | 176
2019-02-09 04:00 | 172 | 172
2019-02-09 04:30 | 174 | 174
2019-02-09 05:00 | 178 | 178
2019-02-09 05:30 | 184 | 184
2019-02-09 06:00 | 187 | 187
2019-02-09 06:30 | 193 | 193
2019-02-09 07:00 | 208 | 208
2019-02-09 07:30 | 222 | 222
2019-02-09 08:00 | 241 | 241
2019-02-09 08:30 | 245 | 244
2019-02-09 09:00 | 247 | 247
2019-02-09 09:30 | 255 | 255
2019-02-09 10:00 | 251 | 251
2019-02-09 10:30 | 253 | 253
2019-02-09 11:00 | 257 | 257
2019-02-09 11:30 | 257 | 257
2019-02-09 12:00 | 259 | 259
2019-02-09 12:30 | 258 | 258
2019-02-09 13:00 | 266 | 265
2019-02-09 13:30 | 270 | 270
2019-02-09 14:00 | 275 | 275
2019-02-09 14:30 | 288 | 288
2019-02-09 15:00 | 294 | 294
2019-02-09 15:30 | 300 | 300
2019-02-09 16:00 | 312 | 312
2019-02-09 16:30 | 330 | 330
2019-02-09 17:00 | 339 | 339
2019-02-09 17:30 | 345 | 345
2019-02-09 18:00 | 361 | 361
2019-02-09 18:30 | 362 | 362
2019-02-09 19:00 | 361 | 361
2019-02-09 19:30 | 355 | 355
2019-02-09 20:00 | 342 | 342
2019-02-09 20:30 | 328 | 328
2019-02-09 21:00 | 320 | 319
2019-02-09 21:30 | 306 | 304
2019-02-09 22:00 | 301 | 297
2019-02-09 22:30 | 294 | 291
2019-02-09 23:00 | 238 | 237
2019-02-09 23:30 | 222 | 220
2019-02-10 | 204 | 203
2019-02-10 00:30 | 193 | 192
2019-02-10 01:00 | 188 | 186
2019-02-10 01:30 | 187 | 185
2019-02-10 02:00 | 187 | 184
2019-02-10 02:30 | 184 | 181
2019-02-10 03:00 | 180 | 177
2019-02-10 03:30 | 179 | 176
2019-02-10 04:00 | 178 | 175
2019-02-10 04:30 | 172 | 169
2019-02-10 05:00 | 176 | 173
2019-02-10 05:30 | 179 | 176
2019-02-10 06:00 | 186 | 185
2019-02-10 06:30 | 196 | 196
2019-02-10 07:00 | 212 | 212
2019-02-10 07:30 | 220 | 220
2019-02-10 08:00 | 231 | 231
2019-02-10 08:30 | 190 | 190
2019-02-10 09:00 | 156 | 156
2019-02-10 09:30 | 161 | 161
2019-02-10 10:00 | 157 | 157
2019-02-10 10:30 | 154 | 154
2019-02-10 11:00 | 152 | 152
2019-02-10 11:30 | 150 | 150
2019-02-10 12:00 | 153 | 153
2019-02-10 12:30 | 154 | 154
2019-02-10 13:00 | 154 | 154
2019-02-10 13:30 | 159 | 159
2019-02-10 14:00 | 158 | 157
2019-02-10 14:30 | 164 | 163
2019-02-10 15:00 | 171 | 170
2019-02-10 15:30 | 181 | 181
2019-02-10 16:00 | 213 | 213
2019-02-10 16:30 | 299 | 299
2019-02-10 17:00 | 298 | 298
2019-02-10 17:30 | 300 | 300
2019-02-10 18:00 | 301 | 301
2019-02-10 18:30 | 307 | 307
2019-02-10 19:00 | 303 | 303
2019-02-10 19:30 | 300 | 300
2019-02-10 20:00 | 287 | 287
2019-02-10 20:30 | 278 | 277
2019-02-10 21:00 | 265 | 265
2019-02-10 21:30 | 256 | 256
2019-02-10 22:00 | 242 | 242
2019-02-10 22:30 | 233 | 233
2019-02-10 23:00 | 222 | 222
2019-02-10 23:30 | 208 | 208
2019-02-11 | 198 | 198
2019-02-11 00:30 | 195 | 195
2019-02-11 01:00 | 194 | 194
2019-02-11 01:30 | 194 | 194
2019-02-11 02:00 | 192 | 192
2019-02-11 02:30 | 189 | 189
2019-02-11 03:00 | 192 | 192
2019-02-11 03:30 | 190 | 190
2019-02-11 04:00 | 190 | 190
2019-02-11 04:30 | 189 | 189
2019-02-11 05:00 | 195 | 195
2019-02-11 05:30 | 209 | 209
2019-02-11 06:00 | 222 | 222
2019-02-11 06:30 | 237 | 236
2019-02-11 07:00 | 264 | 264
2019-02-11 07:30 | 268 | 268
2019-02-11 08:00 | 271 | 271
2019-02-11 08:30 | 274 | 274
2019-02-11 09:00 | 280 | 280
2019-02-11 09:30 | 277 | 277
2019-02-11 10:00 | 268 | 268
2019-02-11 10:30 | 267 | 267
2019-02-11 11:00 | 266 | 266
2019-02-11 11:30 | 267 | 267
2019-02-11 12:00 | 266 | 266
2019-02-11 12:30 | 272 | 272
2019-02-11 13:00 | 283 | 283
2019-02-11 13:30 | 290 | 290
2019-02-11 14:00 | 299 | 299
2019-02-11 14:30 | 304 | 304
2019-02-11 15:00 | 315 | 315
2019-02-11 15:30 | 326 | 326
2019-02-11 16:00 | 335 | 335
2019-02-11 16:30 | 342 | 342
2019-02-11 17:00 | 344 | 343
2019-02-11 17:30 | 341 | 340
2019-02-11 18:00 | 341 | 340
2019-02-11 18:30 | 329 | 329
2019-02-11 19:00 | 333 | 332
2019-02-11 19:30 | 329 | 327
2019-02-11 20:00 | 315 | 315
2019-02-11 20:30 | 300 | 300
2019-02-11 21:00 | 286 | 286
2019-02-11 21:30 | 266 | 266
2019-02-11 22:00 | 246 | 246
2019-02-11 22:30 | 230 | 230
2019-02-11 23:00 | 213 | 213
2019-02-11 23:30 | 204 | 204
2019-02-12 | 189 | 189
2019-02-12 00:30 | 183 | 183
2019-02-12 01:00 | 179 | 179
2019-02-12 01:30 | 162 | 162
2019-02-12 02:00 | 175 | 175
2019-02-12 02:30 | 175 | 175
2019-02-12 03:00 | 169 | 168
2019-02-12 03:30 | 175 | 175
2019-02-12 04:00 | 181 | 181
2019-02-12 04:30 | 184 | 184
2019-02-12 05:00 | 195 | 195
2019-02-12 05:30 | 203 | 203
2019-02-12 06:00 | 226 | 225
2019-02-12 06:30 | 245 | 243
2019-02-12 07:00 | 263 | 263
2019-02-12 07:30 | 275 | 274
2019-02-12 08:00 | 279 | 279
2019-02-12 08:30 | 240 | 240
2019-02-12 09:00 | 192 | 191
2019-02-12 09:30 | 193 | 192
2019-02-12 10:00 | 195 | 194
2019-02-12 10:30 | 199 | 198
2019-02-12 11:00 | 203 | 201
2019-02-12 11:30 | 207 | 205
2019-02-12 12:00 | 214 | 212
2019-02-12 12:30 | 220 | 218
2019-02-12 13:00 | 231 | 229
2019-02-12 13:30 | 242 | 240
2019-02-12 14:00 | 354 | 353
2019-02-12 14:30 | 410 | 409
2019-02-12 15:00 | 425 | 425
2019-02-12 15:30 | 445 | 445
2019-02-12 16:00 | 449 | 449
2019-02-12 16:30 | 441 | 441
2019-02-12 17:00 | 437 | 436
2019-02-12 17:30 | 439 | 439
2019-02-12 18:00 | 412 | 412
2019-02-12 18:30 | 408 | 408
2019-02-12 19:00 | 408 | 408
2019-02-12 19:30 | 394 | 394
2019-02-12 20:00 | 380 | 380
2019-02-12 20:30 | 368 | 367
2019-02-12 21:00 | 344 | 342
2019-02-12 21:30 | 321 | 320
2019-02-12 22:00 | 295 | 294
2019-02-12 22:30 | 281 | 281
2019-02-12 23:00 | 264 | 263
2019-02-12 23:30 | 249 | 248
2019-02-13 | 230 | 229
2019-02-13 00:30 | 224 | 224
2019-02-13 01:00 | 219 | 219
2019-02-13 01:30 | 212 | 212
2019-02-13 02:00 | 206 | 206
2019-02-13 02:30 | 201 | 201
2019-02-13 03:00 | 198 | 198
2019-02-13 03:30 | 192 | 192
2019-02-13 04:00 | 191 | 191
2019-02-13 04:30 | 195 | 195
2019-02-13 05:00 | 207 | 207
2019-02-13 05:30 | 226 | 226
2019-02-13 06:00 | 250 | 250
2019-02-13 06:30 | 265 | 265
2019-02-13 07:00 | 290 | 290
2019-02-13 07:30 | 311 | 311
2019-02-13 08:00 | 345 | 345
2019-02-13 08:30 | 354 | 354
2019-02-13 09:00 | 355 | 355
2019-02-13 09:30 | 356 | 356
2019-02-13 10:00 | 361 | 361
2019-02-13 10:30 | 370 | 370
2019-02-13 11:00 | 378 | 378
2019-02-13 11:30 | 390 | 390
2019-02-13 12:00 | 396 | 396
2019-02-13 12:30 | 406 | 406
2019-02-13 13:00 | 418 | 418
2019-02-13 13:30 | 423 | 423
2019-02-13 14:00 | 428 | 428
2019-02-13 14:30 | 438 | 438
2019-02-13 15:00 | 451 | 451
2019-02-13 15:30 | 456 | 456
2019-02-13 16:00 | 445 | 445
2019-02-13 16:30 | 456 | 456
2019-02-13 17:00 | 456 | 456
2019-02-13 17:30 | 452 | 452
2019-02-13 18:00 | 440 | 440
2019-02-13 18:30 | 435 | 435
2019-02-13 19:00 | 427 | 427
2019-02-13 19:30 | 414 | 414
2019-02-13 20:00 | 407 | 407
2019-02-13 20:30 | 390 | 390
2019-02-13 21:00 | 363 | 363
2019-02-13 21:30 | 346 | 346
2019-02-13 22:00 | 310 | 310
2019-02-13 22:30 | 297 | 297
2019-02-13 23:00 | 274 | 273
2019-02-13 23:30 | 249 | 249
2019-02-14 | 234 | 234
2019-02-14 00:30 | 225 | 225
2019-02-14 01:00 | 213 | 213
2019-02-14 01:30 | 207 | 207
2019-02-14 02:00 | 202 | 202
2019-02-14 02:30 | 199 | 199
2019-02-14 03:00 | 198 | 198
2019-02-14 03:30 | 199 | 198
2019-02-14 04:00 | 201 | 201
2019-02-14 04:30 | 202 | 202
2019-02-14 05:00 | 212 | 212
2019-02-14 05:30 | 223 | 223
2019-02-14 06:00 | 262 | 262
2019-02-14 06:30 | 285 | 285
2019-02-14 07:00 | 281 | 281
2019-02-14 07:30 | 302 | 302
2019-02-14 08:00 | 324 | 324
2019-02-14 08:30 | 333 | 333
2019-02-14 09:00 | 328 | 328
2019-02-14 09:30 | 328 | 328
2019-02-14 10:00 | 331 | 331
2019-02-14 10:30 | 326 | 326
2019-02-14 11:00 | 317 | 317
2019-02-14 11:30 | 326 | 326
2019-02-14 12:00 | 309 | 309
2019-02-14 12:30 | 311 | 311
2019-02-14 13:00 | 322 | 322
2019-02-14 13:30 | 320 | 320
2019-02-14 14:00 | 322 | 322
2019-02-14 14:30 | 313 | 313
2019-02-14 15:00 | 318 | 318
2019-02-14 15:30 | 322 | 322
2019-02-14 16:00 | 326 | 325
2019-02-14 16:30 | 329 | 328
2019-02-14 17:00 | 327 | 326
2019-02-14 17:30 | 327 | 326
2019-02-14 18:00 | 320 | 319
2019-02-14 18:30 | 325 | 325
2019-02-14 19:00 | 322 | 322
2019-02-14 19:30 | 316 | 315
2019-02-14 20:00 | 300 | 299
2019-02-14 20:30 | 285 | 285
2019-02-14 21:00 | 273 | 273
2019-02-14 21:30 | 261 | 261
2019-02-14 22:00 | 247 | 247
2019-02-14 22:30 | 238 | 237
2019-02-14 23:00 | 219 | 219
2019-02-14 23:30 | 205 | 204
2019-02-15 | 197 | 195
2019-02-15 00:30 | 192 | 190
2019-02-15 01:00 | 191 | 189
2019-02-15 01:30 | 186 | 184
2019-02-15 02:00 | 184 | 182
2019-02-15 02:30 | 180 | 179
2019-02-15 03:00 | 184 | 183
2019-02-15 03:30 | 185 | 183
2019-02-15 04:00 | 189 | 187
2019-02-15 04:30 | 191 | 190
2019-02-15 05:00 | 201 | 199
2019-02-15 05:30 | 208 | 207
2019-02-15 06:00 | 222 | 222
2019-02-15 06:30 | 233 | 233
2019-02-15 07:00 | 254 | 253
2019-02-15 07:30 | 260 | 259
2019-02-15 08:00 | 264 | 264
2019-02-15 08:30 | 266 | 266
2019-02-15 09:00 | 266 | 266
2019-02-15 09:30 | 270 | 270
2019-02-15 10:00 | 272 | 272
2019-02-15 10:30 | 273 | 273
2019-02-15 11:00 | 280 | 278
2019-02-15 11:30 | 289 | 288
2019-02-15 12:00 | 287 | 285
2019-02-15 12:30 | 261 | 260
2019-02-15 13:00 | 265 | 265
2019-02-15 13:30 | 273 | 273
2019-02-15 14:00 | 277 | 277
2019-02-15 14:30 | 279 | 279
2019-02-15 15:00 | 288 | 287
2019-02-15 15:30 | 301 | 300
2019-02-15 16:00 | 313 | 312
2019-02-15 16:30 | 316 | 315
2019-02-15 17:00 | 307 | 305
2019-02-15 17:30 | 304 | 301
2019-02-15 18:00 | 298 | 294
2019-02-15 18:30 | 298 | 295
2019-02-15 19:00 | 294 | 292
2019-02-15 19:30 | 287 | 284
2019-02-15 20:00 | 268 | 267
2019-02-15 20:30 | 260 | 259
2019-02-15 21:00 | 251 | 249
2019-02-15 21:30 | 242 | 242
2019-02-15 22:00 | 237 | 237
2019-02-15 22:30 | 229 | 229
2019-02-15 23:00 | 210 | 210
2019-02-15 23:30 | 198 | 198
2019-02-16 | 188 | 187
2019-02-16 00:30 | 183 | 181
2019-02-16 01:00 | 178 | 176
2019-02-16 01:30 | 175 | 173
2019-02-16 02:00 | 173 | 171
2019-02-16 02:30 | 174 | 172
2019-02-16 03:00 | 170 | 168
2019-02-16 03:30 | 168 | 165
2019-02-16 04:00 | 171 | 168
2019-02-16 04:30 | 169 | 167
2019-02-16 05:00 | 172 | 169
2019-02-16 05:30 | 178 | 175
2019-02-16 06:00 | 186 | 184
2019-02-16 06:30 | 195 | 194
2019-02-16 07:00 | 208 | 207
2019-02-16 07:30 | 217 | 217
2019-02-16 08:00 | 222 | 222
2019-02-16 08:30 | 220 | 220
2019-02-16 09:00 | 224 | 224
2019-02-16 09:30 | 235 | 235
2019-02-16 10:00 | 251 | 251
2019-02-16 10:30 | 251 | 251
2019-02-16 11:00 | 255 | 255
2019-02-16 11:30 | 259 | 259
2019-02-16 12:00 | 255 | 255
2019-02-16 12:30 | 248 | 248
2019-02-16 13:00 | 257 | 257
2019-02-16 13:30 | 260 | 259
2019-02-16 14:00 | 260 | 259
2019-02-16 14:30 | 270 | 269
2019-02-16 15:00 | 260 | 260
2019-02-16 15:30 | 264 | 263
2019-02-16 16:00 | 277 | 277
2019-02-16 16:30 | 284 | 284
2019-02-16 17:00 | 284 | 284
2019-02-16 17:30 | 278 | 278
2019-02-16 18:00 | 278 | 278
2019-02-16 18:30 | 283 | 283
2019-02-16 19:00 | 279 | 279
2019-02-16 19:30 | 275 | 275
2019-02-16 20:00 | 270 | 269
2019-02-16 20:30 | 258 | 257
2019-02-16 21:00 | 241 | 241
2019-02-16 21:30 | 227 | 227
2019-02-16 22:00 | 228 | 228
2019-02-16 22:30 | 224 | 223
2019-02-16 23:00 | 207 | 206
2019-02-16 23:30 | 195 | 194
2019-02-17 | 183 | 181
2019-02-17 00:30 | 180 | 179
2019-02-17 01:00 | 179 | 178
2019-02-17 01:30 | 178 | 177
2019-02-17 02:00 | 175 | 175
2019-02-17 02:30 | 176 | 175
2019-02-17 03:00 | 173 | 173
2019-02-17 03:30 | 169 | 168
2019-02-17 04:00 | 161 | 160
2019-02-17 04:30 | 160 | 159
2019-02-17 05:00 | 168 | 167
2019-02-17 05:30 | 171 | 170
2019-02-17 06:00 | 176 | 175
2019-02-17 06:30 | 182 | 181
2019-02-17 07:00 | 191 | 191
2019-02-17 07:30 | 198 | 198
2019-02-17 08:00 | 205 | 205
2019-02-17 08:30 | 211 | 211
2019-02-17 09:00 | 220 | 219
2019-02-17 09:30 | 226 | 226
2019-02-17 10:00 | 230 | 230
2019-02-17 10:30 | 231 | 231
2019-02-17 11:00 | 231 | 231
2019-02-17 11:30 | 233 | 233
2019-02-17 12:00 | 229 | 228
2019-02-17 12:30 | 230 | 230
2019-02-17 13:00 | 232 | 232
2019-02-17 13:30 | 239 | 239
2019-02-17 14:00 | 244 | 244
2019-02-17 14:30 | 253 | 253
2019-02-17 15:00 | 268 | 268
2019-02-17 15:30 | 280 | 280
2019-02-17 16:00 | 297 | 297
2019-02-17 16:30 | 310 | 310
2019-02-17 17:00 | 311 | 311
2019-02-17 17:30 | 307 | 307
2019-02-17 18:00 | 303 | 303
2019-02-17 18:30 | 304 | 304
2019-02-17 19:00 | 302 | 302
2019-02-17 19:30 | 297 | 297
2019-02-17 20:00 | 282 | 281
2019-02-17 20:30 | 261 | 261
2019-02-17 21:00 | 249 | 249
2019-02-17 21:30 | 236 | 236
2019-02-17 22:00 | 226 | 226
2019-02-17 22:30 | 219 | 219
2019-02-17 23:00 | 204 | 204
2019-02-17 23:30 | 188 | 187
2019-02-18 | 178 | 177
2019-02-18 00:30 | 177 | 176
2019-02-18 01:00 | 176 | 174
2019-02-18 01:30 | 173 | 172
2019-02-18 02:00 | 176 | 174
2019-02-18 02:30 | 171 | 170
2019-02-18 03:00 | 170 | 169
2019-02-18 03:30 | 170 | 169
2019-02-18 04:00 | 173 | 173
2019-02-18 04:30 | 175 | 174
2019-02-18 05:00 | 186 | 186
2019-02-18 05:30 | 196 | 196
2019-02-18 06:00 | 209 | 209
2019-02-18 06:30 | 223 | 222
2019-02-18 07:00 | 246 | 246
2019-02-18 07:30 | 249 | 248
2019-02-18 08:00 | 255 | 254
2019-02-18 08:30 | 267 | 267
2019-02-18 09:00 | 274 | 273
2019-02-18 09:30 | 277 | 277
2019-02-18 10:00 | 276 | 276
2019-02-18 10:30 | 269 | 269
2019-02-18 11:00 | 261 | 261
2019-02-18 11:30 | 257 | 257
2019-02-18 12:00 | 259 | 258
2019-02-18 12:30 | 262 | 261
2019-02-18 13:00 | 281 | 281
2019-02-18 13:30 | 289 | 289
2019-02-18 14:00 | 296 | 296
2019-02-18 14:30 | 305 | 305
2019-02-18 15:00 | 320 | 320
2019-02-18 15:30 | 332 | 332
2019-02-18 16:00 | 344 | 343
2019-02-18 16:30 | 349 | 348
2019-02-18 17:00 | 352 | 351
2019-02-18 17:30 | 346 | 345
2019-02-18 18:00 | 334 | 332
2019-02-18 18:30 | 333 | 332
2019-02-18 19:00 | 325 | 324
2019-02-18 19:30 | 313 | 313
2019-02-18 20:00 | 299 | 299
2019-02-18 20:30 | 278 | 278
2019-02-18 21:00 | 264 | 264
2019-02-18 21:30 | 248 | 248
2019-02-18 22:00 | 234 | 234
2019-02-18 22:30 | 223 | 223
2019-02-18 23:00 | 208 | 208
2019-02-18 23:30 | 193 | 192
2019-02-19 | 183 | 182
2019-02-19 00:30 | 179 | 177
2019-02-19 01:00 | 177 | 175
2019-02-19 01:30 | 176 | 174
2019-02-19 02:00 | 172 | 171
2019-02-19 02:30 | 169 | 168
2019-02-19 03:00 | 165 | 164
2019-02-19 03:30 | 168 | 167
2019-02-19 04:00 | 171 | 171
2019-02-19 04:30 | 174 | 174
2019-02-19 05:00 | 187 | 187
2019-02-19 05:30 | 195 | 195
2019-02-19 06:00 | 212 | 212
2019-02-19 06:30 | 227 | 227
2019-02-19 07:00 | 244 | 244
2019-02-19 07:30 | 248 | 248
2019-02-19 08:00 | 252 | 252
2019-02-19 08:30 | 253 | 253
2019-02-19 09:00 | 258 | 258
2019-02-19 09:30 | 259 | 259
2019-02-19 10:00 | 263 | 263
2019-02-19 10:30 | 270 | 269
2019-02-19 11:00 | 271 | 270
2019-02-19 11:30 | 276 | 275
2019-02-19 12:00 | 281 | 281
2019-02-19 12:30 | 287 | 286
2019-02-19 13:00 | 294 | 294
2019-02-19 13:30 | 303 | 303
2019-02-19 14:00 | 314 | 313
2019-02-19 14:30 | 322 | 322
2019-02-19 15:00 | 333 | 333
2019-02-19 15:30 | 352 | 352
2019-02-19 16:00 | 366 | 366
2019-02-19 16:30 | 366 | 366
2019-02-19 17:00 | 360 | 359
2019-02-19 17:30 | 357 | 356
2019-02-19 18:00 | 354 | 352
2019-02-19 18:30 | 354 | 353
2019-02-19 19:00 | 352 | 351
2019-02-19 19:30 | 348 | 346
2019-02-19 20:00 | 335 | 332
2019-02-19 20:30 | 314 | 312
2019-02-19 21:00 | 297 | 296
2019-02-19 21:30 | 280 | 278
2019-02-19 22:00 | 262 | 262
2019-02-19 22:30 | 257 | 257
2019-02-19 23:00 | 236 | 235
2019-02-19 23:30 | 217 | 216
2019-02-20 | 202 | 200
2019-02-20 00:30 | 194 | 191
2019-02-20 01:00 | 185 | 183
2019-02-20 01:30 | 180 | 179
2019-02-20 02:00 | 179 | 178
2019-02-20 02:30 | 179 | 178
2019-02-20 03:00 | 179 | 177
2019-02-20 03:30 | 177 | 176
2019-02-20 04:00 | 181 | 180
2019-02-20 04:30 | 183 | 182
2019-02-20 05:00 | 195 | 194
2019-02-20 05:30 | 209 | 209
2019-02-20 06:00 | 237 | 237
2019-02-20 06:30 | 260 | 260
2019-02-20 07:00 | 300 | 300
2019-02-20 07:30 | 311 | 310
2019-02-20 08:00 | 318 | 317
2019-02-20 08:30 | 328 | 328
2019-02-20 09:00 | 332 | 332
2019-02-20 09:30 | 331 | 331
2019-02-20 10:00 | 332 | 332
2019-02-20 10:30 | 333 | 333
2019-02-20 11:00 | 336 | 334
2019-02-20 11:30 | 337 | 335
2019-02-20 12:00 | 336 | 335
2019-02-20 12:30 | 332 | 331
2019-02-20 13:00 | 333 | 331
2019-02-20 13:30 | 330 | 329
2019-02-20 14:00 | 334 | 332
2019-02-20 14:30 | 342 | 341
2019-02-20 15:00 | 357 | 356
2019-02-20 15:30 | 370 | 369
2019-02-20 16:00 | 374 | 373
2019-02-20 16:30 | 368 | 367
2019-02-20 17:00 | 367 | 365
2019-02-20 17:30 | 364 | 362
2019-02-20 18:00 | 358 | 357
2019-02-20 18:30 | 361 | 361
2019-02-20 19:00 | 359 | 358
2019-02-20 19:30 | 348 | 347
2019-02-20 20:00 | 340 | 338
2019-02-20 20:30 | 321 | 321
2019-02-20 21:00 | 306 | 304
2019-02-20 21:30 | 284 | 282
2019-02-20 22:00 | 267 | 266
2019-02-20 22:30 | 256 | 256
2019-02-20 23:00 | 235 | 234
2019-02-20 23:30 | 216 | 215
2019-02-21 | 205 | 204
2019-02-21 00:30 | 202 | 202
2019-02-21 01:00 | 199 | 199
2019-02-21 01:30 | 197 | 196
2019-02-21 02:00 | 196 | 196
2019-02-21 02:30 | 194 | 193
2019-02-21 03:00 | 194 | 193
2019-02-21 03:30 | 194 | 193
2019-02-21 04:00 | 195 | 195
2019-02-21 04:30 | 198 | 197
2019-02-21 05:00 | 208 | 207
2019-02-21 05:30 | 215 | 215
2019-02-21 06:00 | 236 | 236
2019-02-21 06:30 | 253 | 253
2019-02-21 07:00 | 297 | 297
2019-02-21 07:30 | 306 | 306
2019-02-21 08:00 | 315 | 314
2019-02-21 08:30 | 328 | 328
2019-02-21 09:00 | 340 | 340
2019-02-21 09:30 | 344 | 344
2019-02-21 10:00 | 338 | 337
2019-02-21 10:30 | 336 | 336
2019-02-21 11:00 | 334 | 334
2019-02-21 11:30 | 344 | 343
2019-02-21 12:00 | 337 | 336
2019-02-21 12:30 | 346 | 346
2019-02-21 13:00 | 348 | 347
2019-02-21 13:30 | 344 | 343
2019-02-21 14:00 | 339 | 339
2019-02-21 14:30 | 345 | 345
2019-02-21 15:00 | 352 | 352
2019-02-21 15:30 | 369 | 369
2019-02-21 16:00 | 377 | 377
2019-02-21 16:30 | 382 | 381
2019-02-21 17:00 | 365 | 364
2019-02-21 17:30 | 357 | 356
2019-02-21 18:00 | 347 | 345
2019-02-21 18:30 | 354 | 353
2019-02-21 19:00 | 344 | 343
2019-02-21 19:30 | 337 | 336
2019-02-21 20:00 | 318 | 318
2019-02-21 20:30 | 308 | 307
2019-02-21 21:00 | 290 | 289
2019-02-21 21:30 | 268 | 267
2019-02-21 22:00 | 258 | 256
2019-02-21 22:30 | 250 | 248
2019-02-21 23:00 | 225 | 225
2019-02-21 23:30 | 210 | 210
2019-02-22 | 202 | 202
2019-02-22 00:30 | 197 | 196
2019-02-22 01:00 | 184 | 183
2019-02-22 01:30 | 174 | 173
2019-02-22 02:00 | 174 | 173
2019-02-22 02:30 | 174 | 173
2019-02-22 03:00 | 172 | 171
2019-02-22 03:30 | 171 | 170
2019-02-22 04:00 | 169 | 168
2019-02-22 04:30 | 173 | 172
2019-02-22 05:00 | 192 | 192
2019-02-22 05:30 | 201 | 200
2019-02-22 06:00 | 222 | 221
2019-02-22 06:30 | 237 | 237
2019-02-22 07:00 | 255 | 255
2019-02-22 07:30 | 264 | 264
2019-02-22 08:00 | 263 | 263
2019-02-22 08:30 | 271 | 271
2019-02-22 09:00 | 268 | 268
2019-02-22 09:30 | 271 | 271
2019-02-22 10:00 | 260 | 260
2019-02-22 10:30 | 243 | 243
2019-02-22 11:00 | 248 | 248
2019-02-22 11:30 | 268 | 268
2019-02-22 12:00 | 257 | 257
2019-02-22 12:30 | 258 | 257
2019-02-22 13:00 | 243 | 243
2019-02-22 13:30 | 242 | 241
2019-02-22 14:00 | 246 | 246
2019-02-22 14:30 | 253 | 252
2019-02-22 15:00 | 267 | 267
2019-02-22 15:30 | 269 | 269
2019-02-22 16:00 | 272 | 272
2019-02-22 16:30 | 289 | 288
2019-02-22 17:00 | 285 | 285
2019-02-22 17:30 | 276 | 275
2019-02-22 18:00 | 270 | 267
2019-02-22 18:30 | 275 | 273
2019-02-22 19:00 | 271 | 269
2019-02-22 19:30 | 269 | 267
2019-02-22 20:00 | 263 | 263
2019-02-22 20:30 | 254 | 254
2019-02-22 21:00 | 247 | 247
2019-02-22 21:30 | 239 | 239
2019-02-22 22:00 | 231 | 231
2019-02-22 22:30 | 224 | 224
2019-02-22 23:00 | 210 | 210
2019-02-22 23:30 | 198 | 197
2019-02-23 | 186 | 185
2019-02-23 00:30 | 180 | 179
2019-02-23 01:00 | 172 | 172
2019-02-23 01:30 | 169 | 168
2019-02-23 02:00 | 166 | 166
2019-02-23 02:30 | 166 | 165
2019-02-23 03:00 | 166 | 165
2019-02-23 03:30 | 164 | 163
2019-02-23 04:00 | 163 | 162
2019-02-23 04:30 | 163 | 162
2019-02-23 05:00 | 176 | 175
2019-02-23 05:30 | 179 | 178
2019-02-23 06:00 | 191 | 191
2019-02-23 06:30 | 203 | 203
2019-02-23 07:00 | 211 | 211
2019-02-23 07:30 | 212 | 212
2019-02-23 08:00 | 213 | 212
2019-02-23 08:30 | 218 | 217
2019-02-23 09:00 | 230 | 230
2019-02-23 09:30 | 225 | 224
2019-02-23 10:00 | 219 | 219
2019-02-23 10:30 | 220 | 219
2019-02-23 11:00 | 218 | 217
2019-02-23 11:30 | 217 | 216
2019-02-23 12:00 | 222 | 221
2019-02-23 12:30 | 222 | 221
2019-02-23 13:00 | 215 | 215
2019-02-23 13:30 | 218 | 217
2019-02-23 14:00 | 223 | 223
2019-02-23 14:30 | 233 | 233
2019-02-23 15:00 | 220 | 219
2019-02-23 15:30 | 230 | 229
2019-02-23 16:00 | 241 | 240
2019-02-23 16:30 | 258 | 257
2019-02-23 17:00 | 260 | 259
2019-02-23 17:30 | 264 | 264
2019-02-23 18:00 | 259 | 258
2019-02-23 18:30 | 264 | 264
2019-02-23 19:00 | 263 | 263
2019-02-23 19:30 | 257 | 256
2019-02-23 20:00 | 247 | 247
2019-02-23 20:30 | 238 | 238
2019-02-23 21:00 | 227 | 227
2019-02-23 21:30 | 222 | 222
2019-02-23 22:00 | 217 | 216
2019-02-23 22:30 | 216 | 216
2019-02-23 23:00 | 204 | 203
2019-02-23 23:30 | 193 | 192
2019-02-24 | 184 | 184
2019-02-24 00:30 | 181 | 180
2019-02-24 01:00 | 176 | 176
2019-02-24 01:30 | 167 | 166
2019-02-24 02:00 | 163 | 162
2019-02-24 02:30 | 163 | 162
2019-02-24 03:00 | 163 | 162
2019-02-24 03:30 | 162 | 161
2019-02-24 04:00 | 164 | 163
2019-02-24 04:30 | 163 | 162
2019-02-24 05:00 | 166 | 165
2019-02-24 05:30 | 171 | 170
2019-02-24 06:00 | 178 | 177
2019-02-24 06:30 | 183 | 182
2019-02-24 07:00 | 194 | 194
2019-02-24 07:30 | 203 | 203
2019-02-24 08:00 | 205 | 205
2019-02-24 08:30 | 207 | 207
2019-02-24 09:00 | 216 | 216
2019-02-24 09:30 | 208 | 208
2019-02-24 10:00 | 210 | 210
2019-02-24 10:30 | 221 | 221
2019-02-24 11:00 | 226 | 226
2019-02-24 11:30 | 221 | 221
2019-02-24 12:00 | 212 | 212
2019-02-24 12:30 | 221 | 221
2019-02-24 13:00 | 224 | 224
2019-02-24 13:30 | 226 | 226
2019-02-24 14:00 | 227 | 227
2019-02-24 14:30 | 224 | 224
2019-02-24 15:00 | 223 | 223
2019-02-24 15:30 | 231 | 231
2019-02-24 16:00 | 244 | 244
2019-02-24 16:30 | 252 | 252
2019-02-24 17:00 | 257 | 255
2019-02-24 17:30 | 262 | 260
2019-02-24 18:00 | 270 | 269
2019-02-24 18:30 | 275 | 274
2019-02-24 19:00 | 273 | 272
2019-02-24 19:30 | 267 | 266
2019-02-24 20:00 | 255 | 253
2019-02-24 20:30 | 238 | 238
2019-02-24 21:00 | 231 | 231
2019-02-24 21:30 | 221 | 221
2019-02-24 22:00 | 220 | 219
2019-02-24 22:30 | 218 | 217
2019-02-24 23:00 | 206 | 205
2019-02-24 23:30 | 199 | 197
2019-02-25 | 186 | 185
2019-02-25 00:30 | 183 | 182
2019-02-25 01:00 | 181 | 180
2019-02-25 01:30 | 177 | 176
2019-02-25 02:00 | 176 | 175
2019-02-25 02:30 | 174 | 173
2019-02-25 03:00 | 176 | 175
2019-02-25 03:30 | 176 | 175
2019-02-25 04:00 | 176 | 175
2019-02-25 04:30 | 179 | 178
2019-02-25 05:00 | 187 | 187
2019-02-25 05:30 | 202 | 201
2019-02-25 06:00 | 216 | 216
2019-02-25 06:30 | 229 | 228
2019-02-25 07:00 | 252 | 252
2019-02-25 07:30 | 265 | 264
2019-02-25 08:00 | 269 | 269
2019-02-25 08:30 | 269 | 269
2019-02-25 09:00 | 267 | 267
2019-02-25 09:30 | 262 | 262
2019-02-25 10:00 | 263 | 263
2019-02-25 10:30 | 263 | 262
2019-02-25 11:00 | 262 | 262
2019-02-25 11:30 | 251 | 251
2019-02-25 12:00 | 270 | 270
2019-02-25 12:30 | 261 | 261
2019-02-25 13:00 | 269 | 269
2019-02-25 13:30 | 263 | 263
2019-02-25 14:00 | 272 | 272
2019-02-25 14:30 | 267 | 267
2019-02-25 15:00 | 264 | 264
2019-02-25 15:30 | 259 | 259
2019-02-25 16:00 | 283 | 283
2019-02-25 16:30 | 284 | 284
2019-02-25 17:00 | 281 | 280
2019-02-25 17:30 | 280 | 279
2019-02-25 18:00 | 285 | 284
2019-02-25 18:30 | 291 | 290
2019-02-25 19:00 | 275 | 274
2019-02-25 19:30 | 276 | 275
2019-02-25 20:00 | 266 | 266
2019-02-25 20:30 | 251 | 251
2019-02-25 21:00 | 243 | 242
2019-02-25 21:30 | 233 | 233
2019-02-25 22:00 | 231 | 230
2019-02-25 22:30 | 226 | 225
2019-02-25 23:00 | 213 | 212
2019-02-25 23:30 | 200 | 198
2019-02-26 | 188 | 188
2019-02-26 00:30 | 183 | 182
2019-02-26 01:00 | 178 | 177
2019-02-26 01:30 | 173 | 172
2019-02-26 02:00 | 174 | 172
2019-02-26 02:30 | 172 | 171
2019-02-26 03:00 | 172 | 170
2019-02-26 03:30 | 165 | 164
2019-02-26 04:00 | 171 | 170
2019-02-26 04:30 | 173 | 172
2019-02-26 05:00 | 187 | 187
2019-02-26 05:30 | 199 | 199
2019-02-26 06:00 | 217 | 217
2019-02-26 06:30 | 233 | 233
2019-02-26 07:00 | 251 | 251
2019-02-26 07:30 | 252 | 252
2019-02-26 08:00 | 257 | 257
2019-02-26 08:30 | 259 | 259
2019-02-26 09:00 | 242 | 242
2019-02-26 09:30 | 251 | 251
2019-02-26 10:00 | 250 | 250
2019-02-26 10:30 | 242 | 242
2019-02-26 11:00 | 236 | 236
2019-02-26 11:30 | 235 | 235
2019-02-26 12:00 | 239 | 239
2019-02-26 12:30 | 242 | 241
2019-02-26 13:00 | 248 | 248
2019-02-26 13:30 | 253 | 253
2019-02-26 14:00 | 258 | 257
2019-02-26 14:30 | 263 | 262
2019-02-26 15:00 | 270 | 269
2019-02-26 15:30 | 279 | 278
2019-02-26 16:00 | 284 | 283
2019-02-26 16:30 | 287 | 287
2019-02-26 17:00 | 288 | 288
2019-02-26 17:30 | 281 | 280
2019-02-26 18:00 | 276 | 275
2019-02-26 18:30 | 280 | 280
2019-02-26 19:00 | 278 | 278
2019-02-26 19:30 | 274 | 273
2019-02-26 20:00 | 263 | 263
2019-02-26 20:30 | 250 | 250
2019-02-26 21:00 | 239 | 239
2019-02-26 21:30 | 230 | 229
2019-02-26 22:00 | 222 | 221
2019-02-26 22:30 | 220 | 219
2019-02-26 23:00 | 207 | 206
2019-02-26 23:30 | 194 | 194
2019-02-27 | 174 | 173
2019-02-27 00:30 | 166 | 165
2019-02-27 01:00 | 162 | 161
2019-02-27 01:30 | 160 | 159
2019-02-27 02:00 | 158 | 156
2019-02-27 02:30 | 156 | 155
2019-02-27 03:00 | 159 | 157
2019-02-27 03:30 | 162 | 161
2019-02-27 04:00 | 167 | 166
2019-02-27 04:30 | 169 | 168
2019-02-27 05:00 | 186 | 185
2019-02-27 05:30 | 198 | 197
2019-02-27 06:00 | 211 | 211
2019-02-27 06:30 | 225 | 225
2019-02-27 07:00 | 242 | 241
2019-02-27 07:30 | 246 | 246
2019-02-27 08:00 | 252 | 252
2019-02-27 08:30 | 250 | 250
2019-02-27 09:00 | 250 | 250
2019-02-27 09:30 | 284 | 284
2019-02-27 10:00 | 298 | 298
2019-02-27 10:30 | 292 | 292
2019-02-27 11:00 | 278 | 278
2019-02-27 11:30 | 268 | 268
2019-02-27 12:00 | 251 | 251
2019-02-27 12:30 | 247 | 247
2019-02-27 13:00 | 251 | 250
2019-02-27 13:30 | 261 | 261
2019-02-27 14:00 | 273 | 272
2019-02-27 14:30 | 272 | 271
2019-02-27 15:00 | 270 | 270
2019-02-27 15:30 | 277 | 277
2019-02-27 16:00 | 274 | 273
2019-02-27 16:30 | 285 | 284
2019-02-27 17:00 | 287 | 286
2019-02-27 17:30 | 283 | 282
2019-02-27 18:00 | 276 | 275
2019-02-27 18:30 | 281 | 280
2019-02-27 19:00 | 277 | 275
2019-02-27 19:30 | 269 | 268
2019-02-27 20:00 | 262 | 261
2019-02-27 20:30 | 251 | 251
2019-02-27 21:00 | 247 | 246
2019-02-27 21:30 | 235 | 235
2019-02-27 22:00 | 227 | 226
2019-02-27 22:30 | 221 | 221
2019-02-27 23:00 | 209 | 208
2019-02-27 23:30 | 196 | 194
2019-02-28 | 185 | 182
2019-02-28 00:30 | 179 | 176
2019-02-28 01:00 | 176 | 172
2019-02-28 01:30 | 173 | 170
2019-02-28 02:00 | 172 | 168
2019-02-28 02:30 | 171 | 166
2019-02-28 03:00 | 169 | 165
2019-02-28 03:30 | 169 | 165
2019-02-28 04:00 | 175 | 172
2019-02-28 04:30 | 180 | 177
2019-02-28 05:00 | 196 | 194
2019-02-28 05:30 | 204 | 203
2019-02-28 06:00 | 228 | 227
2019-02-28 06:30 | 242 | 242
2019-02-28 07:00 | 259 | 258
2019-02-28 07:30 | 268 | 267
2019-02-28 08:00 | 272 | 271
2019-02-28 08:30 | 277 | 273
2019-02-28 09:00 | 283 | 280
2019-02-28 09:30 | 277 | 276
2019-02-28 10:00 | 263 | 262
2019-02-28 10:30 | 275 | 275
2019-02-28 11:00 | 255 | 255
2019-02-28 11:30 | 253 | 253
2019-02-28 12:00 | 254 | 253
2019-02-28 12:30 | 261 | 260
2019-02-28 13:00 | 263 | 263
2019-02-28 13:30 | 263 | 263
2019-02-28 14:00 | 271 | 271
2019-02-28 14:30 | 291 | 291
2019-02-28 15:00 | 277 | 276
2019-02-28 15:30 | 281 | 279
2019-02-28 16:00 | 286 | 284
2019-02-28 16:30 | 290 | 288
2019-02-28 17:00 | 292 | 290
2019-02-28 17:30 | 292 | 291
2019-02-28 18:00 | 293 | 292
2019-02-28 18:30 | 296 | 295
2019-02-28 19:00 | 291 | 290
2019-02-28 19:30 | 289 | 287
2019-02-28 20:00 | 276 | 276
2019-02-28 20:30 | 264 | 264
2019-02-28 21:00 | 254 | 253
2019-02-28 21:30 | 242 | 240
2019-02-28 22:00 | 239 | 237
2019-02-28 22:30 | 236 | 234
2019-02-28 23:00 | 228 | 227
2019-02-28 23:30 | 219 | 218
2019-03-01 | 227 | 226

## 24. Historic ratings
|  | 2016 Winter | 2016/17 Summer | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer
PQ Rating (MVA) |  | 851 | 851 | 851 | 851 | 851 | 851
Transformers | H031T01 | 417 | 417 | 417 | 417 | 417 | 417
| H031T02 | 434 | 434 | 434 | 434 | 434 | 434

## 26. Unplanned outages
Unplanned Outage Date/Time | Element Affected | Element Type | Outage Cause | Outage Duration (mins) | Customer Outage Duration (mins) | MW Lost (Instantaneous) | MW Minutes
42448.6502 | 8825 - S003 Greenbank to H031 Molendinar | FEEDER | Storm | 0.16667 | - | - | -
42448.6502 | H031 275KV 2 TRANSFORMER | TRANSFORMER | Storm | 0.16667 | - | - | -
43210.5972 | H031 110KV 3 CAPACITOR | CAPACITOR | HV Maint | 468019.0333 | - | - | -