## Cover Page
AER Rule | Field Name | Value(s)
1 | Constrained connection point ID | H035 Strathmore
2 | Constraint primary driver | Asset condition
3 | Constraint investment type | Asset renewal
4 | Constrained connection point latitude (decimal degrees) | -20.5006
| Constrained connection point longitude (decimal degrees) | 147.7755
5 | Effect on residential customers
| Annual Energy | Not available
| Maximum Demand | Not available
6, 7 | Effect on industrial and commercial customers
| Annual Energy | Not available
| Maximum Demand | Not available
8 | Load profile (maximum day, MVA)
50% PoE
Load profile (minimum day, MVA)
Minimum demand data (MVA)
| Max. demand, maximum demand day (MVA) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| 10% PoE | 763.4 | 778.1 | 778.7 | 786.2 | 788.5 | 938.3 | 940.3 | 939.3 | 937.3 | 930.9 | 930.2
| 50% PoE | 741.3 | 746.8 | 746.8 | 754.6 | 756.7 | 843.9 | 845.7 | 844.6 | 839.1 | 843.6 | 848.9
9 | Max. demand, minimum demand day (MW) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Maximum demand data | 416.5 | 415.1 | 415.6 | 422.2 | 423.7 | 423.3 | 429.1 | 433.4 | 432.9 | 432.6 | 432.4
10 | Load profile (maximum day, MW)
Load profile 50%
| Max. demand, maximum demand day (MW) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| 10% PoE | 930.9 | 911.2 | 889.9 | 899.2 | 951.4 | 1056.7 | 1025.7 | 1024.3 | 1007 | 865.3 | 1014.2
| 50% PoE | 740.2 | 745.7 | 746.1 | 753.9 | 756.3 | 843.3 | 844.8 | 842.9 | 834.6 | 843 | 848
11 | Load profile (minimum day, MW)
Minimum demand data (MW)
| Min. demand, minimum demand day (MW) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Mininum demand data | -338.8 | -391.4 | -400.8 | -411.7 | -420.7 | -428.4 | -439.6 | -451.4 | -465 | -466.5 | -479.1
12 | Voltage level (kV) | 275
13 | Maximum load at risk per year | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Load at risk (MW, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Load at risk (MVA, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Load duration curve
15 | Preferred investment | Strathmore 275kV and 132kV partial secondary systems replacement
16 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Capital cost ($m, nominal) | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Operating cost ($m, nominal) | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
18 | Preferred investment cost accuracy | 0.3
19 | Preferred investment proposed timing | 2022-12-31
20 | Demand reduction to defer the investment by 1 year | 0
21 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Annual deferral value ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Load transfer capacity (MVA) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
23 | Historic load trace
24 | Historic ratings
25 | Limitation asset | Feeders
26 | Unplanned outages
27 | Maximum fault level (kA) | 9.8
28 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Economic cost ($m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | VCR ($m/MWh) | 0.03971
30 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Annual unserved energy (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 8. Load profile max (50% PoE)
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:00 | 581.7 | 580.7 | 580.9 | 590.5 | 592.2 | 592 | 592 | 592.1 | 591.2 | 591.4 | 592.5
0:30 | 585.9 | 586.1 | 586.1 | 595 | 596.7 | 595.8 | 596.4 | 596.5 | 596.9 | 596.3 | 598
1:00 | 562.4 | 561.9 | 562 | 569.9 | 571.5 | 571.6 | 571.5 | 571.5 | 571.4 | 571.5 | 576.3
1:30 | 551.1 | 553.4 | 553.5 | 561.2 | 562.6 | 562.2 | 562.1 | 562.1 | 562.1 | 562 | 564.1
2:00 | 544.2 | 544.8 | 544.9 | 553.4 | 555 | 554.9 | 554.9 | 554.8 | 554.7 | 555.1 | 557.1
2:30 | 535.2 | 535.4 | 535.5 | 542.8 | 544.4 | 544.3 | 544.3 | 544.5 | 544.3 | 544.5 | 548.9
3:00 | 529 | 529.2 | 529.3 | 537.9 | 538.3 | 538.5 | 540.2 | 538.1 | 538.2 | 538.9 | 542
3:30 | 527.7 | 526.3 | 526.8 | 535.2 | 541.8 | 537.5 | 537.1 | 536.6 | 536.2 | 536.3 | 541.8
4:00 | 518 | 517.2 | 517.4 | 527.8 | 527.3 | 529.9 | 528.8 | 530.5 | 530.4 | 530.1 | 533.7
4:30 | 519.7 | 519.2 | 520 | 525.5 | 527.2 | 527.8 | 529.8 | 528.3 | 529.2 | 532.2 | 533.3
5:00 | 514.3 | 515.5 | 515.1 | 522.6 | 525.3 | 523.6 | 524.8 | 527.5 | 525.8 | 523.6 | 527.8
5:30 | 513.2 | 513 | 511.6 | 520.2 | 521.8 | 523.9 | 525.3 | 526.6 | 526.6 | 526.8 | 525.3
6:00 | 503.8 | 503 | 503.1 | 511.2 | 512.8 | 512.6 | 513 | 513 | 513.2 | 513.4 | 517.2
6:30 | 577.4 | 573.7 | 575.5 | 582.1 | 582.6 | 581.9 | 582.5 | 584.5 | 584.7 | 584.7 | 583.4
7:00 | 485 | 469.4 | 467.8 | 462 | 462.3 | 462 | 461 | 458.8 | 457.6 | 456.5 | 460.1
7:30 | 458.2 | 442.5 | 439.9 | 444.9 | 445 | 443.4 | 440.4 | 424.7 | 425.1 | 423.4 | 425.7
8:00 | 426.3 | 433.6 | 439.3 | 431 | 432.4 | 430.1 | 429.8 | 433.9 | 433.2 | 432.2 | 434.6
8:30 | 426.7 | 427.9 | 428.4 | 426.8 | 433 | 435.8 | 436.5 | 444.5 | 443.3 | 444.3 | 450.4
9:00 | 493.6 | 513.8 | 516.6 | 514.3 | 516.7 | 518.8 | 524.7 | 548.1 | 553.3 | 554.1 | 544.3
9:30 | 527.1 | 552.4 | 556.8 | 553.1 | 569.7 | 570.3 | 562.9 | 588 | 592.7 | 597.8 | 597.8
10:00 | 557.4 | 564.8 | 583.4 | 582.7 | 592.8 | 601.2 | 600.2 | 611.5 | 616.2 | 610.4 | 617.1
10:30 | 551.6 | 586.3 | 593.6 | 599.1 | 607.8 | 612.8 | 620.5 | 634.6 | 642.5 | 632.6 | 621.8
11:00 | 568.6 | 594.9 | 597.1 | 611.7 | 617 | 622.4 | 635.3 | 643.8 | -651.9 | -644.2 | -658.6
11:30 | 576.8 | 607.6 | 613.8 | 618 | 625 | 631.2 | -638.4 | 644.9 | -659.5 | -668.2 | -660.1
12:00 | 569.4 | 595.9 | 595.3 | 597.4 | 601.3 | 619.1 | 627.7 | 638.2 | -649.3 | -652.8 | -658.4
12:30 | 575.8 | 614 | 619.6 | 621.6 | 622.2 | 658.4 | -640 | 658.4 | -673.3 | -684 | -690.6
13:00 | 581.5 | 621.2 | 627.7 | 627.3 | 670.8 | 670.8 | -648.4 | 670.8 | -683.8 | -694.1 | -701.6
13:30 | 575.1 | 614.2 | 620.6 | 624.8 | 633.1 | 633.8 | -643.6 | 644.3 | -669.6 | -677 | -694.5
14:00 | 559 | 592.8 | 598.7 | 602.9 | 608.5 | 619.5 | 627.8 | 637.8 | -648.1 | -660.4 | -672.7
14:30 | 572.9 | 608.5 | 616 | 618.8 | 625.2 | 629.1 | 636.1 | 647.7 | -652.1 | -655.3 | -662.7
15:00 | 561.1 | 598.6 | 603.8 | 605.9 | 611.5 | 616.6 | 623.7 | 633.4 | -647 | -646.3 | -634.5
15:30 | 531.8 | 553.3 | 557.2 | 556.7 | 562.6 | 569.7 | 574.9 | 583.2 | 590 | 597.7 | 605.1
16:00 | 473.8 | 487.5 | 487.3 | 493.9 | 500.2 | 503.7 | 508.9 | 513.2 | 514.4 | 524.8 | 527.2
16:30 | 480.2 | 456.5 | 463.9 | 476.6 | 476.7 | 468.2 | 466.2 | 475 | 475.8 | 479.5 | 492.4
17:00 | 492.4 | 470.1 | 469 | 474.9 | 473.8 | 471.9 | 469.7 | 466.3 | 462.9 | 461.1 | 471.7
17:30 | 588.5 | 569.3 | 568.9 | 574.1 | 575.2 | 573 | 571.2 | 569.4 | 565 | 564.7 | 571.7
18:00 | 725.3 | 712.7 | 712.7 | 724.9 | 725.8 | 724.6 | 724.6 | 722.7 | 722.6 | 723.4 | 730.6
18:30 | 741.3 | 746.8 | 746.8 | 754.6 | 756.7 | 782.5 | 784.4 | 781.9 | 783.3 | 785 | 790.9
19:00 | 727 | 727.7 | 730.1 | 737.1 | 738.6 | 789.8 | 795.3 | 794.5 | 795.9 | 790.1 | 801.3
19:30 | 709.7 | 714.7 | 715.5 | 723.2 | 725.2 | 836.6 | 838.3 | 836.7 | 835.1 | 836.1 | 842.3
20:00 | 692.8 | 694.6 | 697.4 | 706.7 | 708.7 | 843.9 | 845.7 | 844.6 | 835.1 | 843.6 | 848.9
20:30 | 643.9 | 647.6 | 644.9 | 654.4 | 656.3 | 828.7 | 833.1 | 830.1 | 839.1 | 832.2 | 836
21:00 | 660.5 | 659.9 | 659 | 670.7 | 671.1 | 790.5 | 790.7 | 790.6 | 790.9 | 791.9 | 798.6
21:30 | 710.7 | 710.2 | 710 | 727 | 729.2 | 745.9 | 745.4 | 745.9 | 745.9 | 745.6 | 750.3
22:00 | 689.5 | 689 | 691.7 | 699.8 | 702 | 703.1 | 702.8 | 702.9 | 702.9 | 703.4 | 712.6
22:30 | 653.1 | 652.5 | 652.9 | 662.6 | 664.6 | 665.7 | 665.9 | 667.7 | 665.9 | 668.2 | 670.2
23:00 | 615.7 | 617 | 617.1 | 627.8 | 629.7 | 631.9 | 631.7 | 630.9 | 630.8 | 635.6 | 634.1
23:30 | 582.8 | 581.4 | 583.9 | 594.2 | 595.6 | 596.1 | 596.2 | 597.1 | 597.4 | 596.4 | 599.7

## 8. Load profile min
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:00 | 286.6 | 285.5 | 266.5 | 268.1 | 292.8 | 291.1 | 292 | 291.9 | 291.5 | 338.1 | 337.6
0:30 | 270.1 | 270.4 | 251.4 | 254.5 | 277.1 | 274.1 | 272.3 | 275.3 | 275.7 | 329.8 | 332.9
1:00 | 249.6 | 250 | 232.4 | 235.6 | 257.7 | 255.7 | 253.3 | 252.9 | 255.7 | 324.9 | 325.4
1:30 | 230.3 | 224.8 | 196.7 | 204.3 | 257.7 | 237.2 | 230.6 | 231.9 | 235.2 | 317 | 317.2
2:00 | 225.6 | 225.3 | 189.4 | 190.6 | 231 | 230.7 | 230.3 | 230.7 | 230.2 | 311.3 | 312.1
2:30 | 214.8 | 216.3 | 194.3 | 182.7 | 215.8 | 214.9 | 214.5 | 213.8 | 216.4 | 312.4 | 315.3
3:00 | 211.2 | 213.8 | 175.7 | 174.3 | 210.6 | 211.7 | 211 | 209 | 207 | 308.3 | 312.7
3:30 | 193.4 | 194.9 | 181.1 | 176.2 | 198.2 | 195 | 196.1 | 197.5 | 192.6 | 311.8 | 312.2
4:00 | 195.9 | 197.9 | 172.6 | 174.5 | 196.3 | 196.4 | 200.7 | 195.1 | 195.5 | 313.6 | 311.7
4:30 | 192 | 194.4 | 172.1 | 171 | 194.1 | 198.8 | 197.8 | 197 | 197.5 | 302.4 | 311.2
5:00 | 200.7 | 203.7 | 175.2 | 171.3 | 199.6 | 205.2 | 203.4 | 206.9 | 206.5 | 306.6 | 310.7
5:30 | 213.2 | 214.4 | 180.6 | 189.7 | 217.5 | 223.9 | 223.3 | 212.4 | 212.8 | 301.1 | 301.7
6:00 | 199.2 | 208.4 | 179.2 | 176.2 | 208.5 | 211.4 | 210.5 | 207.5 | 211.4 | 302.3 | 310.1
6:30 | 222 | 226.6 | 225.5 | 231.9 | 231.7 | 223.5 | 231.4 | 230.6 | 226.4 | 286.2 | 292.6
7:00 | 387.3 | 383.9 | 252.5 | 255.1 | 385.7 | 389.8 | 389.5 | 386.6 | 386.6 | 363.7 | 354.5
7:30 | 249.7 | 246.9 | 389.2 | 396.3 | 263 | 261.9 | 260.4 | 250.3 | 260.9 | 434.4 | 427.1
8:00 | 358.6 | 350.4 | 419.9 | 429.1 | 346.2 | 346.2 | 347.6 | 350.7 | 353.9 | -587 | -586.1
8:30 | -465 | -483.3 | 557.6 | 560.2 | -480 | -484.9 | -486 | -490 | -493.3 | -706.4 | -709.1
9:00 | -592.6 | -623.8 | -695.4 | -691.4 | -629.2 | -633.3 | -638.9 | -641.6 | -646 | -830.7 | -832
9:30 | -704.8 | -746.1 | -776.4 | -781.6 | -749.5 | -756.8 | -762.5 | -764 | -768.2 | -914.7 | -917.9
10:00 | -773.5 | -815.2 | -826.5 | -830.8 | -835.2 | -839 | -849 | -854.9 | -861.2 | -956 | -960.4
10:30 | -844.8 | -893.8 | -882.1 | -888.1 | -909.7 | -916 | -923 | -930.2 | -937.1 | -995.8 | -985.6
11:00 | -853.7 | -902.6 | -928.1 | -935.6 | -928.6 | -933.8 | -942.1 | -933.5 | -929.1 | -1000.8 | -993.8
11:30 | -916.3 | -974.7 | -930 | -937.8 | -996 | -1001.6 | -1010.4 | -1019.1 | -1003.7 | -1023.6 | -1030.1
12:00 | -918.8 | -962.7 | -957.1 | -972.6 | -988.3 | -993.6 | -1003.8 | -1015.2 | -1031.6 | -1041.4 | -1047.2
12:30 | -936 | -981.3 | -956.3 | -968 | -1008.5 | -1014.2 | -1022.8 | -1035.1 | -1053.3 | -1043.2 | -1063.6
13:00 | -916.1 | -965.8 | -963.7 | -944.2 | -1002.5 | -1010 | -1018.3 | -1029.8 | -1034.5 | -1047.9 | -1055.9
13:30 | -906.2 | -951.9 | -971.1 | -950.8 | -983 | -990.7 | -999.8 | -1010 | -1020.4 | -1045.1 | -1056.1
14:00 | -911.8 | -964.3 | -987 | -995.7 | -988.3 | -996.5 | -1004.9 | -1014 | -1023.8 | -1008 | -1022.3
14:30 | -895.8 | -950.3 | -993.2 | -1004.7 | -975.3 | -980.6 | -983.5 | -993.5 | -1002.7 | -995.5 | -904.7
15:00 | -882.2 | -941.4 | -974.8 | -983.9 | -957.5 | -963.7 | -969.9 | -979.3 | -986.8 | -954.4 | -965
15:30 | -836.2 | -894.8 | -959.6 | -963.4 | -916.6 | -920.1 | -925.3 | -930.7 | -938.5 | -934 | -921.8
16:00 | -790.6 | -832.5 | -916.8 | -926.3 | -851.5 | -855.2 | -861.1 | -865.7 | -872.8 | -874.8 | -878.5
16:30 | -721.8 | -753.4 | -865.6 | -862 | -766.5 | -766.3 | -770 | -770.2 | -778.2 | -701.1 | -699.9
17:00 | -531.6 | -546.4 | -615.1 | -608 | -557.5 | -558.5 | -554.1 | -558.6 | -560.1 | -528.3 | -529.9
17:30 | 351.8 | 349 | -380.8 | -378.4 | 346.9 | 337 | 333.1 | 341.5 | 333.3 | 371.7 | 350.6
18:00 | 314.4 | 323.4 | 250.7 | 268.4 | 328.3 | 328.4 | 328.7 | 328.6 | 328.6 | 339.4 | 344.3
18:30 | 372.4 | 372 | 283.8 | 303.3 | 378.3 | 378.1 | 389.3 | 393.5 | 388.9 | 366.8 | 367.3
19:00 | 412.5 | 411.8 | 315.4 | 318.8 | 421.5 | 424.3 | 434.2 | 433.4 | 433.3 | 378.7 | 383.3
19:30 | 422 | 430.9 | 322.3 | 329.2 | 427.8 | 430.1 | 432.6 | 441.6 | 443.7 | 360.3 | 370
20:00 | 411.5 | 410.9 | 316.5 | 327.4 | 419.5 | 417.8 | 423.9 | 428.8 | 428.6 | 348.2 | 351.7
20:30 | 414.5 | 413.1 | 287 | 284.3 | 419.5 | 419.1 | 420.2 | 398.3 | 397.7 | 356.3 | 353.7
21:00 | 411.6 | 384 | 271.5 | 274.3 | 391.2 | 390.8 | 390.4 | 390 | 389.7 | 360.3 | 353.5
21:30 | 397.3 | 392.8 | 274.6 | 283.2 | 401.3 | 399.9 | 409.8 | 410.9 | 410.8 | 354.3 | 357.5
22:00 | 379.3 | 375.9 | 262.3 | 264.8 | 394.3 | 394.6 | 392.3 | 394.1 | 394.8 | 354.1 | 356.8
22:30 | 377.2 | 375.7 | 272.9 | 275 | 384.3 | 384.4 | 382.8 | 383 | 382.9 | 351.6 | 357
23:00 | 362.7 | 360.8 | 269 | 273.5 | 369.1 | 367.7 | 367.6 | 367.7 | 367.3 | 348 | 345
23:30 | 331.6 | 329.8 | 253.6 | 257.3 | 335.9 | 337.6 | 336.3 | 335.2 | 336.3 | 328.6 | 327.8

## 10. Load profile (50% PoE)
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:00 | 580.9 | 580 | 580.1 | 589.1 | 590.8 | 590.7 | 590.9 | 591 | 590.5 | 590.7 | 592.3
0:30 | 584.2 | 583.3 | 583.5 | 592.5 | 594.2 | 594 | 594.3 | 594.2 | 594.2 | 594.4 | 596.8
1:00 | 561.8 | 560.8 | 560.9 | 569.4 | 571.1 | 570.9 | 571.1 | 570.9 | 571.1 | 571.2 | 575.3
1:30 | 549.5 | 551.1 | 551.2 | 559.7 | 561.3 | 561.2 | 561.4 | 561.4 | 561.4 | 561.4 | 562.6
2:00 | 542.9 | 544.2 | 544.2 | 552.6 | 554.2 | 554.7 | 554.7 | 554.6 | 554.6 | 554.3 | 555.4
2:30 | 535.1 | 533.8 | 533.8 | 542.2 | 543.9 | 544.1 | 544.2 | 543.9 | 544.2 | 544 | 547.9
3:00 | 528.8 | 527.6 | 527.7 | 535.8 | 537.6 | 537.5 | 537.4 | 537.8 | 537.8 | 537.6 | 541.6
3:30 | 525.5 | 524.7 | 524.7 | 533.5 | 534.8 | 535.6 | 535 | 535.6 | 535.9 | 535.9 | 538.2
4:00 | 517.7 | 516.9 | 517 | 525.1 | 526.7 | 526.4 | 526.8 | 526.4 | 526.4 | 526.6 | 530
4:30 | 518.3 | 517.3 | 517.2 | 525.2 | 527 | 527.2 | 526.7 | 526.9 | 527 | 527.1 | 527.9
5:00 | 514 | 512.9 | 513 | 521.2 | 522.5 | 522.8 | 522.7 | 522.9 | 522.5 | 522.6 | 524.4
5:30 | 512.2 | 511.2 | 511.1 | 519.6 | 521.3 | 521.3 | 521.2 | 521 | 521.1 | 521.2 | 524.8
6:00 | 501.8 | 500.9 | 501.1 | 509 | 510.6 | 510.7 | 510.8 | 510.7 | 510.9 | 511.1 | 515.1
6:30 | 474.8 | 474.1 | 473.8 | 481.3 | 482.4 | 482.3 | 482.5 | 482.4 | 482.5 | 482.8 | 486.4
7:00 | 374.8 | 358.5 | 357.5 | 361.2 | 361.6 | 361 | 359.9 | 358.2 | 356.9 | 355.8 | 358.6
7:30 | 341.4 | 319.9 | 317.8 | 320.3 | 319.4 | 317.8 | 316 | 314 | 311.7 | 310 | 312.6
8:00 | 278.9 | 250.9 | 248.3 | 248.7 | 246.5 | 244.3 | 241.2 | 237.3 | 233.6 | 230.8 | 230.7
8:30 | 235.8 | 203.9 | 200.3 | 198.8 | 195.6 | 192.4 | 188.5 | 183.4 | 178.7 | 174.8 | 176.1
9:00 | 160.1 | 117.2 | 111.6 | 107.2 | 102.2 | 97.5 | 91.1 | 83.2 | 75.9 | 69.7 | 68.5
9:30 | 147 | 104.2 | 98.2 | 92.8 | 86.9 | 82 | 75.1 | 66.5 | 58.2 | 50.9 | 48.4
10:00 | 127.1 | 84.6 | 77.6 | 71.3 | 65.2 | 60.1 | 52.8 | 43.3 | 34.4 | 39.8 | 36
10:30 | 107.3 | 62.8 | 55.4 | 48.9 | 42.5 | 36.4 | 27.6 | 17.6 | 7.7 | 15.7 | 12
11:00 | 95.9 | 50.5 | 42.9 | 34.6 | 26.8 | 20.3 | 10.6 | 0.2 | -10.5 | -3.3 | -7
11:30 | 89 | 42.2 | 33.8 | 25.4 | 17.6 | 9.7 | -0.5 | -11 | -22.3 | -31.8 | -19
12:00 | 99.8 | 54.2 | 46 | 39.2 | 31.5 | 22.7 | 12.9 | 3.1 | -8.2 | -18.2 | -23.3
12:30 | 84.4 | 32.6 | 23.6 | 15.3 | 6.6 | -1.9 | -13.5 | -26.1 | -39.2 | -50.8 | -57.8
13:00 | 77 | 23.5 | 14.4 | 6.1 | -3.5 | -11.4 | -23.4 | -35.9 | -49.8 | -61.3 | -68.3
13:30 | 91.1 | 38.1 | 28.7 | 20.3 | 10.8 | 2.9 | -8.5 | -20 | -34 | -45.3 | -52
14:00 | 114 | 61.1 | 52.3 | 44.1 | 35.1 | 27 | 16.3 | 3.4 | -9.6 | -21.2 | -27
14:30 | 95.6 | 42.8 | 34.3 | 27.1 | 18.5 | 10.7 | 0.9 | -11.6 | -23.5 | -33.7 | -39.2
15:00 | 113.7 | 60.6 | 52.9 | 46.4 | 38.9 | 31.2 | 21.9 | 9.9 | -1.5 | -10.8 | -14.5
15:30 | 166.6 | 115.8 | 108.9 | 104.1 | 97.1 | 90.5 | 82.2 | 72.2 | 62.6 | 54.5 | 51.4
16:00 | 229.3 | 182.6 | 177.1 | 174 | 168.1 | 162.9 | 156 | 148.3 | 140.5 | 133.8 | 133.4
16:30 | 303.2 | 261.3 | 256.6 | 255.7 | 252.1 | 248 | 242.6 | 236.3 | 230.2 | 225.3 | 226.3
17:00 | 390.2 | 356.9 | 354.7 | 357.2 | 355.4 | 352.6 | 349.1 | 345.2 | 341.3 | 338.6 | 341.3
17:30 | 511.4 | 484.1 | 482.9 | 488.4 | 488.7 | 486.6 | 484.6 | 481.5 | 479.1 | 477.6 | 482
18:00 | 646.4 | 634.5 | 634.6 | 642.5 | 643.5 | 642.3 | 642.3 | 640.4 | 640.1 | 640.5 | 646.8
18:30 | 740.2 | 745.7 | 746.1 | 753.9 | 756.3 | 782.1 | 784 | 781.5 | 782.9 | 784.5 | 790.5
19:00 | 725.1 | 725.7 | 728.7 | 736.1 | 737.4 | 787.9 | 793.3 | 793.9 | 794.1 | 789.9 | 800.8
19:30 | 709 | 713.7 | 714.3 | 722.5 | 724.7 | 835.2 | 837 | 835.4 | 834.6 | 835.5 | 841.6
20:00 | 691.7 | 693.5 | 695.1 | 702.9 | 705.2 | 843.3 | 844.8 | 842.9 | 834.6 | 843 | 848
20:30 | 642.9 | 643 | 643.4 | 652.6 | 654.9 | 828 | 829.8 | 829.2 | 830.6 | 831.1 | 835.3
21:00 | 659.7 | 659.1 | 657.7 | 667.8 | 670.7 | 790.2 | 790.4 | 790.3 | 790.3 | 791.3 | 798
21:30 | 710.2 | 709.6 | 709.3 | 721.4 | 723.5 | 745.6 | 744.2 | 745.7 | 745.7 | 744.9 | 750.1
22:00 | 689.1 | 688.6 | 689.5 | 699.3 | 701.3 | 701.9 | 702.4 | 702.5 | 702.5 | 703.1 | 710.4
22:30 | 652.3 | 651.8 | 652.1 | 662.4 | 664.3 | 665.1 | 665.3 | 666.1 | 665.3 | 666.6 | 669.6
23:00 | 615.3 | 616.3 | 617 | 627.3 | 629.3 | 629.9 | 630.1 | 630.1 | 629.6 | 632 | 633.4
23:30 | 582.2 | 581 | 583.3 | 593.1 | 595.5 | 595.8 | 595.9 | 595.8 | 595.8 | 596 | 597.7

## 11. Load profile min
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:00 | 271.2 | 270.2 | 270.2 | 274.9 | 275.9 | 275.8 | 275.9 | 274.9 | 275 | 274.4 | 273.9
0:30 | 250.7 | 249.6 | 249.3 | 254 | 255 | 254.9 | 254.6 | 253.5 | 253.8 | 254.3 | 254.8
1:00 | 229 | 227.9 | 227.7 | 232.3 | 232.9 | 232.6 | 232.5 | 232.1 | 231.7 | 231.6 | 231.6
1:30 | 206.5 | 206 | 205.5 | 209.7 | 232.9 | 210.2 | 210.3 | 208.4 | 208.3 | 208.5 | 208.6
2:00 | 200.1 | 199.2 | 198.9 | 203 | 203.9 | 203.7 | 203.8 | 201.9 | 201.5 | 201.2 | 200.9
2:30 | 181 | 179.7 | 180 | 183 | 183.8 | 184.4 | 184.8 | 182.3 | 182.8 | 182.1 | 181.4
3:00 | 179 | 177.6 | 177.6 | 181.4 | 182.5 | 181.7 | 181.8 | 179.9 | 180.3 | 180.1 | 179.9
3:30 | 161.5 | 160.4 | 160.1 | 164.3 | 164.4 | 164.5 | 164.6 | 163.6 | 163.1 | 163.2 | 163.3
4:00 | 162 | 160.8 | 160 | 164.2 | 165 | 165.2 | 164.9 | 163 | 162.8 | 162.8 | 162.9
4:30 | 164 | 162.4 | 162.4 | 166.3 | 166.9 | 167.1 | 167 | 165.9 | 165.5 | 165.6 | 165.7
5:00 | 174.8 | 173.8 | 174 | 178.3 | 179.5 | 178.6 | 179 | 177.4 | 177.4 | 177.6 | 177.8
5:30 | 184.5 | 183.3 | 183.2 | 187 | 187.7 | 187.9 | 188 | 185.2 | 186.1 | 185.4 | 184.7
6:00 | 168.4 | 168.2 | 167.1 | 171.6 | 172.7 | 172.4 | 172.7 | 170.5 | 171 | 176 | 181.1
6:30 | 194.7 | 193.5 | 193.8 | 198.1 | 199.4 | 199.7 | 199.5 | 197.5 | 198 | 199 | 199.9
7:00 | 147.7 | 147.1 | 147.3 | 149.2 | 150.3 | 150.2 | 150.3 | 150.5 | 150.7 | 151.1 | 151.5
7:30 | 198.6 | 197.9 | 197.5 | 199.4 | 200.4 | 200.7 | 200.9 | 200.1 | 200.3 | 200.8 | 201.4
8:00 | 95.4 | 81.7 | 80.9 | 83.4 | 83.7 | 83.1 | 82.3 | 82 | 81.2 | 80.8 | 80.5
8:30 | -10.3 | -37 | -38.9 | -39 | -39.5 | -41.6 | -43.8 | -46 | -48.6 | -50.9 | -53.2
9:00 | -107.3 | -144.1 | -148.1 | -151.2 | -153.9 | -156.9 | -161.5 | -167.4 | -172.6 | -177.2 | -181.9
9:30 | -174.6 | -218 | -222.9 | -227.4 | -231.4 | -235.8 | -241.8 | -248.3 | -255.2 | -262.5 | -269.9
10:00 | -228.9 | -276.8 | -283.3 | -290.2 | -297.4 | -302.4 | -310.6 | -318.5 | -327.3 | -335.5 | -343.8
10:30 | -271 | -321.6 | -330.1 | -339.2 | -346.6 | -352.7 | -361.8 | -371.7 | -382.1 | -361.5 | -342
11:00 | -290.5 | -343.1 | -351.6 | -362 | -370.4 | -378 | -388.1 | -380.3 | -380.2 | -387.8 | -395.6
11:30 | -326.7 | -380.8 | -389.5 | -401.1 | -410.1 | -418.2 | -429 | -440.6 | -423.2 | -435.7 | -448.5
12:00 | -330.3 | -380.7 | -389.6 | -401 | -409.6 | -416.9 | -427.3 | -438.7 | -452.3 | -433.4 | -415.2
12:30 | -338.8 | -391.4 | -400.8 | -411.7 | -420.7 | -428.4 | -439.6 | -451.4 | -465 | -446.7 | -429.1
13:00 | -329.5 | -382 | -391.4 | -402 | -410.6 | -418.2 | -429.4 | -441.4 | -454.2 | -466.5 | -479.1
13:30 | -319.8 | -371.1 | -380.2 | -389.9 | -398 | -406 | -416.4 | -427.6 | -441.8 | -454.6 | -467.9
14:00 | -319 | -370.8 | -379.4 | -389.8 | -397.7 | -405.3 | -415.5 | -426.3 | -438.7 | -450.8 | -463.2
14:30 | -303.8 | -354.7 | -362.9 | -371.5 | -379 | -386.1 | -395.7 | -405 | -416.6 | -427.8 | -439.4
15:00 | -282 | -332.2 | -339.5 | -347.3 | -353.8 | -360.4 | -369 | -378.1 | -388.6 | -398.3 | -408.3
15:30 | -234.5 | -281.2 | -287.6 | -293.8 | -300 | -305.5 | -312.8 | -319.8 | -328.5 | -336.6 | -344.8
16:00 | -200.4 | -244.2 | -249.4 | -254.6 | -259.8 | -264.4 | -270.5 | -275.6 | -282.8 | -289.5 | -296.3
16:30 | -152.5 | -189.2 | -192.7 | -195.7 | -199 | -202.4 | -206.5 | -210.1 | -215.3 | -219.9 | -224.7
17:00 | -35.4 | -62.5 | -64.6 | -63.1 | -64.7 | -66.8 | -68.9 | -70.4 | -72.9 | -75.4 | -77.9
17:30 | 118.2 | 100.9 | 99.8 | 103.3 | 103.5 | 102.3 | 101.2 | 100.3 | 98.9 | 98.1 | 97.2
18:00 | 300.3 | 309.3 | 309.2 | 314.8 | 315.7 | 315.4 | 315.4 | 314.1 | 314.1 | 314.3 | 314.5
18:30 | 364.8 | 364 | 364.1 | 370.5 | 371.6 | 371 | 380.8 | 380.4 | 380.4 | 380.3 | 380.2
19:00 | 407 | 405.5 | 405.6 | 413 | 414.2 | 413.7 | 424.1 | 423.4 | 423.3 | 423.3 | 423.2
19:30 | 416.5 | 415.1 | 415.6 | 422.2 | 423.7 | 423.3 | 429.1 | 433.4 | 432.9 | 432.6 | 432.4
20:00 | 407.3 | 406.1 | 406.1 | 413.8 | 415.2 | 414.3 | 417.5 | 425.4 | 424.2 | 425.2 | 426.2
20:30 | 395.8 | 394.6 | 393.9 | 398.8 | 400.1 | 399.7 | 397.9 | 394.5 | 394.1 | 393.9 | 393.7
21:00 | 380.2 | 376.9 | 377.2 | 384.2 | 385.6 | 385.3 | 384.5 | 384.6 | 384.5 | 384.4 | 384.3
21:30 | 389.3 | 388.6 | 388.2 | 395 | 396.4 | 395.7 | 405.7 | 406.8 | 406.8 | 406.7 | 406.6
22:00 | 369.8 | 368.1 | 368.1 | 375.7 | 387 | 386.7 | 387.2 | 386.9 | 386.9 | 387.1 | 387.4
22:30 | 369.8 | 368.4 | 368.2 | 376.1 | 377.3 | 377 | 376.6 | 376.2 | 376.2 | 376.1 | 376
23:00 | 352.9 | 351.9 | 351.8 | 359.1 | 360.4 | 359.7 | 359.3 | 359.4 | 359.3 | 359.5 | 359.8
23:30 | 320 | 318.6 | 318.2 | 324.7 | 325.9 | 325.9 | 325.9 | 325.6 | 325 | 324.5 | 323.9

## 14. Load duration curve
*The data range is from 01-03-18 to 01-03-19

## 23. Historic load trace
Date/Time | Load (MVA) | Load (MW)
2016-03-01 00:30 | 656 | 656
2016-03-01 01:00 | 639 | 639
2016-03-01 01:30 | 625 | 625
2016-03-01 02:00 | 607 | 607
2016-03-01 02:30 | 599 | 599
2016-03-01 03:00 | 595 | 595
2016-03-01 03:30 | 590 | 590
2016-03-01 04:00 | 591 | 591
2016-03-01 04:30 | 585 | 585
2016-03-01 05:00 | 577 | 577
2016-03-01 05:30 | 584 | 583
2016-03-01 06:00 | 600 | 600
2016-03-01 06:30 | 602 | 602
2016-03-01 07:00 | 612 | 612
2016-03-01 07:30 | 679 | 679
2016-03-01 08:00 | 690 | 690
2016-03-01 08:30 | 690 | 690
2016-03-01 09:00 | 695 | 695
2016-03-01 09:30 | 678 | 678
2016-03-01 10:00 | 657 | 657
2016-03-01 10:30 | 664 | 663
2016-03-01 11:00 | 670 | 670
2016-03-01 11:30 | 678 | 678
2016-03-01 12:00 | 676 | 675
2016-03-01 12:30 | 658 | 658
2016-03-01 13:00 | 711 | 711
2016-03-01 13:30 | 741 | 741
2016-03-01 14:00 | 770 | 770
2016-03-01 14:30 | 720 | 719
2016-03-01 15:00 | 778 | 778
2016-03-01 15:30 | 794 | 793
2016-03-01 16:00 | 763 | 762
2016-03-01 16:30 | 828 | 827
2016-03-01 17:00 | 833 | 831
2016-03-01 17:30 | 837 | 837
2016-03-01 18:00 | 837 | 837
2016-03-01 18:30 | 839 | 839
2016-03-01 19:00 | 798 | 798
2016-03-01 19:30 | 820 | 820
2016-03-01 20:00 | 861 | 861
2016-03-01 20:30 | 843 | 843
2016-03-01 21:00 | 819 | 819
2016-03-01 21:30 | 791 | 791
2016-03-01 22:00 | 757 | 757
2016-03-01 22:30 | 690 | 689
2016-03-01 23:00 | 656 | 654
2016-03-01 23:30 | 657 | 657
2016-03-02 | 635 | 635
2016-03-02 00:30 | 621 | 621
2016-03-02 01:00 | 615 | 615
2016-03-02 01:30 | 601 | 601
2016-03-02 02:00 | 598 | 598
2016-03-02 02:30 | 585 | 585
2016-03-02 03:00 | 580 | 579
2016-03-02 03:30 | 572 | 571
2016-03-02 04:00 | 563 | 563
2016-03-02 04:30 | 563 | 563
2016-03-02 05:00 | 569 | 568
2016-03-02 05:30 | 584 | 583
2016-03-02 06:00 | 592 | 591
2016-03-02 06:30 | 587 | 587
2016-03-02 07:00 | 614 | 613
2016-03-02 07:30 | 671 | 671
2016-03-02 08:00 | 695 | 694
2016-03-02 08:30 | 707 | 705
2016-03-02 09:00 | 727 | 726
2016-03-02 09:30 | 711 | 710
2016-03-02 10:00 | 694 | 694
2016-03-02 10:30 | 703 | 703
2016-03-02 11:00 | 708 | 708
2016-03-02 11:30 | 720 | 720
2016-03-02 12:00 | 742 | 742
2016-03-02 12:30 | 763 | 762
2016-03-02 13:00 | 678 | 676
2016-03-02 13:30 | 620 | 620
2016-03-02 14:00 | 650 | 650
2016-03-02 14:30 | 652 | 652
2016-03-02 15:00 | 652 | 652
2016-03-02 15:30 | 659 | 659
2016-03-02 16:00 | 676 | 676
2016-03-02 16:30 | 677 | 677
2016-03-02 17:00 | 678 | 677
2016-03-02 17:30 | 665 | 664
2016-03-02 18:00 | 662 | 662
2016-03-02 18:30 | 682 | 682
2016-03-02 19:00 | 663 | 663
2016-03-02 19:30 | 631 | 631
2016-03-02 20:00 | 619 | 619
2016-03-02 20:30 | 675 | 675
2016-03-02 21:00 | 661 | 661
2016-03-02 21:30 | 639 | 639
2016-03-02 22:00 | 724 | 724
2016-03-02 22:30 | 718 | 717
2016-03-02 23:00 | 691 | 691
2016-03-02 23:30 | 660 | 660
2016-03-03 | 648 | 648
2016-03-03 00:30 | 630 | 630
2016-03-03 01:00 | 600 | 599
2016-03-03 01:30 | 585 | 585
2016-03-03 02:00 | 583 | 583
2016-03-03 02:30 | 581 | 580
2016-03-03 03:00 | 575 | 575
2016-03-03 03:30 | 571 | 570
2016-03-03 04:00 | 571 | 570
2016-03-03 04:30 | 573 | 572
2016-03-03 05:00 | 576 | 575
2016-03-03 05:30 | 590 | 589
2016-03-03 06:00 | 605 | 604
2016-03-03 06:30 | 635 | 634
2016-03-03 07:00 | 654 | 653
2016-03-03 07:30 | 687 | 687
2016-03-03 08:00 | 708 | 708
2016-03-03 08:30 | 718 | 718
2016-03-03 09:00 | 723 | 723
2016-03-03 09:30 | 720 | 720
2016-03-03 10:00 | 708 | 708
2016-03-03 10:30 | 717 | 717
2016-03-03 11:00 | 710 | 710
2016-03-03 11:30 | 692 | 692
2016-03-03 12:00 | 669 | 669
2016-03-03 12:30 | 682 | 682
2016-03-03 13:00 | 671 | 670
2016-03-03 13:30 | 682 | 682
2016-03-03 14:00 | 683 | 683
2016-03-03 14:30 | 680 | 680
2016-03-03 15:00 | 687 | 687
2016-03-03 15:30 | 684 | 684
2016-03-03 16:00 | 685 | 685
2016-03-03 16:30 | 690 | 690
2016-03-03 17:00 | 661 | 661
2016-03-03 17:30 | 645 | 645
2016-03-03 18:00 | 647 | 647
2016-03-03 18:30 | 629 | 629
2016-03-03 19:00 | 639 | 639
2016-03-03 19:30 | 637 | 637
2016-03-03 20:00 | 621 | 621
2016-03-03 20:30 | 678 | 678
2016-03-03 21:00 | 650 | 650
2016-03-03 21:30 | 674 | 674
2016-03-03 22:00 | 650 | 650
2016-03-03 22:30 | 642 | 642
2016-03-03 23:00 | 622 | 622
2016-03-03 23:30 | 593 | 592
2016-03-04 | 577 | 576
2016-03-04 00:30 | 562 | 561
2016-03-04 01:00 | 554 | 554
2016-03-04 01:30 | 549 | 549
2016-03-04 02:00 | 542 | 542
2016-03-04 02:30 | 541 | 540
2016-03-04 03:00 | 542 | 541
2016-03-04 03:30 | 536 | 535
2016-03-04 04:00 | 535 | 534
2016-03-04 04:30 | 534 | 533
2016-03-04 05:00 | 538 | 537
2016-03-04 05:30 | 549 | 548
2016-03-04 06:00 | 570 | 570
2016-03-04 06:30 | 606 | 606
2016-03-04 07:00 | 633 | 633
2016-03-04 07:30 | 664 | 664
2016-03-04 08:00 | 687 | 687
2016-03-04 08:30 | 693 | 693
2016-03-04 09:00 | 697 | 697
2016-03-04 09:30 | 694 | 694
2016-03-04 10:00 | 684 | 683
2016-03-04 10:30 | 663 | 663
2016-03-04 11:00 | 631 | 631
2016-03-04 11:30 | 617 | 617
2016-03-04 12:00 | 622 | 622
2016-03-04 12:30 | 621 | 621
2016-03-04 13:00 | 534 | 534
2016-03-04 13:30 | 494 | 493
2016-03-04 14:00 | 510 | 509
2016-03-04 14:30 | 516 | 515
2016-03-04 15:00 | 521 | 521
2016-03-04 15:30 | 520 | 519
2016-03-04 16:00 | 513 | 512
2016-03-04 16:30 | 510 | 510
2016-03-04 17:00 | 525 | 525
2016-03-04 17:30 | 539 | 538
2016-03-04 18:00 | 527 | 526
2016-03-04 18:30 | 519 | 519
2016-03-04 19:00 | 528 | 527
2016-03-04 19:30 | 529 | 528
2016-03-04 20:00 | 520 | 519
2016-03-04 20:30 | 613 | 613
2016-03-04 21:00 | 630 | 630
2016-03-04 21:30 | 614 | 614
2016-03-04 22:00 | 595 | 595
2016-03-04 22:30 | 598 | 598
2016-03-04 23:00 | 589 | 589
2016-03-04 23:30 | 569 | 568
2016-03-05 | 557 | 556
2016-03-05 00:30 | 545 | 544
2016-03-05 01:00 | 532 | 531
2016-03-05 01:30 | 522 | 521
2016-03-05 02:00 | 515 | 514
2016-03-05 02:30 | 514 | 513
2016-03-05 03:00 | 510 | 509
2016-03-05 03:30 | 509 | 507
2016-03-05 04:00 | 512 | 511
2016-03-05 04:30 | 511 | 509
2016-03-05 05:00 | 514 | 512
2016-03-05 05:30 | 522 | 520
2016-03-05 06:00 | 524 | 523
2016-03-05 06:30 | 532 | 531
2016-03-05 07:00 | 546 | 545
2016-03-05 07:30 | 571 | 570
2016-03-05 08:00 | 591 | 590
2016-03-05 08:30 | 609 | 609
2016-03-05 09:00 | 618 | 618
2016-03-05 09:30 | 608 | 608
2016-03-05 10:00 | 559 | 559
2016-03-05 10:30 | 550 | 550
2016-03-05 11:00 | 552 | 551
2016-03-05 11:30 | 553 | 552
2016-03-05 12:00 | 554 | 553
2016-03-05 12:30 | 545 | 544
2016-03-05 13:00 | 527 | 527
2016-03-05 13:30 | 546 | 545
2016-03-05 14:00 | 566 | 566
2016-03-05 14:30 | 577 | 577
2016-03-05 15:00 | 588 | 588
2016-03-05 15:30 | 596 | 595
2016-03-05 16:00 | 603 | 603
2016-03-05 16:30 | 611 | 611
2016-03-05 17:00 | 619 | 619
2016-03-05 17:30 | 632 | 632
2016-03-05 18:00 | 642 | 642
2016-03-05 18:30 | 651 | 651
2016-03-05 19:00 | 664 | 664
2016-03-05 19:30 | 671 | 671
2016-03-05 20:00 | 656 | 656
2016-03-05 20:30 | 641 | 641
2016-03-05 21:00 | 626 | 626
2016-03-05 21:30 | 615 | 615
2016-03-05 22:00 | 602 | 602
2016-03-05 22:30 | 607 | 607
2016-03-05 23:00 | 596 | 595
2016-03-05 23:30 | 577 | 577
2016-03-06 | 561 | 560
2016-03-06 00:30 | 547 | 546
2016-03-06 01:00 | 536 | 535
2016-03-06 01:30 | 525 | 524
2016-03-06 02:00 | 519 | 518
2016-03-06 02:30 | 518 | 517
2016-03-06 03:00 | 515 | 514
2016-03-06 03:30 | 514 | 513
2016-03-06 04:00 | 516 | 515
2016-03-06 04:30 | 514 | 513
2016-03-06 05:00 | 508 | 507
2016-03-06 05:30 | 509 | 507
2016-03-06 06:00 | 510 | 509
2016-03-06 06:30 | 516 | 515
2016-03-06 07:00 | 525 | 524
2016-03-06 07:30 | 537 | 536
2016-03-06 08:00 | 537 | 536
2016-03-06 08:30 | 512 | 512
2016-03-06 09:00 | 534 | 533
2016-03-06 09:30 | 560 | 559
2016-03-06 10:00 | 555 | 555
2016-03-06 10:30 | 551 | 551
2016-03-06 11:00 | 544 | 544
2016-03-06 11:30 | 549 | 549
2016-03-06 12:00 | 548 | 548
2016-03-06 12:30 | 547 | 547
2016-03-06 13:00 | 558 | 558
2016-03-06 13:30 | 577 | 577
2016-03-06 14:00 | 601 | 600
2016-03-06 14:30 | 605 | 605
2016-03-06 15:00 | 612 | 612
2016-03-06 15:30 | 617 | 617
2016-03-06 16:00 | 633 | 633
2016-03-06 16:30 | 642 | 642
2016-03-06 17:00 | 649 | 649
2016-03-06 17:30 | 670 | 670
2016-03-06 18:00 | 686 | 686
2016-03-06 18:30 | 703 | 703
2016-03-06 19:00 | 688 | 688
2016-03-06 19:30 | 686 | 686
2016-03-06 20:00 | 702 | 702
2016-03-06 20:30 | 707 | 707
2016-03-06 21:00 | 695 | 695
2016-03-06 21:30 | 672 | 672
2016-03-06 22:00 | 649 | 649
2016-03-06 22:30 | 625 | 625
2016-03-06 23:00 | 600 | 600
2016-03-06 23:30 | 578 | 578
2016-03-07 | 563 | 563
2016-03-07 00:30 | 552 | 551
2016-03-07 01:00 | 533 | 533
2016-03-07 01:30 | 521 | 521
2016-03-07 02:00 | 519 | 517
2016-03-07 02:30 | 512 | 511
2016-03-07 03:00 | 508 | 506
2016-03-07 03:30 | 502 | 500
2016-03-07 04:00 | 504 | 503
2016-03-07 04:30 | 506 | 504
2016-03-07 05:00 | 509 | 508
2016-03-07 05:30 | 522 | 521
2016-03-07 06:00 | 541 | 540
2016-03-07 06:30 | 573 | 572
2016-03-07 07:00 | 592 | 592
2016-03-07 07:30 | 638 | 637
2016-03-07 08:00 | 661 | 661
2016-03-07 08:30 | 669 | 669
2016-03-07 09:00 | 676 | 676
2016-03-07 09:30 | 668 | 668
2016-03-07 10:00 | 658 | 658
2016-03-07 10:30 | 649 | 649
2016-03-07 11:00 | 611 | 611
2016-03-07 11:30 | 631 | 631
2016-03-07 12:00 | 639 | 639
2016-03-07 12:30 | 653 | 653
2016-03-07 13:00 | 650 | 650
2016-03-07 13:30 | 668 | 668
2016-03-07 14:00 | 694 | 694
2016-03-07 14:30 | 623 | 623
2016-03-07 15:00 | 568 | 568
2016-03-07 15:30 | 568 | 568
2016-03-07 16:00 | 578 | 578
2016-03-07 16:30 | 580 | 579
2016-03-07 17:00 | 557 | 557
2016-03-07 17:30 | 537 | 536
2016-03-07 18:00 | 533 | 532
2016-03-07 18:30 | 548 | 547
2016-03-07 19:00 | 601 | 600
2016-03-07 19:30 | 640 | 639
2016-03-07 20:00 | 629 | 629
2016-03-07 20:30 | 609 | 609
2016-03-07 21:00 | 591 | 591
2016-03-07 21:30 | 677 | 677
2016-03-07 22:00 | 682 | 682
2016-03-07 22:30 | 653 | 653
2016-03-07 23:00 | 632 | 632
2016-03-07 23:30 | 571 | 571
2016-03-08 | 579 | 579
2016-03-08 00:30 | 566 | 566
2016-03-08 01:00 | 558 | 557
2016-03-08 01:30 | 547 | 546
2016-03-08 02:00 | 535 | 534
2016-03-08 02:30 | 531 | 530
2016-03-08 03:00 | 530 | 528
2016-03-08 03:30 | 528 | 527
2016-03-08 04:00 | 532 | 530
2016-03-08 04:30 | 529 | 527
2016-03-08 05:00 | 532 | 531
2016-03-08 05:30 | 545 | 544
2016-03-08 06:00 | 556 | 555
2016-03-08 06:30 | 589 | 588
2016-03-08 07:00 | 618 | 618
2016-03-08 07:30 | 659 | 659
2016-03-08 08:00 | 675 | 675
2016-03-08 08:30 | 689 | 689
2016-03-08 09:00 | 690 | 690
2016-03-08 09:30 | 683 | 683
2016-03-08 10:00 | 648 | 648
2016-03-08 10:30 | 647 | 647
2016-03-08 11:00 | 653 | 653
2016-03-08 11:30 | 657 | 657
2016-03-08 12:00 | 662 | 662
2016-03-08 12:30 | 662 | 662
2016-03-08 13:00 | 673 | 673
2016-03-08 13:30 | 605 | 605
2016-03-08 14:00 | 569 | 568
2016-03-08 14:30 | 581 | 581
2016-03-08 15:00 | 526 | 525
2016-03-08 15:30 | 444 | 443
2016-03-08 16:00 | 513 | 511
2016-03-08 16:30 | 561 | 560
2016-03-08 17:00 | 578 | 578
2016-03-08 17:30 | 576 | 576
2016-03-08 18:00 | 576 | 575
2016-03-08 18:30 | 590 | 590
2016-03-08 19:00 | 643 | 643
2016-03-08 19:30 | 655 | 655
2016-03-08 20:00 | 694 | 694
2016-03-08 20:30 | 661 | 661
2016-03-08 21:00 | 655 | 655
2016-03-08 21:30 | 692 | 692
2016-03-08 22:00 | 679 | 679
2016-03-08 22:30 | 655 | 655
2016-03-08 23:00 | 625 | 625
2016-03-08 23:30 | 605 | 605
2016-03-09 | 589 | 589
2016-03-09 00:30 | 573 | 573
2016-03-09 01:00 | 561 | 560
2016-03-09 01:30 | 552 | 551
2016-03-09 02:00 | 546 | 545
2016-03-09 02:30 | 530 | 529
2016-03-09 03:00 | 533 | 532
2016-03-09 03:30 | 531 | 529
2016-03-09 04:00 | 527 | 526
2016-03-09 04:30 | 530 | 529
2016-03-09 05:00 | 539 | 538
2016-03-09 05:30 | 552 | 551
2016-03-09 06:00 | 572 | 571
2016-03-09 06:30 | 600 | 600
2016-03-09 07:00 | 623 | 623
2016-03-09 07:30 | 656 | 656
2016-03-09 08:00 | 679 | 679
2016-03-09 08:30 | 692 | 692
2016-03-09 09:00 | 700 | 700
2016-03-09 09:30 | 691 | 691
2016-03-09 10:00 | 659 | 659
2016-03-09 10:30 | 647 | 647
2016-03-09 11:00 | 644 | 644
2016-03-09 11:30 | 651 | 651
2016-03-09 12:00 | 650 | 650
2016-03-09 12:30 | 622 | 622
2016-03-09 13:00 | 633 | 633
2016-03-09 13:30 | 637 | 637
2016-03-09 14:00 | 638 | 638
2016-03-09 14:30 | 612 | 612
2016-03-09 15:00 | 437 | 437
2016-03-09 15:30 | 373 | 370
2016-03-09 16:00 | 361 | 356
2016-03-09 16:30 | 328 | 322
2016-03-09 17:00 | 480 | 475
2016-03-09 17:30 | 491 | 489
2016-03-09 18:00 | 540 | 539
2016-03-09 18:30 | 558 | 558
2016-03-09 19:00 | 579 | 578
2016-03-09 19:30 | 629 | 629
2016-03-09 20:00 | 669 | 669
2016-03-09 20:30 | 750 | 750
2016-03-09 21:00 | 741 | 740
2016-03-09 21:30 | 721 | 720
2016-03-09 22:00 | 690 | 690
2016-03-09 22:30 | 664 | 664
2016-03-09 23:00 | 641 | 641
2016-03-09 23:30 | 613 | 613
2016-03-10 | 593 | 592
2016-03-10 00:30 | 578 | 578
2016-03-10 01:00 | 562 | 562
2016-03-10 01:30 | 554 | 554
2016-03-10 02:00 | 552 | 552
2016-03-10 02:30 | 549 | 549
2016-03-10 03:00 | 539 | 539
2016-03-10 03:30 | 539 | 539
2016-03-10 04:00 | 538 | 537
2016-03-10 04:30 | 541 | 541
2016-03-10 05:00 | 545 | 544
2016-03-10 05:30 | 561 | 561
2016-03-10 06:00 | 577 | 577
2016-03-10 06:30 | 608 | 607
2016-03-10 07:00 | 634 | 634
2016-03-10 07:30 | 677 | 677
2016-03-10 08:00 | 697 | 697
2016-03-10 08:30 | 705 | 705
2016-03-10 09:00 | 704 | 703
2016-03-10 09:30 | 692 | 691
2016-03-10 10:00 | 672 | 671
2016-03-10 10:30 | 666 | 666
2016-03-10 11:00 | 653 | 653
2016-03-10 11:30 | 650 | 650
2016-03-10 12:00 | 656 | 656
2016-03-10 12:30 | 659 | 659
2016-03-10 13:00 | 663 | 663
2016-03-10 13:30 | 672 | 672
2016-03-10 14:00 | 689 | 689
2016-03-10 14:30 | 625 | 625
2016-03-10 15:00 | 598 | 598
2016-03-10 15:30 | 634 | 634
2016-03-10 16:00 | 650 | 650
2016-03-10 16:30 | 588 | 588
2016-03-10 17:00 | 580 | 580
2016-03-10 17:30 | 577 | 577
2016-03-10 18:00 | 585 | 585
2016-03-10 18:30 | 594 | 594
2016-03-10 19:00 | 616 | 616
2016-03-10 19:30 | 617 | 617
2016-03-10 20:00 | 661 | 661
2016-03-10 20:30 | 652 | 652
2016-03-10 21:00 | 700 | 700
2016-03-10 21:30 | 682 | 682
2016-03-10 22:00 | 655 | 655
2016-03-10 22:30 | 653 | 653
2016-03-10 23:00 | 626 | 626
2016-03-10 23:30 | 601 | 601
2016-03-11 | 583 | 583
2016-03-11 00:30 | 566 | 566
2016-03-11 01:00 | 550 | 550
2016-03-11 01:30 | 539 | 538
2016-03-11 02:00 | 537 | 536
2016-03-11 02:30 | 535 | 535
2016-03-11 03:00 | 530 | 529
2016-03-11 03:30 | 529 | 528
2016-03-11 04:00 | 526 | 525
2016-03-11 04:30 | 522 | 522
2016-03-11 05:00 | 529 | 529
2016-03-11 05:30 | 543 | 542
2016-03-11 06:00 | 559 | 558
2016-03-11 06:30 | 594 | 593
2016-03-11 07:00 | 618 | 618
2016-03-11 07:30 | 652 | 652
2016-03-11 08:00 | 671 | 671
2016-03-11 08:30 | 679 | 679
2016-03-11 09:00 | 681 | 680
2016-03-11 09:30 | 675 | 675
2016-03-11 10:00 | 656 | 656
2016-03-11 10:30 | 651 | 651
2016-03-11 11:00 | 655 | 655
2016-03-11 11:30 | 598 | 598
2016-03-11 12:00 | 529 | 529
2016-03-11 12:30 | 526 | 526
2016-03-11 13:00 | 522 | 522
2016-03-11 13:30 | 521 | 521
2016-03-11 14:00 | 537 | 537
2016-03-11 14:30 | 504 | 504
2016-03-11 15:00 | 424 | 424
2016-03-11 15:30 | 428 | 427
2016-03-11 16:00 | 457 | 456
2016-03-11 16:30 | 510 | 509
2016-03-11 17:00 | 529 | 529
2016-03-11 17:30 | 550 | 550
2016-03-11 18:00 | 561 | 561
2016-03-11 18:30 | 561 | 561
2016-03-11 19:00 | 579 | 579
2016-03-11 19:30 | 589 | 589
2016-03-11 20:00 | 633 | 633
2016-03-11 20:30 | 627 | 626
2016-03-11 21:00 | 675 | 675
2016-03-11 21:30 | 662 | 662
2016-03-11 22:00 | 642 | 641
2016-03-11 22:30 | 621 | 621
2016-03-11 23:00 | 598 | 598
2016-03-11 23:30 | 578 | 578
2016-03-12 | 565 | 565
2016-03-12 00:30 | 569 | 569
2016-03-12 01:00 | 557 | 557
2016-03-12 01:30 | 544 | 544
2016-03-12 02:00 | 535 | 535
2016-03-12 02:30 | 528 | 528
2016-03-12 03:00 | 520 | 520
2016-03-12 03:30 | 516 | 515
2016-03-12 04:00 | 513 | 513
2016-03-12 04:30 | 516 | 515
2016-03-12 05:00 | 511 | 511
2016-03-12 05:30 | 518 | 517
2016-03-12 06:00 | 515 | 515
2016-03-12 06:30 | 528 | 528
2016-03-12 07:00 | 538 | 537
2016-03-12 07:30 | 555 | 555
2016-03-12 08:00 | 572 | 572
2016-03-12 08:30 | 595 | 595
2016-03-12 09:00 | 556 | 556
2016-03-12 09:30 | 529 | 529
2016-03-12 10:00 | 502 | 502
2016-03-12 10:30 | 505 | 505
2016-03-12 11:00 | 502 | 501
2016-03-12 11:30 | 516 | 516
2016-03-12 12:00 | 524 | 524
2016-03-12 12:30 | 516 | 516
2016-03-12 13:00 | 506 | 505
2016-03-12 13:30 | 506 | 506
2016-03-12 14:00 | 473 | 473
2016-03-12 14:30 | 473 | 473
2016-03-12 15:00 | 476 | 475
2016-03-12 15:30 | 482 | 482
2016-03-12 16:00 | 498 | 498
2016-03-12 16:30 | 499 | 499
2016-03-12 17:00 | 511 | 511
2016-03-12 17:30 | 519 | 519
2016-03-12 18:00 | 519 | 519
2016-03-12 18:30 | 586 | 586
2016-03-12 19:00 | 565 | 565
2016-03-12 19:30 | 665 | 665
2016-03-12 20:00 | 686 | 685
2016-03-12 20:30 | 665 | 664
2016-03-12 21:00 | 650 | 650
2016-03-12 21:30 | 632 | 632
2016-03-12 22:00 | 614 | 614
2016-03-12 22:30 | 613 | 613
2016-03-12 23:00 | 591 | 591
2016-03-12 23:30 | 570 | 570
2016-03-13 | 557 | 557
2016-03-13 00:30 | 546 | 546
2016-03-13 01:00 | 533 | 533
2016-03-13 01:30 | 516 | 516
2016-03-13 02:00 | 513 | 513
2016-03-13 02:30 | 510 | 510
2016-03-13 03:00 | 500 | 500
2016-03-13 03:30 | 496 | 496
2016-03-13 04:00 | 494 | 493
2016-03-13 04:30 | 494 | 494
2016-03-13 05:00 | 492 | 491
2016-03-13 05:30 | 495 | 495
2016-03-13 06:00 | 498 | 498
2016-03-13 06:30 | 499 | 499
2016-03-13 07:00 | 501 | 501
2016-03-13 07:30 | 515 | 514
2016-03-13 08:00 | 528 | 528
2016-03-13 08:30 | 552 | 552
2016-03-13 09:00 | 565 | 565
2016-03-13 09:30 | 565 | 564
2016-03-13 10:00 | 556 | 556
2016-03-13 10:30 | 556 | 555
2016-03-13 11:00 | 562 | 562
2016-03-13 11:30 | 572 | 572
2016-03-13 12:00 | 583 | 583
2016-03-13 12:30 | 593 | 593
2016-03-13 13:00 | 598 | 598
2016-03-13 13:30 | 598 | 597
2016-03-13 14:00 | 623 | 623
2016-03-13 14:30 | 632 | 632
2016-03-13 15:00 | 641 | 640
2016-03-13 15:30 | 652 | 651
2016-03-13 16:00 | 669 | 668
2016-03-13 16:30 | 669 | 668
2016-03-13 17:00 | 672 | 672
2016-03-13 17:30 | 696 | 696
2016-03-13 18:00 | 712 | 712
2016-03-13 18:30 | 721 | 720
2016-03-13 19:00 | 666 | 665
2016-03-13 19:30 | 706 | 706
2016-03-13 20:00 | 726 | 726
2016-03-13 20:30 | 706 | 705
2016-03-13 21:00 | 689 | 689
2016-03-13 21:30 | 668 | 668
2016-03-13 22:00 | 644 | 643
2016-03-13 22:30 | 639 | 639
2016-03-13 23:00 | 618 | 617
2016-03-13 23:30 | 592 | 592
2016-03-14 | 571 | 571
2016-03-14 00:30 | 555 | 555
2016-03-14 01:00 | 545 | 545
2016-03-14 01:30 | 531 | 531
2016-03-14 02:00 | 527 | 527
2016-03-14 02:30 | 519 | 519
2016-03-14 03:00 | 515 | 515
2016-03-14 03:30 | 512 | 512
2016-03-14 04:00 | 507 | 507
2016-03-14 04:30 | 507 | 507
2016-03-14 05:00 | 510 | 510
2016-03-14 05:30 | 527 | 527
2016-03-14 06:00 | 549 | 549
2016-03-14 06:30 | 575 | 575
2016-03-14 07:00 | 609 | 609
2016-03-14 07:30 | 650 | 650
2016-03-14 08:00 | 675 | 675
2016-03-14 08:30 | 684 | 684
2016-03-14 09:00 | 690 | 690
2016-03-14 09:30 | 685 | 685
2016-03-14 10:00 | 669 | 668
2016-03-14 10:30 | 668 | 667
2016-03-14 11:00 | 677 | 677
2016-03-14 11:30 | 684 | 683
2016-03-14 12:00 | 636 | 636
2016-03-14 12:30 | 619 | 618
2016-03-14 13:00 | 586 | 586
2016-03-14 13:30 | 594 | 593
2016-03-14 14:00 | 592 | 592
2016-03-14 14:30 | 639 | 638
2016-03-14 15:00 | 672 | 672
2016-03-14 15:30 | 616 | 615
2016-03-14 16:00 | 622 | 622
2016-03-14 16:30 | 620 | 620
2016-03-14 17:00 | 628 | 628
2016-03-14 17:30 | 549 | 549
2016-03-14 18:00 | 594 | 594
2016-03-14 18:30 | 624 | 624
2016-03-14 19:00 | 598 | 598
2016-03-14 19:30 | 623 | 623
2016-03-14 20:00 | 640 | 640
2016-03-14 20:30 | 622 | 621
2016-03-14 21:00 | 654 | 654
2016-03-14 21:30 | 633 | 633
2016-03-14 22:00 | 603 | 603
2016-03-14 22:30 | 591 | 591
2016-03-14 23:00 | 560 | 560
2016-03-14 23:30 | 591 | 591
2016-03-15 | 590 | 590
2016-03-15 00:30 | 573 | 573
2016-03-15 01:00 | 558 | 558
2016-03-15 01:30 | 543 | 543
2016-03-15 02:00 | 537 | 537
2016-03-15 02:30 | 535 | 534
2016-03-15 03:00 | 533 | 533
2016-03-15 03:30 | 531 | 531
2016-03-15 04:00 | 530 | 530
2016-03-15 04:30 | 531 | 531
2016-03-15 05:00 | 535 | 535
2016-03-15 05:30 | 551 | 551
2016-03-15 06:00 | 564 | 564
2016-03-15 06:30 | 446 | 446
2016-03-15 07:00 | 499 | 499
2016-03-15 07:30 | 640 | 640
2016-03-15 08:00 | 671 | 671
2016-03-15 08:30 | 674 | 673
2016-03-15 09:00 | 643 | 642
2016-03-15 09:30 | 665 | 665
2016-03-15 10:00 | 652 | 652
2016-03-15 10:30 | 657 | 657
2016-03-15 11:00 | 658 | 658
2016-03-15 11:30 | 653 | 653
2016-03-15 12:00 | 674 | 673
2016-03-15 12:30 | 682 | 682
2016-03-15 13:00 | 688 | 687
2016-03-15 13:30 | 677 | 676
2016-03-15 14:00 | 692 | 691
2016-03-15 14:30 | 632 | 631
2016-03-15 15:00 | 639 | 638
2016-03-15 15:30 | 587 | 586
2016-03-15 16:00 | 595 | 595
2016-03-15 16:30 | 591 | 591
2016-03-15 17:00 | 588 | 588
2016-03-15 17:30 | 584 | 584
2016-03-15 18:00 | 583 | 583
2016-03-15 18:30 | 596 | 596
2016-03-15 19:00 | 621 | 621
2016-03-15 19:30 | 619 | 619
2016-03-15 20:00 | 606 | 606
2016-03-15 20:30 | 638 | 638
2016-03-15 21:00 | 694 | 694
2016-03-15 21:30 | 680 | 679
2016-03-15 22:00 | 650 | 649
2016-03-15 22:30 | 644 | 643
2016-03-15 23:00 | 594 | 593
2016-03-15 23:30 | 593 | 593
2016-03-16 | 578 | 578
2016-03-16 00:30 | 559 | 559
2016-03-16 01:00 | 548 | 548
2016-03-16 01:30 | 539 | 539
2016-03-16 02:00 | 537 | 537
2016-03-16 02:30 | 531 | 531
2016-03-16 03:00 | 527 | 527
2016-03-16 03:30 | 525 | 525
2016-03-16 04:00 | 527 | 527
2016-03-16 04:30 | 529 | 529
2016-03-16 05:00 | 534 | 534
2016-03-16 05:30 | 545 | 545
2016-03-16 06:00 | 565 | 565
2016-03-16 06:30 | 589 | 589
2016-03-16 07:00 | 541 | 540
2016-03-16 07:30 | 621 | 621
2016-03-16 08:00 | 656 | 656
2016-03-16 08:30 | 674 | 673
2016-03-16 09:00 | 636 | 636
2016-03-16 09:30 | 639 | 639
2016-03-16 10:00 | 629 | 628
2016-03-16 10:30 | 578 | 577
2016-03-16 11:00 | 533 | 532
2016-03-16 11:30 | 527 | 527
2016-03-16 12:00 | 548 | 548
2016-03-16 12:30 | 525 | 525
2016-03-16 13:00 | 484 | 484
2016-03-16 13:30 | 452 | 452
2016-03-16 14:00 | 314 | 314
2016-03-16 14:30 | 424 | 421
2016-03-16 15:00 | 545 | 545
2016-03-16 15:30 | 544 | 544
2016-03-16 16:00 | 482 | 482
2016-03-16 16:30 | 474 | 474
2016-03-16 17:00 | 522 | 522
2016-03-16 17:30 | 573 | 573
2016-03-16 18:00 | 603 | 603
2016-03-16 18:30 | 614 | 614
2016-03-16 19:00 | 568 | 568
2016-03-16 19:30 | 571 | 571
2016-03-16 20:00 | 605 | 604
2016-03-16 20:30 | 589 | 589
2016-03-16 21:00 | 637 | 637
2016-03-16 21:30 | 627 | 627
2016-03-16 22:00 | 598 | 597
2016-03-16 22:30 | 599 | 599
2016-03-16 23:00 | 585 | 585
2016-03-16 23:30 | 566 | 565
2016-03-17 | 548 | 548
2016-03-17 00:30 | 535 | 535
2016-03-17 01:00 | 527 | 527
2016-03-17 01:30 | 516 | 516
2016-03-17 02:00 | 504 | 504
2016-03-17 02:30 | 502 | 502
2016-03-17 03:00 | 497 | 497
2016-03-17 03:30 | 497 | 497
2016-03-17 04:00 | 496 | 495
2016-03-17 04:30 | 497 | 497
2016-03-17 05:00 | 503 | 503
2016-03-17 05:30 | 519 | 519
2016-03-17 06:00 | 539 | 538
2016-03-17 06:30 | 569 | 569
2016-03-17 07:00 | 597 | 597
2016-03-17 07:30 | 635 | 635
2016-03-17 08:00 | 654 | 654
2016-03-17 08:30 | 642 | 642
2016-03-17 09:00 | 662 | 662
2016-03-17 09:30 | 651 | 651
2016-03-17 10:00 | 613 | 613
2016-03-17 10:30 | 605 | 605
2016-03-17 11:00 | 577 | 577
2016-03-17 11:30 | 539 | 539
2016-03-17 12:00 | 517 | 517
2016-03-17 12:30 | 560 | 560
2016-03-17 13:00 | 577 | 577
2016-03-17 13:30 | 483 | 483
2016-03-17 14:00 | 438 | 438
2016-03-17 14:30 | 453 | 452
2016-03-17 15:00 | 493 | 492
2016-03-17 15:30 | 439 | 439
2016-03-17 16:00 | 434 | 433
2016-03-17 16:30 | 436 | 435
2016-03-17 17:00 | 440 | 439
2016-03-17 17:30 | 445 | 444
2016-03-17 18:00 | 455 | 454
2016-03-17 18:30 | 464 | 463
2016-03-17 19:00 | 439 | 439
2016-03-17 19:30 | 428 | 427
2016-03-17 20:00 | 458 | 457
2016-03-17 20:30 | 454 | 454
2016-03-17 21:00 | 439 | 439
2016-03-17 21:30 | 422 | 421
2016-03-17 22:00 | 400 | 399
2016-03-17 22:30 | 399 | 397
2016-03-17 23:00 | 412 | 411
2016-03-17 23:30 | 415 | 413
2016-03-18 | 468 | 466
2016-03-18 00:30 | 481 | 480
2016-03-18 01:00 | 469 | 469
2016-03-18 01:30 | 463 | 462
2016-03-18 02:00 | 460 | 459
2016-03-18 02:30 | 472 | 471
2016-03-18 03:00 | 472 | 471
2016-03-18 03:30 | 468 | 467
2016-03-18 04:00 | 471 | 470
2016-03-18 04:30 | 471 | 471
2016-03-18 05:00 | 477 | 476
2016-03-18 05:30 | 494 | 493
2016-03-18 06:00 | 513 | 513
2016-03-18 06:30 | 546 | 546
2016-03-18 07:00 | 572 | 572
2016-03-18 07:30 | 608 | 608
2016-03-18 08:00 | 632 | 632
2016-03-18 08:30 | 646 | 646
2016-03-18 09:00 | 642 | 642
2016-03-18 09:30 | 614 | 614
2016-03-18 10:00 | 598 | 598
2016-03-18 10:30 | 591 | 591
2016-03-18 11:00 | 586 | 586
2016-03-18 11:30 | 519 | 519
2016-03-18 12:00 | 499 | 499
2016-03-18 12:30 | 505 | 505
2016-03-18 13:00 | 538 | 538
2016-03-18 13:30 | 488 | 488
2016-03-18 14:00 | 493 | 493
2016-03-18 14:30 | 495 | 494
2016-03-18 15:00 | 497 | 496
2016-03-18 15:30 | 497 | 497
2016-03-18 16:00 | 507 | 507
2016-03-18 16:30 | 482 | 482
2016-03-18 17:00 | 446 | 446
2016-03-18 17:30 | 437 | 436
2016-03-18 18:00 | 484 | 483
2016-03-18 18:30 | 466 | 466
2016-03-18 19:00 | 483 | 482
2016-03-18 19:30 | 525 | 525
2016-03-18 20:00 | 512 | 512
2016-03-18 20:30 | 499 | 499
2016-03-18 21:00 | 537 | 537
2016-03-18 21:30 | 523 | 523
2016-03-18 22:00 | 506 | 506
2016-03-18 22:30 | 433 | 432
2016-03-18 23:00 | 471 | 470
2016-03-18 23:30 | 478 | 478
2016-03-19 | 470 | 470
2016-03-19 00:30 | 521 | 521
2016-03-19 01:00 | 520 | 520
2016-03-19 01:30 | 512 | 512
2016-03-19 02:00 | 506 | 506
2016-03-19 02:30 | 496 | 496
2016-03-19 03:00 | 493 | 493
2016-03-19 03:30 | 493 | 492
2016-03-19 04:00 | 483 | 483
2016-03-19 04:30 | 487 | 487
2016-03-19 05:00 | 486 | 486
2016-03-19 05:30 | 490 | 489
2016-03-19 06:00 | 498 | 497
2016-03-19 06:30 | 507 | 507
2016-03-19 07:00 | 514 | 514
2016-03-19 07:30 | 541 | 541
2016-03-19 08:00 | 558 | 558
2016-03-19 08:30 | 568 | 568
2016-03-19 09:00 | 581 | 581
2016-03-19 09:30 | 555 | 555
2016-03-19 10:00 | 557 | 557
2016-03-19 10:30 | 557 | 557
2016-03-19 11:00 | 565 | 565
2016-03-19 11:30 | 570 | 570
2016-03-19 12:00 | 578 | 578
2016-03-19 12:30 | 544 | 544
2016-03-19 13:00 | 447 | 446
2016-03-19 13:30 | 472 | 471
2016-03-19 14:00 | 460 | 459
2016-03-19 14:30 | 504 | 503
2016-03-19 15:00 | 524 | 524
2016-03-19 15:30 | 535 | 535
2016-03-19 16:00 | 549 | 549
2016-03-19 16:30 | 500 | 500
2016-03-19 17:00 | 505 | 505
2016-03-19 17:30 | 526 | 526
2016-03-19 18:00 | 565 | 564
2016-03-19 18:30 | 637 | 637
2016-03-19 19:00 | 668 | 667
2016-03-19 19:30 | 742 | 742
2016-03-19 20:00 | 735 | 734
2016-03-19 20:30 | 713 | 712
2016-03-19 21:00 | 696 | 695
2016-03-19 21:30 | 671 | 670
2016-03-19 22:00 | 648 | 648
2016-03-19 22:30 | 575 | 575
2016-03-19 23:00 | 554 | 553
2016-03-19 23:30 | 535 | 535
2016-03-20 | 545 | 545
2016-03-20 00:30 | 540 | 539
2016-03-20 01:00 | 528 | 528
2016-03-20 01:30 | 520 | 520
2016-03-20 02:00 | 513 | 512
2016-03-20 02:30 | 508 | 507
2016-03-20 03:00 | 500 | 499
2016-03-20 03:30 | 497 | 495
2016-03-20 04:00 | 501 | 500
2016-03-20 04:30 | 502 | 501
2016-03-20 05:00 | 497 | 496
2016-03-20 05:30 | 499 | 498
2016-03-20 06:00 | 499 | 498
2016-03-20 06:30 | 506 | 505
2016-03-20 07:00 | 507 | 505
2016-03-20 07:30 | 514 | 514
2016-03-20 08:00 | 529 | 528
2016-03-20 08:30 | 547 | 546
2016-03-20 09:00 | 558 | 558
2016-03-20 09:30 | 562 | 561
2016-03-20 10:00 | 549 | 548
2016-03-20 10:30 | 558 | 558
2016-03-20 11:00 | 572 | 572
2016-03-20 11:30 | 571 | 570
2016-03-20 12:00 | 581 | 581
2016-03-20 12:30 | 600 | 600
2016-03-20 13:00 | 611 | 611
2016-03-20 13:30 | 631 | 631
2016-03-20 14:00 | 659 | 659
2016-03-20 14:30 | 675 | 675
2016-03-20 15:00 | 688 | 688
2016-03-20 15:30 | 699 | 699
2016-03-20 16:00 | 710 | 710
2016-03-20 16:30 | 723 | 723
2016-03-20 17:00 | 735 | 735
2016-03-20 17:30 | 742 | 741
2016-03-20 18:00 | 701 | 701
2016-03-20 18:30 | 693 | 693
2016-03-20 19:00 | 693 | 693
2016-03-20 19:30 | 739 | 739
2016-03-20 20:00 | 716 | 716
2016-03-20 20:30 | 751 | 751
2016-03-20 21:00 | 736 | 736
2016-03-20 21:30 | 702 | 702
2016-03-20 22:00 | 676 | 676
2016-03-20 22:30 | 642 | 642
2016-03-20 23:00 | 616 | 616
2016-03-20 23:30 | 594 | 593
2016-03-21 | 583 | 582
2016-03-21 00:30 | 563 | 563
2016-03-21 01:00 | 550 | 549
2016-03-21 01:30 | 539 | 538
2016-03-21 02:00 | 532 | 531
2016-03-21 02:30 | 528 | 527
2016-03-21 03:00 | 519 | 518
2016-03-21 03:30 | 521 | 520
2016-03-21 04:00 | 521 | 520
2016-03-21 04:30 | 522 | 521
2016-03-21 05:00 | 526 | 525
2016-03-21 05:30 | 534 | 533
2016-03-21 06:00 | 546 | 545
2016-03-21 06:30 | 587 | 586
2016-03-21 07:00 | 616 | 616
2016-03-21 07:30 | 661 | 661
2016-03-21 08:00 | 712 | 712
2016-03-21 08:30 | 725 | 724
2016-03-21 09:00 | 683 | 682
2016-03-21 09:30 | 659 | 659
2016-03-21 10:00 | 699 | 699
2016-03-21 10:30 | 706 | 706
2016-03-21 11:00 | 712 | 712
2016-03-21 11:30 | 714 | 714
2016-03-21 12:00 | 722 | 722
2016-03-21 12:30 | 734 | 734
2016-03-21 13:00 | 737 | 736
2016-03-21 13:30 | 741 | 741
2016-03-21 14:00 | 731 | 731
2016-03-21 14:30 | 752 | 752
2016-03-21 15:00 | 785 | 784
2016-03-21 15:30 | 792 | 792
2016-03-21 16:00 | 806 | 805
2016-03-21 16:30 | 802 | 801
2016-03-21 17:00 | 750 | 750
2016-03-21 17:30 | 715 | 715
2016-03-21 18:00 | 743 | 743
2016-03-21 18:30 | 788 | 788
2016-03-21 19:00 | 784 | 784
2016-03-21 19:30 | 764 | 764
2016-03-21 20:00 | 768 | 768
2016-03-21 20:30 | 740 | 739
2016-03-21 21:00 | 721 | 721
2016-03-21 21:30 | 688 | 688
2016-03-21 22:00 | 650 | 650
2016-03-21 22:30 | 598 | 598
2016-03-21 23:00 | 551 | 551
2016-03-21 23:30 | 549 | 548
2016-03-22 | 558 | 557
2016-03-22 00:30 | 543 | 542
2016-03-22 01:00 | 533 | 532
2016-03-22 01:30 | 526 | 525
2016-03-22 02:00 | 516 | 514
2016-03-22 02:30 | 557 | 555
2016-03-22 03:00 | 555 | 554
2016-03-22 03:30 | 558 | 557
2016-03-22 04:00 | 556 | 555
2016-03-22 04:30 | 559 | 558
2016-03-22 05:00 | 564 | 563
2016-03-22 05:30 | 571 | 570
2016-03-22 06:00 | 575 | 574
2016-03-22 06:30 | 569 | 569
2016-03-22 07:00 | 566 | 565
2016-03-22 07:30 | 628 | 628
2016-03-22 08:00 | 670 | 670
2016-03-22 08:30 | 680 | 680
2016-03-22 09:00 | 690 | 690
2016-03-22 09:30 | 686 | 686
2016-03-22 10:00 | 666 | 666
2016-03-22 10:30 | 673 | 673
2016-03-22 11:00 | 677 | 677
2016-03-22 11:30 | 685 | 685
2016-03-22 12:00 | 699 | 699
2016-03-22 12:30 | 704 | 704
2016-03-22 13:00 | 713 | 713
2016-03-22 13:30 | 734 | 733
2016-03-22 14:00 | 758 | 758
2016-03-22 14:30 | 769 | 768
2016-03-22 15:00 | 778 | 777
2016-03-22 15:30 | 787 | 786
2016-03-22 16:00 | 808 | 807
2016-03-22 16:30 | 817 | 816
2016-03-22 17:00 | 822 | 822
2016-03-22 17:30 | 827 | 826
2016-03-22 18:00 | 822 | 822
2016-03-22 18:30 | 831 | 831
2016-03-22 19:00 | 800 | 800
2016-03-22 19:30 | 811 | 811
2016-03-22 20:00 | 839 | 839
2016-03-22 20:30 | 827 | 827
2016-03-22 21:00 | 803 | 803
2016-03-22 21:30 | 766 | 766
2016-03-22 22:00 | 730 | 730
2016-03-22 22:30 | 665 | 665
2016-03-22 23:00 | 601 | 601
2016-03-22 23:30 | 615 | 615
2016-03-23 | 611 | 610
2016-03-23 00:30 | 577 | 577
2016-03-23 01:00 | 580 | 580
2016-03-23 01:30 | 570 | 570
2016-03-23 02:00 | 559 | 559
2016-03-23 02:30 | 553 | 553
2016-03-23 03:00 | 548 | 548
2016-03-23 03:30 | 545 | 545
2016-03-23 04:00 | 543 | 543
2016-03-23 04:30 | 546 | 546
2016-03-23 05:00 | 543 | 543
2016-03-23 05:30 | 556 | 556
2016-03-23 06:00 | 575 | 575
2016-03-23 06:30 | 607 | 607
2016-03-23 07:00 | 645 | 645
2016-03-23 07:30 | 699 | 699
2016-03-23 08:00 | 729 | 728
2016-03-23 08:30 | 736 | 735
2016-03-23 09:00 | 739 | 739
2016-03-23 09:30 | 730 | 729
2016-03-23 10:00 | 690 | 689
2016-03-23 10:30 | 607 | 606
2016-03-23 11:00 | 619 | 619
2016-03-23 11:30 | 623 | 623
2016-03-23 12:00 | 624 | 624
2016-03-23 12:30 | 634 | 634
2016-03-23 13:00 | 634 | 634
2016-03-23 13:30 | 655 | 655
2016-03-23 14:00 | 680 | 680
2016-03-23 14:30 | 693 | 693
2016-03-23 15:00 | 694 | 694
2016-03-23 15:30 | 690 | 690
2016-03-23 16:00 | 702 | 702
2016-03-23 16:30 | 707 | 706
2016-03-23 17:00 | 646 | 646
2016-03-23 17:30 | 620 | 620
2016-03-23 18:00 | 622 | 622
2016-03-23 18:30 | 628 | 628
2016-03-23 19:00 | 656 | 656
2016-03-23 19:30 | 655 | 655
2016-03-23 20:00 | 640 | 640
2016-03-23 20:30 | 677 | 677
2016-03-23 21:00 | 666 | 666
2016-03-23 21:30 | 642 | 642
2016-03-23 22:00 | 604 | 604
2016-03-23 22:30 | 489 | 489
2016-03-23 23:00 | 494 | 494
2016-03-23 23:30 | 495 | 495
2016-03-24 | 476 | 476
2016-03-24 00:30 | 565 | 564
2016-03-24 01:00 | 580 | 580
2016-03-24 01:30 | 568 | 568
2016-03-24 02:00 | 558 | 558
2016-03-24 02:30 | 554 | 554
2016-03-24 03:00 | 543 | 543
2016-03-24 03:30 | 541 | 541
2016-03-24 04:00 | 538 | 538
2016-03-24 04:30 | 537 | 537
2016-03-24 05:00 | 544 | 544
2016-03-24 05:30 | 556 | 556
2016-03-24 06:00 | 580 | 580
2016-03-24 06:30 | 605 | 605
2016-03-24 07:00 | 576 | 576
2016-03-24 07:30 | 622 | 622
2016-03-24 08:00 | 687 | 687
2016-03-24 08:30 | 697 | 696
2016-03-24 09:00 | 688 | 688
2016-03-24 09:30 | 673 | 673
2016-03-24 10:00 | 667 | 667
2016-03-24 10:30 | 650 | 650
2016-03-24 11:00 | 652 | 652
2016-03-24 11:30 | 658 | 658
2016-03-24 12:00 | 621 | 621
2016-03-24 12:30 | 597 | 597
2016-03-24 13:00 | 602 | 602
2016-03-24 13:30 | 567 | 567
2016-03-24 14:00 | 587 | 587
2016-03-24 14:30 | 590 | 590
2016-03-24 15:00 | 586 | 586
2016-03-24 15:30 | 581 | 581
2016-03-24 16:00 | 576 | 576
2016-03-24 16:30 | 578 | 578
2016-03-24 17:00 | 582 | 582
2016-03-24 17:30 | 575 | 575
2016-03-24 18:00 | 582 | 582
2016-03-24 18:30 | 583 | 583
2016-03-24 19:00 | 607 | 607
2016-03-24 19:30 | 602 | 602
2016-03-24 20:00 | 597 | 597
2016-03-24 20:30 | 582 | 582
2016-03-24 21:00 | 567 | 567
2016-03-24 21:30 | 536 | 536
2016-03-24 22:00 | 512 | 512
2016-03-24 22:30 | 508 | 508
2016-03-24 23:00 | 493 | 492
2016-03-24 23:30 | 468 | 467
2016-03-25 | 443 | 442
2016-03-25 00:30 | 538 | 537
2016-03-25 01:00 | 553 | 552
2016-03-25 01:30 | 536 | 536
2016-03-25 02:00 | 527 | 527
2016-03-25 02:30 | 515 | 515
2016-03-25 03:00 | 515 | 514
2016-03-25 03:30 | 512 | 512
2016-03-25 04:00 | 508 | 508
2016-03-25 04:30 | 507 | 507
2016-03-25 05:00 | 508 | 508
2016-03-25 05:30 | 514 | 514
2016-03-25 06:00 | 516 | 516
2016-03-25 06:30 | 521 | 521
2016-03-25 07:00 | 523 | 522
2016-03-25 07:30 | 543 | 543
2016-03-25 08:00 | 551 | 551
2016-03-25 08:30 | 559 | 559
2016-03-25 09:00 | 562 | 562
2016-03-25 09:30 | 557 | 557
2016-03-25 10:00 | 547 | 547
2016-03-25 10:30 | 548 | 548
2016-03-25 11:00 | 551 | 551
2016-03-25 11:30 | 555 | 555
2016-03-25 12:00 | 559 | 559
2016-03-25 12:30 | 570 | 570
2016-03-25 13:00 | 562 | 562
2016-03-25 13:30 | 556 | 556
2016-03-25 14:00 | 575 | 575
2016-03-25 14:30 | 578 | 578
2016-03-25 15:00 | 585 | 585
2016-03-25 15:30 | 595 | 595
2016-03-25 16:00 | 608 | 608
2016-03-25 16:30 | 621 | 621
2016-03-25 17:00 | 634 | 634
2016-03-25 17:30 | 648 | 648
2016-03-25 18:00 | 659 | 659
2016-03-25 18:30 | 669 | 668
2016-03-25 19:00 | 694 | 694
2016-03-25 19:30 | 694 | 693
2016-03-25 20:00 | 675 | 674
2016-03-25 20:30 | 659 | 659
2016-03-25 21:00 | 635 | 635
2016-03-25 21:30 | 620 | 620
2016-03-25 22:00 | 610 | 610
2016-03-25 22:30 | 614 | 614
2016-03-25 23:00 | 592 | 592
2016-03-25 23:30 | 574 | 574
2016-03-26 | 557 | 557
2016-03-26 00:30 | 544 | 544
2016-03-26 01:00 | 530 | 530
2016-03-26 01:30 | 521 | 521
2016-03-26 02:00 | 515 | 515
2016-03-26 02:30 | 511 | 511
2016-03-26 03:00 | 502 | 501
2016-03-26 03:30 | 501 | 500
2016-03-26 04:00 | 501 | 501
2016-03-26 04:30 | 502 | 502
2016-03-26 05:00 | 501 | 501
2016-03-26 05:30 | 509 | 508
2016-03-26 06:00 | 505 | 505
2016-03-26 06:30 | 513 | 512
2016-03-26 07:00 | 517 | 517
2016-03-26 07:30 | 533 | 533
2016-03-26 08:00 | 546 | 546
2016-03-26 08:30 | 559 | 559
2016-03-26 09:00 | 566 | 566
2016-03-26 09:30 | 560 | 560
2016-03-26 10:00 | 543 | 543
2016-03-26 10:30 | 545 | 545
2016-03-26 11:00 | 542 | 542
2016-03-26 11:30 | 542 | 542
2016-03-26 12:00 | 543 | 543
2016-03-26 12:30 | 547 | 547
2016-03-26 13:00 | 546 | 546
2016-03-26 13:30 | 548 | 548
2016-03-26 14:00 | 567 | 567
2016-03-26 14:30 | 585 | 585
2016-03-26 15:00 | 599 | 599
2016-03-26 15:30 | 610 | 610
2016-03-26 16:00 | 618 | 618
2016-03-26 16:30 | 638 | 638
2016-03-26 17:00 | 657 | 657
2016-03-26 17:30 | 675 | 674
2016-03-26 18:00 | 682 | 682
2016-03-26 18:30 | 684 | 684
2016-03-26 19:00 | 699 | 698
2016-03-26 19:30 | 698 | 698
2016-03-26 20:00 | 683 | 683
2016-03-26 20:30 | 664 | 664
2016-03-26 21:00 | 647 | 647
2016-03-26 21:30 | 630 | 630
2016-03-26 22:00 | 619 | 619
2016-03-26 22:30 | 617 | 617
2016-03-26 23:00 | 598 | 598
2016-03-26 23:30 | 581 | 581
2016-03-27 | 569 | 569
2016-03-27 00:30 | 553 | 553
2016-03-27 01:00 | 538 | 538
2016-03-27 01:30 | 528 | 528
2016-03-27 02:00 | 521 | 521
2016-03-27 02:30 | 512 | 512
2016-03-27 03:00 | 506 | 506
2016-03-27 03:30 | 507 | 506
2016-03-27 04:00 | 505 | 505
2016-03-27 04:30 | 507 | 507
2016-03-27 05:00 | 504 | 504
2016-03-27 05:30 | 510 | 510
2016-03-27 06:00 | 513 | 512
2016-03-27 06:30 | 510 | 510
2016-03-27 07:00 | 513 | 512
2016-03-27 07:30 | 527 | 527
2016-03-27 08:00 | 536 | 536
2016-03-27 08:30 | 546 | 546
2016-03-27 09:00 | 555 | 555
2016-03-27 09:30 | 547 | 547
2016-03-27 10:00 | 536 | 536
2016-03-27 10:30 | 541 | 541
2016-03-27 11:00 | 542 | 542
2016-03-27 11:30 | 550 | 550
2016-03-27 12:00 | 551 | 551
2016-03-27 12:30 | 557 | 557
2016-03-27 13:00 | 562 | 562
2016-03-27 13:30 | 564 | 564
2016-03-27 14:00 | 584 | 584
2016-03-27 14:30 | 593 | 593
2016-03-27 15:00 | 603 | 603
2016-03-27 15:30 | 622 | 622
2016-03-27 16:00 | 636 | 636
2016-03-27 16:30 | 643 | 643
2016-03-27 17:00 | 650 | 650
2016-03-27 17:30 | 662 | 661
2016-03-27 18:00 | 676 | 676
2016-03-27 18:30 | 682 | 682
2016-03-27 19:00 | 705 | 705
2016-03-27 19:30 | 706 | 706
2016-03-27 20:00 | 693 | 693
2016-03-27 20:30 | 676 | 676
2016-03-27 21:00 | 665 | 665
2016-03-27 21:30 | 648 | 648
2016-03-27 22:00 | 628 | 628
2016-03-27 22:30 | 629 | 629
2016-03-27 23:00 | 616 | 616
2016-03-27 23:30 | 596 | 596
2016-03-28 | 577 | 577
2016-03-28 00:30 | 560 | 560
2016-03-28 01:00 | 550 | 550
2016-03-28 01:30 | 546 | 546
2016-03-28 02:00 | 535 | 535
2016-03-28 02:30 | 529 | 529
2016-03-28 03:00 | 523 | 523
2016-03-28 03:30 | 522 | 522
2016-03-28 04:00 | 524 | 524
2016-03-28 04:30 | 523 | 522
2016-03-28 05:00 | 521 | 520
2016-03-28 05:30 | 524 | 523
2016-03-28 06:00 | 523 | 523
2016-03-28 06:30 | 529 | 529
2016-03-28 07:00 | 539 | 538
2016-03-28 07:30 | 555 | 555
2016-03-28 08:00 | 568 | 568
2016-03-28 08:30 | 582 | 581
2016-03-28 09:00 | 587 | 587
2016-03-28 09:30 | 580 | 580
2016-03-28 10:00 | 569 | 569
2016-03-28 10:30 | 572 | 572
2016-03-28 11:00 | 576 | 576
2016-03-28 11:30 | 588 | 588
2016-03-28 12:00 | 596 | 596
2016-03-28 12:30 | 602 | 602
2016-03-28 13:00 | 604 | 604
2016-03-28 13:30 | 609 | 609
2016-03-28 14:00 | 627 | 627
2016-03-28 14:30 | 638 | 638
2016-03-28 15:00 | 646 | 646
2016-03-28 15:30 | 660 | 660
2016-03-28 16:00 | 672 | 671
2016-03-28 16:30 | 682 | 682
2016-03-28 17:00 | 698 | 698
2016-03-28 17:30 | 714 | 714
2016-03-28 18:00 | 725 | 725
2016-03-28 18:30 | 736 | 735
2016-03-28 19:00 | 741 | 741
2016-03-28 19:30 | 706 | 705
2016-03-28 20:00 | 736 | 736
2016-03-28 20:30 | 722 | 722
2016-03-28 21:00 | 696 | 695
2016-03-28 21:30 | 680 | 679
2016-03-28 22:00 | 653 | 653
2016-03-28 22:30 | 643 | 643
2016-03-28 23:00 | 619 | 619
2016-03-28 23:30 | 603 | 603
2016-03-29 | 588 | 588
2016-03-29 00:30 | 570 | 570
2016-03-29 01:00 | 557 | 557
2016-03-29 01:30 | 545 | 545
2016-03-29 02:00 | 539 | 539
2016-03-29 02:30 | 535 | 535
2016-03-29 03:00 | 533 | 532
2016-03-29 03:30 | 529 | 529
2016-03-29 04:00 | 522 | 522
2016-03-29 04:30 | 520 | 520
2016-03-29 05:00 | 523 | 522
2016-03-29 05:30 | 535 | 535
2016-03-29 06:00 | 550 | 550
2016-03-29 06:30 | 573 | 572
2016-03-29 07:00 | 598 | 597
2016-03-29 07:30 | 632 | 632
2016-03-29 08:00 | 656 | 656
2016-03-29 08:30 | 676 | 675
2016-03-29 09:00 | 683 | 683
2016-03-29 09:30 | 682 | 682
2016-03-29 10:00 | 666 | 666
2016-03-29 10:30 | 670 | 670
2016-03-29 11:00 | 673 | 673
2016-03-29 11:30 | 685 | 685
2016-03-29 12:00 | 686 | 686
2016-03-29 12:30 | 692 | 691
2016-03-29 13:00 | 693 | 692
2016-03-29 13:30 | 698 | 698
2016-03-29 14:00 | 722 | 722
2016-03-29 14:30 | 732 | 732
2016-03-29 15:00 | 732 | 732
2016-03-29 15:30 | 741 | 741
2016-03-29 16:00 | 752 | 751
2016-03-29 16:30 | 725 | 725
2016-03-29 17:00 | 629 | 629
2016-03-29 17:30 | 625 | 625
2016-03-29 18:00 | 617 | 617
2016-03-29 18:30 | 632 | 632
2016-03-29 19:00 | 663 | 663
2016-03-29 19:30 | 667 | 667
2016-03-29 20:00 | 665 | 665
2016-03-29 20:30 | 645 | 645
2016-03-29 21:00 | 618 | 618
2016-03-29 21:30 | 594 | 594
2016-03-29 22:00 | 568 | 568
2016-03-29 22:30 | 540 | 540
2016-03-29 23:00 | 509 | 509
2016-03-29 23:30 | 535 | 534
2016-03-30 | 540 | 540
2016-03-30 00:30 | 582 | 582
2016-03-30 01:00 | 582 | 581
2016-03-30 01:30 | 571 | 571
2016-03-30 02:00 | 554 | 553
2016-03-30 02:30 | 554 | 554
2016-03-30 03:00 | 548 | 547
2016-03-30 03:30 | 550 | 549
2016-03-30 04:00 | 547 | 547
2016-03-30 04:30 | 549 | 549
2016-03-30 05:00 | 547 | 546
2016-03-30 05:30 | 552 | 552
2016-03-30 06:00 | 564 | 564
2016-03-30 06:30 | 588 | 587
2016-03-30 07:00 | 613 | 612
2016-03-30 07:30 | 639 | 639
2016-03-30 08:00 | 659 | 659
2016-03-30 08:30 | 674 | 674
2016-03-30 09:00 | 682 | 682
2016-03-30 09:30 | 677 | 677
2016-03-30 10:00 | 663 | 663
2016-03-30 10:30 | 669 | 669
2016-03-30 11:00 | 668 | 668
2016-03-30 11:30 | 656 | 656
2016-03-30 12:00 | 624 | 624
2016-03-30 12:30 | 632 | 632
2016-03-30 13:00 | 633 | 633
2016-03-30 13:30 | 635 | 635
2016-03-30 14:00 | 651 | 651
2016-03-30 14:30 | 663 | 663
2016-03-30 15:00 | 682 | 682
2016-03-30 15:30 | 693 | 692
2016-03-30 16:00 | 684 | 683
2016-03-30 16:30 | 619 | 618
2016-03-30 17:00 | 560 | 559
2016-03-30 17:30 | 562 | 562
2016-03-30 18:00 | 559 | 559
2016-03-30 18:30 | 569 | 569
2016-03-30 19:00 | 595 | 595
2016-03-30 19:30 | 615 | 615
2016-03-30 20:00 | 606 | 606
2016-03-30 20:30 | 583 | 582
2016-03-30 21:00 | 558 | 558
2016-03-30 21:30 | 533 | 533
2016-03-30 22:00 | 510 | 510
2016-03-30 22:30 | 477 | 477
2016-03-30 23:00 | 517 | 516
2016-03-30 23:30 | 513 | 513
2016-03-31 | 492 | 492
2016-03-31 00:30 | 475 | 475
2016-03-31 01:00 | 453 | 452
2016-03-31 01:30 | 436 | 435
2016-03-31 02:00 | 428 | 427
2016-03-31 02:30 | 427 | 424
2016-03-31 03:00 | 434 | 431
2016-03-31 03:30 | 436 | 433
2016-03-31 04:00 | 428 | 426
2016-03-31 04:30 | 426 | 423
2016-03-31 05:00 | 425 | 423
2016-03-31 05:30 | 435 | 432
2016-03-31 06:00 | 458 | 455
2016-03-31 06:30 | 409 | 406
2016-03-31 07:00 | 409 | 405
2016-03-31 07:30 | 432 | 428
2016-03-31 08:00 | 450 | 448
2016-03-31 08:30 | 465 | 463
2016-03-31 09:00 | 478 | 476
2016-03-31 09:30 | 468 | 467
2016-03-31 10:00 | 451 | 450
2016-03-31 10:30 | 460 | 458
2016-03-31 11:00 | 458 | 457
2016-03-31 11:30 | 468 | 467
2016-03-31 12:00 | 473 | 472
2016-03-31 12:30 | 480 | 479
2016-03-31 13:00 | 478 | 477
2016-03-31 13:30 | 451 | 450
2016-03-31 14:00 | 502 | 501
2016-03-31 14:30 | 521 | 520
2016-03-31 15:00 | 527 | 526
2016-03-31 15:30 | 544 | 544
2016-03-31 16:00 | 551 | 551
2016-03-31 16:30 | 558 | 558
2016-03-31 17:00 | 560 | 560
2016-03-31 17:30 | 557 | 557
2016-03-31 18:00 | 563 | 563
2016-03-31 18:30 | 578 | 577
2016-03-31 19:00 | 602 | 602
2016-03-31 19:30 | 593 | 593
2016-03-31 20:00 | 578 | 578
2016-03-31 20:30 | 573 | 573
2016-03-31 21:00 | 555 | 555
2016-03-31 21:30 | 589 | 589
2016-03-31 22:00 | 592 | 592
2016-03-31 22:30 | 562 | 562
2016-03-31 23:00 | 536 | 536
2016-03-31 23:30 | 512 | 512
2016-04-01 | 498 | 497
2016-04-01 00:30 | 479 | 478
2016-04-01 01:00 | 462 | 460
2016-04-01 01:30 | 452 | 449
2016-04-01 02:00 | 446 | 444
2016-04-01 02:30 | 436 | 433
2016-04-01 03:00 | 433 | 430
2016-04-01 03:30 | 425 | 422
2016-04-01 04:00 | 426 | 423
2016-04-01 04:30 | 423 | 419
2016-04-01 05:00 | 431 | 428
2016-04-01 05:30 | 439 | 437
2016-04-01 06:00 | 453 | 451
2016-04-01 06:30 | 477 | 476
2016-04-01 07:00 | 432 | 430
2016-04-01 07:30 | 449 | 446
2016-04-01 08:00 | 466 | 465
2016-04-01 08:30 | 465 | 464
2016-04-01 09:00 | 487 | 486
2016-04-01 09:30 | 482 | 481
2016-04-01 10:00 | 470 | 469
2016-04-01 10:30 | 475 | 474
2016-04-01 11:00 | 482 | 481
2016-04-01 11:30 | 482 | 482
2016-04-01 12:00 | 481 | 481
2016-04-01 12:30 | 492 | 491
2016-04-01 13:00 | 495 | 494
2016-04-01 13:30 | 510 | 509
2016-04-01 14:00 | 525 | 525
2016-04-01 14:30 | 514 | 514
2016-04-01 15:00 | 518 | 518
2016-04-01 15:30 | 529 | 528
2016-04-01 16:00 | 540 | 540
2016-04-01 16:30 | 554 | 554
2016-04-01 17:00 | 562 | 562
2016-04-01 17:30 | 558 | 558
2016-04-01 18:00 | 549 | 549
2016-04-01 18:30 | 557 | 557
2016-04-01 19:00 | 580 | 580
2016-04-01 19:30 | 591 | 591
2016-04-01 20:00 | 579 | 579
2016-04-01 20:30 | 620 | 620
2016-04-01 21:00 | 659 | 659
2016-04-01 21:30 | 722 | 722
2016-04-01 22:00 | 721 | 721
2016-04-01 22:30 | 690 | 690
2016-04-01 23:00 | 658 | 658
2016-04-01 23:30 | 641 | 641
2016-04-02 | 625 | 625
2016-04-02 00:30 | 608 | 608
2016-04-02 01:00 | 592 | 592
2016-04-02 01:30 | 576 | 576
2016-04-02 02:00 | 567 | 567
2016-04-02 02:30 | 563 | 563
2016-04-02 03:00 | 555 | 555
2016-04-02 03:30 | 557 | 557
2016-04-02 04:00 | 552 | 552
2016-04-02 04:30 | 550 | 549
2016-04-02 05:00 | 542 | 542
2016-04-02 05:30 | 550 | 549
2016-04-02 06:00 | 561 | 560
2016-04-02 06:30 | 563 | 563
2016-04-02 07:00 | 569 | 569
2016-04-02 07:30 | 592 | 591
2016-04-02 08:00 | 612 | 612
2016-04-02 08:30 | 635 | 635
2016-04-02 09:00 | 648 | 648
2016-04-02 09:30 | 648 | 647
2016-04-02 10:00 | 633 | 633
2016-04-02 10:30 | 633 | 633
2016-04-02 11:00 | 637 | 637
2016-04-02 11:30 | 554 | 554
2016-04-02 12:00 | 491 | 491
2016-04-02 12:30 | 500 | 499
2016-04-02 13:00 | 507 | 507
2016-04-02 13:30 | 517 | 516
2016-04-02 14:00 | 540 | 539
2016-04-02 14:30 | 526 | 526
2016-04-02 15:00 | 524 | 524
2016-04-02 15:30 | 534 | 534
2016-04-02 16:00 | 555 | 555
2016-04-02 16:30 | 566 | 566
2016-04-02 17:00 | 578 | 578
2016-04-02 17:30 | 584 | 584
2016-04-02 18:00 | 588 | 588
2016-04-02 18:30 | 597 | 597
2016-04-02 19:00 | 612 | 612
2016-04-02 19:30 | 605 | 605
2016-04-02 20:00 | 586 | 586
2016-04-02 20:30 | 707 | 707
2016-04-02 21:00 | 731 | 728
2016-04-02 21:30 | 718 | 714
2016-04-02 22:00 | 697 | 694
2016-04-02 22:30 | 679 | 677
2016-04-02 23:00 | 655 | 653
2016-04-02 23:30 | 633 | 632
2016-04-03 | 613 | 613
2016-04-03 00:30 | 593 | 593
2016-04-03 01:00 | 576 | 576
2016-04-03 01:30 | 564 | 564
2016-04-03 02:00 | 555 | 554
2016-04-03 02:30 | 547 | 546
2016-04-03 03:00 | 545 | 544
2016-04-03 03:30 | 541 | 539
2016-04-03 04:00 | 532 | 530
2016-04-03 04:30 | 535 | 533
2016-04-03 05:00 | 535 | 533
2016-04-03 05:30 | 537 | 535
2016-04-03 06:00 | 539 | 537
2016-04-03 06:30 | 539 | 537
2016-04-03 07:00 | 541 | 540
2016-04-03 07:30 | 558 | 557
2016-04-03 08:00 | 569 | 568
2016-04-03 08:30 | 576 | 576
2016-04-03 09:00 | 581 | 581
2016-04-03 09:30 | 574 | 573
2016-04-03 10:00 | 561 | 561
2016-04-03 10:30 | 557 | 556
2016-04-03 11:00 | 544 | 543
2016-04-03 11:30 | 540 | 539
2016-04-03 12:00 | 544 | 543
2016-04-03 12:30 | 552 | 551
2016-04-03 13:00 | 565 | 564
2016-04-03 13:30 | 572 | 572
2016-04-03 14:00 | 578 | 578
2016-04-03 14:30 | 600 | 600
2016-04-03 15:00 | 628 | 628
2016-04-03 15:30 | 645 | 645
2016-04-03 16:00 | 657 | 657
2016-04-03 16:30 | 670 | 670
2016-04-03 17:00 | 687 | 687
2016-04-03 17:30 | 705 | 705
2016-04-03 18:00 | 720 | 719
2016-04-03 18:30 | 726 | 725
2016-04-03 19:00 | 770 | 769
2016-04-03 19:30 | 764 | 762
2016-04-03 20:00 | 743 | 742
2016-04-03 20:30 | 743 | 741
2016-04-03 21:00 | 727 | 726
2016-04-03 21:30 | 707 | 706
2016-04-03 22:00 | 678 | 677
2016-04-03 22:30 | 651 | 651
2016-04-03 23:00 | 622 | 622
2016-04-03 23:30 | 598 | 598
2016-04-04 | 587 | 587
2016-04-04 00:30 | 568 | 568
2016-04-04 01:00 | 554 | 554
2016-04-04 01:30 | 546 | 545
2016-04-04 02:00 | 536 | 536
2016-04-04 02:30 | 532 | 532
2016-04-04 03:00 | 529 | 528
2016-04-04 03:30 | 524 | 524
2016-04-04 04:00 | 524 | 523
2016-04-04 04:30 | 520 | 520
2016-04-04 05:00 | 527 | 527
2016-04-04 05:30 | 539 | 539
2016-04-04 06:00 | 557 | 557
2016-04-04 06:30 | 580 | 580
2016-04-04 07:00 | 605 | 605
2016-04-04 07:30 | 639 | 639
2016-04-04 08:00 | 660 | 659
2016-04-04 08:30 | 680 | 680
2016-04-04 09:00 | 682 | 682
2016-04-04 09:30 | 666 | 666
2016-04-04 10:00 | 647 | 647
2016-04-04 10:30 | 647 | 647
2016-04-04 11:00 | 656 | 656
2016-04-04 11:30 | 660 | 659
2016-04-04 12:00 | 664 | 663
2016-04-04 12:30 | 671 | 670
2016-04-04 13:00 | 680 | 680
2016-04-04 13:30 | 688 | 688
2016-04-04 14:00 | 715 | 715
2016-04-04 14:30 | 620 | 619
2016-04-04 15:00 | 564 | 564
2016-04-04 15:30 | 579 | 578
2016-04-04 16:00 | 592 | 592
2016-04-04 16:30 | 600 | 600
2016-04-04 17:00 | 610 | 610
2016-04-04 17:30 | 605 | 605
2016-04-04 18:00 | 607 | 607
2016-04-04 18:30 | 622 | 622
2016-04-04 19:00 | 649 | 649
2016-04-04 19:30 | 667 | 667
2016-04-04 20:00 | 650 | 650
2016-04-04 20:30 | 628 | 628
2016-04-04 21:00 | 719 | 719
2016-04-04 21:30 | 727 | 727
2016-04-04 22:00 | 704 | 704
2016-04-04 22:30 | 676 | 676
2016-04-04 23:00 | 646 | 646
2016-04-04 23:30 | 618 | 618
2016-04-05 | 599 | 599
2016-04-05 00:30 | 585 | 585
2016-04-05 01:00 | 573 | 573
2016-04-05 01:30 | 562 | 562
2016-04-05 02:00 | 549 | 549
2016-04-05 02:30 | 541 | 541
2016-04-05 03:00 | 534 | 534
2016-04-05 03:30 | 533 | 533
2016-04-05 04:00 | 533 | 533
2016-04-05 04:30 | 533 | 533
2016-04-05 05:00 | 538 | 538
2016-04-05 05:30 | 549 | 549
2016-04-05 06:00 | 565 | 565
2016-04-05 06:30 | 588 | 588
2016-04-05 07:00 | 609 | 609
2016-04-05 07:30 | 641 | 641
2016-04-05 08:00 | 660 | 660
2016-04-05 08:30 | 675 | 675
2016-04-05 09:00 | 679 | 679
2016-04-05 09:30 | 674 | 674
2016-04-05 10:00 | 660 | 660
2016-04-05 10:30 | 662 | 662
2016-04-05 11:00 | 663 | 663
2016-04-05 11:30 | 669 | 669
2016-04-05 12:00 | 674 | 674
2016-04-05 12:30 | 679 | 678
2016-04-05 13:00 | 684 | 684
2016-04-05 13:30 | 708 | 708
2016-04-05 14:00 | 732 | 732
2016-04-05 14:30 | 713 | 712
2016-04-05 15:00 | 712 | 711
2016-04-05 15:30 | 717 | 716
2016-04-05 16:00 | 601 | 600
2016-04-05 16:30 | 581 | 581
2016-04-05 17:00 | 591 | 591
2016-04-05 17:30 | 594 | 594
2016-04-05 18:00 | 593 | 593
2016-04-05 18:30 | 611 | 611
2016-04-05 19:00 | 635 | 635
2016-04-05 19:30 | 656 | 656
2016-04-05 20:00 | 644 | 643
2016-04-05 20:30 | 624 | 624
2016-04-05 21:00 | 713 | 713
2016-04-05 21:30 | 723 | 722
2016-04-05 22:00 | 702 | 702
2016-04-05 22:30 | 672 | 672
2016-04-05 23:00 | 649 | 649
2016-04-05 23:30 | 624 | 624
2016-04-06 | 604 | 604
2016-04-06 00:30 | 585 | 585
2016-04-06 01:00 | 568 | 568
2016-04-06 01:30 | 560 | 560
2016-04-06 02:00 | 555 | 555
2016-04-06 02:30 | 546 | 546
2016-04-06 03:00 | 540 | 540
2016-04-06 03:30 | 534 | 534
2016-04-06 04:00 | 532 | 532
2016-04-06 04:30 | 535 | 535
2016-04-06 05:00 | 538 | 537
2016-04-06 05:30 | 543 | 543
2016-04-06 06:00 | 562 | 562
2016-04-06 06:30 | 586 | 586
2016-04-06 07:00 | 609 | 609
2016-04-06 07:30 | 639 | 639
2016-04-06 08:00 | 660 | 660
2016-04-06 08:30 | 675 | 674
2016-04-06 09:00 | 681 | 681
2016-04-06 09:30 | 671 | 671
2016-04-06 10:00 | 652 | 651
2016-04-06 10:30 | 654 | 653
2016-04-06 11:00 | 655 | 655
2016-04-06 11:30 | 670 | 669
2016-04-06 12:00 | 675 | 674
2016-04-06 12:30 | 682 | 680
2016-04-06 13:00 | 691 | 690
2016-04-06 13:30 | 714 | 713
2016-04-06 14:00 | 736 | 735
2016-04-06 14:30 | 632 | 630
2016-04-06 15:00 | 577 | 576
2016-04-06 15:30 | 586 | 586
2016-04-06 16:00 | 599 | 598
2016-04-06 16:30 | 604 | 604
2016-04-06 17:00 | 615 | 614
2016-04-06 17:30 | 613 | 612
2016-04-06 18:00 | 612 | 611
2016-04-06 18:30 | 632 | 631
2016-04-06 19:00 | 655 | 654
2016-04-06 19:30 | 669 | 668
2016-04-06 20:00 | 664 | 663
2016-04-06 20:30 | 646 | 645
2016-04-06 21:00 | 618 | 617
2016-04-06 21:30 | 708 | 707
2016-04-06 22:00 | 723 | 721
2016-04-06 22:30 | 696 | 694
2016-04-06 23:00 | 666 | 664
2016-04-06 23:30 | 646 | 645
2016-04-07 | 629 | 628
2016-04-07 00:30 | 610 | 609
2016-04-07 01:00 | 593 | 592
2016-04-07 01:30 | 581 | 580
2016-04-07 02:00 | 572 | 571
2016-04-07 02:30 | 564 | 563
2016-04-07 03:00 | 562 | 562
2016-04-07 03:30 | 562 | 562
2016-04-07 04:00 | 556 | 556
2016-04-07 04:30 | 555 | 555
2016-04-07 05:00 | 553 | 553
2016-04-07 05:30 | 566 | 566
2016-04-07 06:00 | 584 | 584
2016-04-07 06:30 | 613 | 613
2016-04-07 07:00 | 635 | 635
2016-04-07 07:30 | 662 | 661
2016-04-07 08:00 | 693 | 693
2016-04-07 08:30 | 705 | 704
2016-04-07 09:00 | 717 | 716
2016-04-07 09:30 | 710 | 708
2016-04-07 10:00 | 675 | 674
2016-04-07 10:30 | 672 | 671
2016-04-07 11:00 | 686 | 684
2016-04-07 11:30 | 695 | 694
2016-04-07 12:00 | 686 | 685
2016-04-07 12:30 | 688 | 686
2016-04-07 13:00 | 695 | 693
2016-04-07 13:30 | 705 | 703
2016-04-07 14:00 | 725 | 723
2016-04-07 14:30 | 715 | 711
2016-04-07 15:00 | 713 | 710
2016-04-07 15:30 | 719 | 716
2016-04-07 16:00 | 726 | 723
2016-04-07 16:30 | 729 | 726
2016-04-07 17:00 | 738 | 735
2016-04-07 17:30 | 691 | 688
2016-04-07 18:00 | 620 | 617
2016-04-07 18:30 | 616 | 615
2016-04-07 19:00 | 639 | 638
2016-04-07 19:30 | 657 | 655
2016-04-07 20:00 | 642 | 640
2016-04-07 20:30 | 621 | 620
2016-04-07 21:00 | 719 | 718
2016-04-07 21:30 | 729 | 726
2016-04-07 22:00 | 715 | 713
2016-04-07 22:30 | 691 | 689
2016-04-07 23:00 | 666 | 664
2016-04-07 23:30 | 645 | 643
2016-04-08 | 622 | 620
2016-04-08 00:30 | 603 | 601
2016-04-08 01:00 | 584 | 583
2016-04-08 01:30 | 572 | 572
2016-04-08 02:00 | 564 | 564
2016-04-08 02:30 | 559 | 558
2016-04-08 03:00 | 552 | 552
2016-04-08 03:30 | 553 | 553
2016-04-08 04:00 | 549 | 549
2016-04-08 04:30 | 548 | 548
2016-04-08 05:00 | 554 | 554
2016-04-08 05:30 | 566 | 566
2016-04-08 06:00 | 585 | 585
2016-04-08 06:30 | 611 | 610
2016-04-08 07:00 | 627 | 627
2016-04-08 07:30 | 661 | 660
2016-04-08 08:00 | 669 | 667
2016-04-08 08:30 | 684 | 683
2016-04-08 09:00 | 690 | 688
2016-04-08 09:30 | 678 | 677
2016-04-08 10:00 | 642 | 641
2016-04-08 10:30 | 647 | 647
2016-04-08 11:00 | 642 | 641
2016-04-08 11:30 | 638 | 637
2016-04-08 12:00 | 602 | 601
2016-04-08 12:30 | 535 | 534
2016-04-08 13:00 | 555 | 555
2016-04-08 13:30 | 572 | 571
2016-04-08 14:00 | 589 | 589
2016-04-08 14:30 | 567 | 567
2016-04-08 15:00 | 492 | 492
2016-04-08 15:30 | 468 | 468
2016-04-08 16:00 | 462 | 462
2016-04-08 16:30 | 478 | 478
2016-04-08 17:00 | 451 | 451
2016-04-08 17:30 | 470 | 470
2016-04-08 18:00 | 479 | 479
2016-04-08 18:30 | 549 | 549
2016-04-08 19:00 | 527 | 527
2016-04-08 19:30 | 607 | 607
2016-04-08 20:00 | 647 | 647
2016-04-08 20:30 | 631 | 630
2016-04-08 21:00 | 601 | 601
2016-04-08 21:30 | 677 | 677
2016-04-08 22:00 | 669 | 668
2016-04-08 22:30 | 645 | 644
2016-04-08 23:00 | 625 | 624
2016-04-08 23:30 | 602 | 602
2016-04-09 | 588 | 588
2016-04-09 00:30 | 569 | 568
2016-04-09 01:00 | 549 | 548
2016-04-09 01:30 | 538 | 538
2016-04-09 02:00 | 531 | 531
2016-04-09 02:30 | 524 | 524
2016-04-09 03:00 | 521 | 521
2016-04-09 03:30 | 519 | 519
2016-04-09 04:00 | 515 | 515
2016-04-09 04:30 | 513 | 513
2016-04-09 05:00 | 510 | 510
2016-04-09 05:30 | 518 | 518
2016-04-09 06:00 | 525 | 525
2016-04-09 06:30 | 530 | 530
2016-04-09 07:00 | 540 | 540
2016-04-09 07:30 | 557 | 557
2016-04-09 08:00 | 578 | 578
2016-04-09 08:30 | 600 | 600
2016-04-09 09:00 | 614 | 614
2016-04-09 09:30 | 571 | 571
2016-04-09 10:00 | 523 | 523
2016-04-09 10:30 | 545 | 545
2016-04-09 11:00 | 556 | 556
2016-04-09 11:30 | 571 | 571
2016-04-09 12:00 | 574 | 574
2016-04-09 12:30 | 599 | 599
2016-04-09 13:00 | 611 | 611
2016-04-09 13:30 | 617 | 616
2016-04-09 14:00 | 630 | 630
2016-04-09 14:30 | 631 | 630
2016-04-09 15:00 | 628 | 627
2016-04-09 15:30 | 631 | 630
2016-04-09 16:00 | 637 | 636
2016-04-09 16:30 | 465 | 464
2016-04-09 17:00 | 396 | 395
2016-04-09 17:30 | 386 | 385
2016-04-09 18:00 | 384 | 384
2016-04-09 18:30 | 250 | 249
2016-04-09 19:00 | 262 | 259
2016-04-09 19:30 | 391 | 388
2016-04-09 20:00 | 420 | 419
2016-04-09 20:30 | 436 | 435
2016-04-09 21:00 | 522 | 521
2016-04-09 21:30 | 541 | 541
2016-04-09 22:00 | 538 | 538
2016-04-09 22:30 | 518 | 518
2016-04-09 23:00 | 449 | 449
2016-04-09 23:30 | 448 | 448
2016-04-10 | 469 | 469
2016-04-10 00:30 | 565 | 564
2016-04-10 01:00 | 566 | 566
2016-04-10 01:30 | 552 | 552
2016-04-10 02:00 | 540 | 540
2016-04-10 02:30 | 533 | 533
2016-04-10 03:00 | 529 | 529
2016-04-10 03:30 | 523 | 523
2016-04-10 04:00 | 522 | 522
2016-04-10 04:30 | 521 | 521
2016-04-10 05:00 | 525 | 525
2016-04-10 05:30 | 523 | 523
2016-04-10 06:00 | 530 | 530
2016-04-10 06:30 | 534 | 534
2016-04-10 07:00 | 540 | 540
2016-04-10 07:30 | 554 | 554
2016-04-10 08:00 | 568 | 568
2016-04-10 08:30 | 585 | 585
2016-04-10 09:00 | 597 | 597
2016-04-10 09:30 | 590 | 590
2016-04-10 10:00 | 580 | 580
2016-04-10 10:30 | 576 | 576
2016-04-10 11:00 | 577 | 577
2016-04-10 11:30 | 572 | 572
2016-04-10 12:00 | 591 | 591
2016-04-10 12:30 | 589 | 589
2016-04-10 13:00 | 580 | 580
2016-04-10 13:30 | 595 | 595
2016-04-10 14:00 | 620 | 620
2016-04-10 14:30 | 604 | 604
2016-04-10 15:00 | 607 | 607
2016-04-10 15:30 | 621 | 621
2016-04-10 16:00 | 634 | 634
2016-04-10 16:30 | 643 | 642
2016-04-10 17:00 | 652 | 651
2016-04-10 17:30 | 614 | 613
2016-04-10 18:00 | 444 | 444
2016-04-10 18:30 | 428 | 428
2016-04-10 19:00 | 468 | 468
2016-04-10 19:30 | 549 | 549
2016-04-10 20:00 | 522 | 522
2016-04-10 20:30 | 514 | 514
2016-04-10 21:00 | 579 | 579
2016-04-10 21:30 | 646 | 646
2016-04-10 22:00 | 605 | 605
2016-04-10 22:30 | 529 | 529
2016-04-10 23:00 | 510 | 510
2016-04-10 23:30 | 502 | 502
2016-04-11 | 578 | 578
2016-04-11 00:30 | 560 | 560
2016-04-11 01:00 | 546 | 546
2016-04-11 01:30 | 541 | 541
2016-04-11 02:00 | 533 | 533
2016-04-11 02:30 | 522 | 522
2016-04-11 03:00 | 522 | 522
2016-04-11 03:30 | 520 | 520
2016-04-11 04:00 | 520 | 520
2016-04-11 04:30 | 519 | 519
2016-04-11 05:00 | 526 | 526
2016-04-11 05:30 | 540 | 540
2016-04-11 06:00 | 563 | 563
2016-04-11 06:30 | 516 | 516
2016-04-11 07:00 | 499 | 499
2016-04-11 07:30 | 621 | 621
2016-04-11 08:00 | 680 | 680
2016-04-11 08:30 | 691 | 691
2016-04-11 09:00 | 689 | 688
2016-04-11 09:30 | 681 | 680
2016-04-11 10:00 | 663 | 663
2016-04-11 10:30 | 672 | 671
2016-04-11 11:00 | 678 | 678
2016-04-11 11:30 | 685 | 685
2016-04-11 12:00 | 686 | 686
2016-04-11 12:30 | 687 | 686
2016-04-11 13:00 | 692 | 691
2016-04-11 13:30 | 711 | 711
2016-04-11 14:00 | 683 | 683
2016-04-11 14:30 | 594 | 594
2016-04-11 15:00 | 591 | 591
2016-04-11 15:30 | 600 | 600
2016-04-11 16:00 | 622 | 622
2016-04-11 16:30 | 530 | 530
2016-04-11 17:00 | 385 | 385
2016-04-11 17:30 | 380 | 378
2016-04-11 18:00 | 380 | 378
2016-04-11 18:30 | 414 | 412
2016-04-11 19:00 | 378 | 377
2016-04-11 19:30 | 354 | 352
2016-04-11 20:00 | 339 | 337
2016-04-11 20:30 | 412 | 410
2016-04-11 21:00 | 514 | 513
2016-04-11 21:30 | 639 | 639
2016-04-11 22:00 | 644 | 643
2016-04-11 22:30 | 644 | 644
2016-04-11 23:00 | 624 | 624
2016-04-11 23:30 | 602 | 601
2016-04-12 | 584 | 584
2016-04-12 00:30 | 566 | 566
2016-04-12 01:00 | 552 | 552
2016-04-12 01:30 | 543 | 543
2016-04-12 02:00 | 540 | 540
2016-04-12 02:30 | 537 | 537
2016-04-12 03:00 | 530 | 530
2016-04-12 03:30 | 522 | 522
2016-04-12 04:00 | 519 | 519
2016-04-12 04:30 | 516 | 516
2016-04-12 05:00 | 518 | 518
2016-04-12 05:30 | 497 | 497
2016-04-12 06:00 | 501 | 500
2016-04-12 06:30 | 503 | 503
2016-04-12 07:00 | 530 | 530
2016-04-12 07:30 | 562 | 562
2016-04-12 08:00 | 579 | 579
2016-04-12 08:30 | 586 | 586
2016-04-12 09:00 | 585 | 584
2016-04-12 09:30 | 571 | 571
2016-04-12 10:00 | 549 | 549
2016-04-12 10:30 | 553 | 553
2016-04-12 11:00 | 562 | 562
2016-04-12 11:30 | 569 | 569
2016-04-12 12:00 | 579 | 579
2016-04-12 12:30 | 587 | 587
2016-04-12 13:00 | 592 | 592
2016-04-12 13:30 | 608 | 608
2016-04-12 14:00 | 631 | 631
2016-04-12 14:30 | 546 | 545
2016-04-12 15:00 | 492 | 492
2016-04-12 15:30 | 465 | 464
2016-04-12 16:00 | 440 | 440
2016-04-12 16:30 | 446 | 446
2016-04-12 17:00 | 448 | 448
2016-04-12 17:30 | 444 | 443
2016-04-12 18:00 | 384 | 384
2016-04-12 18:30 | 236 | 234
2016-04-12 19:00 | 270 | 265
2016-04-12 19:30 | 509 | 507
2016-04-12 20:00 | 511 | 511
2016-04-12 20:30 | 575 | 575
2016-04-12 21:00 | 565 | 565
2016-04-12 21:30 | 656 | 656
2016-04-12 22:00 | 666 | 665
2016-04-12 22:30 | 646 | 646
2016-04-12 23:00 | 627 | 627
2016-04-12 23:30 | 604 | 604
2016-04-13 | 581 | 581
2016-04-13 00:30 | 558 | 558
2016-04-13 01:00 | 545 | 545
2016-04-13 01:30 | 534 | 534
2016-04-13 02:00 | 527 | 527
2016-04-13 02:30 | 519 | 519
2016-04-13 03:00 | 517 | 517
2016-04-13 03:30 | 519 | 519
2016-04-13 04:00 | 513 | 513
2016-04-13 04:30 | 513 | 512
2016-04-13 05:00 | 517 | 517
2016-04-13 05:30 | 532 | 532
2016-04-13 06:00 | 555 | 555
2016-04-13 06:30 | 587 | 587
2016-04-13 07:00 | 617 | 617
2016-04-13 07:30 | 648 | 648
2016-04-13 08:00 | 665 | 664
2016-04-13 08:30 | 666 | 665
2016-04-13 09:00 | 665 | 665
2016-04-13 09:30 | 656 | 656
2016-04-13 10:00 | 635 | 635
2016-04-13 10:30 | 635 | 635
2016-04-13 11:00 | 641 | 640
2016-04-13 11:30 | 649 | 648
2016-04-13 12:00 | 658 | 658
2016-04-13 12:30 | 665 | 665
2016-04-13 13:00 | 671 | 671
2016-04-13 13:30 | 689 | 689
2016-04-13 14:00 | 711 | 710
2016-04-13 14:30 | 698 | 697
2016-04-13 15:00 | 702 | 701
2016-04-13 15:30 | 709 | 708
2016-04-13 16:00 | 697 | 697
2016-04-13 16:30 | 590 | 589
2016-04-13 17:00 | 497 | 497
2016-04-13 17:30 | 405 | 405
2016-04-13 18:00 | 337 | 336
2016-04-13 18:30 | 355 | 353
2016-04-13 19:00 | 379 | 377
2016-04-13 19:30 | 425 | 424
2016-04-13 20:00 | 417 | 416
2016-04-13 20:30 | 424 | 423
2016-04-13 21:00 | 428 | 427
2016-04-13 21:30 | 581 | 581
2016-04-13 22:00 | 649 | 648
2016-04-13 22:30 | 529 | 528
2016-04-13 23:00 | 507 | 507
2016-04-13 23:30 | 492 | 492
2016-04-14 | 490 | 490
2016-04-14 00:30 | 485 | 485
2016-04-14 01:00 | 543 | 543
2016-04-14 01:30 | 556 | 556
2016-04-14 02:00 | 546 | 546
2016-04-14 02:30 | 543 | 543
2016-04-14 03:00 | 541 | 541
2016-04-14 03:30 | 498 | 498
2016-04-14 04:00 | 531 | 531
2016-04-14 04:30 | 536 | 536
2016-04-14 05:00 | 542 | 542
2016-04-14 05:30 | 557 | 557
2016-04-14 06:00 | 578 | 578
2016-04-14 06:30 | 609 | 609
2016-04-14 07:00 | 562 | 562
2016-04-14 07:30 | 621 | 621
2016-04-14 08:00 | 656 | 656
2016-04-14 08:30 | 695 | 695
2016-04-14 09:00 | 696 | 695
2016-04-14 09:30 | 678 | 678
2016-04-14 10:00 | 666 | 665
2016-04-14 10:30 | 662 | 662
2016-04-14 11:00 | 660 | 659
2016-04-14 11:30 | 656 | 655
2016-04-14 12:00 | 625 | 624
2016-04-14 12:30 | 557 | 557
2016-04-14 13:00 | 523 | 523
2016-04-14 13:30 | 543 | 543
2016-04-14 14:00 | 657 | 657
2016-04-14 14:30 | 683 | 683
2016-04-14 15:00 | 678 | 677
2016-04-14 15:30 | 604 | 604
2016-04-14 16:00 | 525 | 525
2016-04-14 16:30 | 527 | 527
2016-04-14 17:00 | 437 | 437
2016-04-14 17:30 | 362 | 361
2016-04-14 18:00 | 186 | 183
2016-04-14 18:30 | 108 | 87
2016-04-14 19:00 | 139 | 107
2016-04-14 19:30 | 271 | 256
2016-04-14 20:00 | 333 | 326
2016-04-14 20:30 | 395 | 392
2016-04-14 21:00 | 452 | 451
2016-04-14 21:30 | 437 | 436
2016-04-14 22:00 | 432 | 432
2016-04-14 22:30 | 294 | 292
2016-04-14 23:00 | 256 | 251
2016-04-14 23:30 | 374 | 370
2016-04-15 | 380 | 378
2016-04-15 00:30 | 442 | 441
2016-04-15 01:00 | 524 | 523
2016-04-15 01:30 | 520 | 520
2016-04-15 02:00 | 510 | 510
2016-04-15 02:30 | 510 | 510
2016-04-15 03:00 | 506 | 506
2016-04-15 03:30 | 502 | 502
2016-04-15 04:00 | 496 | 496
2016-04-15 04:30 | 503 | 502
2016-04-15 05:00 | 511 | 511
2016-04-15 05:30 | 523 | 523
2016-04-15 06:00 | 541 | 541
2016-04-15 06:30 | 578 | 578
2016-04-15 07:00 | 568 | 568
2016-04-15 07:30 | 619 | 619
2016-04-15 08:00 | 653 | 653
2016-04-15 08:30 | 661 | 661
2016-04-15 09:00 | 657 | 657
2016-04-15 09:30 | 651 | 651
2016-04-15 10:00 | 630 | 630
2016-04-15 10:30 | 630 | 630
2016-04-15 11:00 | 642 | 642
2016-04-15 11:30 | 654 | 654
2016-04-15 12:00 | 654 | 654
2016-04-15 12:30 | 654 | 654
2016-04-15 13:00 | 653 | 653
2016-04-15 13:30 | 658 | 658
2016-04-15 14:00 | 664 | 663
2016-04-15 14:30 | 652 | 652
2016-04-15 15:00 | 640 | 640
2016-04-15 15:30 | 558 | 558
2016-04-15 16:00 | 602 | 602
2016-04-15 16:30 | 648 | 648
2016-04-15 17:00 | 652 | 652
2016-04-15 17:30 | 650 | 650
2016-04-15 18:00 | 642 | 642
2016-04-15 18:30 | 642 | 641
2016-04-15 19:00 | 653 | 653
2016-04-15 19:30 | 668 | 667
2016-04-15 20:00 | 668 | 668
2016-04-15 20:30 | 655 | 655
2016-04-15 21:00 | 649 | 649
2016-04-15 21:30 | 633 | 633
2016-04-15 22:00 | 641 | 641
2016-04-15 22:30 | 627 | 627
2016-04-15 23:00 | 612 | 612
2016-04-15 23:30 | 539 | 539
2016-04-16 | 488 | 488
2016-04-16 00:30 | 441 | 441
2016-04-16 01:00 | 508 | 507
2016-04-16 01:30 | 527 | 526
2016-04-16 02:00 | 515 | 515
2016-04-16 02:30 | 503 | 502
2016-04-16 03:00 | 499 | 499
2016-04-16 03:30 | 495 | 494
2016-04-16 04:00 | 490 | 490
2016-04-16 04:30 | 486 | 486
2016-04-16 05:00 | 424 | 424
2016-04-16 05:30 | 422 | 421
2016-04-16 06:00 | 435 | 434
2016-04-16 06:30 | 448 | 447
2016-04-16 07:00 | 457 | 456
2016-04-16 07:30 | 504 | 503
2016-04-16 08:00 | 528 | 527
2016-04-16 08:30 | 543 | 543
2016-04-16 09:00 | 558 | 558
2016-04-16 09:30 | 558 | 558
2016-04-16 10:00 | 551 | 551
2016-04-16 10:30 | 554 | 553
2016-04-16 11:00 | 558 | 558
2016-04-16 11:30 | 560 | 559
2016-04-16 12:00 | 556 | 556
2016-04-16 12:30 | 551 | 551
2016-04-16 13:00 | 554 | 554
2016-04-16 13:30 | 560 | 560
2016-04-16 14:00 | 550 | 550
2016-04-16 14:30 | 530 | 530
2016-04-16 15:00 | 541 | 541
2016-04-16 15:30 | 543 | 543
2016-04-16 16:00 | 545 | 545
2016-04-16 16:30 | 552 | 552
2016-04-16 17:00 | 571 | 571
2016-04-16 17:30 | 586 | 586
2016-04-16 18:00 | 592 | 592
2016-04-16 18:30 | 605 | 605
2016-04-16 19:00 | 616 | 616
2016-04-16 19:30 | 635 | 635
2016-04-16 20:00 | 631 | 631
2016-04-16 20:30 | 613 | 613
2016-04-16 21:00 | 597 | 597
2016-04-16 21:30 | 581 | 581
2016-04-16 22:00 | 578 | 578
2016-04-16 22:30 | 566 | 566
2016-04-16 23:00 | 576 | 576
2016-04-16 23:30 | 543 | 543
2016-04-17 | 555 | 555
2016-04-17 00:30 | 538 | 538
2016-04-17 01:00 | 523 | 523
2016-04-17 01:30 | 512 | 511
2016-04-17 02:00 | 502 | 501
2016-04-17 02:30 | 491 | 491
2016-04-17 03:00 | 490 | 489
2016-04-17 03:30 | 486 | 485
2016-04-17 04:00 | 482 | 481
2016-04-17 04:30 | 480 | 479
2016-04-17 05:00 | 477 | 476
2016-04-17 05:30 | 483 | 482
2016-04-17 06:00 | 486 | 485
2016-04-17 06:30 | 496 | 495
2016-04-17 07:00 | 501 | 500
2016-04-17 07:30 | 512 | 511
2016-04-17 08:00 | 530 | 529
2016-04-17 08:30 | 536 | 535
2016-04-17 09:00 | 548 | 548
2016-04-17 09:30 | 547 | 547
2016-04-17 10:00 | 538 | 538
2016-04-17 10:30 | 540 | 539
2016-04-17 11:00 | 545 | 545
2016-04-17 11:30 | 540 | 540
2016-04-17 12:00 | 546 | 546
2016-04-17 12:30 | 554 | 554
2016-04-17 13:00 | 559 | 559
2016-04-17 13:30 | 575 | 575
2016-04-17 14:00 | 598 | 598
2016-04-17 14:30 | 577 | 577
2016-04-17 15:00 | 579 | 579
2016-04-17 15:30 | 575 | 575
2016-04-17 16:00 | 590 | 590
2016-04-17 16:30 | 602 | 602
2016-04-17 17:00 | 535 | 535
2016-04-17 17:30 | 539 | 539
2016-04-17 18:00 | 519 | 519
2016-04-17 18:30 | 538 | 538
2016-04-17 19:00 | 589 | 589
2016-04-17 19:30 | 598 | 598
2016-04-17 20:00 | 584 | 584
2016-04-17 20:30 | 564 | 564
2016-04-17 21:00 | 626 | 626
2016-04-17 21:30 | 636 | 636
2016-04-17 22:00 | 625 | 625
2016-04-17 22:30 | 603 | 603
2016-04-17 23:00 | 582 | 582
2016-04-17 23:30 | 568 | 568
2016-04-18 | 555 | 555
2016-04-18 00:30 | 538 | 538
2016-04-18 01:00 | 522 | 522
2016-04-18 01:30 | 508 | 508
2016-04-18 02:00 | 498 | 498
2016-04-18 02:30 | 494 | 494
2016-04-18 03:00 | 490 | 489
2016-04-18 03:30 | 487 | 487
2016-04-18 04:00 | 489 | 489
2016-04-18 04:30 | 491 | 490
2016-04-18 05:00 | 497 | 497
2016-04-18 05:30 | 514 | 514
2016-04-18 06:00 | 535 | 535
2016-04-18 06:30 | 570 | 570
2016-04-18 07:00 | 601 | 601
2016-04-18 07:30 | 632 | 632
2016-04-18 08:00 | 657 | 657
2016-04-18 08:30 | 666 | 665
2016-04-18 09:00 | 661 | 661
2016-04-18 09:30 | 648 | 648
2016-04-18 10:00 | 624 | 624
2016-04-18 10:30 | 616 | 616
2016-04-18 11:00 | 601 | 601
2016-04-18 11:30 | 593 | 593
2016-04-18 12:00 | 600 | 600
2016-04-18 12:30 | 608 | 608
2016-04-18 13:00 | 613 | 613
2016-04-18 13:30 | 626 | 626
2016-04-18 14:00 | 630 | 629
2016-04-18 14:30 | 633 | 633
2016-04-18 15:00 | 632 | 632
2016-04-18 15:30 | 660 | 660
2016-04-18 16:00 | 672 | 672
2016-04-18 16:30 | 683 | 683
2016-04-18 17:00 | 692 | 691
2016-04-18 17:30 | 610 | 609
2016-04-18 18:00 | 500 | 500
2016-04-18 18:30 | 479 | 478
2016-04-18 19:00 | 496 | 496
2016-04-18 19:30 | 580 | 580
2016-04-18 20:00 | 591 | 591
2016-04-18 20:30 | 586 | 586
2016-04-18 21:00 | 679 | 679
2016-04-18 21:30 | 659 | 658
2016-04-18 22:00 | 658 | 658
2016-04-18 22:30 | 649 | 649
2016-04-18 23:00 | 615 | 615
2016-04-18 23:30 | 496 | 496
2016-04-19 | 520 | 519
2016-04-19 00:30 | 567 | 567
2016-04-19 01:00 | 553 | 553
2016-04-19 01:30 | 532 | 532
2016-04-19 02:00 | 524 | 524
2016-04-19 02:30 | 517 | 517
2016-04-19 03:00 | 510 | 510
2016-04-19 03:30 | 508 | 507
2016-04-19 04:00 | 508 | 507
2016-04-19 04:30 | 508 | 508
2016-04-19 05:00 | 514 | 514
2016-04-19 05:30 | 530 | 530
2016-04-19 06:00 | 550 | 549
2016-04-19 06:30 | 565 | 565
2016-04-19 07:00 | 542 | 542
2016-04-19 07:30 | 599 | 599
2016-04-19 08:00 | 637 | 637
2016-04-19 08:30 | 655 | 655
2016-04-19 09:00 | 649 | 649
2016-04-19 09:30 | 636 | 636
2016-04-19 10:00 | 619 | 619
2016-04-19 10:30 | 619 | 619
2016-04-19 11:00 | 623 | 623
2016-04-19 11:30 | 637 | 637
2016-04-19 12:00 | 646 | 646
2016-04-19 12:30 | 644 | 644
2016-04-19 13:00 | 647 | 647
2016-04-19 13:30 | 660 | 660
2016-04-19 14:00 | 669 | 668
2016-04-19 14:30 | 663 | 660
2016-04-19 15:00 | 657 | 655
2016-04-19 15:30 | 661 | 659
2016-04-19 16:00 | 616 | 614
2016-04-19 16:30 | 557 | 555
2016-04-19 17:00 | 538 | 537
2016-04-19 17:30 | 546 | 545
2016-04-19 18:00 | 474 | 474
2016-04-19 18:30 | 345 | 345
2016-04-19 19:00 | 445 | 444
2016-04-19 19:30 | 561 | 561
2016-04-19 20:00 | 572 | 572
2016-04-19 20:30 | 615 | 614
2016-04-19 21:00 | 630 | 629
2016-04-19 21:30 | 605 | 604
2016-04-19 22:00 | 600 | 599
2016-04-19 22:30 | 520 | 519
2016-04-19 23:00 | 487 | 487
2016-04-19 23:30 | 432 | 432
2016-04-20 | 469 | 469
2016-04-20 00:30 | 507 | 507
2016-04-20 01:00 | 522 | 522
2016-04-20 01:30 | 509 | 509
2016-04-20 02:00 | 500 | 500
2016-04-20 02:30 | 497 | 497
2016-04-20 03:00 | 494 | 494
2016-04-20 03:30 | 495 | 495
2016-04-20 04:00 | 491 | 491
2016-04-20 04:30 | 493 | 493
2016-04-20 05:00 | 503 | 503
2016-04-20 05:30 | 518 | 518
2016-04-20 06:00 | 536 | 536
2016-04-20 06:30 | 564 | 564
2016-04-20 07:00 | 525 | 525
2016-04-20 07:30 | 574 | 573
2016-04-20 08:00 | 626 | 626
2016-04-20 08:30 | 638 | 637
2016-04-20 09:00 | 651 | 650
2016-04-20 09:30 | 638 | 637
2016-04-20 10:00 | 616 | 614
2016-04-20 10:30 | 614 | 612
2016-04-20 11:00 | 628 | 627
2016-04-20 11:30 | 634 | 632
2016-04-20 12:00 | 638 | 636
2016-04-20 12:30 | 637 | 636
2016-04-20 13:00 | 637 | 636
2016-04-20 13:30 | 661 | 659
2016-04-20 14:00 | 684 | 682
2016-04-20 14:30 | 672 | 669
2016-04-20 15:00 | 655 | 652
2016-04-20 15:30 | 663 | 661
2016-04-20 16:00 | 670 | 667
2016-04-20 16:30 | 681 | 679
2016-04-20 17:00 | 685 | 682
2016-04-20 17:30 | 679 | 677
2016-04-20 18:00 | 674 | 672
2016-04-20 18:30 | 679 | 676
2016-04-20 19:00 | 689 | 686
2016-04-20 19:30 | 702 | 699
2016-04-20 20:00 | 703 | 700
2016-04-20 20:30 | 690 | 687
2016-04-20 21:00 | 676 | 673
2016-04-20 21:30 | 658 | 656
2016-04-20 22:00 | 656 | 654
2016-04-20 22:30 | 645 | 643
2016-04-20 23:00 | 629 | 628
2016-04-20 23:30 | 606 | 605
2016-04-21 | 589 | 588
2016-04-21 00:30 | 560 | 559
2016-04-21 01:00 | 539 | 539
2016-04-21 01:30 | 520 | 520
2016-04-21 02:00 | 511 | 511
2016-04-21 02:30 | 506 | 506
2016-04-21 03:00 | 504 | 504
2016-04-21 03:30 | 500 | 500
2016-04-21 04:00 | 501 | 501
2016-04-21 04:30 | 500 | 500
2016-04-21 05:00 | 506 | 506
2016-04-21 05:30 | 520 | 520
2016-04-21 06:00 | 538 | 538
2016-04-21 06:30 | 568 | 568
2016-04-21 07:00 | 596 | 596
2016-04-21 07:30 | 622 | 621
2016-04-21 08:00 | 646 | 645
2016-04-21 08:30 | 660 | 658
2016-04-21 09:00 | 656 | 653
2016-04-21 09:30 | 644 | 642
2016-04-21 10:00 | 627 | 625
2016-04-21 10:30 | 629 | 627
2016-04-21 11:00 | 630 | 628
2016-04-21 11:30 | 632 | 630
2016-04-21 12:00 | 578 | 576
2016-04-21 12:30 | 555 | 554
2016-04-21 13:00 | 558 | 558
2016-04-21 13:30 | 558 | 558
2016-04-21 14:00 | 542 | 541
2016-04-21 14:30 | 536 | 536
2016-04-21 15:00 | 536 | 536
2016-04-21 15:30 | 559 | 559
2016-04-21 16:00 | 585 | 585
2016-04-21 16:30 | 587 | 587
2016-04-21 17:00 | 562 | 562
2016-04-21 17:30 | 526 | 526
2016-04-21 18:00 | 487 | 487
2016-04-21 18:30 | 386 | 386
2016-04-21 19:00 | 316 | 316
2016-04-21 19:30 | 415 | 413
2016-04-21 20:00 | 415 | 415
2016-04-21 20:30 | 418 | 418
2016-04-21 21:00 | 556 | 556
2016-04-21 21:30 | 606 | 605
2016-04-21 22:00 | 631 | 629
2016-04-21 22:30 | 530 | 528
2016-04-21 23:00 | 554 | 553
2016-04-21 23:30 | 546 | 546
2016-04-22 | 580 | 580
2016-04-22 00:30 | 566 | 565
2016-04-22 01:00 | 541 | 540
2016-04-22 01:30 | 518 | 518
2016-04-22 02:00 | 510 | 510
2016-04-22 02:30 | 503 | 503
2016-04-22 03:00 | 502 | 502
2016-04-22 03:30 | 500 | 500
2016-04-22 04:00 | 499 | 499
2016-04-22 04:30 | 500 | 500
2016-04-22 05:00 | 508 | 508
2016-04-22 05:30 | 515 | 515
2016-04-22 06:00 | 532 | 532
2016-04-22 06:30 | 517 | 517
2016-04-22 07:00 | 518 | 518
2016-04-22 07:30 | 608 | 608
2016-04-22 08:00 | 636 | 635
2016-04-22 08:30 | 649 | 648
2016-04-22 09:00 | 652 | 650
2016-04-22 09:30 | 634 | 633
2016-04-22 10:00 | 616 | 614
2016-04-22 10:30 | 613 | 612
2016-04-22 11:00 | 615 | 614
2016-04-22 11:30 | 610 | 609
2016-04-22 12:00 | 615 | 614
2016-04-22 12:30 | 629 | 628
2016-04-22 13:00 | 636 | 634
2016-04-22 13:30 | 627 | 625
2016-04-22 14:00 | 588 | 586
2016-04-22 14:30 | 505 | 504
2016-04-22 15:00 | 497 | 496
2016-04-22 15:30 | 467 | 467
2016-04-22 16:00 | 431 | 431
2016-04-22 16:30 | 451 | 451
2016-04-22 17:00 | 475 | 475
2016-04-22 17:30 | 462 | 462
2016-04-22 18:00 | 397 | 397
2016-04-22 18:30 | 385 | 385
2016-04-22 19:00 | 414 | 414
2016-04-22 19:30 | 524 | 524
2016-04-22 20:00 | 538 | 537
2016-04-22 20:30 | 526 | 525
2016-04-22 21:00 | 574 | 573
2016-04-22 21:30 | 561 | 559
2016-04-22 22:00 | 561 | 559
2016-04-22 22:30 | 492 | 490
2016-04-22 23:00 | 385 | 384
2016-04-22 23:30 | 385 | 385
2016-04-23 | 398 | 398
2016-04-23 00:30 | 439 | 439
2016-04-23 01:00 | 518 | 518
2016-04-23 01:30 | 513 | 512
2016-04-23 02:00 | 501 | 500
2016-04-23 02:30 | 494 | 493
2016-04-23 03:00 | 487 | 486
2016-04-23 03:30 | 484 | 484
2016-04-23 04:00 | 481 | 481
2016-04-23 04:30 | 479 | 478
2016-04-23 05:00 | 477 | 477
2016-04-23 05:30 | 484 | 484
2016-04-23 06:00 | 492 | 491
2016-04-23 06:30 | 506 | 505
2016-04-23 07:00 | 513 | 512
2016-04-23 07:30 | 535 | 534
2016-04-23 08:00 | 548 | 546
2016-04-23 08:30 | 561 | 559
2016-04-23 09:00 | 566 | 564
2016-04-23 09:30 | 558 | 556
2016-04-23 10:00 | 542 | 541
2016-04-23 10:30 | 550 | 549
2016-04-23 11:00 | 549 | 548
2016-04-23 11:30 | 543 | 542
2016-04-23 12:00 | 545 | 544
2016-04-23 12:30 | 547 | 546
2016-04-23 13:00 | 552 | 550
2016-04-23 13:30 | 561 | 560
2016-04-23 14:00 | 580 | 579
2016-04-23 14:30 | 561 | 559
2016-04-23 15:00 | 558 | 556
2016-04-23 15:30 | 563 | 561
2016-04-23 16:00 | 574 | 573
2016-04-23 16:30 | 505 | 503
2016-04-23 17:00 | 464 | 462
2016-04-23 17:30 | 480 | 479
2016-04-23 18:00 | 447 | 446
2016-04-23 18:30 | 468 | 468
2016-04-23 19:00 | 498 | 497
2016-04-23 19:30 | 656 | 655
2016-04-23 20:00 | 661 | 657
2016-04-23 20:30 | 646 | 644
2016-04-23 21:00 | 638 | 636
2016-04-23 21:30 | 616 | 614
2016-04-23 22:00 | 614 | 612
2016-04-23 22:30 | 592 | 590
2016-04-23 23:00 | 585 | 584
2016-04-23 23:30 | 575 | 574
2016-04-24 | 565 | 563
2016-04-24 00:30 | 543 | 542
2016-04-24 01:00 | 524 | 523
2016-04-24 01:30 | 506 | 505
2016-04-24 02:00 | 498 | 498
2016-04-24 02:30 | 489 | 488
2016-04-24 03:00 | 483 | 482
2016-04-24 03:30 | 475 | 475
2016-04-24 04:00 | 477 | 477
2016-04-24 04:30 | 480 | 480
2016-04-24 05:00 | 480 | 480
2016-04-24 05:30 | 486 | 486
2016-04-24 06:00 | 488 | 487
2016-04-24 06:30 | 490 | 490
2016-04-24 07:00 | 491 | 491
2016-04-24 07:30 | 498 | 498
2016-04-24 08:00 | 510 | 510
2016-04-24 08:30 | 526 | 525
2016-04-24 09:00 | 531 | 530
2016-04-24 09:30 | 531 | 531
2016-04-24 10:00 | 519 | 519
2016-04-24 10:30 | 519 | 519
2016-04-24 11:00 | 525 | 525
2016-04-24 11:30 | 528 | 527
2016-04-24 12:00 | 526 | 526
2016-04-24 12:30 | 528 | 527
2016-04-24 13:00 | 524 | 524
2016-04-24 13:30 | 540 | 540
2016-04-24 14:00 | 544 | 544
2016-04-24 14:30 | 529 | 529
2016-04-24 15:00 | 530 | 530
2016-04-24 15:30 | 544 | 544
2016-04-24 16:00 | 552 | 551
2016-04-24 16:30 | 566 | 566
2016-04-24 17:00 | 579 | 578
2016-04-24 17:30 | 584 | 584
2016-04-24 18:00 | 495 | 494
2016-04-24 18:30 | 489 | 489
2016-04-24 19:00 | 515 | 515
2016-04-24 19:30 | 530 | 530
2016-04-24 20:00 | 523 | 523
2016-04-24 20:30 | 515 | 515
2016-04-24 21:00 | 590 | 590
2016-04-24 21:30 | 611 | 611
2016-04-24 22:00 | 611 | 610
2016-04-24 22:30 | 581 | 580
2016-04-24 23:00 | 561 | 561
2016-04-24 23:30 | 503 | 503
2016-04-25 | 455 | 455
2016-04-25 00:30 | 496 | 496
2016-04-25 01:00 | 481 | 480
2016-04-25 01:30 | 501 | 501
2016-04-25 02:00 | 493 | 493
2016-04-25 02:30 | 487 | 487
2016-04-25 03:00 | 481 | 481
2016-04-25 03:30 | 480 | 480
2016-04-25 04:00 | 481 | 481
2016-04-25 04:30 | 480 | 480
2016-04-25 05:00 | 483 | 483
2016-04-25 05:30 | 486 | 486
2016-04-25 06:00 | 483 | 483
2016-04-25 06:30 | 496 | 496
2016-04-25 07:00 | 504 | 504
2016-04-25 07:30 | 518 | 518
2016-04-25 08:00 | 526 | 525
2016-04-25 08:30 | 535 | 534
2016-04-25 09:00 | 536 | 536
2016-04-25 09:30 | 521 | 520
2016-04-25 10:00 | 506 | 505
2016-04-25 10:30 | 506 | 505
2016-04-25 11:00 | 508 | 507
2016-04-25 11:30 | 505 | 505
2016-04-25 12:00 | 508 | 508
2016-04-25 12:30 | 512 | 511
2016-04-25 13:00 | 520 | 519
2016-04-25 13:30 | 536 | 536
2016-04-25 14:00 | 555 | 554
2016-04-25 14:30 | 541 | 540
2016-04-25 15:00 | 541 | 540
2016-04-25 15:30 | 549 | 548
2016-04-25 16:00 | 559 | 558
2016-04-25 16:30 | 579 | 578
2016-04-25 17:00 | 602 | 601
2016-04-25 17:30 | 617 | 616
2016-04-25 18:00 | 554 | 552
2016-04-25 18:30 | 460 | 459
2016-04-25 19:00 | 509 | 509
2016-04-25 19:30 | 637 | 637
2016-04-25 20:00 | 650 | 648
2016-04-25 20:30 | 605 | 603
2016-04-25 21:00 | 637 | 636
2016-04-25 21:30 | 622 | 621
2016-04-25 22:00 | 615 | 614
2016-04-25 22:30 | 584 | 583
2016-04-25 23:00 | 574 | 573
2016-04-25 23:30 | 523 | 523
2016-04-26 | 529 | 529
2016-04-26 00:30 | 531 | 531
2016-04-26 01:00 | 517 | 517
2016-04-26 01:30 | 506 | 506
2016-04-26 02:00 | 492 | 492
2016-04-26 02:30 | 485 | 485
2016-04-26 03:00 | 480 | 480
2016-04-26 03:30 | 482 | 482
2016-04-26 04:00 | 476 | 476
2016-04-26 04:30 | 481 | 481
2016-04-26 05:00 | 486 | 486
2016-04-26 05:30 | 503 | 503
2016-04-26 06:00 | 519 | 519
2016-04-26 06:30 | 470 | 470
2016-04-26 07:00 | 493 | 493
2016-04-26 07:30 | 568 | 568
2016-04-26 08:00 | 612 | 612
2016-04-26 08:30 | 621 | 619
2016-04-26 09:00 | 633 | 631
2016-04-26 09:30 | 622 | 620
2016-04-26 10:00 | 611 | 610
2016-04-26 10:30 | 611 | 609
2016-04-26 11:00 | 611 | 610
2016-04-26 11:30 | 612 | 610
2016-04-26 12:00 | 583 | 582
2016-04-26 12:30 | 606 | 605
2016-04-26 13:00 | 595 | 594
2016-04-26 13:30 | 613 | 612
2016-04-26 14:00 | 553 | 551
2016-04-26 14:30 | 486 | 485
2016-04-26 15:00 | 489 | 489
2016-04-26 15:30 | 479 | 479
2016-04-26 16:00 | 404 | 404
2016-04-26 16:30 | 358 | 358
2016-04-26 17:00 | 386 | 385
2016-04-26 17:30 | 501 | 501
2016-04-26 18:00 | 387 | 387
2016-04-26 18:30 | 416 | 415
2016-04-26 19:00 | 463 | 462
2016-04-26 19:30 | 543 | 543
2016-04-26 20:00 | 632 | 632
2016-04-26 20:30 | 587 | 584
2016-04-26 21:00 | 620 | 619
2016-04-26 21:30 | 601 | 599
2016-04-26 22:00 | 604 | 602
2016-04-26 22:30 | 450 | 448
2016-04-26 23:00 | 424 | 424
2016-04-26 23:30 | 441 | 441
2016-04-27 | 472 | 472
2016-04-27 00:30 | 528 | 527
2016-04-27 01:00 | 534 | 533
2016-04-27 01:30 | 518 | 517
2016-04-27 02:00 | 490 | 490
2016-04-27 02:30 | 498 | 497
2016-04-27 03:00 | 494 | 494
2016-04-27 03:30 | 489 | 489
2016-04-27 04:00 | 484 | 484
2016-04-27 04:30 | 478 | 478
2016-04-27 05:00 | 499 | 499
2016-04-27 05:30 | 517 | 517
2016-04-27 06:00 | 534 | 533
2016-04-27 06:30 | 493 | 492
2016-04-27 07:00 | 516 | 515
2016-04-27 07:30 | 594 | 594
2016-04-27 08:00 | 638 | 637
2016-04-27 08:30 | 650 | 648
2016-04-27 09:00 | 662 | 661
2016-04-27 09:30 | 643 | 641
2016-04-27 10:00 | 579 | 577
2016-04-27 10:30 | 566 | 565
2016-04-27 11:00 | 576 | 575
2016-04-27 11:30 | 577 | 577
2016-04-27 12:00 | 571 | 570
2016-04-27 12:30 | 579 | 578
2016-04-27 13:00 | 569 | 569
2016-04-27 13:30 | 484 | 483
2016-04-27 14:00 | 454 | 454
2016-04-27 14:30 | 375 | 375
2016-04-27 15:00 | 330 | 329
2016-04-27 15:30 | 330 | 328
2016-04-27 16:00 | 317 | 316
2016-04-27 16:30 | 314 | 312
2016-04-27 17:00 | 345 | 343
2016-04-27 17:30 | 257 | 255
2016-04-27 18:00 | 149 | 143
2016-04-27 18:30 | 214 | 206
2016-04-27 19:00 | 254 | 249
2016-04-27 19:30 | 299 | 296
2016-04-27 20:00 | 298 | 296
2016-04-27 20:30 | 280 | 279
2016-04-27 21:00 | 352 | 351
2016-04-27 21:30 | 306 | 305
2016-04-27 22:00 | 429 | 428
2016-04-27 22:30 | 157 | 157
2016-04-27 23:00 | 130 | 117
2016-04-27 23:30 | 160 | 145
2016-04-28 | 210 | 201
2016-04-28 00:30 | 346 | 342
2016-04-28 01:00 | 335 | 334
2016-04-28 01:30 | 384 | 383
2016-04-28 02:00 | 329 | 328
2016-04-28 02:30 | 371 | 370
2016-04-28 03:00 | 370 | 370
2016-04-28 03:30 | 373 | 373
2016-04-28 04:00 | 371 | 371
2016-04-28 04:30 | 374 | 373
2016-04-28 05:00 | 378 | 377
2016-04-28 05:30 | 302 | 302
2016-04-28 06:00 | 364 | 362
2016-04-28 06:30 | 328 | 328
2016-04-28 07:00 | 307 | 306
2016-04-28 07:30 | 374 | 373
2016-04-28 08:00 | 397 | 397
2016-04-28 08:30 | 384 | 383
2016-04-28 09:00 | 392 | 391
2016-04-28 09:30 | 364 | 363
2016-04-28 10:00 | 375 | 374
2016-04-28 10:30 | 436 | 435
2016-04-28 11:00 | 416 | 416
2016-04-28 11:30 | 483 | 483
2016-04-28 12:00 | 495 | 495
2016-04-28 12:30 | 499 | 499
2016-04-28 13:00 | 502 | 502
2016-04-28 13:30 | 514 | 514
2016-04-28 14:00 | 511 | 511
2016-04-28 14:30 | 447 | 447
2016-04-28 15:00 | 455 | 455
2016-04-28 15:30 | 500 | 500
2016-04-28 16:00 | 449 | 449
2016-04-28 16:30 | 344 | 344
2016-04-28 17:00 | 342 | 341
2016-04-28 17:30 | 342 | 340
2016-04-28 18:00 | 340 | 338
2016-04-28 18:30 | 339 | 338
2016-04-28 19:00 | 269 | 268
2016-04-28 19:30 | 377 | 375
2016-04-28 20:00 | 314 | 313
2016-04-28 20:30 | 263 | 261
2016-04-28 21:00 | 262 | 258
2016-04-28 21:30 | 442 | 440
2016-04-28 22:00 | 432 | 432
2016-04-28 22:30 | 266 | 266
2016-04-28 23:00 | 221 | 217
2016-04-28 23:30 | 305 | 301
2016-04-29 | 361 | 360
2016-04-29 00:30 | 354 | 353
2016-04-29 01:00 | 400 | 399
2016-04-29 01:30 | 397 | 397
2016-04-29 02:00 | 387 | 387
2016-04-29 02:30 | 384 | 384
2016-04-29 03:00 | 380 | 380
2016-04-29 03:30 | 385 | 385
2016-04-29 04:00 | 384 | 383
2016-04-29 04:30 | 387 | 387
2016-04-29 05:00 | 394 | 394
2016-04-29 05:30 | 349 | 349
2016-04-29 06:00 | 406 | 405
2016-04-29 06:30 | 392 | 392
2016-04-29 07:00 | 335 | 334
2016-04-29 07:30 | 475 | 474
2016-04-29 08:00 | 530 | 530
2016-04-29 08:30 | 539 | 538
2016-04-29 09:00 | 533 | 533
2016-04-29 09:30 | 536 | 536
2016-04-29 10:00 | 513 | 513
2016-04-29 10:30 | 530 | 530
2016-04-29 11:00 | 541 | 540
2016-04-29 11:30 | 526 | 526
2016-04-29 12:00 | 526 | 526
2016-04-29 12:30 | 524 | 524
2016-04-29 13:00 | 511 | 510
2016-04-29 13:30 | 519 | 519
2016-04-29 14:00 | 544 | 544
2016-04-29 14:30 | 531 | 531
2016-04-29 15:00 | 515 | 515
2016-04-29 15:30 | 511 | 511
2016-04-29 16:00 | 544 | 544
2016-04-29 16:30 | 481 | 481
2016-04-29 17:00 | 473 | 473
2016-04-29 17:30 | 455 | 455
2016-04-29 18:00 | 364 | 364
2016-04-29 18:30 | 340 | 339
2016-04-29 19:00 | 349 | 348
2016-04-29 19:30 | 395 | 394
2016-04-29 20:00 | 487 | 486
2016-04-29 20:30 | 504 | 504
2016-04-29 21:00 | 556 | 556
2016-04-29 21:30 | 539 | 538
2016-04-29 22:00 | 526 | 525
2016-04-29 22:30 | 507 | 507
2016-04-29 23:00 | 539 | 539
2016-04-29 23:30 | 583 | 583
2016-04-30 | 569 | 568
2016-04-30 00:30 | 555 | 554
2016-04-30 01:00 | 537 | 536
2016-04-30 01:30 | 502 | 502
2016-04-30 02:00 | 520 | 520
2016-04-30 02:30 | 514 | 513
2016-04-30 03:00 | 503 | 503
2016-04-30 03:30 | 502 | 502
2016-04-30 04:00 | 501 | 501
2016-04-30 04:30 | 501 | 501
2016-04-30 05:00 | 502 | 502
2016-04-30 05:30 | 510 | 510
2016-04-30 06:00 | 515 | 514
2016-04-30 06:30 | 531 | 531
2016-04-30 07:00 | 539 | 539
2016-04-30 07:30 | 562 | 562
2016-04-30 08:00 | 581 | 580
2016-04-30 08:30 | 600 | 599
2016-04-30 09:00 | 612 | 610
2016-04-30 09:30 | 587 | 584
2016-04-30 10:00 | 584 | 582
2016-04-30 10:30 | 583 | 581
2016-04-30 11:00 | 572 | 570
2016-04-30 11:30 | 565 | 564
2016-04-30 12:00 | 564 | 562
2016-04-30 12:30 | 559 | 557
2016-04-30 13:00 | 555 | 553
2016-04-30 13:30 | 555 | 554
2016-04-30 14:00 | 563 | 562
2016-04-30 14:30 | 570 | 569
2016-04-30 15:00 | 579 | 578
2016-04-30 15:30 | 586 | 584
2016-04-30 16:00 | 597 | 596
2016-04-30 16:30 | 608 | 606
2016-04-30 17:00 | 617 | 614
2016-04-30 17:30 | 641 | 639
2016-04-30 18:00 | 601 | 598
2016-04-30 18:30 | 584 | 581
2016-04-30 19:00 | 640 | 638
2016-04-30 19:30 | 660 | 657
2016-04-30 20:00 | 647 | 643
2016-04-30 20:30 | 650 | 647
2016-04-30 21:00 | 661 | 659
2016-04-30 21:30 | 649 | 646
2016-04-30 22:00 | 628 | 625
2016-04-30 22:30 | 587 | 585
2016-04-30 23:00 | 567 | 566
2016-04-30 23:30 | 552 | 551
2016-05-01 | 565 | 564
2016-05-01 00:30 | 556 | 555
2016-05-01 01:00 | 541 | 540
2016-05-01 01:30 | 529 | 528
2016-05-01 02:00 | 516 | 516
2016-05-01 02:30 | 511 | 511
2016-05-01 03:00 | 507 | 507
2016-05-01 03:30 | 504 | 504
2016-05-01 04:00 | 500 | 500
2016-05-01 04:30 | 499 | 499
2016-05-01 05:00 | 501 | 501
2016-05-01 05:30 | 501 | 500
2016-05-01 06:00 | 501 | 501
2016-05-01 06:30 | 511 | 511
2016-05-01 07:00 | 516 | 515
2016-05-01 07:30 | 532 | 532
2016-05-01 08:00 | 545 | 545
2016-05-01 08:30 | 558 | 558
2016-05-01 09:00 | 576 | 575
2016-05-01 09:30 | 565 | 564
2016-05-01 10:00 | 549 | 548
2016-05-01 10:30 | 560 | 559
2016-05-01 11:00 | 562 | 562
2016-05-01 11:30 | 560 | 559
2016-05-01 12:00 | 558 | 557
2016-05-01 12:30 | 560 | 559
2016-05-01 13:00 | 546 | 545
2016-05-01 13:30 | 542 | 541
2016-05-01 14:00 | 548 | 547
2016-05-01 14:30 | 556 | 555
2016-05-01 15:00 | 561 | 560
2016-05-01 15:30 | 568 | 567
2016-05-01 16:00 | 595 | 594
2016-05-01 16:30 | 624 | 623
2016-05-01 17:00 | 637 | 635
2016-05-01 17:30 | 629 | 627
2016-05-01 18:00 | 562 | 559
2016-05-01 18:30 | 475 | 474
2016-05-01 19:00 | 460 | 459
2016-05-01 19:30 | 486 | 486
2016-05-01 20:00 | 471 | 471
2016-05-01 20:30 | 438 | 438
2016-05-01 21:00 | 518 | 518
2016-05-01 21:30 | 539 | 539
2016-05-01 22:00 | 624 | 624
2016-05-01 22:30 | 620 | 619
2016-05-01 23:00 | 602 | 601
2016-05-01 23:30 | 570 | 569
2016-05-02 | 546 | 545
2016-05-02 00:30 | 556 | 555
2016-05-02 01:00 | 540 | 540
2016-05-02 01:30 | 525 | 525
2016-05-02 02:00 | 517 | 517
2016-05-02 02:30 | 512 | 512
2016-05-02 03:00 | 511 | 511
2016-05-02 03:30 | 510 | 510
2016-05-02 04:00 | 509 | 508
2016-05-02 04:30 | 506 | 506
2016-05-02 05:00 | 505 | 505
2016-05-02 05:30 | 507 | 507
2016-05-02 06:00 | 512 | 512
2016-05-02 06:30 | 522 | 522
2016-05-02 07:00 | 530 | 530
2016-05-02 07:30 | 547 | 547
2016-05-02 08:00 | 562 | 562
2016-05-02 08:30 | 571 | 570
2016-05-02 09:00 | 581 | 580
2016-05-02 09:30 | 574 | 573
2016-05-02 10:00 | 538 | 537
2016-05-02 10:30 | 530 | 529
2016-05-02 11:00 | 533 | 533
2016-05-02 11:30 | 532 | 532
2016-05-02 12:00 | 543 | 542
2016-05-02 12:30 | 547 | 546
2016-05-02 13:00 | 553 | 552
2016-05-02 13:30 | 562 | 561
2016-05-02 14:00 | 566 | 565
2016-05-02 14:30 | 584 | 583
2016-05-02 15:00 | 610 | 609
2016-05-02 15:30 | 629 | 627
2016-05-02 16:00 | 648 | 645
2016-05-02 16:30 | 648 | 645
2016-05-02 17:00 | 586 | 583
2016-05-02 17:30 | 550 | 549
2016-05-02 18:00 | 419 | 418
2016-05-02 18:30 | 432 | 432
2016-05-02 19:00 | 529 | 529
2016-05-02 19:30 | 643 | 642
2016-05-02 20:00 | 665 | 662
2016-05-02 20:30 | 704 | 702
2016-05-02 21:00 | 700 | 697
2016-05-02 21:30 | 680 | 678
2016-05-02 22:00 | 658 | 656
2016-05-02 22:30 | 630 | 629
2016-05-02 23:00 | 564 | 563
2016-05-02 23:30 | 557 | 556
2016-05-03 | 553 | 553
2016-05-03 00:30 | 558 | 557
2016-05-03 01:00 | 546 | 546
2016-05-03 01:30 | 531 | 531
2016-05-03 02:00 | 523 | 522
2016-05-03 02:30 | 519 | 519
2016-05-03 03:00 | 513 | 513
2016-05-03 03:30 | 510 | 510
2016-05-03 04:00 | 512 | 512
2016-05-03 04:30 | 513 | 513
2016-05-03 05:00 | 520 | 520
2016-05-03 05:30 | 530 | 530
2016-05-03 06:00 | 550 | 550
2016-05-03 06:30 | 551 | 551
2016-05-03 07:00 | 549 | 549
2016-05-03 07:30 | 461 | 461
2016-05-03 08:00 | 412 | 412
2016-05-03 08:30 | 500 | 500
2016-05-03 09:00 | 541 | 541
2016-05-03 09:30 | 567 | 567
2016-05-03 10:00 | 572 | 571
2016-05-03 10:30 | 572 | 571
2016-05-03 11:00 | 571 | 570
2016-05-03 11:30 | 578 | 576
2016-05-03 12:00 | 573 | 571
2016-05-03 12:30 | 512 | 511
2016-05-03 13:00 | 504 | 503
2016-05-03 13:30 | 530 | 530
2016-05-03 14:00 | 542 | 542
2016-05-03 14:30 | 553 | 552
2016-05-03 15:00 | 555 | 554
2016-05-03 15:30 | 555 | 554
2016-05-03 16:00 | 563 | 562
2016-05-03 16:30 | 563 | 562
2016-05-03 17:00 | 580 | 579
2016-05-03 17:30 | 577 | 575
2016-05-03 18:00 | 550 | 549
2016-05-03 18:30 | 569 | 568
2016-05-03 19:00 | 616 | 615
2016-05-03 19:30 | 606 | 604
2016-05-03 20:00 | 589 | 588
2016-05-03 20:30 | 584 | 582
2016-05-03 21:00 | 565 | 563
2016-05-03 21:30 | 540 | 539
2016-05-03 22:00 | 519 | 518
2016-05-03 22:30 | 504 | 503
2016-05-03 23:00 | 491 | 490
2016-05-03 23:30 | 470 | 470
2016-05-04 | 453 | 453
2016-05-04 00:30 | 434 | 434
2016-05-04 01:00 | 426 | 426
2016-05-04 01:30 | 413 | 412
2016-05-04 02:00 | 407 | 406
2016-05-04 02:30 | 407 | 406
2016-05-04 03:00 | 402 | 401
2016-05-04 03:30 | 398 | 398
2016-05-04 04:00 | 396 | 396
2016-05-04 04:30 | 399 | 399
2016-05-04 05:00 | 403 | 403
2016-05-04 05:30 | 418 | 418
2016-05-04 06:00 | 432 | 432
2016-05-04 06:30 | 462 | 462
2016-05-04 07:00 | 435 | 435
2016-05-04 07:30 | 432 | 432
2016-05-04 08:00 | 488 | 488
2016-05-04 08:30 | 490 | 490
2016-05-04 09:00 | 491 | 491
2016-05-04 09:30 | 489 | 489
2016-05-04 10:00 | 500 | 500
2016-05-04 10:30 | 508 | 508
2016-05-04 11:00 | 510 | 510
2016-05-04 11:30 | 515 | 515
2016-05-04 12:00 | 535 | 535
2016-05-04 12:30 | 536 | 536
2016-05-04 13:00 | 539 | 539
2016-05-04 13:30 | 545 | 545
2016-05-04 14:00 | 553 | 552
2016-05-04 14:30 | 556 | 555
2016-05-04 15:00 | 525 | 524
2016-05-04 15:30 | 529 | 529
2016-05-04 16:00 | 537 | 537
2016-05-04 16:30 | 569 | 569
2016-05-04 17:00 | 559 | 558
2016-05-04 17:30 | 484 | 483
2016-05-04 18:00 | 435 | 435
2016-05-04 18:30 | 458 | 458
2016-05-04 19:00 | 485 | 485
2016-05-04 19:30 | 473 | 473
2016-05-04 20:00 | 511 | 511
2016-05-04 20:30 | 539 | 539
2016-05-04 21:00 | 560 | 559
2016-05-04 21:30 | 536 | 536
2016-05-04 22:00 | 511 | 511
2016-05-04 22:30 | 543 | 543
2016-05-04 23:00 | 613 | 613
2016-05-04 23:30 | 597 | 595
2016-05-05 | 577 | 575
2016-05-05 00:30 | 560 | 559
2016-05-05 01:00 | 551 | 550
2016-05-05 01:30 | 541 | 540
2016-05-05 02:00 | 533 | 532
2016-05-05 02:30 | 526 | 525
2016-05-05 03:00 | 522 | 522
2016-05-05 03:30 | 516 | 516
2016-05-05 04:00 | 513 | 513
2016-05-05 04:30 | 518 | 518
2016-05-05 05:00 | 522 | 522
2016-05-05 05:30 | 544 | 544
2016-05-05 06:00 | 556 | 555
2016-05-05 06:30 | 568 | 568
2016-05-05 07:00 | 535 | 535
2016-05-05 07:30 | 534 | 534
2016-05-05 08:00 | 536 | 536
2016-05-05 08:30 | 526 | 526
2016-05-05 09:00 | 596 | 596
2016-05-05 09:30 | 632 | 631
2016-05-05 10:00 | 648 | 646
2016-05-05 10:30 | 654 | 651
2016-05-05 11:00 | 678 | 676
2016-05-05 11:30 | 673 | 669
2016-05-05 12:00 | 657 | 654
2016-05-05 12:30 | 639 | 636
2016-05-05 13:00 | 635 | 633
2016-05-05 13:30 | 641 | 640
2016-05-05 14:00 | 653 | 652
2016-05-05 14:30 | 665 | 663
2016-05-05 15:00 | 651 | 649
2016-05-05 15:30 | 649 | 647
2016-05-05 16:00 | 657 | 655
2016-05-05 16:30 | 663 | 662
2016-05-05 17:00 | 670 | 668
2016-05-05 17:30 | 603 | 601
2016-05-05 18:00 | 583 | 583
2016-05-05 18:30 | 634 | 633
2016-05-05 19:00 | 633 | 632
2016-05-05 19:30 | 670 | 669
2016-05-05 20:00 | 693 | 691
2016-05-05 20:30 | 694 | 692
2016-05-05 21:00 | 673 | 670
2016-05-05 21:30 | 628 | 627
2016-05-05 22:00 | 600 | 599
2016-05-05 22:30 | 611 | 610
2016-05-05 23:00 | 617 | 617
2016-05-05 23:30 | 600 | 599
2016-05-06 | 585 | 585
2016-05-06 00:30 | 568 | 567
2016-05-06 01:00 | 548 | 548
2016-05-06 01:30 | 537 | 537
2016-05-06 02:00 | 526 | 526
2016-05-06 02:30 | 524 | 524
2016-05-06 03:00 | 521 | 521
2016-05-06 03:30 | 517 | 517
2016-05-06 04:00 | 517 | 517
2016-05-06 04:30 | 516 | 516
2016-05-06 05:00 | 519 | 518
2016-05-06 05:30 | 532 | 532
2016-05-06 06:00 | 554 | 553
2016-05-06 06:30 | 576 | 575
2016-05-06 07:00 | 548 | 546
2016-05-06 07:30 | 541 | 540
2016-05-06 08:00 | 528 | 527
2016-05-06 08:30 | 569 | 569
2016-05-06 09:00 | 609 | 607
2016-05-06 09:30 | 605 | 604
2016-05-06 10:00 | 609 | 608
2016-05-06 10:30 | 609 | 608
2016-05-06 11:00 | 608 | 606
2016-05-06 11:30 | 636 | 635
2016-05-06 12:00 | 642 | 640
2016-05-06 12:30 | 638 | 637
2016-05-06 13:00 | 641 | 639
2016-05-06 13:30 | 646 | 644
2016-05-06 14:00 | 651 | 649
2016-05-06 14:30 | 618 | 616
2016-05-06 15:00 | 626 | 624
2016-05-06 15:30 | 629 | 628
2016-05-06 16:00 | 615 | 614
2016-05-06 16:30 | 633 | 632
2016-05-06 17:00 | 650 | 649
2016-05-06 17:30 | 633 | 632
2016-05-06 18:00 | 578 | 576
2016-05-06 18:30 | 612 | 611
2016-05-06 19:00 | 673 | 672
2016-05-06 19:30 | 663 | 661
2016-05-06 20:00 | 650 | 648
2016-05-06 20:30 | 633 | 631
2016-05-06 21:00 | 618 | 616
2016-05-06 21:30 | 600 | 599
2016-05-06 22:00 | 580 | 579
2016-05-06 22:30 | 567 | 566
2016-05-06 23:00 | 557 | 557
2016-05-06 23:30 | 560 | 559
2016-05-07 | 568 | 567
2016-05-07 00:30 | 564 | 564
2016-05-07 01:00 | 548 | 547
2016-05-07 01:30 | 535 | 535
2016-05-07 02:00 | 528 | 527
2016-05-07 02:30 | 518 | 518
2016-05-07 03:00 | 513 | 513
2016-05-07 03:30 | 509 | 509
2016-05-07 04:00 | 509 | 509
2016-05-07 04:30 | 509 | 509
2016-05-07 05:00 | 510 | 510
2016-05-07 05:30 | 516 | 516
2016-05-07 06:00 | 515 | 515
2016-05-07 06:30 | 525 | 525
2016-05-07 07:00 | 504 | 504
2016-05-07 07:30 | 512 | 512
2016-05-07 08:00 | 530 | 530
2016-05-07 08:30 | 544 | 543
2016-05-07 09:00 | 556 | 556
2016-05-07 09:30 | 534 | 534
2016-05-07 10:00 | 559 | 559
2016-05-07 10:30 | 558 | 557
2016-05-07 11:00 | 539 | 538
2016-05-07 11:30 | 536 | 536
2016-05-07 12:00 | 531 | 530
2016-05-07 12:30 | 531 | 531
2016-05-07 13:00 | 537 | 536
2016-05-07 13:30 | 543 | 543
2016-05-07 14:00 | 541 | 540
2016-05-07 14:30 | 542 | 542
2016-05-07 15:00 | 543 | 542
2016-05-07 15:30 | 562 | 561
2016-05-07 16:00 | 575 | 574
2016-05-07 16:30 | 579 | 578
2016-05-07 17:00 | 579 | 578
2016-05-07 17:30 | 593 | 592
2016-05-07 18:00 | 535 | 534
2016-05-07 18:30 | 564 | 563
2016-05-07 19:00 | 611 | 610
2016-05-07 19:30 | 636 | 634
2016-05-07 20:00 | 630 | 628
2016-05-07 20:30 | 630 | 628
2016-05-07 21:00 | 614 | 612
2016-05-07 21:30 | 596 | 594
2016-05-07 22:00 | 578 | 577
2016-05-07 22:30 | 528 | 527
2016-05-07 23:00 | 547 | 547
2016-05-07 23:30 | 548 | 547
2016-05-08 | 546 | 545
2016-05-08 00:30 | 544 | 544
2016-05-08 01:00 | 531 | 531
2016-05-08 01:30 | 520 | 520
2016-05-08 02:00 | 511 | 511
2016-05-08 02:30 | 504 | 504
2016-05-08 03:00 | 496 | 496
2016-05-08 03:30 | 491 | 491
2016-05-08 04:00 | 488 | 488
2016-05-08 04:30 | 495 | 495
2016-05-08 05:00 | 495 | 495
2016-05-08 05:30 | 497 | 497
2016-05-08 06:00 | 499 | 499
2016-05-08 06:30 | 505 | 505
2016-05-08 07:00 | 479 | 479
2016-05-08 07:30 | 482 | 482
2016-05-08 08:00 | 496 | 496
2016-05-08 08:30 | 516 | 516
2016-05-08 09:00 | 527 | 527
2016-05-08 09:30 | 484 | 484
2016-05-08 10:00 | 474 | 474
2016-05-08 10:30 | 475 | 475
2016-05-08 11:00 | 503 | 503
2016-05-08 11:30 | 508 | 508
2016-05-08 12:00 | 513 | 513
2016-05-08 12:30 | 508 | 508
2016-05-08 13:00 | 512 | 512
2016-05-08 13:30 | 510 | 510
2016-05-08 14:00 | 514 | 514
2016-05-08 14:30 | 474 | 474
2016-05-08 15:00 | 506 | 506
2016-05-08 15:30 | 525 | 525
2016-05-08 16:00 | 540 | 540
2016-05-08 16:30 | 552 | 552
2016-05-08 17:00 | 559 | 559
2016-05-08 17:30 | 552 | 551
2016-05-08 18:00 | 553 | 553
2016-05-08 18:30 | 570 | 570
2016-05-08 19:00 | 622 | 622
2016-05-08 19:30 | 644 | 643
2016-05-08 20:00 | 637 | 635
2016-05-08 20:30 | 615 | 613
2016-05-08 21:00 | 614 | 613
2016-05-08 21:30 | 601 | 600
2016-05-08 22:00 | 586 | 584
2016-05-08 22:30 | 572 | 571
2016-05-08 23:00 | 581 | 581
2016-05-08 23:30 | 563 | 562
2016-05-09 | 542 | 542
2016-05-09 00:30 | 536 | 536
2016-05-09 01:00 | 525 | 525
2016-05-09 01:30 | 515 | 515
2016-05-09 02:00 | 510 | 510
2016-05-09 02:30 | 504 | 504
2016-05-09 03:00 | 501 | 501
2016-05-09 03:30 | 500 | 500
2016-05-09 04:00 | 499 | 499
2016-05-09 04:30 | 500 | 500
2016-05-09 05:00 | 502 | 502
2016-05-09 05:30 | 526 | 526
2016-05-09 06:00 | 544 | 543
2016-05-09 06:30 | 572 | 572
2016-05-09 07:00 | 571 | 570
2016-05-09 07:30 | 599 | 599
2016-05-09 08:00 | 612 | 612
2016-05-09 08:30 | 618 | 618
2016-05-09 09:00 | 608 | 608
2016-05-09 09:30 | 522 | 522
2016-05-09 10:00 | 536 | 536
2016-05-09 10:30 | 477 | 477
2016-05-09 11:00 | 467 | 467
2016-05-09 11:30 | 461 | 461
2016-05-09 12:00 | 463 | 463
2016-05-09 12:30 | 485 | 485
2016-05-09 13:00 | 480 | 480
2016-05-09 13:30 | 458 | 458
2016-05-09 14:00 | 445 | 445
2016-05-09 14:30 | 472 | 471
2016-05-09 15:00 | 472 | 472
2016-05-09 15:30 | 483 | 483
2016-05-09 16:00 | 443 | 443
2016-05-09 16:30 | 506 | 506
2016-05-09 17:00 | 509 | 509
2016-05-09 17:30 | 414 | 414
2016-05-09 18:00 | 374 | 372
2016-05-09 18:30 | 407 | 404
2016-05-09 19:00 | 482 | 479
2016-05-09 19:30 | 547 | 546
2016-05-09 20:00 | 511 | 511
2016-05-09 20:30 | 476 | 475
2016-05-09 21:00 | 497 | 495
2016-05-09 21:30 | 476 | 474
2016-05-09 22:00 | 459 | 457
2016-05-09 22:30 | 508 | 505
2016-05-09 23:00 | 561 | 559
2016-05-09 23:30 | 556 | 555
2016-05-10 | 549 | 548
2016-05-10 00:30 | 548 | 548
2016-05-10 01:00 | 534 | 533
2016-05-10 01:30 | 541 | 540
2016-05-10 02:00 | 536 | 535
2016-05-10 02:30 | 532 | 531
2016-05-10 03:00 | 524 | 523
2016-05-10 03:30 | 521 | 520
2016-05-10 04:00 | 517 | 515
2016-05-10 04:30 | 519 | 518
2016-05-10 05:00 | 490 | 488
2016-05-10 05:30 | 464 | 462
2016-05-10 06:00 | 487 | 484
2016-05-10 06:30 | 518 | 516
2016-05-10 07:00 | 556 | 554
2016-05-10 07:30 | 583 | 582
2016-05-10 08:00 | 612 | 611
2016-05-10 08:30 | 564 | 564
2016-05-10 09:00 | 541 | 540
2016-05-10 09:30 | 560 | 558
2016-05-10 10:00 | 561 | 560
2016-05-10 10:30 | 566 | 565
2016-05-10 11:00 | 569 | 569
2016-05-10 11:30 | 569 | 568
2016-05-10 12:00 | 551 | 550
2016-05-10 12:30 | 475 | 473
2016-05-10 13:00 | 486 | 483
2016-05-10 13:30 | 499 | 496
2016-05-10 14:00 | 510 | 508
2016-05-10 14:30 | 520 | 518
2016-05-10 15:00 | 524 | 522
2016-05-10 15:30 | 524 | 523
2016-05-10 16:00 | 530 | 529
2016-05-10 16:30 | 541 | 540
2016-05-10 17:00 | 545 | 544
2016-05-10 17:30 | 537 | 536
2016-05-10 18:00 | 459 | 458
2016-05-10 18:30 | 501 | 498
2016-05-10 19:00 | 526 | 524
2016-05-10 19:30 | 566 | 565
2016-05-10 20:00 | 576 | 575
2016-05-10 20:30 | 556 | 555
2016-05-10 21:00 | 533 | 532
2016-05-10 21:30 | 506 | 504
2016-05-10 22:00 | 474 | 472
2016-05-10 22:30 | 538 | 535
2016-05-10 23:00 | 641 | 639
2016-05-10 23:30 | 616 | 616
2016-05-11 | 599 | 598
2016-05-11 00:30 | 587 | 587
2016-05-11 01:00 | 571 | 570
2016-05-11 01:30 | 553 | 552
2016-05-11 02:00 | 544 | 543
2016-05-11 02:30 | 542 | 541
2016-05-11 03:00 | 534 | 532
2016-05-11 03:30 | 533 | 532
2016-05-11 04:00 | 533 | 531
2016-05-11 04:30 | 530 | 529
2016-05-11 05:00 | 531 | 530
2016-05-11 05:30 | 548 | 547
2016-05-11 06:00 | 568 | 567
2016-05-11 06:30 | 560 | 559
2016-05-11 07:00 | 569 | 568
2016-05-11 07:30 | 612 | 611
2016-05-11 08:00 | 623 | 622
2016-05-11 08:30 | 601 | 601
2016-05-11 09:00 | 608 | 608
2016-05-11 09:30 | 622 | 621
2016-05-11 10:00 | 621 | 620
2016-05-11 10:30 | 617 | 616
2016-05-11 11:00 | 616 | 615
2016-05-11 11:30 | 613 | 613
2016-05-11 12:00 | 615 | 614
2016-05-11 12:30 | 596 | 595
2016-05-11 13:00 | 588 | 587
2016-05-11 13:30 | 595 | 594
2016-05-11 14:00 | 594 | 593
2016-05-11 14:30 | 604 | 603
2016-05-11 15:00 | 601 | 600
2016-05-11 15:30 | 597 | 596
2016-05-11 16:00 | 601 | 600
2016-05-11 16:30 | 607 | 606
2016-05-11 17:00 | 606 | 606
2016-05-11 17:30 | 611 | 610
2016-05-11 18:00 | 600 | 599
2016-05-11 18:30 | 640 | 639
2016-05-11 19:00 | 662 | 661
2016-05-11 19:30 | 644 | 644
2016-05-11 20:00 | 627 | 626
2016-05-11 20:30 | 605 | 604
2016-05-11 21:00 | 584 | 584
2016-05-11 21:30 | 566 | 565
2016-05-11 22:00 | 541 | 540
2016-05-11 22:30 | 539 | 537
2016-05-11 23:00 | 523 | 522
2016-05-11 23:30 | 497 | 495
2016-05-12 | 490 | 488
2016-05-12 00:30 | 514 | 511
2016-05-12 01:00 | 507 | 504
2016-05-12 01:30 | 496 | 493
2016-05-12 02:00 | 489 | 487
2016-05-12 02:30 | 484 | 482
2016-05-12 03:00 | 481 | 479
2016-05-12 03:30 | 483 | 480
2016-05-12 04:00 | 483 | 481
2016-05-12 04:30 | 485 | 482
2016-05-12 05:00 | 489 | 486
2016-05-12 05:30 | 506 | 504
2016-05-12 06:00 | 519 | 517
2016-05-12 06:30 | 551 | 549
2016-05-12 07:00 | 550 | 548
2016-05-12 07:30 | 563 | 562
2016-05-12 08:00 | 586 | 585
2016-05-12 08:30 | 586 | 585
2016-05-12 09:00 | 538 | 537
2016-05-12 09:30 | 535 | 532
2016-05-12 10:00 | 528 | 525
2016-05-12 10:30 | 515 | 512
2016-05-12 11:00 | 509 | 507
2016-05-12 11:30 | 509 | 507
2016-05-12 12:00 | 516 | 514
2016-05-12 12:30 | 541 | 539
2016-05-12 13:00 | 554 | 552
2016-05-12 13:30 | 561 | 559
2016-05-12 14:00 | 571 | 570
2016-05-12 14:30 | 572 | 571
2016-05-12 15:00 | 571 | 570
2016-05-12 15:30 | 573 | 572
2016-05-12 16:00 | 591 | 590
2016-05-12 16:30 | 595 | 594
2016-05-12 17:00 | 599 | 598
2016-05-12 17:30 | 605 | 604
2016-05-12 18:00 | 589 | 588
2016-05-12 18:30 | 620 | 619
2016-05-12 19:00 | 654 | 653
2016-05-12 19:30 | 673 | 673
2016-05-12 20:00 | 658 | 658
2016-05-12 20:30 | 647 | 647
2016-05-12 21:00 | 628 | 628
2016-05-12 21:30 | 601 | 601
2016-05-12 22:00 | 579 | 578
2016-05-12 22:30 | 547 | 546
2016-05-12 23:00 | 523 | 522
2016-05-12 23:30 | 502 | 500
2016-05-13 | 515 | 512
2016-05-13 00:30 | 504 | 502
2016-05-13 01:00 | 490 | 487
2016-05-13 01:30 | 482 | 478
2016-05-13 02:00 | 475 | 471
2016-05-13 02:30 | 474 | 470
2016-05-13 03:00 | 470 | 467
2016-05-13 03:30 | 470 | 466
2016-05-13 04:00 | 469 | 465
2016-05-13 04:30 | 475 | 471
2016-05-13 05:00 | 480 | 476
2016-05-13 05:30 | 494 | 491
2016-05-13 06:00 | 491 | 488
2016-05-13 06:30 | 512 | 510
2016-05-13 07:00 | 543 | 541
2016-05-13 07:30 | 570 | 568
2016-05-13 08:00 | 575 | 574
2016-05-13 08:30 | 579 | 578
2016-05-13 09:00 | 583 | 582
2016-05-13 09:30 | 574 | 573
2016-05-13 10:00 | 562 | 561
2016-05-13 10:30 | 558 | 557
2016-05-13 11:00 | 548 | 546
2016-05-13 11:30 | 544 | 542
2016-05-13 12:00 | 544 | 542
2016-05-13 12:30 | 533 | 531
2016-05-13 13:00 | 530 | 528
2016-05-13 13:30 | 537 | 536
2016-05-13 14:00 | 543 | 541
2016-05-13 14:30 | 549 | 548
2016-05-13 15:00 | 551 | 549
2016-05-13 15:30 | 553 | 551
2016-05-13 16:00 | 564 | 563
2016-05-13 16:30 | 577 | 576
2016-05-13 17:00 | 585 | 584
2016-05-13 17:30 | 587 | 586
2016-05-13 18:00 | 575 | 574
2016-05-13 18:30 | 599 | 598
2016-05-13 19:00 | 618 | 617
2016-05-13 19:30 | 600 | 600
2016-05-13 20:00 | 608 | 607
2016-05-13 20:30 | 592 | 591
2016-05-13 21:00 | 580 | 579
2016-05-13 21:30 | 559 | 557
2016-05-13 22:00 | 544 | 543
2016-05-13 22:30 | 524 | 523
2016-05-13 23:00 | 546 | 544
2016-05-13 23:30 | 528 | 526
2016-05-14 | 518 | 516
2016-05-14 00:30 | 506 | 504
2016-05-14 01:00 | 491 | 489
2016-05-14 01:30 | 481 | 477
2016-05-14 02:00 | 473 | 469
2016-05-14 02:30 | 471 | 467
2016-05-14 03:00 | 469 | 465
2016-05-14 03:30 | 470 | 466
2016-05-14 04:00 | 467 | 463
2016-05-14 04:30 | 471 | 467
2016-05-14 05:00 | 470 | 466
2016-05-14 05:30 | 474 | 470
2016-05-14 06:00 | 480 | 476
2016-05-14 06:30 | 468 | 464
2016-05-14 07:00 | 474 | 470
2016-05-14 07:30 | 486 | 482
2016-05-14 08:00 | 501 | 498
2016-05-14 08:30 | 513 | 511
2016-05-14 09:00 | 515 | 512
2016-05-14 09:30 | 531 | 529
2016-05-14 10:00 | 526 | 524
2016-05-14 10:30 | 521 | 519
2016-05-14 11:00 | 497 | 495
2016-05-14 11:30 | 490 | 487
2016-05-14 12:00 | 488 | 486
2016-05-14 12:30 | 487 | 485
2016-05-14 13:00 | 489 | 486
2016-05-14 13:30 | 490 | 488
2016-05-14 14:00 | 497 | 495
2016-05-14 14:30 | 500 | 498
2016-05-14 15:00 | 505 | 503
2016-05-14 15:30 | 511 | 509
2016-05-14 16:00 | 515 | 513
2016-05-14 16:30 | 527 | 526
2016-05-14 17:00 | 546 | 545
2016-05-14 17:30 | 561 | 560
2016-05-14 18:00 | 571 | 571
2016-05-14 18:30 | 586 | 585
2016-05-14 19:00 | 596 | 596
2016-05-14 19:30 | 601 | 600
2016-05-14 20:00 | 591 | 591
2016-05-14 20:30 | 579 | 579
2016-05-14 21:00 | 566 | 565
2016-05-14 21:30 | 554 | 553
2016-05-14 22:00 | 547 | 547
2016-05-14 22:30 | 579 | 578
2016-05-14 23:00 | 568 | 567
2016-05-14 23:30 | 548 | 547
2016-05-15 | 535 | 534
2016-05-15 00:30 | 524 | 523
2016-05-15 01:00 | 510 | 508
2016-05-15 01:30 | 498 | 496
2016-05-15 02:00 | 490 | 488
2016-05-15 02:30 | 486 | 483
2016-05-15 03:00 | 483 | 480
2016-05-15 03:30 | 481 | 478
2016-05-15 04:00 | 476 | 473
2016-05-15 04:30 | 474 | 472
2016-05-15 05:00 | 472 | 469
2016-05-15 05:30 | 480 | 477
2016-05-15 06:00 | 485 | 482
2016-05-15 06:30 | 494 | 491
2016-05-15 07:00 | 496 | 493
2016-05-15 07:30 | 463 | 461
2016-05-15 08:00 | 467 | 464
2016-05-15 08:30 | 481 | 478
2016-05-15 09:00 | 485 | 482
2016-05-15 09:30 | 487 | 485
2016-05-15 10:00 | 490 | 488
2016-05-15 10:30 | 485 | 483
2016-05-15 11:00 | 469 | 467
2016-05-15 11:30 | 465 | 462
2016-05-15 12:00 | 457 | 454
2016-05-15 12:30 | 467 | 465
2016-05-15 13:00 | 461 | 458
2016-05-15 13:30 | 462 | 459
2016-05-15 14:00 | 467 | 464
2016-05-15 14:30 | 475 | 472
2016-05-15 15:00 | 490 | 487
2016-05-15 15:30 | 497 | 495
2016-05-15 16:00 | 504 | 502
2016-05-15 16:30 | 520 | 519
2016-05-15 17:00 | 545 | 543
2016-05-15 17:30 | 566 | 565
2016-05-15 18:00 | 549 | 548
2016-05-15 18:30 | 555 | 555
2016-05-15 19:00 | 594 | 593
2016-05-15 19:30 | 621 | 620
2016-05-15 20:00 | 608 | 608
2016-05-15 20:30 | 586 | 586
2016-05-15 21:00 | 569 | 569
2016-05-15 21:30 | 548 | 548
2016-05-15 22:00 | 520 | 519
2016-05-15 22:30 | 530 | 529
2016-05-15 23:00 | 513 | 511
2016-05-15 23:30 | 498 | 496
2016-05-16 | 481 | 479
2016-05-16 00:30 | 475 | 473
2016-05-16 01:00 | 446 | 444
2016-05-16 01:30 | 433 | 429
2016-05-16 02:00 | 426 | 423
2016-05-16 02:30 | 424 | 420
2016-05-16 03:00 | 422 | 418
2016-05-16 03:30 | 424 | 420
2016-05-16 04:00 | 422 | 418
2016-05-16 04:30 | 443 | 439
2016-05-16 05:00 | 469 | 466
2016-05-16 05:30 | 474 | 471
2016-05-16 06:00 | 513 | 510
2016-05-16 06:30 | 547 | 545
2016-05-16 07:00 | 583 | 582
2016-05-16 07:30 | 576 | 575
2016-05-16 08:00 | 580 | 579
2016-05-16 08:30 | 583 | 582
2016-05-16 09:00 | 582 | 581
2016-05-16 09:30 | 586 | 586
2016-05-16 10:00 | 586 | 585
2016-05-16 10:30 | 572 | 572
2016-05-16 11:00 | 567 | 566
2016-05-16 11:30 | 574 | 573
2016-05-16 12:00 | 579 | 578
2016-05-16 12:30 | 594 | 593
2016-05-16 13:00 | 586 | 586
2016-05-16 13:30 | 568 | 568
2016-05-16 14:00 | 582 | 582
2016-05-16 14:30 | 596 | 594
2016-05-16 15:00 | 586 | 585
2016-05-16 15:30 | 593 | 592
2016-05-16 16:00 | 605 | 604
2016-05-16 16:30 | 610 | 609
2016-05-16 17:00 | 616 | 616
2016-05-16 17:30 | 617 | 616
2016-05-16 18:00 | 616 | 615
2016-05-16 18:30 | 647 | 646
2016-05-16 19:00 | 660 | 660
2016-05-16 19:30 | 642 | 642
2016-05-16 20:00 | 620 | 620
2016-05-16 20:30 | 593 | 592
2016-05-16 21:00 | 539 | 538
2016-05-16 21:30 | 492 | 490
2016-05-16 22:00 | 471 | 468
2016-05-16 22:30 | 468 | 465
2016-05-16 23:00 | 467 | 464
2016-05-16 23:30 | 448 | 445
2016-05-17 | 433 | 430
2016-05-17 00:30 | 452 | 448
2016-05-17 01:00 | 438 | 435
2016-05-17 01:30 | 448 | 444
2016-05-17 02:00 | 482 | 479
2016-05-17 02:30 | 485 | 483
2016-05-17 03:00 | 492 | 489
2016-05-17 03:30 | 497 | 495
2016-05-17 04:00 | 496 | 494
2016-05-17 04:30 | 491 | 489
2016-05-17 05:00 | 500 | 498
2016-05-17 05:30 | 521 | 519
2016-05-17 06:00 | 539 | 538
2016-05-17 06:30 | 568 | 567
2016-05-17 07:00 | 595 | 594
2016-05-17 07:30 | 594 | 593
2016-05-17 08:00 | 598 | 597
2016-05-17 08:30 | 599 | 598
2016-05-17 09:00 | 598 | 597
2016-05-17 09:30 | 590 | 589
2016-05-17 10:00 | 582 | 581
2016-05-17 10:30 | 587 | 586
2016-05-17 11:00 | 568 | 566
2016-05-17 11:30 | 556 | 555
2016-05-17 12:00 | 554 | 553
2016-05-17 12:30 | 566 | 565
2016-05-17 13:00 | 564 | 563
2016-05-17 13:30 | 569 | 568
2016-05-17 14:00 | 576 | 574
2016-05-17 14:30 | 584 | 583
2016-05-17 15:00 | 568 | 567
2016-05-17 15:30 | 574 | 573
2016-05-17 16:00 | 588 | 587
2016-05-17 16:30 | 577 | 576
2016-05-17 17:00 | 599 | 598
2016-05-17 17:30 | 596 | 596
2016-05-17 18:00 | 560 | 560
2016-05-17 18:30 | 592 | 591
2016-05-17 19:00 | 628 | 628
2016-05-17 19:30 | 630 | 630
2016-05-17 20:00 | 632 | 632
2016-05-17 20:30 | 599 | 598
2016-05-17 21:00 | 593 | 593
2016-05-17 21:30 | 577 | 577
2016-05-17 22:00 | 556 | 555
2016-05-17 22:30 | 553 | 552
2016-05-17 23:00 | 538 | 536
2016-05-17 23:30 | 506 | 505
2016-05-18 | 473 | 470
2016-05-18 00:30 | 486 | 484
2016-05-18 01:00 | 531 | 529
2016-05-18 01:30 | 525 | 523
2016-05-18 02:00 | 525 | 524
2016-05-18 02:30 | 519 | 518
2016-05-18 03:00 | 518 | 516
2016-05-18 03:30 | 521 | 519
2016-05-18 04:00 | 516 | 515
2016-05-18 04:30 | 514 | 513
2016-05-18 05:00 | 523 | 522
2016-05-18 05:30 | 539 | 538
2016-05-18 06:00 | 556 | 555
2016-05-18 06:30 | 538 | 537
2016-05-18 07:00 | 534 | 533
2016-05-18 07:30 | 576 | 575
2016-05-18 08:00 | 601 | 600
2016-05-18 08:30 | 607 | 606
2016-05-18 09:00 | 606 | 606
2016-05-18 09:30 | 609 | 608
2016-05-18 10:00 | 607 | 606
2016-05-18 10:30 | 607 | 606
2016-05-18 11:00 | 581 | 580
2016-05-18 11:30 | 575 | 574
2016-05-18 12:00 | 580 | 579
2016-05-18 12:30 | 584 | 583
2016-05-18 13:00 | 577 | 577
2016-05-18 13:30 | 581 | 580
2016-05-18 14:00 | 587 | 586
2016-05-18 14:30 | 589 | 589
2016-05-18 15:00 | 593 | 592
2016-05-18 15:30 | 599 | 599
2016-05-18 16:00 | 609 | 608
2016-05-18 16:30 | 614 | 613
2016-05-18 17:00 | 546 | 546
2016-05-18 17:30 | 485 | 484
2016-05-18 18:00 | 457 | 454
2016-05-18 18:30 | 504 | 501
2016-05-18 19:00 | 520 | 518
2016-05-18 19:30 | 524 | 522
2016-05-18 20:00 | 516 | 514
2016-05-18 20:30 | 483 | 481
2016-05-18 21:00 | 478 | 475
2016-05-18 21:30 | 453 | 451
2016-05-18 22:00 | 446 | 443
2016-05-18 22:30 | 421 | 418
2016-05-18 23:00 | 397 | 394
2016-05-18 23:30 | 377 | 372
2016-05-19 | 410 | 405
2016-05-19 00:30 | 514 | 510
2016-05-19 01:00 | 532 | 530
2016-05-19 01:30 | 518 | 517
2016-05-19 02:00 | 513 | 512
2016-05-19 02:30 | 508 | 507
2016-05-19 03:00 | 503 | 502
2016-05-19 03:30 | 502 | 501
2016-05-19 04:00 | 503 | 502
2016-05-19 04:30 | 505 | 504
2016-05-19 05:00 | 512 | 511
2016-05-19 05:30 | 527 | 526
2016-05-19 06:00 | 545 | 544
2016-05-19 06:30 | 583 | 582
2016-05-19 07:00 | 564 | 564
2016-05-19 07:30 | 588 | 587
2016-05-19 08:00 | 595 | 595
2016-05-19 08:30 | 590 | 590
2016-05-19 09:00 | 593 | 592
2016-05-19 09:30 | 595 | 594
2016-05-19 10:00 | 593 | 592
2016-05-19 10:30 | 591 | 591
2016-05-19 11:00 | 567 | 567
2016-05-19 11:30 | 544 | 543
2016-05-19 12:00 | 563 | 562
2016-05-19 12:30 | 583 | 582
2016-05-19 13:00 | 582 | 581
2016-05-19 13:30 | 581 | 580
2016-05-19 14:00 | 587 | 587
2016-05-19 14:30 | 601 | 600
2016-05-19 15:00 | 600 | 599
2016-05-19 15:30 | 604 | 603
2016-05-19 16:00 | 608 | 607
2016-05-19 16:30 | 506 | 506
2016-05-19 17:00 | 460 | 457
2016-05-19 17:30 | 466 | 463
2016-05-19 18:00 | 470 | 467
2016-05-19 18:30 | 517 | 514
2016-05-19 19:00 | 524 | 522
2016-05-19 19:30 | 512 | 510
2016-05-19 20:00 | 491 | 490
2016-05-19 20:30 | 470 | 468
2016-05-19 21:00 | 474 | 472
2016-05-19 21:30 | 568 | 567
2016-05-19 22:00 | 581 | 581
2016-05-19 22:30 | 550 | 550
2016-05-19 23:00 | 529 | 528
2016-05-19 23:30 | 503 | 502
2016-05-20 | 503 | 502
2016-05-20 00:30 | 551 | 549
2016-05-20 01:00 | 534 | 534
2016-05-20 01:30 | 521 | 520
2016-05-20 02:00 | 515 | 514
2016-05-20 02:30 | 510 | 508
2016-05-20 03:00 | 504 | 503
2016-05-20 03:30 | 506 | 505
2016-05-20 04:00 | 503 | 501
2016-05-20 04:30 | 507 | 506
2016-05-20 05:00 | 508 | 507
2016-05-20 05:30 | 527 | 526
2016-05-20 06:00 | 551 | 550
2016-05-20 06:30 | 563 | 563
2016-05-20 07:00 | 530 | 529
2016-05-20 07:30 | 562 | 562
2016-05-20 08:00 | 559 | 558
2016-05-20 08:30 | 598 | 598
2016-05-20 09:00 | 602 | 602
2016-05-20 09:30 | 610 | 610
2016-05-20 10:00 | 600 | 599
2016-05-20 10:30 | 596 | 596
2016-05-20 11:00 | 564 | 564
2016-05-20 11:30 | 563 | 562
2016-05-20 12:00 | 570 | 570
2016-05-20 12:30 | 569 | 569
2016-05-20 13:00 | 573 | 572
2016-05-20 13:30 | 578 | 577
2016-05-20 14:00 | 604 | 603
2016-05-20 14:30 | 606 | 606
2016-05-20 15:00 | 597 | 597
2016-05-20 15:30 | 594 | 594
2016-05-20 16:00 | 591 | 591
2016-05-20 16:30 | 595 | 595
2016-05-20 17:00 | 597 | 597
2016-05-20 17:30 | 584 | 584
2016-05-20 18:00 | 593 | 593
2016-05-20 18:30 | 608 | 608
2016-05-20 19:00 | 621 | 621
2016-05-20 19:30 | 603 | 603
2016-05-20 20:00 | 600 | 600
2016-05-20 20:30 | 559 | 559
2016-05-20 21:00 | 550 | 550
2016-05-20 21:30 | 567 | 566
2016-05-20 22:00 | 565 | 564
2016-05-20 22:30 | 481 | 480
2016-05-20 23:00 | 537 | 536
2016-05-20 23:30 | 519 | 519
2016-05-21 | 503 | 503
2016-05-21 00:30 | 511 | 510
2016-05-21 01:00 | 509 | 508
2016-05-21 01:30 | 511 | 510
2016-05-21 02:00 | 502 | 501
2016-05-21 02:30 | 498 | 497
2016-05-21 03:00 | 493 | 492
2016-05-21 03:30 | 488 | 487
2016-05-21 04:00 | 485 | 484
2016-05-21 04:30 | 486 | 485
2016-05-21 05:00 | 489 | 488
2016-05-21 05:30 | 496 | 495
2016-05-21 06:00 | 498 | 498
2016-05-21 06:30 | 513 | 512
2016-05-21 07:00 | 479 | 478
2016-05-21 07:30 | 490 | 489
2016-05-21 08:00 | 515 | 514
2016-05-21 08:30 | 538 | 537
2016-05-21 09:00 | 553 | 553
2016-05-21 09:30 | 551 | 551
2016-05-21 10:00 | 550 | 550
2016-05-21 10:30 | 543 | 542
2016-05-21 11:00 | 530 | 530
2016-05-21 11:30 | 526 | 525
2016-05-21 12:00 | 524 | 524
2016-05-21 12:30 | 518 | 517
2016-05-21 13:00 | 516 | 515
2016-05-21 13:30 | 501 | 500
2016-05-21 14:00 | 499 | 499
2016-05-21 14:30 | 509 | 509
2016-05-21 15:00 | 510 | 510
2016-05-21 15:30 | 511 | 511
2016-05-21 16:00 | 513 | 513
2016-05-21 16:30 | 517 | 516
2016-05-21 17:00 | 472 | 472
2016-05-21 17:30 | 471 | 470
2016-05-21 18:00 | 472 | 471
2016-05-21 18:30 | 499 | 498
2016-05-21 19:00 | 526 | 525
2016-05-21 19:30 | 523 | 523
2016-05-21 20:00 | 518 | 517
2016-05-21 20:30 | 499 | 499
2016-05-21 21:00 | 487 | 486
2016-05-21 21:30 | 478 | 477
2016-05-21 22:00 | 490 | 489
2016-05-21 22:30 | 475 | 474
2016-05-21 23:00 | 461 | 460
2016-05-21 23:30 | 444 | 443
2016-05-22 | 436 | 434
2016-05-22 00:30 | 425 | 424
2016-05-22 01:00 | 440 | 438
2016-05-22 01:30 | 488 | 486
2016-05-22 02:00 | 478 | 477
2016-05-22 02:30 | 468 | 467
2016-05-22 03:00 | 418 | 417
2016-05-22 03:30 | 408 | 406
2016-05-22 04:00 | 388 | 386
2016-05-22 04:30 | 374 | 372
2016-05-22 05:00 | 361 | 358
2016-05-22 05:30 | 368 | 365
2016-05-22 06:00 | 369 | 367
2016-05-22 06:30 | 378 | 375
2016-05-22 07:00 | 386 | 383
2016-05-22 07:30 | 401 | 399
2016-05-22 08:00 | 422 | 419
2016-05-22 08:30 | 445 | 443
2016-05-22 09:00 | 456 | 454
2016-05-22 09:30 | 468 | 467
2016-05-22 10:00 | 471 | 470
2016-05-22 10:30 | 469 | 468
2016-05-22 11:00 | 468 | 467
2016-05-22 11:30 | 468 | 467
2016-05-22 12:00 | 472 | 471
2016-05-22 12:30 | 476 | 476
2016-05-22 13:00 | 459 | 458
2016-05-22 13:30 | 461 | 460
2016-05-22 14:00 | 456 | 455
2016-05-22 14:30 | 452 | 451
2016-05-22 15:00 | 462 | 461
2016-05-22 15:30 | 462 | 461
2016-05-22 16:00 | 472 | 471
2016-05-22 16:30 | 483 | 482
2016-05-22 17:00 | 468 | 468
2016-05-22 17:30 | 484 | 483
2016-05-22 18:00 | 461 | 461
2016-05-22 18:30 | 479 | 478
2016-05-22 19:00 | 522 | 522
2016-05-22 19:30 | 525 | 525
2016-05-22 20:00 | 506 | 505
2016-05-22 20:30 | 490 | 490
2016-05-22 21:00 | 475 | 475
2016-05-22 21:30 | 461 | 460
2016-05-22 22:00 | 448 | 448
2016-05-22 22:30 | 458 | 457
2016-05-22 23:00 | 428 | 427
2016-05-22 23:30 | 390 | 388
2016-05-23 | 380 | 378
2016-05-23 00:30 | 373 | 371
2016-05-23 01:00 | 356 | 353
2016-05-23 01:30 | 344 | 340
2016-05-23 02:00 | 339 | 334
2016-05-23 02:30 | 342 | 337
2016-05-23 03:00 | 337 | 333
2016-05-23 03:30 | 335 | 330
2016-05-23 04:00 | 338 | 333
2016-05-23 04:30 | 343 | 339
2016-05-23 05:00 | 348 | 344
2016-05-23 05:30 | 361 | 357
2016-05-23 06:00 | 380 | 376
2016-05-23 06:30 | 421 | 418
2016-05-23 07:00 | 375 | 373
2016-05-23 07:30 | 448 | 446
2016-05-23 08:00 | 495 | 494
2016-05-23 08:30 | 521 | 520
2016-05-23 09:00 | 534 | 534
2016-05-23 09:30 | 544 | 543
2016-05-23 10:00 | 534 | 534
2016-05-23 10:30 | 529 | 529
2016-05-23 11:00 | 533 | 533
2016-05-23 11:30 | 530 | 530
2016-05-23 12:00 | 527 | 527
2016-05-23 12:30 | 530 | 530
2016-05-23 13:00 | 517 | 516
2016-05-23 13:30 | 497 | 497
2016-05-23 14:00 | 502 | 502
2016-05-23 14:30 | 510 | 509
2016-05-23 15:00 | 523 | 522
2016-05-23 15:30 | 525 | 525
2016-05-23 16:00 | 513 | 513
2016-05-23 16:30 | 429 | 429
2016-05-23 17:00 | 381 | 379
2016-05-23 17:30 | 374 | 371
2016-05-23 18:00 | 397 | 394
2016-05-23 18:30 | 436 | 433
2016-05-23 19:00 | 442 | 440
2016-05-23 19:30 | 422 | 420
2016-05-23 20:00 | 403 | 401
2016-05-23 20:30 | 381 | 379
2016-05-23 21:00 | 474 | 472
2016-05-23 21:30 | 484 | 484
2016-05-23 22:00 | 466 | 466
2016-05-23 22:30 | 463 | 462
2016-05-23 23:00 | 446 | 445
2016-05-23 23:30 | 424 | 423
2016-05-24 | 414 | 412
2016-05-24 00:30 | 400 | 398
2016-05-24 01:00 | 391 | 389
2016-05-24 01:30 | 374 | 372
2016-05-24 02:00 | 367 | 364
2016-05-24 02:30 | 362 | 359
2016-05-24 03:00 | 359 | 356
2016-05-24 03:30 | 358 | 355
2016-05-24 04:00 | 355 | 352
2016-05-24 04:30 | 357 | 354
2016-05-24 05:00 | 356 | 352
2016-05-24 05:30 | 351 | 348
2016-05-24 06:00 | 325 | 322
2016-05-24 06:30 | 346 | 343
2016-05-24 07:00 | 379 | 376
2016-05-24 07:30 | 419 | 417
2016-05-24 08:00 | 445 | 443
2016-05-24 08:30 | 453 | 451
2016-05-24 09:00 | 452 | 450
2016-05-24 09:30 | 440 | 439
2016-05-24 10:00 | 427 | 425
2016-05-24 10:30 | 429 | 426
2016-05-24 11:00 | 427 | 425
2016-05-24 11:30 | 422 | 420
2016-05-24 12:00 | 425 | 422
2016-05-24 12:30 | 422 | 420
2016-05-24 13:00 | 409 | 407
2016-05-24 13:30 | 409 | 405
2016-05-24 14:00 | 426 | 422
2016-05-24 14:30 | 435 | 432
2016-05-24 15:00 | 435 | 432
2016-05-24 15:30 | 458 | 456
2016-05-24 16:00 | 458 | 456
2016-05-24 16:30 | 434 | 432
2016-05-24 17:00 | 444 | 441
2016-05-24 17:30 | 465 | 463
2016-05-24 18:00 | 480 | 478
2016-05-24 18:30 | 503 | 502
2016-05-24 19:00 | 516 | 514
2016-05-24 19:30 | 519 | 518
2016-05-24 20:00 | 484 | 483
2016-05-24 20:30 | 500 | 499
2016-05-24 21:00 | 494 | 493
2016-05-24 21:30 | 477 | 476
2016-05-24 22:00 | 447 | 446
2016-05-24 22:30 | 442 | 440
2016-05-24 23:00 | 429 | 426
2016-05-24 23:30 | 411 | 407
2016-05-25 | 400 | 396
2016-05-25 00:30 | 387 | 383
2016-05-25 01:00 | 370 | 365
2016-05-25 01:30 | 361 | 355
2016-05-25 02:00 | 356 | 349
2016-05-25 02:30 | 352 | 345
2016-05-25 03:00 | 353 | 346
2016-05-25 03:30 | 353 | 347
2016-05-25 04:00 | 355 | 348
2016-05-25 04:30 | 364 | 358
2016-05-25 05:00 | 371 | 365
2016-05-25 05:30 | 383 | 378
2016-05-25 06:00 | 404 | 399
2016-05-25 06:30 | 450 | 446
2016-05-25 07:00 | 488 | 485
2016-05-25 07:30 | 549 | 547
2016-05-25 08:00 | 591 | 590
2016-05-25 08:30 | 624 | 624
2016-05-25 09:00 | 605 | 604
2016-05-25 09:30 | 588 | 587
2016-05-25 10:00 | 547 | 546
2016-05-25 10:30 | 515 | 512
2016-05-25 11:00 | 504 | 501
2016-05-25 11:30 | 482 | 479
2016-05-25 12:00 | 487 | 484
2016-05-25 12:30 | 494 | 492
2016-05-25 13:00 | 487 | 485
2016-05-25 13:30 | 487 | 485
2016-05-25 14:00 | 449 | 447
2016-05-25 14:30 | 380 | 377
2016-05-25 15:00 | 356 | 350
2016-05-25 15:30 | 357 | 350
2016-05-25 16:00 | 357 | 350
2016-05-25 16:30 | 374 | 367
2016-05-25 17:00 | 352 | 345
2016-05-25 17:30 | 326 | 318
2016-05-25 18:00 | 334 | 325
2016-05-25 18:30 | 374 | 367
2016-05-25 19:00 | 395 | 389
2016-05-25 19:30 | 394 | 388
2016-05-25 20:00 | 385 | 379
2016-05-25 20:30 | 369 | 362
2016-05-25 21:00 | 352 | 344
2016-05-25 21:30 | 392 | 384
2016-05-25 22:00 | 399 | 393
2016-05-25 22:30 | 376 | 370
2016-05-25 23:00 | 357 | 350
2016-05-25 23:30 | 346 | 338
2016-05-26 | 332 | 323
2016-05-26 00:30 | 329 | 319
2016-05-26 01:00 | 305 | 294
2016-05-26 01:30 | 324 | 312
2016-05-26 02:00 | 332 | 321
2016-05-26 02:30 | 357 | 347
2016-05-26 03:00 | 357 | 348
2016-05-26 03:30 | 360 | 351
2016-05-26 04:00 | 356 | 348
2016-05-26 04:30 | 359 | 350
2016-05-26 05:00 | 368 | 360
2016-05-26 05:30 | 382 | 375
2016-05-26 06:00 | 401 | 394
2016-05-26 06:30 | 323 | 315
2016-05-26 07:00 | 305 | 295
2016-05-26 07:30 | 311 | 299
2016-05-26 08:00 | 310 | 298
2016-05-26 08:30 | 300 | 287
2016-05-26 09:00 | 284 | 270
2016-05-26 09:30 | 291 | 277
2016-05-26 10:00 | 314 | 301
2016-05-26 10:30 | 303 | 291
2016-05-26 11:00 | 339 | 328
2016-05-26 11:30 | 369 | 361
2016-05-26 12:00 | 409 | 402
2016-05-26 12:30 | 435 | 430
2016-05-26 13:00 | 449 | 445
2016-05-26 13:30 | 455 | 450
2016-05-26 14:00 | 406 | 402
2016-05-26 14:30 | 386 | 379
2016-05-26 15:00 | 387 | 380
2016-05-26 15:30 | 400 | 394
2016-05-26 16:00 | 400 | 394
2016-05-26 16:30 | 403 | 397
2016-05-26 17:00 | 394 | 388
2016-05-26 17:30 | 390 | 384
2016-05-26 18:00 | 398 | 392
2016-05-26 18:30 | 437 | 432
2016-05-26 19:00 | 460 | 456
2016-05-26 19:30 | 445 | 442
2016-05-26 20:00 | 431 | 428
2016-05-26 20:30 | 414 | 411
2016-05-26 21:00 | 408 | 404
2016-05-26 21:30 | 386 | 381
2016-05-26 22:00 | 364 | 359
2016-05-26 22:30 | 337 | 331
2016-05-26 23:00 | 314 | 306
2016-05-26 23:30 | 293 | 282
2016-05-27 | 286 | 274
2016-05-27 00:30 | 330 | 319
2016-05-27 01:00 | 379 | 371
2016-05-27 01:30 | 446 | 441
2016-05-27 02:00 | 442 | 438
2016-05-27 02:30 | 440 | 436
2016-05-27 03:00 | 433 | 430
2016-05-27 03:30 | 432 | 428
2016-05-27 04:00 | 436 | 432
2016-05-27 04:30 | 438 | 434
2016-05-27 05:00 | 442 | 438
2016-05-27 05:30 | 454 | 450
2016-05-27 06:00 | 468 | 465
2016-05-27 06:30 | 495 | 493
2016-05-27 07:00 | 530 | 528
2016-05-27 07:30 | 577 | 575
2016-05-27 08:00 | 572 | 572
2016-05-27 08:30 | 576 | 575
2016-05-27 09:00 | 585 | 585
2016-05-27 09:30 | 581 | 581
2016-05-27 10:00 | 560 | 559
2016-05-27 10:30 | 566 | 565
2016-05-27 11:00 | 578 | 576
2016-05-27 11:30 | 579 | 578
2016-05-27 12:00 | 585 | 584
2016-05-27 12:30 | 572 | 571
2016-05-27 13:00 | 576 | 575
2016-05-27 13:30 | 574 | 573
2016-05-27 14:00 | 579 | 578
2016-05-27 14:30 | 597 | 596
2016-05-27 15:00 | 601 | 600
2016-05-27 15:30 | 596 | 595
2016-05-27 16:00 | 609 | 608
2016-05-27 16:30 | 624 | 623
2016-05-27 17:00 | 631 | 631
2016-05-27 17:30 | 629 | 629
2016-05-27 18:00 | 614 | 613
2016-05-27 18:30 | 631 | 630
2016-05-27 19:00 | 633 | 632
2016-05-27 19:30 | 619 | 619
2016-05-27 20:00 | 600 | 599
2016-05-27 20:30 | 594 | 593
2016-05-27 21:00 | 586 | 585
2016-05-27 21:30 | 569 | 568
2016-05-27 22:00 | 553 | 552
2016-05-27 22:30 | 543 | 541
2016-05-27 23:00 | 529 | 527
2016-05-27 23:30 | 504 | 503
2016-05-28 | 491 | 489
2016-05-28 00:30 | 489 | 486
2016-05-28 01:00 | 475 | 472
2016-05-28 01:30 | 464 | 461
2016-05-28 02:00 | 458 | 454
2016-05-28 02:30 | 447 | 443
2016-05-28 03:00 | 445 | 440
2016-05-28 03:30 | 439 | 434
2016-05-28 04:00 | 437 | 432
2016-05-28 04:30 | 436 | 431
2016-05-28 05:00 | 434 | 429
2016-05-28 05:30 | 439 | 434
2016-05-28 06:00 | 447 | 442
2016-05-28 06:30 | 456 | 452
2016-05-28 07:00 | 458 | 454
2016-05-28 07:30 | 478 | 474
2016-05-28 08:00 | 491 | 488
2016-05-28 08:30 | 503 | 501
2016-05-28 09:00 | 504 | 502
2016-05-28 09:30 | 462 | 460
2016-05-28 10:00 | 443 | 440
2016-05-28 10:30 | 479 | 476
2016-05-28 11:00 | 473 | 471
2016-05-28 11:30 | 486 | 483
2016-05-28 12:00 | 491 | 488
2016-05-28 12:30 | 489 | 487
2016-05-28 13:00 | 497 | 494
2016-05-28 13:30 | 502 | 500
2016-05-28 14:00 | 513 | 511
2016-05-28 14:30 | 522 | 520
2016-05-28 15:00 | 531 | 530
2016-05-28 15:30 | 539 | 538
2016-05-28 16:00 | 550 | 549
2016-05-28 16:30 | 563 | 562
2016-05-28 17:00 | 465 | 464
2016-05-28 17:30 | 430 | 426
2016-05-28 18:00 | 434 | 429
2016-05-28 18:30 | 451 | 447
2016-05-28 19:00 | 460 | 456
2016-05-28 19:30 | 592 | 589
2016-05-28 20:00 | 616 | 615
2016-05-28 20:30 | 598 | 597
2016-05-28 21:00 | 583 | 583
2016-05-28 21:30 | 564 | 563
2016-05-28 22:00 | 555 | 553
2016-05-28 22:30 | 541 | 539
2016-05-28 23:00 | 520 | 518
2016-05-28 23:30 | 508 | 506
2016-05-29 | 499 | 497
2016-05-29 00:30 | 484 | 481
2016-05-29 01:00 | 471 | 468
2016-05-29 01:30 | 457 | 454
2016-05-29 02:00 | 451 | 447
2016-05-29 02:30 | 442 | 438
2016-05-29 03:00 | 435 | 430
2016-05-29 03:30 | 434 | 430
2016-05-29 04:00 | 430 | 426
2016-05-29 04:30 | 431 | 426
2016-05-29 05:00 | 432 | 427
2016-05-29 05:30 | 440 | 435
2016-05-29 06:00 | 447 | 442
2016-05-29 06:30 | 447 | 442
2016-05-29 07:00 | 449 | 445
2016-05-29 07:30 | 461 | 457
2016-05-29 08:00 | 474 | 470
2016-05-29 08:30 | 490 | 487
2016-05-29 09:00 | 495 | 492
2016-05-29 09:30 | 505 | 502
2016-05-29 10:00 | 509 | 507
2016-05-29 10:30 | 505 | 503
2016-05-29 11:00 | 480 | 478
2016-05-29 11:30 | 472 | 469
2016-05-29 12:00 | 478 | 474
2016-05-29 12:30 | 482 | 479
2016-05-29 13:00 | 487 | 484
2016-05-29 13:30 | 492 | 489
2016-05-29 14:00 | 503 | 500
2016-05-29 14:30 | 513 | 510
2016-05-29 15:00 | 518 | 516
2016-05-29 15:30 | 526 | 524
2016-05-29 16:00 | 531 | 529
2016-05-29 16:30 | 541 | 540
2016-05-29 17:00 | 562 | 561
2016-05-29 17:30 | 560 | 559
2016-05-29 18:00 | 540 | 540
2016-05-29 18:30 | 569 | 569
2016-05-29 19:00 | 599 | 599
2016-05-29 19:30 | 590 | 589
2016-05-29 20:00 | 573 | 572
2016-05-29 20:30 | 561 | 560
2016-05-29 21:00 | 544 | 543
2016-05-29 21:30 | 533 | 532
2016-05-29 22:00 | 514 | 513
2016-05-29 22:30 | 534 | 532
2016-05-29 23:00 | 519 | 517
2016-05-29 23:30 | 501 | 499
2016-05-30 | 488 | 486
2016-05-30 00:30 | 481 | 478
2016-05-30 01:00 | 466 | 464
2016-05-30 01:30 | 458 | 455
2016-05-30 02:00 | 449 | 446
2016-05-30 02:30 | 446 | 442
2016-05-30 03:00 | 445 | 442
2016-05-30 03:30 | 438 | 434
2016-05-30 04:00 | 440 | 436
2016-05-30 04:30 | 439 | 435
2016-05-30 05:00 | 405 | 400
2016-05-30 05:30 | 405 | 400
2016-05-30 06:00 | 426 | 421
2016-05-30 06:30 | 419 | 414
2016-05-30 07:00 | 410 | 406
2016-05-30 07:30 | 444 | 441
2016-05-30 08:00 | 465 | 462
2016-05-30 08:30 | 469 | 467
2016-05-30 09:00 | 444 | 442
2016-05-30 09:30 | 448 | 446
2016-05-30 10:00 | 471 | 468
2016-05-30 10:30 | 469 | 467
2016-05-30 11:00 | 457 | 455
2016-05-30 11:30 | 458 | 456
2016-05-30 12:00 | 459 | 457
2016-05-30 12:30 | 455 | 453
2016-05-30 13:00 | 447 | 445
2016-05-30 13:30 | 455 | 453
2016-05-30 14:00 | 460 | 458
2016-05-30 14:30 | 461 | 459
2016-05-30 15:00 | 445 | 444
2016-05-30 15:30 | 434 | 432
2016-05-30 16:00 | 348 | 346
2016-05-30 16:30 | 422 | 417
2016-05-30 17:00 | 353 | 349
2016-05-30 17:30 | 345 | 339
2016-05-30 18:00 | 340 | 334
2016-05-30 18:30 | 370 | 365
2016-05-30 19:00 | 372 | 368
2016-05-30 19:30 | 414 | 411
2016-05-30 20:00 | 409 | 406
2016-05-30 20:30 | 392 | 388
2016-05-30 21:00 | 435 | 431
2016-05-30 21:30 | 436 | 433
2016-05-30 22:00 | 417 | 415
2016-05-30 22:30 | 393 | 390
2016-05-30 23:00 | 383 | 379
2016-05-30 23:30 | 361 | 357
2016-05-31 | 348 | 343
2016-05-31 00:30 | 335 | 329
2016-05-31 01:00 | 327 | 320
2016-05-31 01:30 | 316 | 309
2016-05-31 02:00 | 310 | 302
2016-05-31 02:30 | 307 | 299
2016-05-31 03:00 | 303 | 294
2016-05-31 03:30 | 303 | 294
2016-05-31 04:00 | 307 | 298
2016-05-31 04:30 | 308 | 299
2016-05-31 05:00 | 315 | 305
2016-05-31 05:30 | 329 | 321
2016-05-31 06:00 | 342 | 335
2016-05-31 06:30 | 271 | 263
2016-05-31 07:00 | 266 | 256
2016-05-31 07:30 | 365 | 358
2016-05-31 08:00 | 423 | 419
2016-05-31 08:30 | 454 | 451
2016-05-31 09:00 | 469 | 467
2016-05-31 09:30 | 470 | 468
2016-05-31 10:00 | 461 | 459
2016-05-31 10:30 | 471 | 469
2016-05-31 11:00 | 464 | 462
2016-05-31 11:30 | 439 | 437
2016-05-31 12:00 | 374 | 371
2016-05-31 12:30 | 297 | 291
2016-05-31 13:00 | 312 | 304
2016-05-31 13:30 | 343 | 336
2016-05-31 14:00 | 339 | 334
2016-05-31 14:30 | 355 | 350
2016-05-31 15:00 | 400 | 396
2016-05-31 15:30 | 425 | 422
2016-05-31 16:00 | 436 | 434
2016-05-31 16:30 | 447 | 445
2016-05-31 17:00 | 431 | 430
2016-05-31 17:30 | 362 | 360
2016-05-31 18:00 | 297 | 293
2016-05-31 18:30 | 332 | 326
2016-05-31 19:00 | 336 | 331
2016-05-31 19:30 | 341 | 336
2016-05-31 20:00 | 348 | 343
2016-05-31 20:30 | 375 | 370
2016-05-31 21:00 | 460 | 457
2016-05-31 21:30 | 444 | 442
2016-05-31 22:00 | 430 | 428
2016-05-31 22:30 | 406 | 403
2016-05-31 23:00 | 392 | 389
2016-05-31 23:30 | 375 | 371
2016-06-01 | 358 | 354
2016-06-01 00:30 | 338 | 333
2016-06-01 01:00 | 306 | 301
2016-06-01 01:30 | 302 | 296
2016-06-01 02:00 | 313 | 306
2016-06-01 02:30 | 307 | 300
2016-06-01 03:00 | 302 | 295
2016-06-01 03:30 | 306 | 298
2016-06-01 04:00 | 303 | 295
2016-06-01 04:30 | 306 | 298
2016-06-01 05:00 | 309 | 302
2016-06-01 05:30 | 324 | 317
2016-06-01 06:00 | 344 | 338
2016-06-01 06:30 | 305 | 299
2016-06-01 07:00 | 265 | 257
2016-06-01 07:30 | 354 | 346
2016-06-01 08:00 | 385 | 379
2016-06-01 08:30 | 408 | 404
2016-06-01 09:00 | 437 | 433
2016-06-01 09:30 | 434 | 431
2016-06-01 10:00 | 440 | 437
2016-06-01 10:30 | 434 | 432
2016-06-01 11:00 | 366 | 363
2016-06-01 11:30 | 341 | 336
2016-06-01 12:00 | 383 | 379
2016-06-01 12:30 | 355 | 352
2016-06-01 13:00 | 399 | 397
2016-06-01 13:30 | 408 | 406
2016-06-01 14:00 | 414 | 412
2016-06-01 14:30 | 419 | 416
2016-06-01 15:00 | 429 | 427
2016-06-01 15:30 | 428 | 426
2016-06-01 16:00 | 381 | 378
2016-06-01 16:30 | 411 | 408
2016-06-01 17:00 | 378 | 376
2016-06-01 17:30 | 321 | 318
2016-06-01 18:00 | 264 | 258
2016-06-01 18:30 | 146 | 129
2016-06-01 19:00 | 235 | 216
2016-06-01 19:30 | 236 | 222
2016-06-01 20:00 | 155 | 134
2016-06-01 20:30 | 210 | 189
2016-06-01 21:00 | 250 | 235
2016-06-01 21:30 | 297 | 287
2016-06-01 22:00 | 327 | 319
2016-06-01 22:30 | 147 | 132
2016-06-01 23:00 | 173 | 147
2016-06-01 23:30 | 258 | 242
2016-06-02 | 300 | 292
2016-06-02 00:30 | 449 | 444
2016-06-02 01:00 | 453 | 452
2016-06-02 01:30 | 443 | 441
2016-06-02 02:00 | 436 | 434
2016-06-02 02:30 | 438 | 436
2016-06-02 03:00 | 435 | 433
2016-06-02 03:30 | 427 | 425
2016-06-02 04:00 | 429 | 427
2016-06-02 04:30 | 430 | 427
2016-06-02 05:00 | 432 | 429
2016-06-02 05:30 | 448 | 446
2016-06-02 06:00 | 445 | 443
2016-06-02 06:30 | 465 | 463
2016-06-02 07:00 | 450 | 448
2016-06-02 07:30 | 480 | 479
2016-06-02 08:00 | 495 | 493
2016-06-02 08:30 | 495 | 494
2016-06-02 09:00 | 508 | 507
2016-06-02 09:30 | 507 | 506
2016-06-02 10:00 | 501 | 500
2016-06-02 10:30 | 493 | 492
2016-06-02 11:00 | 487 | 485
2016-06-02 11:30 | 482 | 480
2016-06-02 12:00 | 391 | 389
2016-06-02 12:30 | 391 | 387
2016-06-02 13:00 | 391 | 387
2016-06-02 13:30 | 397 | 393
2016-06-02 14:00 | 390 | 386
2016-06-02 14:30 | 396 | 392
2016-06-02 15:00 | 443 | 440
2016-06-02 15:30 | 403 | 401
2016-06-02 16:00 | 459 | 457
2016-06-02 16:30 | 512 | 511
2016-06-02 17:00 | 529 | 528
2016-06-02 17:30 | 538 | 538
2016-06-02 18:00 | 534 | 533
2016-06-02 18:30 | 556 | 556
2016-06-02 19:00 | 582 | 582
2016-06-02 19:30 | 599 | 599
2016-06-02 20:00 | 594 | 594
2016-06-02 20:30 | 554 | 554
2016-06-02 21:00 | 537 | 536
2016-06-02 21:30 | 539 | 538
2016-06-02 22:00 | 520 | 520
2016-06-02 22:30 | 518 | 517
2016-06-02 23:00 | 500 | 500
2016-06-02 23:30 | 492 | 491
2016-06-03 | 463 | 461
2016-06-03 00:30 | 459 | 458
2016-06-03 01:00 | 448 | 446
2016-06-03 01:30 | 443 | 441
2016-06-03 02:00 | 442 | 439
2016-06-03 02:30 | 435 | 432
2016-06-03 03:00 | 429 | 426
2016-06-03 03:30 | 427 | 424
2016-06-03 04:00 | 427 | 424
2016-06-03 04:30 | 429 | 426
2016-06-03 05:00 | 436 | 433
2016-06-03 05:30 | 449 | 446
2016-06-03 06:00 | 412 | 410
2016-06-03 06:30 | 419 | 416
2016-06-03 07:00 | 448 | 445
2016-06-03 07:30 | 489 | 487
2016-06-03 08:00 | 500 | 499
2016-06-03 08:30 | 499 | 498
2016-06-03 09:00 | 493 | 492
2016-06-03 09:30 | 496 | 495
2016-06-03 10:00 | 515 | 514
2016-06-03 10:30 | 517 | 517
2016-06-03 11:00 | 505 | 504
2016-06-03 11:30 | 492 | 492
2016-06-03 12:00 | 505 | 504
2016-06-03 12:30 | 520 | 519
2016-06-03 13:00 | 458 | 458
2016-06-03 13:30 | 469 | 467
2016-06-03 14:00 | 479 | 478
2016-06-03 14:30 | 507 | 506
2016-06-03 15:00 | 508 | 507
2016-06-03 15:30 | 503 | 502
2016-06-03 16:00 | 476 | 475
2016-06-03 16:30 | 402 | 401
2016-06-03 17:00 | 334 | 331
2016-06-03 17:30 | 330 | 325
2016-06-03 18:00 | 308 | 303
2016-06-03 18:30 | 359 | 354
2016-06-03 19:00 | 383 | 379
2016-06-03 19:30 | 372 | 369
2016-06-03 20:00 | 389 | 385
2016-06-03 20:30 | 400 | 396
2016-06-03 21:00 | 402 | 398
2016-06-03 21:30 | 385 | 381
2016-06-03 22:00 | 399 | 395
2016-06-03 22:30 | 390 | 386
2016-06-03 23:00 | 469 | 465
2016-06-03 23:30 | 509 | 507
2016-06-04 | 493 | 492
2016-06-04 00:30 | 471 | 470
2016-06-04 01:00 | 451 | 449
2016-06-04 01:30 | 432 | 430
2016-06-04 02:00 | 421 | 418
2016-06-04 02:30 | 416 | 413
2016-06-04 03:00 | 407 | 404
2016-06-04 03:30 | 406 | 403
2016-06-04 04:00 | 406 | 402
2016-06-04 04:30 | 406 | 403
2016-06-04 05:00 | 411 | 408
2016-06-04 05:30 | 425 | 422
2016-06-04 06:00 | 426 | 423
2016-06-04 06:30 | 442 | 440
2016-06-04 07:00 | 446 | 444
2016-06-04 07:30 | 465 | 463
2016-06-04 08:00 | 480 | 478
2016-06-04 08:30 | 481 | 479
2016-06-04 09:00 | 480 | 478
2016-06-04 09:30 | 408 | 406
2016-06-04 10:00 | 401 | 398
2016-06-04 10:30 | 397 | 394
2016-06-04 11:00 | 395 | 393
2016-06-04 11:30 | 388 | 386
2016-06-04 12:00 | 384 | 381
2016-06-04 12:30 | 398 | 394
2016-06-04 13:00 | 401 | 397
2016-06-04 13:30 | 404 | 400
2016-06-04 14:00 | 414 | 411
2016-06-04 14:30 | 424 | 421
2016-06-04 15:00 | 426 | 423
2016-06-04 15:30 | 432 | 429
2016-06-04 16:00 | 430 | 427
2016-06-04 16:30 | 440 | 437
2016-06-04 17:00 | 464 | 462
2016-06-04 17:30 | 476 | 474
2016-06-04 18:00 | 497 | 496
2016-06-04 18:30 | 522 | 521
2016-06-04 19:00 | 534 | 533
2016-06-04 19:30 | 514 | 513
2016-06-04 20:00 | 535 | 533
2016-06-04 20:30 | 531 | 530
2016-06-04 21:00 | 522 | 521
2016-06-04 21:30 | 509 | 508
2016-06-04 22:00 | 505 | 503
2016-06-04 22:30 | 491 | 489
2016-06-04 23:00 | 477 | 476
2016-06-04 23:30 | 464 | 462
2016-06-05 | 458 | 455
2016-06-05 00:30 | 443 | 441
2016-06-05 01:00 | 427 | 425
2016-06-05 01:30 | 412 | 408
2016-06-05 02:00 | 398 | 394
2016-06-05 02:30 | 391 | 386
2016-06-05 03:00 | 385 | 380
2016-06-05 03:30 | 386 | 381
2016-06-05 04:00 | 382 | 377
2016-06-05 04:30 | 382 | 377
2016-06-05 05:00 | 385 | 379
2016-06-05 05:30 | 387 | 382
2016-06-05 06:00 | 390 | 385
2016-06-05 06:30 | 397 | 393
2016-06-05 07:00 | 401 | 397
2016-06-05 07:30 | 413 | 408
2016-06-05 08:00 | 426 | 422
2016-06-05 08:30 | 437 | 433
2016-06-05 09:00 | 426 | 422
2016-06-05 09:30 | 415 | 411
2016-06-05 10:00 | 404 | 400
2016-06-05 10:30 | 410 | 406
2016-06-05 11:00 | 395 | 391
2016-06-05 11:30 | 380 | 375
2016-06-05 12:00 | 375 | 369
2016-06-05 12:30 | 359 | 354
2016-06-05 13:00 | 358 | 352
2016-06-05 13:30 | 366 | 360
2016-06-05 14:00 | 370 | 364
2016-06-05 14:30 | 373 | 368
2016-06-05 15:00 | 348 | 342
2016-06-05 15:30 | 362 | 355
2016-06-05 16:00 | 376 | 370
2016-06-05 16:30 | 366 | 361
2016-06-05 17:00 | 416 | 412
2016-06-05 17:30 | 413 | 410
2016-06-05 18:00 | 436 | 433
2016-06-05 18:30 | 460 | 458
2016-06-05 19:00 | 459 | 457
2016-06-05 19:30 | 483 | 480
2016-06-05 20:00 | 488 | 486
2016-06-05 20:30 | 469 | 468
2016-06-05 21:00 | 476 | 474
2016-06-05 21:30 | 484 | 482
2016-06-05 22:00 | 492 | 490
2016-06-05 22:30 | 471 | 469
2016-06-05 23:00 | 459 | 457
2016-06-05 23:30 | 452 | 450
2016-06-06 | 446 | 444
2016-06-06 00:30 | 434 | 432
2016-06-06 01:00 | 417 | 414
2016-06-06 01:30 | 396 | 393
2016-06-06 02:00 | 387 | 382
2016-06-06 02:30 | 379 | 373
2016-06-06 03:00 | 371 | 366
2016-06-06 03:30 | 375 | 369
2016-06-06 04:00 | 376 | 370
2016-06-06 04:30 | 379 | 374
2016-06-06 05:00 | 386 | 381
2016-06-06 05:30 | 401 | 396
2016-06-06 06:00 | 418 | 414
2016-06-06 06:30 | 442 | 438
2016-06-06 07:00 | 464 | 461
2016-06-06 07:30 | 482 | 479
2016-06-06 08:00 | 499 | 497
2016-06-06 08:30 | 502 | 501
2016-06-06 09:00 | 487 | 485
2016-06-06 09:30 | 476 | 474
2016-06-06 10:00 | 469 | 467
2016-06-06 10:30 | 473 | 471
2016-06-06 11:00 | 461 | 459
2016-06-06 11:30 | 446 | 444
2016-06-06 12:00 | 450 | 447
2016-06-06 12:30 | 457 | 455
2016-06-06 13:00 | 456 | 454
2016-06-06 13:30 | 458 | 456
2016-06-06 14:00 | 468 | 465
2016-06-06 14:30 | 476 | 474
2016-06-06 15:00 | 483 | 481
2016-06-06 15:30 | 493 | 492
2016-06-06 16:00 | 508 | 507
2016-06-06 16:30 | 529 | 528
2016-06-06 17:00 | 507 | 506
2016-06-06 17:30 | 493 | 493
2016-06-06 18:00 | 463 | 462
2016-06-06 18:30 | 475 | 475
2016-06-06 19:00 | 489 | 489
2016-06-06 19:30 | 500 | 500
2016-06-06 20:00 | 490 | 489
2016-06-06 20:30 | 484 | 484
2016-06-06 21:00 | 495 | 495
2016-06-06 21:30 | 488 | 488
2016-06-06 22:00 | 498 | 498
2016-06-06 22:30 | 465 | 465
2016-06-06 23:00 | 472 | 471
2016-06-06 23:30 | 486 | 486
2016-06-07 | 481 | 481
2016-06-07 00:30 | 456 | 455
2016-06-07 01:00 | 435 | 434
2016-06-07 01:30 | 425 | 424
2016-06-07 02:00 | 408 | 406
2016-06-07 02:30 | 401 | 399
2016-06-07 03:00 | 395 | 393
2016-06-07 03:30 | 400 | 398
2016-06-07 04:00 | 397 | 395
2016-06-07 04:30 | 396 | 394
2016-06-07 05:00 | 404 | 402
2016-06-07 05:30 | 418 | 417
2016-06-07 06:00 | 436 | 435
2016-06-07 06:30 | 432 | 431
2016-06-07 07:00 | 466 | 465
2016-06-07 07:30 | 499 | 498
2016-06-07 08:00 | 459 | 459
2016-06-07 08:30 | 481 | 481
2016-06-07 09:00 | 482 | 482
2016-06-07 09:30 | 447 | 447
2016-06-07 10:00 | 397 | 396
2016-06-07 10:30 | 393 | 392
2016-06-07 11:00 | 399 | 397
2016-06-07 11:30 | 391 | 389
2016-06-07 12:00 | 395 | 393
2016-06-07 12:30 | 397 | 394
2016-06-07 13:00 | 385 | 382
2016-06-07 13:30 | 376 | 373
2016-06-07 14:00 | 322 | 318
2016-06-07 14:30 | 325 | 320
2016-06-07 15:00 | 357 | 352
2016-06-07 15:30 | 300 | 295
2016-06-07 16:00 | 272 | 265
2016-06-07 16:30 | 288 | 281
2016-06-07 17:00 | 317 | 312
2016-06-07 17:30 | 316 | 312
2016-06-07 18:00 | 281 | 276
2016-06-07 18:30 | 301 | 296
2016-06-07 19:00 | 317 | 313
2016-06-07 19:30 | 310 | 306
2016-06-07 20:00 | 304 | 300
2016-06-07 20:30 | 304 | 299
2016-06-07 21:00 | 314 | 309
2016-06-07 21:30 | 375 | 371
2016-06-07 22:00 | 399 | 396
2016-06-07 22:30 | 348 | 346
2016-06-07 23:00 | 286 | 282
2016-06-07 23:30 | 273 | 268
2016-06-08 | 288 | 282
2016-06-08 00:30 | 314 | 309
2016-06-08 01:00 | 314 | 310
2016-06-08 01:30 | 292 | 287
2016-06-08 02:00 | 234 | 227
2016-06-08 02:30 | 268 | 260
2016-06-08 03:00 | 267 | 260
2016-06-08 03:30 | 267 | 260
2016-06-08 04:00 | 259 | 252
2016-06-08 04:30 | 263 | 255
2016-06-08 05:00 | 276 | 268
2016-06-08 05:30 | 286 | 280
2016-06-08 06:00 | 306 | 300
2016-06-08 06:30 | 257 | 252
2016-06-08 07:00 | 274 | 268
2016-06-08 07:30 | 287 | 280
2016-06-08 08:00 | 293 | 288
2016-06-08 08:30 | 307 | 302
2016-06-08 09:00 | 340 | 335
2016-06-08 09:30 | 330 | 327
2016-06-08 10:00 | 333 | 329
2016-06-08 10:30 | 334 | 330
2016-06-08 11:00 | 315 | 311
2016-06-08 11:30 | 308 | 304
2016-06-08 12:00 | 313 | 309
2016-06-08 12:30 | 317 | 313
2016-06-08 13:00 | 323 | 320
2016-06-08 13:30 | 322 | 319
2016-06-08 14:00 | 332 | 329
2016-06-08 14:30 | 345 | 342
2016-06-08 15:00 | 349 | 346
2016-06-08 15:30 | 362 | 359
2016-06-08 16:00 | 393 | 391
2016-06-08 16:30 | 405 | 404
2016-06-08 17:00 | 328 | 327
2016-06-08 17:30 | 327 | 324
2016-06-08 18:00 | 316 | 313
2016-06-08 18:30 | 327 | 324
2016-06-08 19:00 | 337 | 334
2016-06-08 19:30 | 326 | 323
2016-06-08 20:00 | 319 | 316
2016-06-08 20:30 | 332 | 328
2016-06-08 21:00 | 326 | 322
2016-06-08 21:30 | 358 | 354
2016-06-08 22:00 | 376 | 373
2016-06-08 22:30 | 370 | 368
2016-06-08 23:00 | 412 | 410
2016-06-08 23:30 | 478 | 476
2016-06-09 | 469 | 469
2016-06-09 00:30 | 443 | 442
2016-06-09 01:00 | 420 | 419
2016-06-09 01:30 | 400 | 399
2016-06-09 02:00 | 386 | 384
2016-06-09 02:30 | 384 | 382
2016-06-09 03:00 | 393 | 392
2016-06-09 03:30 | 383 | 381
2016-06-09 04:00 | 382 | 380
2016-06-09 04:30 | 388 | 386
2016-06-09 05:00 | 395 | 393
2016-06-09 05:30 | 405 | 404
2016-06-09 06:00 | 423 | 421
2016-06-09 06:30 | 464 | 463
2016-06-09 07:00 | 470 | 470
2016-06-09 07:30 | 505 | 505
2016-06-09 08:00 | 518 | 518
2016-06-09 08:30 | 530 | 530
2016-06-09 09:00 | 539 | 538
2016-06-09 09:30 | 530 | 530
2016-06-09 10:00 | 533 | 533
2016-06-09 10:30 | 534 | 533
2016-06-09 11:00 | 515 | 515
2016-06-09 11:30 | 505 | 504
2016-06-09 12:00 | 500 | 499
2016-06-09 12:30 | 502 | 501
2016-06-09 13:00 | 507 | 507
2016-06-09 13:30 | 506 | 505
2016-06-09 14:00 | 511 | 511
2016-06-09 14:30 | 516 | 516
2016-06-09 15:00 | 527 | 527
2016-06-09 15:30 | 530 | 530
2016-06-09 16:00 | 536 | 536
2016-06-09 16:30 | 532 | 532
2016-06-09 17:00 | 526 | 526
2016-06-09 17:30 | 533 | 533
2016-06-09 18:00 | 523 | 523
2016-06-09 18:30 | 546 | 546
2016-06-09 19:00 | 555 | 555
2016-06-09 19:30 | 533 | 533
2016-06-09 20:00 | 526 | 526
2016-06-09 20:30 | 541 | 541
2016-06-09 21:00 | 539 | 539
2016-06-09 21:30 | 509 | 509
2016-06-09 22:00 | 497 | 496
2016-06-09 22:30 | 483 | 483
2016-06-09 23:00 | 469 | 468
2016-06-09 23:30 | 454 | 453
2016-06-10 | 448 | 447
2016-06-10 00:30 | 426 | 425
2016-06-10 01:00 | 402 | 400
2016-06-10 01:30 | 389 | 386
2016-06-10 02:00 | 376 | 373
2016-06-10 02:30 | 367 | 364
2016-06-10 03:00 | 367 | 363
2016-06-10 03:30 | 370 | 364
2016-06-10 04:00 | 363 | 357
2016-06-10 04:30 | 364 | 357
2016-06-10 05:00 | 363 | 356
2016-06-10 05:30 | 380 | 374
2016-06-10 06:00 | 389 | 383
2016-06-10 06:30 | 413 | 408
2016-06-10 07:00 | 428 | 425
2016-06-10 07:30 | 452 | 450
2016-06-10 08:00 | 482 | 481
2016-06-10 08:30 | 502 | 502
2016-06-10 09:00 | 495 | 495
2016-06-10 09:30 | 492 | 492
2016-06-10 10:00 | 485 | 485
2016-06-10 10:30 | 481 | 481
2016-06-10 11:00 | 465 | 464
2016-06-10 11:30 | 453 | 452
2016-06-10 12:00 | 456 | 455
2016-06-10 12:30 | 462 | 461
2016-06-10 13:00 | 461 | 460
2016-06-10 13:30 | 476 | 475
2016-06-10 14:00 | 480 | 479
2016-06-10 14:30 | 492 | 491
2016-06-10 15:00 | 495 | 494
2016-06-10 15:30 | 497 | 497
2016-06-10 16:00 | 513 | 512
2016-06-10 16:30 | 514 | 513
2016-06-10 17:00 | 504 | 504
2016-06-10 17:30 | 481 | 481
2016-06-10 18:00 | 467 | 467
2016-06-10 18:30 | 488 | 487
2016-06-10 19:00 | 484 | 483
2016-06-10 19:30 | 469 | 469
2016-06-10 20:00 | 467 | 466
2016-06-10 20:30 | 482 | 481
2016-06-10 21:00 | 478 | 477
2016-06-10 21:30 | 461 | 460
2016-06-10 22:00 | 458 | 457
2016-06-10 22:30 | 453 | 452
2016-06-10 23:00 | 446 | 445
2016-06-10 23:30 | 428 | 426
2016-06-11 | 418 | 416
2016-06-11 00:30 | 401 | 398
2016-06-11 01:00 | 384 | 381
2016-06-11 01:30 | 367 | 364
2016-06-11 02:00 | 353 | 349
2016-06-11 02:30 | 342 | 338
2016-06-11 03:00 | 338 | 334
2016-06-11 03:30 | 342 | 337
2016-06-11 04:00 | 337 | 332
2016-06-11 04:30 | 338 | 333
2016-06-11 05:00 | 341 | 336
2016-06-11 05:30 | 347 | 343
2016-06-11 06:00 | 353 | 349
2016-06-11 06:30 | 371 | 368
2016-06-11 07:00 | 384 | 381
2016-06-11 07:30 | 406 | 403
2016-06-11 08:00 | 424 | 422
2016-06-11 08:30 | 420 | 418
2016-06-11 09:00 | 427 | 425
2016-06-11 09:30 | 429 | 427
2016-06-11 10:00 | 426 | 425
2016-06-11 10:30 | 421 | 419
2016-06-11 11:00 | 401 | 399
2016-06-11 11:30 | 399 | 397
2016-06-11 12:00 | 394 | 392
2016-06-11 12:30 | 395 | 392
2016-06-11 13:00 | 393 | 390
2016-06-11 13:30 | 398 | 395
2016-06-11 14:00 | 404 | 402
2016-06-11 14:30 | 403 | 401
2016-06-11 15:00 | 412 | 410
2016-06-11 15:30 | 427 | 425
2016-06-11 16:00 | 434 | 432
2016-06-11 16:30 | 441 | 439
2016-06-11 17:00 | 415 | 413
2016-06-11 17:30 | 410 | 409
2016-06-11 18:00 | 418 | 416
2016-06-11 18:30 | 458 | 457
2016-06-11 19:00 | 480 | 479
2016-06-11 19:30 | 464 | 463
2016-06-11 20:00 | 454 | 453
2016-06-11 20:30 | 446 | 445
2016-06-11 21:00 | 460 | 459
2016-06-11 21:30 | 445 | 444
2016-06-11 22:00 | 438 | 437
2016-06-11 22:30 | 390 | 388
2016-06-11 23:00 | 409 | 406
2016-06-11 23:30 | 396 | 393
2016-06-12 | 390 | 387
2016-06-12 00:30 | 386 | 383
2016-06-12 01:00 | 374 | 371
2016-06-12 01:30 | 363 | 359
2016-06-12 02:00 | 354 | 350
2016-06-12 02:30 | 344 | 340
2016-06-12 03:00 | 340 | 336
2016-06-12 03:30 | 333 | 329
2016-06-12 04:00 | 334 | 329
2016-06-12 04:30 | 340 | 335
2016-06-12 05:00 | 338 | 333
2016-06-12 05:30 | 345 | 341
2016-06-12 06:00 | 350 | 346
2016-06-12 06:30 | 361 | 357
2016-06-12 07:00 | 360 | 356
2016-06-12 07:30 | 376 | 372
2016-06-12 08:00 | 395 | 392
2016-06-12 08:30 | 392 | 389
2016-06-12 09:00 | 389 | 385
2016-06-12 09:30 | 383 | 380
2016-06-12 10:00 | 407 | 404
2016-06-12 10:30 | 430 | 427
2016-06-12 11:00 | 435 | 433
2016-06-12 11:30 | 433 | 431
2016-06-12 12:00 | 429 | 427
2016-06-12 12:30 | 429 | 427
2016-06-12 13:00 | 434 | 432
2016-06-12 13:30 | 431 | 429
2016-06-12 14:00 | 403 | 401
2016-06-12 14:30 | 405 | 402
2016-06-12 15:00 | 413 | 410
2016-06-12 15:30 | 409 | 406
2016-06-12 16:00 | 415 | 412
2016-06-12 16:30 | 395 | 393
2016-06-12 17:00 | 413 | 411
2016-06-12 17:30 | 421 | 419
2016-06-12 18:00 | 398 | 396
2016-06-12 18:30 | 419 | 417
2016-06-12 19:00 | 438 | 437
2016-06-12 19:30 | 449 | 447
2016-06-12 20:00 | 443 | 441
2016-06-12 20:30 | 415 | 413
2016-06-12 21:00 | 361 | 359
2016-06-12 21:30 | 301 | 297
2016-06-12 22:00 | 277 | 271
2016-06-12 22:30 | 270 | 261
2016-06-12 23:00 | 252 | 243
2016-06-12 23:30 | 269 | 260
2016-06-13 | 373 | 367
2016-06-13 00:30 | 376 | 373
2016-06-13 01:00 | 368 | 364
2016-06-13 01:30 | 352 | 348
2016-06-13 02:00 | 347 | 342
2016-06-13 02:30 | 342 | 337
2016-06-13 03:00 | 339 | 334
2016-06-13 03:30 | 336 | 331
2016-06-13 04:00 | 336 | 330
2016-06-13 04:30 | 333 | 327
2016-06-13 05:00 | 344 | 339
2016-06-13 05:30 | 363 | 358
2016-06-13 06:00 | 382 | 378
2016-06-13 06:30 | 413 | 410
2016-06-13 07:00 | 435 | 432
2016-06-13 07:30 | 459 | 457
2016-06-13 08:00 | 483 | 481
2016-06-13 08:30 | 490 | 488
2016-06-13 09:00 | 488 | 487
2016-06-13 09:30 | 424 | 422
2016-06-13 10:00 | 428 | 426
2016-06-13 10:30 | 413 | 411
2016-06-13 11:00 | 420 | 417
2016-06-13 11:30 | 443 | 441
2016-06-13 12:00 | 445 | 442
2016-06-13 12:30 | 440 | 438
2016-06-13 13:00 | 425 | 423
2016-06-13 13:30 | 422 | 420
2016-06-13 14:00 | 431 | 429
2016-06-13 14:30 | 425 | 422
2016-06-13 15:00 | 448 | 446
2016-06-13 15:30 | 468 | 466
2016-06-13 16:00 | 423 | 421
2016-06-13 16:30 | 391 | 389
2016-06-13 17:00 | 387 | 383
2016-06-13 17:30 | 330 | 326
2016-06-13 18:00 | 166 | 155
2016-06-13 18:30 | 181 | 159
2016-06-13 19:00 | 276 | 262
2016-06-13 19:30 | 324 | 316
2016-06-13 20:00 | 346 | 340
2016-06-13 20:30 | 340 | 335
2016-06-13 21:00 | 334 | 328
2016-06-13 21:30 | 322 | 316
2016-06-13 22:00 | 335 | 329
2016-06-13 22:30 | 317 | 311
2016-06-13 23:00 | 424 | 419
2016-06-13 23:30 | 444 | 441
2016-06-14 | 430 | 428
2016-06-14 00:30 | 411 | 409
2016-06-14 01:00 | 392 | 389
2016-06-14 01:30 | 380 | 376
2016-06-14 02:00 | 369 | 365
2016-06-14 02:30 | 376 | 372
2016-06-14 03:00 | 376 | 372
2016-06-14 03:30 | 374 | 370
2016-06-14 04:00 | 385 | 381
2016-06-14 04:30 | 381 | 377
2016-06-14 05:00 | 388 | 384
2016-06-14 05:30 | 399 | 396
2016-06-14 06:00 | 407 | 404
2016-06-14 06:30 | 404 | 401
2016-06-14 07:00 | 415 | 412
2016-06-14 07:30 | 463 | 460
2016-06-14 08:00 | 522 | 520
2016-06-14 08:30 | 531 | 530
2016-06-14 09:00 | 515 | 515
2016-06-14 09:30 | 514 | 514
2016-06-14 10:00 | 502 | 502
2016-06-14 10:30 | 497 | 497
2016-06-14 11:00 | 481 | 481
2016-06-14 11:30 | 405 | 405
2016-06-14 12:00 | 400 | 398
2016-06-14 12:30 | 392 | 390
2016-06-14 13:00 | 390 | 388
2016-06-14 13:30 | 393 | 391
2016-06-14 14:00 | 402 | 401
2016-06-14 14:30 | 417 | 416
2016-06-14 15:00 | 421 | 420
2016-06-14 15:30 | 345 | 344
2016-06-14 16:00 | 311 | 307
2016-06-14 16:30 | 302 | 294
2016-06-14 17:00 | 294 | 285
2016-06-14 17:30 | 234 | 223
2016-06-14 18:00 | 86 | 22
2016-06-14 18:30 | 126 | 40
2016-06-14 19:00 | 196 | 158
2016-06-14 19:30 | 260 | 241
2016-06-14 20:00 | 276 | 265
2016-06-14 20:30 | 285 | 276
2016-06-14 21:00 | 370 | 363
2016-06-14 21:30 | 352 | 349
2016-06-14 22:00 | 343 | 339
2016-06-14 22:30 | 278 | 272
2016-06-14 23:00 | 286 | 277
2016-06-14 23:30 | 273 | 264
2016-06-15 | 266 | 254
2016-06-15 00:30 | 298 | 287
2016-06-15 01:00 | 310 | 301
2016-06-15 01:30 | 285 | 276
2016-06-15 02:00 | 269 | 259
2016-06-15 02:30 | 258 | 245
2016-06-15 03:00 | 255 | 240
2016-06-15 03:30 | 257 | 242
2016-06-15 04:00 | 259 | 240
2016-06-15 04:30 | 259 | 239
2016-06-15 05:00 | 259 | 237
2016-06-15 05:30 | 270 | 250
2016-06-15 06:00 | 273 | 254
2016-06-15 06:30 | 256 | 237
2016-06-15 07:00 | 207 | 183
2016-06-15 07:30 | 238 | 216
2016-06-15 08:00 | 200 | 181
2016-06-15 08:30 | 209 | 187
2016-06-15 09:00 | 246 | 228
2016-06-15 09:30 | 280 | 268
2016-06-15 10:00 | 219 | 206
2016-06-15 10:30 | 258 | 240
2016-06-15 11:00 | 277 | 263
2016-06-15 11:30 | 294 | 282
2016-06-15 12:00 | 310 | 300
2016-06-15 12:30 | 313 | 305
2016-06-15 13:00 | 339 | 331
2016-06-15 13:30 | 335 | 328
2016-06-15 14:00 | 338 | 332
2016-06-15 14:30 | 339 | 332
2016-06-15 15:00 | 299 | 292
2016-06-15 15:30 | 223 | 209
2016-06-15 16:00 | 201 | 177
2016-06-15 16:30 | 262 | 242
2016-06-15 17:00 | 241 | 228
2016-06-15 17:30 | 238 | 225
2016-06-15 18:00 | 212 | 198
2016-06-15 18:30 | 278 | 266
2016-06-15 19:00 | 301 | 293
2016-06-15 19:30 | 325 | 319
2016-06-15 20:00 | 321 | 316
2016-06-15 20:30 | 317 | 312
2016-06-15 21:00 | 362 | 357
2016-06-15 21:30 | 328 | 325
2016-06-15 22:00 | 342 | 337
2016-06-15 22:30 | 373 | 368
2016-06-15 23:00 | 454 | 451
2016-06-15 23:30 | 442 | 442
2016-06-16 | 425 | 425
2016-06-16 00:30 | 409 | 408
2016-06-16 01:00 | 394 | 392
2016-06-16 01:30 | 372 | 370
2016-06-16 02:00 | 357 | 354
2016-06-16 02:30 | 345 | 341
2016-06-16 03:00 | 348 | 343
2016-06-16 03:30 | 341 | 336
2016-06-16 04:00 | 344 | 339
2016-06-16 04:30 | 340 | 335
2016-06-16 05:00 | 340 | 335
2016-06-16 05:30 | 354 | 349
2016-06-16 06:00 | 364 | 360
2016-06-16 06:30 | 393 | 389
2016-06-16 07:00 | 419 | 417
2016-06-16 07:30 | 435 | 434
2016-06-16 08:00 | 450 | 449
2016-06-16 08:30 | 457 | 456
2016-06-16 09:00 | 465 | 464
2016-06-16 09:30 | 469 | 469
2016-06-16 10:00 | 459 | 458
2016-06-16 10:30 | 454 | 452
2016-06-16 11:00 | 462 | 460
2016-06-16 11:30 | 455 | 451
2016-06-16 12:00 | 468 | 462
2016-06-16 12:30 | 453 | 448
2016-06-16 13:00 | 457 | 450
2016-06-16 13:30 | 452 | 446
2016-06-16 14:00 | 466 | 460
2016-06-16 14:30 | 473 | 467
2016-06-16 15:00 | 467 | 462
2016-06-16 15:30 | 423 | 417
2016-06-16 16:00 | 429 | 421
2016-06-16 16:30 | 429 | 422
2016-06-16 17:00 | 380 | 373
2016-06-16 17:30 | 295 | 281
2016-06-16 18:00 | 252 | 221
2016-06-16 18:30 | 252 | 217
2016-06-16 19:00 | 305 | 279
2016-06-16 19:30 | 309 | 293
2016-06-16 20:00 | 297 | 281
2016-06-16 20:30 | 264 | 244
2016-06-16 21:00 | 269 | 244
2016-06-16 21:30 | 271 | 248
2016-06-16 22:00 | 393 | 376
2016-06-16 22:30 | 368 | 359
2016-06-16 23:00 | 403 | 395
2016-06-16 23:30 | 408 | 402
2016-06-17 | 406 | 400
2016-06-17 00:30 | 387 | 380
2016-06-17 01:00 | 387 | 379
2016-06-17 01:30 | 369 | 360
2016-06-17 02:00 | 354 | 343
2016-06-17 02:30 | 351 | 338
2016-06-17 03:00 | 348 | 334
2016-06-17 03:30 | 342 | 327
2016-06-17 04:00 | 345 | 330
2016-06-17 04:30 | 347 | 332
2016-06-17 05:00 | 358 | 345
2016-06-17 05:30 | 369 | 358
2016-06-17 06:00 | 368 | 358
2016-06-17 06:30 | 370 | 360
2016-06-17 07:00 | 403 | 393
2016-06-17 07:30 | 434 | 428
2016-06-17 08:00 | 456 | 452
2016-06-17 08:30 | 479 | 476
2016-06-17 09:00 | 481 | 479
2016-06-17 09:30 | 471 | 468
2016-06-17 10:00 | 458 | 454
2016-06-17 10:30 | 462 | 458
2016-06-17 11:00 | 405 | 401
2016-06-17 11:30 | 436 | 429
2016-06-17 12:00 | 418 | 413
2016-06-17 12:30 | 408 | 401
2016-06-17 13:00 | 387 | 379
2016-06-17 13:30 | 376 | 367
2016-06-17 14:00 | 385 | 375
2016-06-17 14:30 | 394 | 386
2016-06-17 15:00 | 394 | 386
2016-06-17 15:30 | 405 | 397
2016-06-17 16:00 | 390 | 387
2016-06-17 16:30 | 323 | 318
2016-06-17 17:00 | 182 | 170
2016-06-17 17:30 | 86 | 6
2016-06-17 18:00 | 104 | 2
2016-06-17 18:30 | 157 | 113
2016-06-17 19:00 | 254 | 236
2016-06-17 19:30 | 275 | 264
2016-06-17 20:00 | 265 | 253
2016-06-17 20:30 | 260 | 248
2016-06-17 21:00 | 269 | 257
2016-06-17 21:30 | 254 | 241
2016-06-17 22:00 | 266 | 252
2016-06-17 22:30 | 272 | 259
2016-06-17 23:00 | 269 | 257
2016-06-17 23:30 | 271 | 259
2016-06-18 | 334 | 324
2016-06-18 00:30 | 323 | 315
2016-06-18 01:00 | 305 | 297
2016-06-18 01:30 | 280 | 270
2016-06-18 02:00 | 271 | 259
2016-06-18 02:30 | 263 | 250
2016-06-18 03:00 | 261 | 247
2016-06-18 03:30 | 261 | 247
2016-06-18 04:00 | 259 | 245
2016-06-18 04:30 | 259 | 245
2016-06-18 05:00 | 259 | 245
2016-06-18 05:30 | 264 | 251
2016-06-18 06:00 | 268 | 254
2016-06-18 06:30 | 280 | 268
2016-06-18 07:00 | 291 | 280
2016-06-18 07:30 | 300 | 290
2016-06-18 08:00 | 306 | 296
2016-06-18 08:30 | 318 | 309
2016-06-18 09:00 | 262 | 252
2016-06-18 09:30 | 229 | 215
2016-06-18 10:00 | 248 | 233
2016-06-18 10:30 | 306 | 294
2016-06-18 11:00 | 317 | 308
2016-06-18 11:30 | 241 | 230
2016-06-18 12:00 | 231 | 215
2016-06-18 12:30 | 225 | 207
2016-06-18 13:00 | 223 | 204
2016-06-18 13:30 | 221 | 202
2016-06-18 14:00 | 226 | 207
2016-06-18 14:30 | 231 | 212
2016-06-18 15:00 | 243 | 226
2016-06-18 15:30 | 246 | 231
2016-06-18 16:00 | 232 | 216
2016-06-18 16:30 | 245 | 230
2016-06-18 17:00 | 260 | 247
2016-06-18 17:30 | 266 | 254
2016-06-18 18:00 | 294 | 284
2016-06-18 18:30 | 320 | 312
2016-06-18 19:00 | 338 | 331
2016-06-18 19:30 | 422 | 416
2016-06-18 20:00 | 522 | 519
2016-06-18 20:30 | 522 | 521
2016-06-18 21:00 | 503 | 502
2016-06-18 21:30 | 479 | 478
2016-06-18 22:00 | 490 | 489
2016-06-18 22:30 | 479 | 478
2016-06-18 23:00 | 468 | 467
2016-06-18 23:30 | 447 | 445
2016-06-19 | 437 | 435
2016-06-19 00:30 | 431 | 429
2016-06-19 01:00 | 414 | 412
2016-06-19 01:30 | 395 | 392
2016-06-19 02:00 | 382 | 378
2016-06-19 02:30 | 378 | 374
2016-06-19 03:00 | 379 | 375
2016-06-19 03:30 | 375 | 371
2016-06-19 04:00 | 382 | 378
2016-06-19 04:30 | 381 | 377
2016-06-19 05:00 | 384 | 380
2016-06-19 05:30 | 386 | 382
2016-06-19 06:00 | 391 | 387
2016-06-19 06:30 | 405 | 401
2016-06-19 07:00 | 410 | 406
2016-06-19 07:30 | 417 | 413
2016-06-19 08:00 | 436 | 433
2016-06-19 08:30 | 462 | 459
2016-06-19 09:00 | 471 | 469
2016-06-19 09:30 | 479 | 477
2016-06-19 10:00 | 466 | 464
2016-06-19 10:30 | 450 | 448
2016-06-19 11:00 | 439 | 437
2016-06-19 11:30 | 428 | 425
2016-06-19 12:00 | 425 | 422
2016-06-19 12:30 | 399 | 397
2016-06-19 13:00 | 397 | 393
2016-06-19 13:30 | 394 | 391
2016-06-19 14:00 | 383 | 380
2016-06-19 14:30 | 401 | 397
2016-06-19 15:00 | 400 | 397
2016-06-19 15:30 | 401 | 397
2016-06-19 16:00 | 401 | 397
2016-06-19 16:30 | 398 | 395
2016-06-19 17:00 | 381 | 377
2016-06-19 17:30 | 427 | 423
2016-06-19 18:00 | 455 | 453
2016-06-19 18:30 | 468 | 466
2016-06-19 19:00 | 483 | 481
2016-06-19 19:30 | 474 | 472
2016-06-19 20:00 | 462 | 460
2016-06-19 20:30 | 446 | 444
2016-06-19 21:00 | 436 | 433
2016-06-19 21:30 | 426 | 423
2016-06-19 22:00 | 417 | 414
2016-06-19 22:30 | 421 | 418
2016-06-19 23:00 | 414 | 411
2016-06-19 23:30 | 404 | 400
2016-06-20 | 401 | 397
2016-06-20 00:30 | 385 | 381
2016-06-20 01:00 | 370 | 366
2016-06-20 01:30 | 360 | 355
2016-06-20 02:00 | 351 | 345
2016-06-20 02:30 | 340 | 334
2016-06-20 03:00 | 340 | 333
2016-06-20 03:30 | 346 | 339
2016-06-20 04:00 | 357 | 351
2016-06-20 04:30 | 362 | 357
2016-06-20 05:00 | 369 | 364
2016-06-20 05:30 | 384 | 379
2016-06-20 06:00 | 397 | 393
2016-06-20 06:30 | 430 | 427
2016-06-20 07:00 | 455 | 452
2016-06-20 07:30 | 487 | 486
2016-06-20 08:00 | 508 | 507
2016-06-20 08:30 | 512 | 510
2016-06-20 09:00 | 511 | 510
2016-06-20 09:30 | 505 | 503
2016-06-20 10:00 | 486 | 484
2016-06-20 10:30 | 479 | 477
2016-06-20 11:00 | 455 | 452
2016-06-20 11:30 | 445 | 442
2016-06-20 12:00 | 448 | 445
2016-06-20 12:30 | 454 | 451
2016-06-20 13:00 | 453 | 450
2016-06-20 13:30 | 441 | 439
2016-06-20 14:00 | 451 | 448
2016-06-20 14:30 | 461 | 459
2016-06-20 15:00 | 465 | 463
2016-06-20 15:30 | 473 | 470
2016-06-20 16:00 | 396 | 394
2016-06-20 16:30 | 345 | 340
2016-06-20 17:00 | 351 | 344
2016-06-20 17:30 | 267 | 259
2016-06-20 18:00 | 176 | 158
2016-06-20 18:30 | 201 | 179
2016-06-20 19:00 | 269 | 254
2016-06-20 19:30 | 315 | 306
2016-06-20 20:00 | 292 | 284
2016-06-20 20:30 | 286 | 277
2016-06-20 21:00 | 363 | 356
2016-06-20 21:30 | 347 | 341
2016-06-20 22:00 | 350 | 344
2016-06-20 22:30 | 348 | 342
2016-06-20 23:00 | 341 | 336
2016-06-20 23:30 | 447 | 442
2016-06-21 | 463 | 460
2016-06-21 00:30 | 438 | 436
2016-06-21 01:00 | 414 | 411
2016-06-21 01:30 | 389 | 385
2016-06-21 02:00 | 380 | 376
2016-06-21 02:30 | 369 | 364
2016-06-21 03:00 | 366 | 361
2016-06-21 03:30 | 365 | 360
2016-06-21 04:00 | 360 | 355
2016-06-21 04:30 | 362 | 357
2016-06-21 05:00 | 368 | 363
2016-06-21 05:30 | 387 | 383
2016-06-21 06:00 | 404 | 400
2016-06-21 06:30 | 442 | 439
2016-06-21 07:00 | 475 | 472
2016-06-21 07:30 | 503 | 501
2016-06-21 08:00 | 504 | 502
2016-06-21 08:30 | 512 | 511
2016-06-21 09:00 | 508 | 507
2016-06-21 09:30 | 499 | 498
2016-06-21 10:00 | 483 | 482
2016-06-21 10:30 | 470 | 468
2016-06-21 11:00 | 444 | 442
2016-06-21 11:30 | 434 | 432
2016-06-21 12:00 | 439 | 437
2016-06-21 12:30 | 443 | 441
2016-06-21 13:00 | 444 | 442
2016-06-21 13:30 | 450 | 448
2016-06-21 14:00 | 452 | 450
2016-06-21 14:30 | 455 | 453
2016-06-21 15:00 | 456 | 453
2016-06-21 15:30 | 466 | 463
2016-06-21 16:00 | 478 | 476
2016-06-21 16:30 | 397 | 396
2016-06-21 17:00 | 339 | 335
2016-06-21 17:30 | 343 | 338
2016-06-21 18:00 | 343 | 338
2016-06-21 18:30 | 318 | 313
2016-06-21 19:00 | 297 | 290
2016-06-21 19:30 | 292 | 284
2016-06-21 20:00 | 347 | 340
2016-06-21 20:30 | 330 | 324
2016-06-21 21:00 | 332 | 326
2016-06-21 21:30 | 432 | 428
2016-06-21 22:00 | 462 | 460
2016-06-21 22:30 | 485 | 484
2016-06-21 23:00 | 487 | 485
2016-06-21 23:30 | 477 | 476
2016-06-22 | 465 | 463
2016-06-22 00:30 | 445 | 444
2016-06-22 01:00 | 421 | 419
2016-06-22 01:30 | 398 | 395
2016-06-22 02:00 | 383 | 380
2016-06-22 02:30 | 374 | 371
2016-06-22 03:00 | 368 | 364
2016-06-22 03:30 | 369 | 364
2016-06-22 04:00 | 369 | 365
2016-06-22 04:30 | 372 | 368
2016-06-22 05:00 | 380 | 376
2016-06-22 05:30 | 395 | 391
2016-06-22 06:00 | 409 | 406
2016-06-22 06:30 | 440 | 437
2016-06-22 07:00 | 467 | 465
2016-06-22 07:30 | 501 | 499
2016-06-22 08:00 | 503 | 502
2016-06-22 08:30 | 521 | 520
2016-06-22 09:00 | 521 | 520
2016-06-22 09:30 | 520 | 519
2016-06-22 10:00 | 518 | 517
2016-06-22 10:30 | 508 | 507
2016-06-22 11:00 | 488 | 487
2016-06-22 11:30 | 476 | 475
2016-06-22 12:00 | 473 | 472
2016-06-22 12:30 | 475 | 473
2016-06-22 13:00 | 484 | 482
2016-06-22 13:30 | 489 | 488
2016-06-22 14:00 | 501 | 500
2016-06-22 14:30 | 511 | 510
2016-06-22 15:00 | 504 | 503
2016-06-22 15:30 | 425 | 425
2016-06-22 16:00 | 368 | 366
2016-06-22 16:30 | 378 | 375
2016-06-22 17:00 | 380 | 377
2016-06-22 17:30 | 389 | 386
2016-06-22 18:00 | 376 | 373
2016-06-22 18:30 | 381 | 378
2016-06-22 19:00 | 382 | 378
2016-06-22 19:30 | 376 | 372
2016-06-22 20:00 | 376 | 372
2016-06-22 20:30 | 363 | 359
2016-06-22 21:00 | 348 | 343
2016-06-22 21:30 | 337 | 332
2016-06-22 22:00 | 342 | 337
2016-06-22 22:30 | 350 | 346
2016-06-22 23:00 | 471 | 469
2016-06-22 23:30 | 484 | 484
2016-06-23 | 466 | 465
2016-06-23 00:30 | 436 | 435
2016-06-23 01:00 | 419 | 417
2016-06-23 01:30 | 400 | 398
2016-06-23 02:00 | 384 | 381
2016-06-23 02:30 | 378 | 375
2016-06-23 03:00 | 373 | 370
2016-06-23 03:30 | 368 | 365
2016-06-23 04:00 | 369 | 366
2016-06-23 04:30 | 377 | 373
2016-06-23 05:00 | 381 | 378
2016-06-23 05:30 | 393 | 391
2016-06-23 06:00 | 406 | 403
2016-06-23 06:30 | 438 | 435
2016-06-23 07:00 | 460 | 458
2016-06-23 07:30 | 483 | 482
2016-06-23 08:00 | 499 | 498
2016-06-23 08:30 | 511 | 510
2016-06-23 09:00 | 509 | 508
2016-06-23 09:30 | 522 | 521
2016-06-23 10:00 | 520 | 519
2016-06-23 10:30 | 518 | 517
2016-06-23 11:00 | 487 | 486
2016-06-23 11:30 | 495 | 493
2016-06-23 12:00 | 493 | 492
2016-06-23 12:30 | 479 | 478
2016-06-23 13:00 | 473 | 471
2016-06-23 13:30 | 474 | 472
2016-06-23 14:00 | 481 | 479
2016-06-23 14:30 | 479 | 478
2016-06-23 15:00 | 479 | 477
2016-06-23 15:30 | 397 | 395
2016-06-23 16:00 | 362 | 358
2016-06-23 16:30 | 359 | 354
2016-06-23 17:00 | 383 | 378
2016-06-23 17:30 | 367 | 363
2016-06-23 18:00 | 278 | 272
2016-06-23 18:30 | 269 | 260
2016-06-23 19:00 | 270 | 260
2016-06-23 19:30 | 257 | 247
2016-06-23 20:00 | 340 | 331
2016-06-23 20:30 | 366 | 360
2016-06-23 21:00 | 352 | 347
2016-06-23 21:30 | 352 | 347
2016-06-23 22:00 | 390 | 385
2016-06-23 22:30 | 392 | 388
2016-06-23 23:00 | 399 | 395
2016-06-23 23:30 | 480 | 477
2016-06-24 | 466 | 465
2016-06-24 00:30 | 440 | 438
2016-06-24 01:00 | 422 | 419
2016-06-24 01:30 | 408 | 405
2016-06-24 02:00 | 398 | 394
2016-06-24 02:30 | 391 | 387
2016-06-24 03:00 | 384 | 380
2016-06-24 03:30 | 382 | 378
2016-06-24 04:00 | 382 | 377
2016-06-24 04:30 | 388 | 383
2016-06-24 05:00 | 385 | 381
2016-06-24 05:30 | 400 | 396
2016-06-24 06:00 | 423 | 419
2016-06-24 06:30 | 458 | 455
2016-06-24 07:00 | 448 | 446
2016-06-24 07:30 | 465 | 463
2016-06-24 08:00 | 510 | 509
2016-06-24 08:30 | 530 | 529
2016-06-24 09:00 | 543 | 542
2016-06-24 09:30 | 532 | 531
2016-06-24 10:00 | 535 | 535
2016-06-24 10:30 | 528 | 528
2016-06-24 11:00 | 509 | 508
2016-06-24 11:30 | 503 | 502
2016-06-24 12:00 | 502 | 501
2016-06-24 12:30 | 505 | 504
2016-06-24 13:00 | 505 | 504
2016-06-24 13:30 | 507 | 506
2016-06-24 14:00 | 510 | 509
2016-06-24 14:30 | 521 | 520
2016-06-24 15:00 | 530 | 530
2016-06-24 15:30 | 537 | 537
2016-06-24 16:00 | 492 | 492
2016-06-24 16:30 | 453 | 452
2016-06-24 17:00 | 419 | 417
2016-06-24 17:30 | 414 | 412
2016-06-24 18:00 | 376 | 372
2016-06-24 18:30 | 383 | 379
2016-06-24 19:00 | 392 | 388
2016-06-24 19:30 | 427 | 423
2016-06-24 20:00 | 384 | 381
2016-06-24 20:30 | 360 | 356
2016-06-24 21:00 | 378 | 374
2016-06-24 21:30 | 411 | 407
2016-06-24 22:00 | 439 | 436
2016-06-24 22:30 | 358 | 355
2016-06-24 23:00 | 383 | 378
2016-06-24 23:30 | 385 | 381
2016-06-25 | 359 | 354
2016-06-25 00:30 | 442 | 437
2016-06-25 01:00 | 424 | 422
2016-06-25 01:30 | 406 | 403
2016-06-25 02:00 | 387 | 385
2016-06-25 02:30 | 375 | 371
2016-06-25 03:00 | 371 | 367
2016-06-25 03:30 | 366 | 362
2016-06-25 04:00 | 366 | 362
2016-06-25 04:30 | 379 | 376
2016-06-25 05:00 | 377 | 374
2016-06-25 05:30 | 379 | 376
2016-06-25 06:00 | 390 | 387
2016-06-25 06:30 | 399 | 396
2016-06-25 07:00 | 400 | 397
2016-06-25 07:30 | 414 | 411
2016-06-25 08:00 | 385 | 382
2016-06-25 08:30 | 413 | 410
2016-06-25 09:00 | 452 | 450
2016-06-25 09:30 | 448 | 446
2016-06-25 10:00 | 452 | 450
2016-06-25 10:30 | 442 | 439
2016-06-25 11:00 | 413 | 410
2016-06-25 11:30 | 401 | 398
2016-06-25 12:00 | 403 | 399
2016-06-25 12:30 | 401 | 398
2016-06-25 13:00 | 397 | 394
2016-06-25 13:30 | 390 | 386
2016-06-25 14:00 | 398 | 394
2016-06-25 14:30 | 407 | 403
2016-06-25 15:00 | 410 | 406
2016-06-25 15:30 | 424 | 421
2016-06-25 16:00 | 350 | 346
2016-06-25 16:30 | 293 | 287
2016-06-25 17:00 | 296 | 288
2016-06-25 17:30 | 306 | 299
2016-06-25 18:00 | 294 | 287
2016-06-25 18:30 | 316 | 309
2016-06-25 19:00 | 328 | 322
2016-06-25 19:30 | 422 | 418
2016-06-25 20:00 | 447 | 444
2016-06-25 20:30 | 421 | 418
2016-06-25 21:00 | 396 | 394
2016-06-25 21:30 | 419 | 416
2016-06-25 22:00 | 413 | 410
2016-06-25 22:30 | 429 | 426
2016-06-25 23:00 | 422 | 420
2016-06-25 23:30 | 412 | 409
2016-06-26 | 413 | 410
2016-06-26 00:30 | 413 | 410
2016-06-26 01:00 | 397 | 394
2016-06-26 01:30 | 382 | 378
2016-06-26 02:00 | 372 | 368
2016-06-26 02:30 | 369 | 364
2016-06-26 03:00 | 363 | 358
2016-06-26 03:30 | 356 | 352
2016-06-26 04:00 | 350 | 344
2016-06-26 04:30 | 360 | 355
2016-06-26 05:00 | 362 | 357
2016-06-26 05:30 | 362 | 358
2016-06-26 06:00 | 368 | 363
2016-06-26 06:30 | 375 | 371
2016-06-26 07:00 | 390 | 385
2016-06-26 07:30 | 392 | 388
2016-06-26 08:00 | 392 | 388
2016-06-26 08:30 | 367 | 363
2016-06-26 09:00 | 405 | 401
2016-06-26 09:30 | 379 | 376
2016-06-26 10:00 | 387 | 383
2016-06-26 10:30 | 413 | 410
2016-06-26 11:00 | 409 | 406
2016-06-26 11:30 | 406 | 402
2016-06-26 12:00 | 412 | 408
2016-06-26 12:30 | 416 | 413
2016-06-26 13:00 | 421 | 418
2016-06-26 13:30 | 423 | 420
2016-06-26 14:00 | 411 | 408
2016-06-26 14:30 | 400 | 397
2016-06-26 15:00 | 411 | 408
2016-06-26 15:30 | 419 | 416
2016-06-26 16:00 | 306 | 302
2016-06-26 16:30 | 234 | 224
2016-06-26 17:00 | 115 | 84
2016-06-26 17:30 | 109 | 51
2016-06-26 18:00 | 120 | 67
2016-06-26 18:30 | 149 | 111
2016-06-26 19:00 | 269 | 252
2016-06-26 19:30 | 361 | 354
2016-06-26 20:00 | 370 | 365
2016-06-26 20:30 | 361 | 357
2016-06-26 21:00 | 397 | 393
2016-06-26 21:30 | 413 | 410
2016-06-26 22:00 | 427 | 424
2016-06-26 22:30 | 452 | 450
2016-06-26 23:00 | 444 | 442
2016-06-26 23:30 | 424 | 422
2016-06-27 | 431 | 428
2016-06-27 00:30 | 416 | 414
2016-06-27 01:00 | 403 | 400
2016-06-27 01:30 | 389 | 386
2016-06-27 02:00 | 380 | 376
2016-06-27 02:30 | 373 | 369
2016-06-27 03:00 | 369 | 364
2016-06-27 03:30 | 373 | 369
2016-06-27 04:00 | 369 | 365
2016-06-27 04:30 | 358 | 353
2016-06-27 05:00 | 335 | 329
2016-06-27 05:30 | 336 | 330
2016-06-27 06:00 | 353 | 346
2016-06-27 06:30 | 363 | 358
2016-06-27 07:00 | 333 | 327
2016-06-27 07:30 | 377 | 371
2016-06-27 08:00 | 395 | 390
2016-06-27 08:30 | 395 | 391
2016-06-27 09:00 | 367 | 364
2016-06-27 09:30 | 310 | 305
2016-06-27 10:00 | 333 | 327
2016-06-27 10:30 | 354 | 349
2016-06-27 11:00 | 362 | 357
2016-06-27 11:30 | 366 | 361
2016-06-27 12:00 | 391 | 386
2016-06-27 12:30 | 385 | 381
2016-06-27 13:00 | 364 | 360
2016-06-27 13:30 | 360 | 355
2016-06-27 14:00 | 368 | 362
2016-06-27 14:30 | 367 | 362
2016-06-27 15:00 | 372 | 367
2016-06-27 15:30 | 374 | 369
2016-06-27 16:00 | 369 | 364
2016-06-27 16:30 | 373 | 369
2016-06-27 17:00 | 309 | 304
2016-06-27 17:30 | 259 | 249
2016-06-27 18:00 | 157 | 137
2016-06-27 18:30 | 191 | 166
2016-06-27 19:00 | 204 | 179
2016-06-27 19:30 | 229 | 207
2016-06-27 20:00 | 259 | 242
2016-06-27 20:30 | 210 | 191
2016-06-27 21:00 | 203 | 180
2016-06-27 21:30 | 284 | 268
2016-06-27 22:00 | 348 | 338
2016-06-27 22:30 | 307 | 300
2016-06-27 23:00 | 300 | 291
2016-06-27 23:30 | 353 | 345
2016-06-28 | 345 | 338
2016-06-28 00:30 | 320 | 313
2016-06-28 01:00 | 301 | 292
2016-06-28 01:30 | 280 | 269
2016-06-28 02:00 | 263 | 250
2016-06-28 02:30 | 257 | 242
2016-06-28 03:00 | 252 | 237
2016-06-28 03:30 | 256 | 240
2016-06-28 04:00 | 261 | 246
2016-06-28 04:30 | 269 | 254
2016-06-28 05:00 | 276 | 261
2016-06-28 05:30 | 286 | 273
2016-06-28 06:00 | 304 | 293
2016-06-28 06:30 | 239 | 225
2016-06-28 07:00 | 183 | 160
2016-06-28 07:30 | 233 | 212
2016-06-28 08:00 | 175 | 150
2016-06-28 08:30 | 138 | 93
2016-06-28 09:00 | 232 | 206
2016-06-28 09:30 | 272 | 255
2016-06-28 10:00 | 255 | 242
2016-06-28 10:30 | 270 | 258
2016-06-28 11:00 | 262 | 250
2016-06-28 11:30 | 276 | 263
2016-06-28 12:00 | 254 | 239
2016-06-28 12:30 | 260 | 245
2016-06-28 13:00 | 289 | 276
2016-06-28 13:30 | 311 | 299
2016-06-28 14:00 | 349 | 339
2016-06-28 14:30 | 337 | 329
2016-06-28 15:00 | 335 | 328
2016-06-28 15:30 | 342 | 334
2016-06-28 16:00 | 346 | 338
2016-06-28 16:30 | 311 | 302
2016-06-28 17:00 | 271 | 259
2016-06-28 17:30 | 125 | 93
2016-06-28 18:00 | 107 | 29
2016-06-28 18:30 | 137 | 85
2016-06-28 19:00 | 104 | 27
2016-06-28 19:30 | 107 | 10
2016-06-28 20:00 | 109 | 1
2016-06-28 20:30 | 110 | 21
2016-06-28 21:00 | 114 | 22
2016-06-28 21:30 | 114 | 15
2016-06-28 22:00 | 202 | 170
2016-06-28 22:30 | 178 | 152
2016-06-28 23:00 | 208 | 183
2016-06-28 23:30 | 384 | 372
2016-06-29 | 432 | 427
2016-06-29 00:30 | 408 | 405
2016-06-29 01:00 | 385 | 382
2016-06-29 01:30 | 371 | 367
2016-06-29 02:00 | 359 | 354
2016-06-29 02:30 | 351 | 345
2016-06-29 03:00 | 349 | 343
2016-06-29 03:30 | 351 | 345
2016-06-29 04:00 | 352 | 346
2016-06-29 04:30 | 360 | 355
2016-06-29 05:00 | 366 | 361
2016-06-29 05:30 | 374 | 368
2016-06-29 06:00 | 391 | 385
2016-06-29 06:30 | 402 | 397
2016-06-29 07:00 | 348 | 344
2016-06-29 07:30 | 376 | 371
2016-06-29 08:00 | 395 | 391
2016-06-29 08:30 | 396 | 393
2016-06-29 09:00 | 431 | 428
2016-06-29 09:30 | 441 | 438
2016-06-29 10:00 | 453 | 451
2016-06-29 10:30 | 449 | 447
2016-06-29 11:00 | 446 | 444
2016-06-29 11:30 | 441 | 438
2016-06-29 12:00 | 435 | 432
2016-06-29 12:30 | 435 | 432
2016-06-29 13:00 | 432 | 430
2016-06-29 13:30 | 434 | 431
2016-06-29 14:00 | 438 | 435
2016-06-29 14:30 | 421 | 419
2016-06-29 15:00 | 424 | 421
2016-06-29 15:30 | 433 | 430
2016-06-29 16:00 | 440 | 437
2016-06-29 16:30 | 458 | 455
2016-06-29 17:00 | 392 | 390
2016-06-29 17:30 | 307 | 303
2016-06-29 18:00 | 260 | 251
2016-06-29 18:30 | 291 | 282
2016-06-29 19:00 | 308 | 299
2016-06-29 19:30 | 300 | 292
2016-06-29 20:00 | 314 | 305
2016-06-29 20:30 | 304 | 295
2016-06-29 21:00 | 355 | 347
2016-06-29 21:30 | 392 | 387
2016-06-29 22:00 | 390 | 386
2016-06-29 22:30 | 281 | 275
2016-06-29 23:00 | 270 | 259
2016-06-29 23:30 | 284 | 272
2016-06-30 | 319 | 308
2016-06-30 00:30 | 407 | 400
2016-06-30 01:00 | 395 | 391
2016-06-30 01:30 | 376 | 371
2016-06-30 02:00 | 357 | 351
2016-06-30 02:30 | 341 | 334
2016-06-30 03:00 | 345 | 338
2016-06-30 03:30 | 345 | 339
2016-06-30 04:00 | 341 | 335
2016-06-30 04:30 | 358 | 352
2016-06-30 05:00 | 367 | 361
2016-06-30 05:30 | 378 | 373
2016-06-30 06:00 | 392 | 388
2016-06-30 06:30 | 412 | 408
2016-06-30 07:00 | 351 | 347
2016-06-30 07:30 | 374 | 369
2016-06-30 08:00 | 387 | 383
2016-06-30 08:30 | 398 | 395
2016-06-30 09:00 | 393 | 389
2016-06-30 09:30 | 407 | 404
2016-06-30 10:00 | 442 | 439
2016-06-30 10:30 | 431 | 428
2016-06-30 11:00 | 447 | 445
2016-06-30 11:30 | 437 | 435
2016-06-30 12:00 | 445 | 443
2016-06-30 12:30 | 452 | 451
2016-06-30 13:00 | 441 | 440
2016-06-30 13:30 | 413 | 412
2016-06-30 14:00 | 429 | 426
2016-06-30 14:30 | 440 | 438
2016-06-30 15:00 | 438 | 436
2016-06-30 15:30 | 459 | 457
2016-06-30 16:00 | 455 | 453
2016-06-30 16:30 | 460 | 459
2016-06-30 17:00 | 393 | 392
2016-06-30 17:30 | 399 | 396
2016-06-30 18:00 | 296 | 292
2016-06-30 18:30 | 303 | 297
2016-06-30 19:00 | 355 | 348
2016-06-30 19:30 | 345 | 341
2016-06-30 20:00 | 337 | 332
2016-06-30 20:30 | 286 | 279
2016-06-30 21:00 | 266 | 257
2016-06-30 21:30 | 303 | 293
2016-06-30 22:00 | 354 | 347
2016-06-30 22:30 | 264 | 257
2016-06-30 23:00 | 278 | 268
2016-06-30 23:30 | 379 | 372
2016-07-01 | 419 | 416
2016-07-01 00:30 | 402 | 399
2016-07-01 01:00 | 398 | 395
2016-07-01 01:30 | 382 | 379
2016-07-01 02:00 | 370 | 366
2016-07-01 02:30 | 363 | 359
2016-07-01 03:00 | 356 | 351
2016-07-01 03:30 | 350 | 345
2016-07-01 04:00 | 349 | 344
2016-07-01 04:30 | 352 | 346
2016-07-01 05:00 | 357 | 352
2016-07-01 05:30 | 375 | 370
2016-07-01 06:00 | 395 | 391
2016-07-01 06:30 | 416 | 413
2016-07-01 07:00 | 366 | 363
2016-07-01 07:30 | 386 | 382
2016-07-01 08:00 | 398 | 395
2016-07-01 08:30 | 394 | 391
2016-07-01 09:00 | 418 | 415
2016-07-01 09:30 | 422 | 420
2016-07-01 10:00 | 431 | 429
2016-07-01 10:30 | 421 | 418
2016-07-01 11:00 | 418 | 416
2016-07-01 11:30 | 411 | 409
2016-07-01 12:00 | 425 | 423
2016-07-01 12:30 | 423 | 421
2016-07-01 13:00 | 405 | 403
2016-07-01 13:30 | 439 | 436
2016-07-01 14:00 | 432 | 430
2016-07-01 14:30 | 423 | 421
2016-07-01 15:00 | 417 | 415
2016-07-01 15:30 | 421 | 419
2016-07-01 16:00 | 430 | 428
2016-07-01 16:30 | 454 | 452
2016-07-01 17:00 | 448 | 447
2016-07-01 17:30 | 440 | 438
2016-07-01 18:00 | 383 | 381
2016-07-01 18:30 | 395 | 392
2016-07-01 19:00 | 414 | 411
2016-07-01 19:30 | 424 | 422
2016-07-01 20:00 | 431 | 430
2016-07-01 20:30 | 419 | 417
2016-07-01 21:00 | 400 | 398
2016-07-01 21:30 | 425 | 422
2016-07-01 22:00 | 466 | 464
2016-07-01 22:30 | 460 | 459
2016-07-01 23:00 | 450 | 448
2016-07-01 23:30 | 439 | 438
2016-07-02 | 428 | 426
2016-07-02 00:30 | 417 | 414
2016-07-02 01:00 | 392 | 390
2016-07-02 01:30 | 378 | 374
2016-07-02 02:00 | 364 | 360
2016-07-02 02:30 | 360 | 355
2016-07-02 03:00 | 359 | 354
2016-07-02 03:30 | 362 | 357
2016-07-02 04:00 | 358 | 353
2016-07-02 04:30 | 354 | 349
2016-07-02 05:00 | 357 | 352
2016-07-02 05:30 | 364 | 360
2016-07-02 06:00 | 377 | 372
2016-07-02 06:30 | 386 | 382
2016-07-02 07:00 | 391 | 387
2016-07-02 07:30 | 386 | 382
2016-07-02 08:00 | 393 | 389
2016-07-02 08:30 | 384 | 381
2016-07-02 09:00 | 362 | 358
2016-07-02 09:30 | 400 | 396
2016-07-02 10:00 | 418 | 415
2016-07-02 10:30 | 423 | 421
2016-07-02 11:00 | 423 | 421
2016-07-02 11:30 | 421 | 419
2016-07-02 12:00 | 415 | 413
2016-07-02 12:30 | 413 | 411
2016-07-02 13:00 | 418 | 416
2016-07-02 13:30 | 408 | 406
2016-07-02 14:00 | 387 | 384
2016-07-02 14:30 | 376 | 373
2016-07-02 15:00 | 380 | 376
2016-07-02 15:30 | 390 | 387
2016-07-02 16:00 | 406 | 403
2016-07-02 16:30 | 420 | 418
2016-07-02 17:00 | 421 | 419
2016-07-02 17:30 | 427 | 425
2016-07-02 18:00 | 393 | 391
2016-07-02 18:30 | 444 | 442
2016-07-02 19:00 | 467 | 466
2016-07-02 19:30 | 455 | 454
2016-07-02 20:00 | 445 | 443
2016-07-02 20:30 | 433 | 431
2016-07-02 21:00 | 427 | 425
2016-07-02 21:30 | 412 | 410
2016-07-02 22:00 | 409 | 407
2016-07-02 22:30 | 428 | 425
2016-07-02 23:00 | 409 | 407
2016-07-02 23:30 | 388 | 385
2016-07-03 | 410 | 408
2016-07-03 00:30 | 394 | 392
2016-07-03 01:00 | 376 | 373
2016-07-03 01:30 | 365 | 361
2016-07-03 02:00 | 354 | 349
2016-07-03 02:30 | 356 | 351
2016-07-03 03:00 | 355 | 350
2016-07-03 03:30 | 347 | 343
2016-07-03 04:00 | 347 | 342
2016-07-03 04:30 | 350 | 345
2016-07-03 05:00 | 344 | 339
2016-07-03 05:30 | 356 | 351
2016-07-03 06:00 | 360 | 355
2016-07-03 06:30 | 372 | 367
2016-07-03 07:00 | 369 | 365
2016-07-03 07:30 | 381 | 377
2016-07-03 08:00 | 382 | 378
2016-07-03 08:30 | 374 | 371
2016-07-03 09:00 | 385 | 382
2016-07-03 09:30 | 401 | 398
2016-07-03 10:00 | 408 | 405
2016-07-03 10:30 | 413 | 410
2016-07-03 11:00 | 399 | 396
2016-07-03 11:30 | 393 | 390
2016-07-03 12:00 | 397 | 394
2016-07-03 12:30 | 398 | 395
2016-07-03 13:00 | 382 | 378
2016-07-03 13:30 | 389 | 386
2016-07-03 14:00 | 378 | 375
2016-07-03 14:30 | 375 | 371
2016-07-03 15:00 | 391 | 388
2016-07-03 15:30 | 407 | 404
2016-07-03 16:00 | 413 | 411
2016-07-03 16:30 | 417 | 415
2016-07-03 17:00 | 410 | 408
2016-07-03 17:30 | 428 | 426
2016-07-03 18:00 | 414 | 412
2016-07-03 18:30 | 434 | 432
2016-07-03 19:00 | 466 | 465
2016-07-03 19:30 | 450 | 449
2016-07-03 20:00 | 435 | 434
2016-07-03 20:30 | 428 | 427
2016-07-03 21:00 | 413 | 411
2016-07-03 21:30 | 399 | 397
2016-07-03 22:00 | 403 | 401
2016-07-03 22:30 | 409 | 407
2016-07-03 23:00 | 396 | 394
2016-07-03 23:30 | 387 | 384
2016-07-04 | 391 | 387
2016-07-04 00:30 | 375 | 372
2016-07-04 01:00 | 354 | 351
2016-07-04 01:30 | 338 | 334
2016-07-04 02:00 | 325 | 320
2016-07-04 02:30 | 321 | 315
2016-07-04 03:00 | 315 | 310
2016-07-04 03:30 | 315 | 309
2016-07-04 04:00 | 321 | 316
2016-07-04 04:30 | 320 | 314
2016-07-04 05:00 | 323 | 318
2016-07-04 05:30 | 328 | 322
2016-07-04 06:00 | 345 | 340
2016-07-04 06:30 | 357 | 353
2016-07-04 07:00 | 319 | 315
2016-07-04 07:30 | 347 | 343
2016-07-04 08:00 | 359 | 356
2016-07-04 08:30 | 406 | 404
2016-07-04 09:00 | 421 | 419
2016-07-04 09:30 | 407 | 405
2016-07-04 10:00 | 419 | 418
2016-07-04 10:30 | 427 | 425
2016-07-04 11:00 | 433 | 432
2016-07-04 11:30 | 438 | 437
2016-07-04 12:00 | 469 | 467
2016-07-04 12:30 | 462 | 461
2016-07-04 13:00 | 441 | 440
2016-07-04 13:30 | 442 | 441
2016-07-04 14:00 | 448 | 447
2016-07-04 14:30 | 443 | 442
2016-07-04 15:00 | 438 | 437
2016-07-04 15:30 | 447 | 446
2016-07-04 16:00 | 449 | 448
2016-07-04 16:30 | 447 | 446
2016-07-04 17:00 | 459 | 458
2016-07-04 17:30 | 394 | 393
2016-07-04 18:00 | 205 | 201
2016-07-04 18:30 | 207 | 195
2016-07-04 19:00 | 246 | 234
2016-07-04 19:30 | 305 | 296
2016-07-04 20:00 | 347 | 342
2016-07-04 20:30 | 306 | 302
2016-07-04 21:00 | 291 | 285
2016-07-04 21:30 | 394 | 390
2016-07-04 22:00 | 412 | 411
2016-07-04 22:30 | 414 | 413
2016-07-04 23:00 | 428 | 427
2016-07-04 23:30 | 430 | 429
2016-07-05 | 410 | 409
2016-07-05 00:30 | 404 | 403
2016-07-05 01:00 | 386 | 385
2016-07-05 01:30 | 379 | 376
2016-07-05 02:00 | 370 | 368
2016-07-05 02:30 | 353 | 350
2016-07-05 03:00 | 336 | 332
2016-07-05 03:30 | 334 | 330
2016-07-05 04:00 | 334 | 330
2016-07-05 04:30 | 337 | 332
2016-07-05 05:00 | 339 | 335
2016-07-05 05:30 | 348 | 344
2016-07-05 06:00 | 356 | 352
2016-07-05 06:30 | 342 | 339
2016-07-05 07:00 | 341 | 338
2016-07-05 07:30 | 361 | 358
2016-07-05 08:00 | 365 | 363
2016-07-05 08:30 | 390 | 387
2016-07-05 09:00 | 383 | 381
2016-07-05 09:30 | 379 | 377
2016-07-05 10:00 | 367 | 364
2016-07-05 10:30 | 366 | 363
2016-07-05 11:00 | 367 | 365
2016-07-05 11:30 | 393 | 391
2016-07-05 12:00 | 402 | 400
2016-07-05 12:30 | 400 | 398
2016-07-05 13:00 | 371 | 370
2016-07-05 13:30 | 370 | 367
2016-07-05 14:00 | 393 | 391
2016-07-05 14:30 | 381 | 379
2016-07-05 15:00 | 381 | 378
2016-07-05 15:30 | 319 | 316
2016-07-05 16:00 | 272 | 267
2016-07-05 16:30 | 292 | 284
2016-07-05 17:00 | 265 | 257
2016-07-05 17:30 | 136 | 116
2016-07-05 18:00 | 111 | 66
2016-07-05 18:30 | 158 | 122
2016-07-05 19:00 | 211 | 182
2016-07-05 19:30 | 302 | 284
2016-07-05 20:00 | 288 | 276
2016-07-05 20:30 | 276 | 263
2016-07-05 21:00 | 275 | 261
2016-07-05 21:30 | 284 | 270
2016-07-05 22:00 | 292 | 277
2016-07-05 22:30 | 294 | 284
2016-07-05 23:00 | 301 | 292
2016-07-05 23:30 | 294 | 285
2016-07-06 | 285 | 276
2016-07-06 00:30 | 329 | 320
2016-07-06 01:00 | 376 | 369
2016-07-06 01:30 | 354 | 349
2016-07-06 02:00 | 336 | 330
2016-07-06 02:30 | 323 | 316
2016-07-06 03:00 | 317 | 309
2016-07-06 03:30 | 312 | 304
2016-07-06 04:00 | 311 | 302
2016-07-06 04:30 | 313 | 305
2016-07-06 05:00 | 320 | 312
2016-07-06 05:30 | 338 | 331
2016-07-06 06:00 | 357 | 350
2016-07-06 06:30 | 378 | 373
2016-07-06 07:00 | 333 | 329
2016-07-06 07:30 | 385 | 381
2016-07-06 08:00 | 357 | 353
2016-07-06 08:30 | 296 | 291
2016-07-06 09:00 | 290 | 282
2016-07-06 09:30 | 290 | 281
2016-07-06 10:00 | 307 | 299
2016-07-06 10:30 | 284 | 275
2016-07-06 11:00 | 274 | 264
2016-07-06 11:30 | 396 | 389
2016-07-06 12:00 | 426 | 423
2016-07-06 12:30 | 425 | 422
2016-07-06 13:00 | 422 | 419
2016-07-06 13:30 | 422 | 419
2016-07-06 14:00 | 429 | 427
2016-07-06 14:30 | 418 | 416
2016-07-06 15:00 | 412 | 409
2016-07-06 15:30 | 402 | 400
2016-07-06 16:00 | 328 | 325
2016-07-06 16:30 | 274 | 268
2016-07-06 17:00 | 281 | 270
2016-07-06 17:30 | 178 | 161
2016-07-06 18:00 | 106 | 63
2016-07-06 18:30 | 129 | 73
2016-07-06 19:00 | 133 | 78
2016-07-06 19:30 | 131 | 77
2016-07-06 20:00 | 119 | 52
2016-07-06 20:30 | 124 | 58
2016-07-06 21:00 | 188 | 153
2016-07-06 21:30 | 235 | 212
2016-07-06 22:00 | 277 | 261
2016-07-06 22:30 | 227 | 210
2016-07-06 23:00 | 245 | 226
2016-07-06 23:30 | 261 | 243
2016-07-07 | 369 | 358
2016-07-07 00:30 | 381 | 375
2016-07-07 01:00 | 358 | 352
2016-07-07 01:30 | 342 | 335
2016-07-07 02:00 | 326 | 317
2016-07-07 02:30 | 317 | 308
2016-07-07 03:00 | 321 | 310
2016-07-07 03:30 | 316 | 306
2016-07-07 04:00 | 312 | 301
2016-07-07 04:30 | 319 | 308
2016-07-07 05:00 | 321 | 311
2016-07-07 05:30 | 323 | 313
2016-07-07 06:00 | 333 | 324
2016-07-07 06:30 | 307 | 298
2016-07-07 07:00 | 316 | 306
2016-07-07 07:30 | 369 | 362
2016-07-07 08:00 | 338 | 332
2016-07-07 08:30 | 239 | 227
2016-07-07 09:00 | 262 | 247
2016-07-07 09:30 | 307 | 295
2016-07-07 10:00 | 297 | 286
2016-07-07 10:30 | 254 | 245
2016-07-07 11:00 | 253 | 244
2016-07-07 11:30 | 247 | 237
2016-07-07 12:00 | 251 | 241
2016-07-07 12:30 | 249 | 239
2016-07-07 13:00 | 267 | 258
2016-07-07 13:30 | 271 | 263
2016-07-07 14:00 | 268 | 260
2016-07-07 14:30 | 266 | 258
2016-07-07 15:00 | 242 | 233
2016-07-07 15:30 | 245 | 236
2016-07-07 16:00 | 257 | 248
2016-07-07 16:30 | 227 | 218
2016-07-07 17:00 | 214 | 202
2016-07-07 17:30 | 229 | 217
2016-07-07 18:00 | 221 | 209
2016-07-07 18:30 | 198 | 184
2016-07-07 19:00 | 221 | 207
2016-07-07 19:30 | 222 | 210
2016-07-07 20:00 | 227 | 216
2016-07-07 20:30 | 214 | 202
2016-07-07 21:00 | 219 | 206
2016-07-07 21:30 | 240 | 228
2016-07-07 22:00 | 251 | 242
2016-07-07 22:30 | 190 | 178
2016-07-07 23:00 | 192 | 176
2016-07-07 23:30 | 192 | 174
2016-07-08 | 262 | 249
2016-07-08 00:30 | 258 | 250
2016-07-08 01:00 | 249 | 241
2016-07-08 01:30 | 241 | 232
2016-07-08 02:00 | 237 | 227
2016-07-08 02:30 | 227 | 216
2016-07-08 03:00 | 226 | 214
2016-07-08 03:30 | 219 | 207
2016-07-08 04:00 | 219 | 206
2016-07-08 04:30 | 228 | 215
2016-07-08 05:00 | 230 | 219
2016-07-08 05:30 | 234 | 223
2016-07-08 06:00 | 243 | 233
2016-07-08 06:30 | 258 | 248
2016-07-08 07:00 | 269 | 261
2016-07-08 07:30 | 282 | 275
2016-07-08 08:00 | 285 | 279
2016-07-08 08:30 | 283 | 278
2016-07-08 09:00 | 279 | 274
2016-07-08 09:30 | 274 | 267
2016-07-08 10:00 | 243 | 235
2016-07-08 10:30 | 253 | 243
2016-07-08 11:00 | 283 | 275
2016-07-08 11:30 | 290 | 284
2016-07-08 12:00 | 272 | 266
2016-07-08 12:30 | 264 | 258
2016-07-08 13:00 | 259 | 251
2016-07-08 13:30 | 258 | 250
2016-07-08 14:00 | 258 | 250
2016-07-08 14:30 | 254 | 246
2016-07-08 15:00 | 268 | 259
2016-07-08 15:30 | 273 | 266
2016-07-08 16:00 | 277 | 270
2016-07-08 16:30 | 287 | 281
2016-07-08 17:00 | 284 | 279
2016-07-08 17:30 | 284 | 279
2016-07-08 18:00 | 283 | 278
2016-07-08 18:30 | 286 | 281
2016-07-08 19:00 | 289 | 284
2016-07-08 19:30 | 283 | 278
2016-07-08 20:00 | 283 | 277
2016-07-08 20:30 | 275 | 270
2016-07-08 21:00 | 274 | 267
2016-07-08 21:30 | 261 | 255
2016-07-08 22:00 | 281 | 274
2016-07-08 22:30 | 294 | 288
2016-07-08 23:00 | 288 | 283
2016-07-08 23:30 | 283 | 277
2016-07-09 | 281 | 275
2016-07-09 00:30 | 265 | 258
2016-07-09 01:00 | 250 | 242
2016-07-09 01:30 | 238 | 228
2016-07-09 02:00 | 233 | 221
2016-07-09 02:30 | 225 | 212
2016-07-09 03:00 | 226 | 212
2016-07-09 03:30 | 227 | 214
2016-07-09 04:00 | 226 | 213
2016-07-09 04:30 | 228 | 215
2016-07-09 05:00 | 228 | 216
2016-07-09 05:30 | 230 | 217
2016-07-09 06:00 | 232 | 220
2016-07-09 06:30 | 239 | 228
2016-07-09 07:00 | 246 | 236
2016-07-09 07:30 | 261 | 251
2016-07-09 08:00 | 268 | 259
2016-07-09 08:30 | 278 | 271
2016-07-09 09:00 | 273 | 266
2016-07-09 09:30 | 270 | 262
2016-07-09 10:00 | 270 | 262
2016-07-09 10:30 | 264 | 256
2016-07-09 11:00 | 260 | 252
2016-07-09 11:30 | 261 | 252
2016-07-09 12:00 | 258 | 249
2016-07-09 12:30 | 260 | 251
2016-07-09 13:00 | 260 | 252
2016-07-09 13:30 | 252 | 243
2016-07-09 14:00 | 242 | 232
2016-07-09 14:30 | 250 | 240
2016-07-09 15:00 | 253 | 244
2016-07-09 15:30 | 255 | 246
2016-07-09 16:00 | 257 | 249
2016-07-09 16:30 | 265 | 257
2016-07-09 17:00 | 277 | 270
2016-07-09 17:30 | 289 | 282
2016-07-09 18:00 | 296 | 290
2016-07-09 18:30 | 309 | 304
2016-07-09 19:00 | 311 | 307
2016-07-09 19:30 | 308 | 304
2016-07-09 20:00 | 304 | 300
2016-07-09 20:30 | 294 | 289
2016-07-09 21:00 | 290 | 285
2016-07-09 21:30 | 277 | 272
2016-07-09 22:00 | 278 | 272
2016-07-09 22:30 | 280 | 275
2016-07-09 23:00 | 268 | 263
2016-07-09 23:30 | 260 | 254
2016-07-10 | 257 | 249
2016-07-10 00:30 | 249 | 240
2016-07-10 01:00 | 239 | 230
2016-07-10 01:30 | 236 | 226
2016-07-10 02:00 | 226 | 215
2016-07-10 02:30 | 219 | 206
2016-07-10 03:00 | 218 | 206
2016-07-10 03:30 | 200 | 186
2016-07-10 04:00 | 173 | 154
2016-07-10 04:30 | 162 | 140
2016-07-10 05:00 | 166 | 144
2016-07-10 05:30 | 171 | 150
2016-07-10 06:00 | 175 | 155
2016-07-10 06:30 | 181 | 162
2016-07-10 07:00 | 184 | 165
2016-07-10 07:30 | 191 | 173
2016-07-10 08:00 | 204 | 188
2016-07-10 08:30 | 247 | 235
2016-07-10 09:00 | 259 | 250
2016-07-10 09:30 | 265 | 258
2016-07-10 10:00 | 257 | 250
2016-07-10 10:30 | 251 | 243
2016-07-10 11:00 | 253 | 244
2016-07-10 11:30 | 252 | 243
2016-07-10 12:00 | 250 | 242
2016-07-10 12:30 | 251 | 243
2016-07-10 13:00 | 250 | 241
2016-07-10 13:30 | 247 | 239
2016-07-10 14:00 | 239 | 231
2016-07-10 14:30 | 249 | 240
2016-07-10 15:00 | 250 | 242
2016-07-10 15:30 | 260 | 252
2016-07-10 16:00 | 266 | 259
2016-07-10 16:30 | 272 | 265
2016-07-10 17:00 | 279 | 273
2016-07-10 17:30 | 295 | 290
2016-07-10 18:00 | 305 | 301
2016-07-10 18:30 | 325 | 321
2016-07-10 19:00 | 327 | 324
2016-07-10 19:30 | 312 | 309
2016-07-10 20:00 | 304 | 301
2016-07-10 20:30 | 296 | 292
2016-07-10 21:00 | 290 | 285
2016-07-10 21:30 | 283 | 278
2016-07-10 22:00 | 283 | 277
2016-07-10 22:30 | 280 | 274
2016-07-10 23:00 | 274 | 267
2016-07-10 23:30 | 259 | 252
2016-07-11 | 254 | 246
2016-07-11 00:30 | 250 | 242
2016-07-11 01:00 | 244 | 235
2016-07-11 01:30 | 236 | 226
2016-07-11 02:00 | 228 | 217
2016-07-11 02:30 | 223 | 211
2016-07-11 03:00 | 220 | 206
2016-07-11 03:30 | 224 | 210
2016-07-11 04:00 | 225 | 212
2016-07-11 04:30 | 236 | 225
2016-07-11 05:00 | 242 | 232
2016-07-11 05:30 | 253 | 244
2016-07-11 06:00 | 258 | 250
2016-07-11 06:30 | 276 | 269
2016-07-11 07:00 | 297 | 292
2016-07-11 07:30 | 321 | 316
2016-07-11 08:00 | 333 | 330
2016-07-11 08:30 | 334 | 331
2016-07-11 09:00 | 329 | 326
2016-07-11 09:30 | 326 | 323
2016-07-11 10:00 | 320 | 317
2016-07-11 10:30 | 328 | 325
2016-07-11 11:00 | 328 | 325
2016-07-11 11:30 | 354 | 352
2016-07-11 12:00 | 345 | 343
2016-07-11 12:30 | 339 | 337
2016-07-11 13:00 | 336 | 333
2016-07-11 13:30 | 335 | 333
2016-07-11 14:00 | 337 | 334
2016-07-11 14:30 | 342 | 339
2016-07-11 15:00 | 342 | 339
2016-07-11 15:30 | 336 | 334
2016-07-11 16:00 | 348 | 346
2016-07-11 16:30 | 357 | 355
2016-07-11 17:00 | 309 | 307
2016-07-11 17:30 | 248 | 244
2016-07-11 18:00 | 259 | 252
2016-07-11 18:30 | 253 | 247
2016-07-11 19:00 | 252 | 245
2016-07-11 19:30 | 242 | 234
2016-07-11 20:00 | 239 | 230
2016-07-11 20:30 | 235 | 225
2016-07-11 21:00 | 242 | 233
2016-07-11 21:30 | 313 | 305
2016-07-11 22:00 | 331 | 327
2016-07-11 22:30 | 338 | 334
2016-07-11 23:00 | 329 | 326
2016-07-11 23:30 | 326 | 322
2016-07-12 | 323 | 319
2016-07-12 00:30 | 306 | 302
2016-07-12 01:00 | 286 | 281
2016-07-12 01:30 | 261 | 255
2016-07-12 02:00 | 258 | 250
2016-07-12 02:30 | 252 | 243
2016-07-12 03:00 | 253 | 245
2016-07-12 03:30 | 253 | 244
2016-07-12 04:00 | 249 | 240
2016-07-12 04:30 | 248 | 239
2016-07-12 05:00 | 250 | 241
2016-07-12 05:30 | 269 | 261
2016-07-12 06:00 | 280 | 273
2016-07-12 06:30 | 297 | 291
2016-07-12 07:00 | 316 | 311
2016-07-12 07:30 | 330 | 327
2016-07-12 08:00 | 345 | 342
2016-07-12 08:30 | 349 | 346
2016-07-12 09:00 | 338 | 335
2016-07-12 09:30 | 323 | 321
2016-07-12 10:00 | 321 | 318
2016-07-12 10:30 | 321 | 318
2016-07-12 11:00 | 327 | 323
2016-07-12 11:30 | 326 | 323
2016-07-12 12:00 | 326 | 322
2016-07-12 12:30 | 326 | 323
2016-07-12 13:00 | 326 | 323
2016-07-12 13:30 | 326 | 322
2016-07-12 14:00 | 325 | 321
2016-07-12 14:30 | 328 | 325
2016-07-12 15:00 | 326 | 322
2016-07-12 15:30 | 330 | 326
2016-07-12 16:00 | 336 | 333
2016-07-12 16:30 | 352 | 349
2016-07-12 17:00 | 289 | 286
2016-07-12 17:30 | 233 | 226
2016-07-12 18:00 | 208 | 196
2016-07-12 18:30 | 202 | 188
2016-07-12 19:00 | 228 | 215
2016-07-12 19:30 | 241 | 230
2016-07-12 20:00 | 237 | 228
2016-07-12 20:30 | 236 | 226
2016-07-12 21:00 | 228 | 217
2016-07-12 21:30 | 305 | 296
2016-07-12 22:00 | 324 | 319
2016-07-12 22:30 | 334 | 330
2016-07-12 23:00 | 330 | 326
2016-07-12 23:30 | 323 | 319
2016-07-13 | 308 | 304
2016-07-13 00:30 | 294 | 289
2016-07-13 01:00 | 275 | 269
2016-07-13 01:30 | 258 | 250
2016-07-13 02:00 | 258 | 249
2016-07-13 02:30 | 254 | 245
2016-07-13 03:00 | 248 | 239
2016-07-13 03:30 | 246 | 236
2016-07-13 04:00 | 246 | 235
2016-07-13 04:30 | 259 | 249
2016-07-13 05:00 | 263 | 253
2016-07-13 05:30 | 270 | 261
2016-07-13 06:00 | 278 | 269
2016-07-13 06:30 | 302 | 294
2016-07-13 07:00 | 320 | 314
2016-07-13 07:30 | 341 | 337
2016-07-13 08:00 | 365 | 362
2016-07-13 08:30 | 376 | 374
2016-07-13 09:00 | 371 | 370
2016-07-13 09:30 | 347 | 345
2016-07-13 10:00 | 308 | 305
2016-07-13 10:30 | 307 | 303
2016-07-13 11:00 | 309 | 305
2016-07-13 11:30 | 299 | 296
2016-07-13 12:00 | 298 | 294
2016-07-13 12:30 | 300 | 296
2016-07-13 13:00 | 296 | 292
2016-07-13 13:30 | 264 | 259
2016-07-13 14:00 | 250 | 245
2016-07-13 14:30 | 254 | 247
2016-07-13 15:00 | 255 | 248
2016-07-13 15:30 | 253 | 247
2016-07-13 16:00 | 259 | 252
2016-07-13 16:30 | 258 | 252
2016-07-13 17:00 | 253 | 246
2016-07-13 17:30 | 207 | 198
2016-07-13 18:00 | 205 | 194
2016-07-13 18:30 | 197 | 184
2016-07-13 19:00 | 218 | 206
2016-07-13 19:30 | 213 | 202
2016-07-13 20:00 | 208 | 197
2016-07-13 20:30 | 173 | 159
2016-07-13 21:00 | 195 | 181
2016-07-13 21:30 | 186 | 172
2016-07-13 22:00 | 196 | 182
2016-07-13 22:30 | 240 | 230
2016-07-13 23:00 | 234 | 225
2016-07-13 23:30 | 224 | 214
2016-07-14 | 211 | 200
2016-07-14 00:30 | 194 | 182
2016-07-14 01:00 | 198 | 184
2016-07-14 01:30 | 183 | 168
2016-07-14 02:00 | 176 | 159
2016-07-14 02:30 | 168 | 150
2016-07-14 03:00 | 166 | 146
2016-07-14 03:30 | 166 | 146
2016-07-14 04:00 | 166 | 146
2016-07-14 04:30 | 171 | 151
2016-07-14 05:00 | 172 | 153
2016-07-14 05:30 | 180 | 162
2016-07-14 06:00 | 188 | 171
2016-07-14 06:30 | 212 | 198
2016-07-14 07:00 | 218 | 206
2016-07-14 07:30 | 200 | 188
2016-07-14 08:00 | 227 | 216
2016-07-14 08:30 | 276 | 267
2016-07-14 09:00 | 275 | 270
2016-07-14 09:30 | 277 | 272
2016-07-14 10:00 | 265 | 260
2016-07-14 10:30 | 275 | 269
2016-07-14 11:00 | 271 | 266
2016-07-14 11:30 | 260 | 255
2016-07-14 12:00 | 259 | 253
2016-07-14 12:30 | 263 | 256
2016-07-14 13:00 | 260 | 254
2016-07-14 13:30 | 253 | 247
2016-07-14 14:00 | 249 | 242
2016-07-14 14:30 | 252 | 245
2016-07-14 15:00 | 253 | 247
2016-07-14 15:30 | 257 | 250
2016-07-14 16:00 | 259 | 252
2016-07-14 16:30 | 270 | 263
2016-07-14 17:00 | 279 | 273
2016-07-14 17:30 | 227 | 221
2016-07-14 18:00 | 206 | 196
2016-07-14 18:30 | 222 | 211
2016-07-14 19:00 | 235 | 226
2016-07-14 19:30 | 220 | 211
2016-07-14 20:00 | 191 | 180
2016-07-14 20:30 | 168 | 153
2016-07-14 21:00 | 192 | 177
2016-07-14 21:30 | 214 | 202
2016-07-14 22:00 | 252 | 243
2016-07-14 22:30 | 223 | 216
2016-07-14 23:00 | 234 | 225
2016-07-14 23:30 | 245 | 237
2016-07-15 | 229 | 221
2016-07-15 00:30 | 219 | 208
2016-07-15 01:00 | 205 | 193
2016-07-15 01:30 | 190 | 176
2016-07-15 02:00 | 179 | 164
2016-07-15 02:30 | 173 | 157
2016-07-15 03:00 | 171 | 155
2016-07-15 03:30 | 176 | 159
2016-07-15 04:00 | 174 | 156
2016-07-15 04:30 | 177 | 160
2016-07-15 05:00 | 180 | 163
2016-07-15 05:30 | 185 | 170
2016-07-15 06:00 | 199 | 186
2016-07-15 06:30 | 219 | 208
2016-07-15 07:00 | 204 | 193
2016-07-15 07:30 | 220 | 209
2016-07-15 08:00 | 235 | 226
2016-07-15 08:30 | 252 | 244
2016-07-15 09:00 | 275 | 268
2016-07-15 09:30 | 248 | 242
2016-07-15 10:00 | 239 | 232
2016-07-15 10:30 | 241 | 234
2016-07-15 11:00 | 244 | 237
2016-07-15 11:30 | 288 | 282
2016-07-15 12:00 | 293 | 289
2016-07-15 12:30 | 297 | 293
2016-07-15 13:00 | 290 | 286
2016-07-15 13:30 | 279 | 274
2016-07-15 14:00 | 279 | 274
2016-07-15 14:30 | 280 | 276
2016-07-15 15:00 | 285 | 280
2016-07-15 15:30 | 264 | 260
2016-07-15 16:00 | 268 | 263
2016-07-15 16:30 | 274 | 269
2016-07-15 17:00 | 219 | 213
2016-07-15 17:30 | 215 | 206
2016-07-15 18:00 | 189 | 178
2016-07-15 18:30 | 210 | 198
2016-07-15 19:00 | 217 | 207
2016-07-15 19:30 | 204 | 193
2016-07-15 20:00 | 223 | 212
2016-07-15 20:30 | 218 | 208
2016-07-15 21:00 | 225 | 215
2016-07-15 21:30 | 229 | 219
2016-07-15 22:00 | 251 | 243
2016-07-15 22:30 | 206 | 197
2016-07-15 23:00 | 234 | 225
2016-07-15 23:30 | 275 | 268
2016-07-16 | 314 | 309
2016-07-16 00:30 | 305 | 302
2016-07-16 01:00 | 289 | 285
2016-07-16 01:30 | 272 | 267
2016-07-16 02:00 | 266 | 260
2016-07-16 02:30 | 258 | 251
2016-07-16 03:00 | 253 | 246
2016-07-16 03:30 | 250 | 242
2016-07-16 04:00 | 251 | 243
2016-07-16 04:30 | 253 | 246
2016-07-16 05:00 | 255 | 248
2016-07-16 05:30 | 257 | 250
2016-07-16 06:00 | 265 | 258
2016-07-16 06:30 | 270 | 264
2016-07-16 07:00 | 278 | 272
2016-07-16 07:30 | 292 | 287
2016-07-16 08:00 | 308 | 304
2016-07-16 08:30 | 321 | 317
2016-07-16 09:00 | 327 | 323
2016-07-16 09:30 | 314 | 311
2016-07-16 10:00 | 326 | 323
2016-07-16 10:30 | 325 | 323
2016-07-16 11:00 | 345 | 342
2016-07-16 11:30 | 337 | 335
2016-07-16 12:00 | 332 | 329
2016-07-16 12:30 | 327 | 324
2016-07-16 13:00 | 324 | 321
2016-07-16 13:30 | 319 | 317
2016-07-16 14:00 | 305 | 303
2016-07-16 14:30 | 284 | 281
2016-07-16 15:00 | 287 | 283
2016-07-16 15:30 | 291 | 287
2016-07-16 16:00 | 302 | 298
2016-07-16 16:30 | 309 | 306
2016-07-16 17:00 | 317 | 314
2016-07-16 17:30 | 327 | 325
2016-07-16 18:00 | 341 | 339
2016-07-16 18:30 | 358 | 357
2016-07-16 19:00 | 361 | 359
2016-07-16 19:30 | 351 | 349
2016-07-16 20:00 | 343 | 341
2016-07-16 20:30 | 335 | 332
2016-07-16 21:00 | 328 | 324
2016-07-16 21:30 | 321 | 317
2016-07-16 22:00 | 314 | 309
2016-07-16 22:30 | 318 | 313
2016-07-16 23:00 | 310 | 306
2016-07-16 23:30 | 305 | 301
2016-07-17 | 301 | 297
2016-07-17 00:30 | 291 | 286
2016-07-17 01:00 | 278 | 273
2016-07-17 01:30 | 272 | 265
2016-07-17 02:00 | 261 | 254
2016-07-17 02:30 | 255 | 248
2016-07-17 03:00 | 251 | 243
2016-07-17 03:30 | 250 | 242
2016-07-17 04:00 | 247 | 238
2016-07-17 04:30 | 246 | 238
2016-07-17 05:00 | 249 | 241
2016-07-17 05:30 | 251 | 243
2016-07-17 06:00 | 253 | 246
2016-07-17 06:30 | 257 | 250
2016-07-17 07:00 | 259 | 251
2016-07-17 07:30 | 268 | 261
2016-07-17 08:00 | 282 | 276
2016-07-17 08:30 | 300 | 294
2016-07-17 09:00 | 303 | 298
2016-07-17 09:30 | 306 | 301
2016-07-17 10:00 | 291 | 287
2016-07-17 10:30 | 293 | 289
2016-07-17 11:00 | 294 | 289
2016-07-17 11:30 | 298 | 294
2016-07-17 12:00 | 285 | 280
2016-07-17 12:30 | 280 | 275
2016-07-17 13:00 | 280 | 274
2016-07-17 13:30 | 264 | 259
2016-07-17 14:00 | 258 | 252
2016-07-17 14:30 | 270 | 264
2016-07-17 15:00 | 276 | 270
2016-07-17 15:30 | 275 | 269
2016-07-17 16:00 | 293 | 288
2016-07-17 16:30 | 298 | 294
2016-07-17 17:00 | 307 | 303
2016-07-17 17:30 | 323 | 319
2016-07-17 18:00 | 346 | 343
2016-07-17 18:30 | 361 | 359
2016-07-17 19:00 | 368 | 367
2016-07-17 19:30 | 356 | 355
2016-07-17 20:00 | 350 | 349
2016-07-17 20:30 | 342 | 340
2016-07-17 21:00 | 330 | 328
2016-07-17 21:30 | 319 | 317
2016-07-17 22:00 | 313 | 310
2016-07-17 22:30 | 324 | 320
2016-07-17 23:00 | 315 | 311
2016-07-17 23:30 | 311 | 307
2016-07-18 | 302 | 299
2016-07-18 00:30 | 298 | 294
2016-07-18 01:00 | 282 | 278
2016-07-18 01:30 | 274 | 268
2016-07-18 02:00 | 268 | 262
2016-07-18 02:30 | 264 | 257
2016-07-18 03:00 | 259 | 252
2016-07-18 03:30 | 260 | 252
2016-07-18 04:00 | 258 | 251
2016-07-18 04:30 | 253 | 245
2016-07-18 05:00 | 227 | 218
2016-07-18 05:30 | 235 | 225
2016-07-18 06:00 | 249 | 239
2016-07-18 06:30 | 268 | 262
2016-07-18 07:00 | 286 | 281
2016-07-18 07:30 | 313 | 309
2016-07-18 08:00 | 325 | 323
2016-07-18 08:30 | 299 | 297
2016-07-18 09:00 | 305 | 302
2016-07-18 09:30 | 299 | 295
2016-07-18 10:00 | 290 | 286
2016-07-18 10:30 | 293 | 288
2016-07-18 11:00 | 294 | 289
2016-07-18 11:30 | 293 | 288
2016-07-18 12:00 | 287 | 284
2016-07-18 12:30 | 282 | 278
2016-07-18 13:00 | 276 | 272
2016-07-18 13:30 | 279 | 275
2016-07-18 14:00 | 281 | 277
2016-07-18 14:30 | 273 | 268
2016-07-18 15:00 | 266 | 262
2016-07-18 15:30 | 257 | 253
2016-07-18 16:00 | 261 | 256
2016-07-18 16:30 | 273 | 268
2016-07-18 17:00 | 220 | 214
2016-07-18 17:30 | 210 | 201
2016-07-18 18:00 | 214 | 204
2016-07-18 18:30 | 225 | 215
2016-07-18 19:00 | 225 | 216
2016-07-18 19:30 | 212 | 203
2016-07-18 20:00 | 215 | 206
2016-07-18 20:30 | 207 | 198
2016-07-18 21:00 | 199 | 189
2016-07-18 21:30 | 187 | 176
2016-07-18 22:00 | 221 | 211
2016-07-18 22:30 | 257 | 250
2016-07-18 23:00 | 250 | 245
2016-07-18 23:30 | 246 | 241
2016-07-19 | 236 | 230
2016-07-19 00:30 | 187 | 180
2016-07-19 01:00 | 179 | 166
2016-07-19 01:30 | 171 | 154
2016-07-19 02:00 | 165 | 147
2016-07-19 02:30 | 159 | 139
2016-07-19 03:00 | 161 | 141
2016-07-19 03:30 | 160 | 139
2016-07-19 04:00 | 162 | 142
2016-07-19 04:30 | 172 | 153
2016-07-19 05:00 | 176 | 158
2016-07-19 05:30 | 187 | 171
2016-07-19 06:00 | 183 | 168
2016-07-19 06:30 | 196 | 183
2016-07-19 07:00 | 203 | 194
2016-07-19 07:30 | 217 | 209
2016-07-19 08:00 | 248 | 242
2016-07-19 08:30 | 260 | 255
2016-07-19 09:00 | 255 | 249
2016-07-19 09:30 | 261 | 254
2016-07-19 10:00 | 254 | 247
2016-07-19 10:30 | 252 | 245
2016-07-19 11:00 | 255 | 247
2016-07-19 11:30 | 256 | 248
2016-07-19 12:00 | 249 | 241
2016-07-19 12:30 | 251 | 242
2016-07-19 13:00 | 249 | 241
2016-07-19 13:30 | 249 | 240
2016-07-19 14:00 | 242 | 234
2016-07-19 14:30 | 244 | 235
2016-07-19 15:00 | 233 | 223
2016-07-19 15:30 | 237 | 227
2016-07-19 16:00 | 245 | 236
2016-07-19 16:30 | 245 | 237
2016-07-19 17:00 | 190 | 179
2016-07-19 17:30 | 178 | 163
2016-07-19 18:00 | 185 | 168
2016-07-19 18:30 | 190 | 175
2016-07-19 19:00 | 197 | 183
2016-07-19 19:30 | 212 | 200
2016-07-19 20:00 | 210 | 199
2016-07-19 20:30 | 204 | 191
2016-07-19 21:00 | 192 | 178
2016-07-19 21:30 | 220 | 208
2016-07-19 22:00 | 257 | 248
2016-07-19 22:30 | 272 | 266
2016-07-19 23:00 | 273 | 267
2016-07-19 23:30 | 269 | 264
2016-07-20 | 259 | 253
2016-07-20 00:30 | 245 | 238
2016-07-20 01:00 | 230 | 222
2016-07-20 01:30 | 204 | 194
2016-07-20 02:00 | 176 | 162
2016-07-20 02:30 | 184 | 167
2016-07-20 03:00 | 185 | 170
2016-07-20 03:30 | 201 | 187
2016-07-20 04:00 | 203 | 190
2016-07-20 04:30 | 198 | 184
2016-07-20 05:00 | 201 | 188
2016-07-20 05:30 | 209 | 196
2016-07-20 06:00 | 219 | 208
2016-07-20 06:30 | 243 | 234
2016-07-20 07:00 | 266 | 259
2016-07-20 07:30 | 275 | 270
2016-07-20 08:00 | 285 | 281
2016-07-20 08:30 | 314 | 310
2016-07-20 09:00 | 312 | 310
2016-07-20 09:30 | 310 | 307
2016-07-20 10:00 | 303 | 300
2016-07-20 10:30 | 299 | 296
2016-07-20 11:00 | 296 | 292
2016-07-20 11:30 | 296 | 292
2016-07-20 12:00 | 287 | 282
2016-07-20 12:30 | 282 | 277
2016-07-20 13:00 | 279 | 275
2016-07-20 13:30 | 276 | 271
2016-07-20 14:00 | 268 | 262
2016-07-20 14:30 | 273 | 267
2016-07-20 15:00 | 275 | 270
2016-07-20 15:30 | 274 | 269
2016-07-20 16:00 | 284 | 279
2016-07-20 16:30 | 276 | 271
2016-07-20 17:00 | 229 | 223
2016-07-20 17:30 | 223 | 214
2016-07-20 18:00 | 228 | 219
2016-07-20 18:30 | 235 | 226
2016-07-20 19:00 | 235 | 226
2016-07-20 19:30 | 213 | 203
2016-07-20 20:00 | 210 | 198
2016-07-20 20:30 | 208 | 196
2016-07-20 21:00 | 199 | 188
2016-07-20 21:30 | 242 | 232
2016-07-20 22:00 | 257 | 250
2016-07-20 22:30 | 226 | 218
2016-07-20 23:00 | 238 | 229
2016-07-20 23:30 | 266 | 259
2016-07-21 | 308 | 303
2016-07-21 00:30 | 289 | 286
2016-07-21 01:00 | 278 | 274
2016-07-21 01:30 | 282 | 277
2016-07-21 02:00 | 276 | 271
2016-07-21 02:30 | 274 | 269
2016-07-21 03:00 | 269 | 263
2016-07-21 03:30 | 270 | 264
2016-07-21 04:00 | 271 | 265
2016-07-21 04:30 | 273 | 268
2016-07-21 05:00 | 280 | 275
2016-07-21 05:30 | 288 | 284
2016-07-21 06:00 | 299 | 295
2016-07-21 06:30 | 323 | 321
2016-07-21 07:00 | 342 | 340
2016-07-21 07:30 | 354 | 353
2016-07-21 08:00 | 383 | 382
2016-07-21 08:30 | 390 | 389
2016-07-21 09:00 | 385 | 384
2016-07-21 09:30 | 383 | 382
2016-07-21 10:00 | 380 | 379
2016-07-21 10:30 | 378 | 377
2016-07-21 11:00 | 379 | 379
2016-07-21 11:30 | 379 | 378
2016-07-21 12:00 | 371 | 370
2016-07-21 12:30 | 370 | 369
2016-07-21 13:00 | 368 | 367
2016-07-21 13:30 | 366 | 365
2016-07-21 14:00 | 370 | 369
2016-07-21 14:30 | 378 | 377
2016-07-21 15:00 | 372 | 371
2016-07-21 15:30 | 367 | 367
2016-07-21 16:00 | 363 | 362
2016-07-21 16:30 | 366 | 365
2016-07-21 17:00 | 371 | 370
2016-07-21 17:30 | 367 | 366
2016-07-21 18:00 | 367 | 366
2016-07-21 18:30 | 371 | 371
2016-07-21 19:00 | 375 | 374
2016-07-21 19:30 | 363 | 362
2016-07-21 20:00 | 359 | 358
2016-07-21 20:30 | 353 | 352
2016-07-21 21:00 | 348 | 347
2016-07-21 21:30 | 333 | 332
2016-07-21 22:00 | 336 | 334
2016-07-21 22:30 | 340 | 339
2016-07-21 23:00 | 337 | 335
2016-07-21 23:30 | 331 | 329
2016-07-22 | 319 | 317
2016-07-22 00:30 | 299 | 297
2016-07-22 01:00 | 286 | 283
2016-07-22 01:30 | 288 | 284
2016-07-22 02:00 | 282 | 278
2016-07-22 02:30 | 272 | 269
2016-07-22 03:00 | 268 | 264
2016-07-22 03:30 | 265 | 261
2016-07-22 04:00 | 264 | 259
2016-07-22 04:30 | 267 | 262
2016-07-22 05:00 | 270 | 265
2016-07-22 05:30 | 280 | 276
2016-07-22 06:00 | 288 | 285
2016-07-22 06:30 | 310 | 306
2016-07-22 07:00 | 323 | 320
2016-07-22 07:30 | 344 | 342
2016-07-22 08:00 | 354 | 352
2016-07-22 08:30 | 353 | 352
2016-07-22 09:00 | 347 | 346
2016-07-22 09:30 | 344 | 342
2016-07-22 10:00 | 339 | 338
2016-07-22 10:30 | 336 | 335
2016-07-22 11:00 | 330 | 328
2016-07-22 11:30 | 322 | 320
2016-07-22 12:00 | 319 | 316
2016-07-22 12:30 | 315 | 312
2016-07-22 13:00 | 316 | 313
2016-07-22 13:30 | 315 | 312
2016-07-22 14:00 | 318 | 315
2016-07-22 14:30 | 321 | 318
2016-07-22 15:00 | 327 | 325
2016-07-22 15:30 | 330 | 327
2016-07-22 16:00 | 340 | 337
2016-07-22 16:30 | 345 | 343
2016-07-22 17:00 | 352 | 350
2016-07-22 17:30 | 344 | 342
2016-07-22 18:00 | 343 | 341
2016-07-22 18:30 | 349 | 347
2016-07-22 19:00 | 352 | 351
2016-07-22 19:30 | 350 | 349
2016-07-22 20:00 | 346 | 345
2016-07-22 20:30 | 341 | 339
2016-07-22 21:00 | 332 | 331
2016-07-22 21:30 | 323 | 321
2016-07-22 22:00 | 326 | 324
2016-07-22 22:30 | 343 | 341
2016-07-22 23:00 | 341 | 339
2016-07-22 23:30 | 334 | 333
2016-07-23 | 326 | 324
2016-07-23 00:30 | 325 | 322
2016-07-23 01:00 | 313 | 311
2016-07-23 01:30 | 300 | 298
2016-07-23 02:00 | 290 | 287
2016-07-23 02:30 | 284 | 280
2016-07-23 03:00 | 280 | 276
2016-07-23 03:30 | 278 | 274
2016-07-23 04:00 | 281 | 276
2016-07-23 04:30 | 273 | 268
2016-07-23 05:00 | 270 | 265
2016-07-23 05:30 | 275 | 270
2016-07-23 06:00 | 281 | 276
2016-07-23 06:30 | 291 | 287
2016-07-23 07:00 | 292 | 288
2016-07-23 07:30 | 308 | 303
2016-07-23 08:00 | 303 | 300
2016-07-23 08:30 | 307 | 303
2016-07-23 09:00 | 309 | 305
2016-07-23 09:30 | 304 | 301
2016-07-23 10:00 | 305 | 302
2016-07-23 10:30 | 306 | 302
2016-07-23 11:00 | 303 | 299
2016-07-23 11:30 | 313 | 310
2016-07-23 12:00 | 316 | 313
2016-07-23 12:30 | 314 | 311
2016-07-23 13:00 | 312 | 309
2016-07-23 13:30 | 314 | 311
2016-07-23 14:00 | 315 | 312
2016-07-23 14:30 | 317 | 315
2016-07-23 15:00 | 320 | 318
2016-07-23 15:30 | 324 | 322
2016-07-23 16:00 | 323 | 320
2016-07-23 16:30 | 321 | 318
2016-07-23 17:00 | 322 | 319
2016-07-23 17:30 | 336 | 333
2016-07-23 18:00 | 342 | 340
2016-07-23 18:30 | 356 | 355
2016-07-23 19:00 | 360 | 359
2016-07-23 19:30 | 351 | 350
2016-07-23 20:00 | 349 | 348
2016-07-23 20:30 | 343 | 342
2016-07-23 21:00 | 330 | 329
2016-07-23 21:30 | 320 | 318
2016-07-23 22:00 | 322 | 320
2016-07-23 22:30 | 318 | 316
2016-07-23 23:00 | 330 | 328
2016-07-23 23:30 | 325 | 323
2016-07-24 | 317 | 314
2016-07-24 00:30 | 306 | 304
2016-07-24 01:00 | 296 | 293
2016-07-24 01:30 | 284 | 281
2016-07-24 02:00 | 289 | 285
2016-07-24 02:30 | 295 | 292
2016-07-24 03:00 | 292 | 289
2016-07-24 03:30 | 289 | 285
2016-07-24 04:00 | 289 | 285
2016-07-24 04:30 | 290 | 287
2016-07-24 05:00 | 278 | 274
2016-07-24 05:30 | 268 | 264
2016-07-24 06:00 | 269 | 264
2016-07-24 06:30 | 272 | 267
2016-07-24 07:00 | 277 | 273
2016-07-24 07:30 | 287 | 282
2016-07-24 08:00 | 293 | 289
2016-07-24 08:30 | 295 | 291
2016-07-24 09:00 | 297 | 293
2016-07-24 09:30 | 297 | 293
2016-07-24 10:00 | 300 | 296
2016-07-24 10:30 | 301 | 297
2016-07-24 11:00 | 298 | 294
2016-07-24 11:30 | 302 | 298
2016-07-24 12:00 | 299 | 295
2016-07-24 12:30 | 293 | 289
2016-07-24 13:00 | 291 | 287
2016-07-24 13:30 | 292 | 288
2016-07-24 14:00 | 296 | 293
2016-07-24 14:30 | 300 | 297
2016-07-24 15:00 | 306 | 303
2016-07-24 15:30 | 310 | 307
2016-07-24 16:00 | 317 | 314
2016-07-24 16:30 | 327 | 324
2016-07-24 17:00 | 335 | 333
2016-07-24 17:30 | 338 | 336
2016-07-24 18:00 | 347 | 345
2016-07-24 18:30 | 366 | 365
2016-07-24 19:00 | 375 | 374
2016-07-24 19:30 | 362 | 362
2016-07-24 20:00 | 356 | 355
2016-07-24 20:30 | 346 | 344
2016-07-24 21:00 | 331 | 329
2016-07-24 21:30 | 315 | 313
2016-07-24 22:00 | 307 | 305
2016-07-24 22:30 | 317 | 314
2016-07-24 23:00 | 310 | 307
2016-07-24 23:30 | 315 | 312
2016-07-25 | 310 | 308
2016-07-25 00:30 | 302 | 299
2016-07-25 01:00 | 295 | 292
2016-07-25 01:30 | 298 | 294
2016-07-25 02:00 | 288 | 284
2016-07-25 02:30 | 286 | 282
2016-07-25 03:00 | 286 | 282
2016-07-25 03:30 | 285 | 281
2016-07-25 04:00 | 271 | 266
2016-07-25 04:30 | 270 | 265
2016-07-25 05:00 | 266 | 260
2016-07-25 05:30 | 275 | 270
2016-07-25 06:00 | 286 | 281
2016-07-25 06:30 | 310 | 306
2016-07-25 07:00 | 334 | 331
2016-07-25 07:30 | 350 | 348
2016-07-25 08:00 | 358 | 357
2016-07-25 08:30 | 359 | 358
2016-07-25 09:00 | 348 | 347
2016-07-25 09:30 | 347 | 345
2016-07-25 10:00 | 346 | 344
2016-07-25 10:30 | 341 | 339
2016-07-25 11:00 | 339 | 336
2016-07-25 11:30 | 333 | 331
2016-07-25 12:00 | 342 | 339
2016-07-25 12:30 | 348 | 346
2016-07-25 13:00 | 344 | 342
2016-07-25 13:30 | 340 | 338
2016-07-25 14:00 | 337 | 335
2016-07-25 14:30 | 342 | 340
2016-07-25 15:00 | 347 | 344
2016-07-25 15:30 | 353 | 351
2016-07-25 16:00 | 361 | 359
2016-07-25 16:30 | 367 | 366
2016-07-25 17:00 | 368 | 367
2016-07-25 17:30 | 361 | 359
2016-07-25 18:00 | 355 | 354
2016-07-25 18:30 | 368 | 366
2016-07-25 19:00 | 374 | 372
2016-07-25 19:30 | 359 | 358
2016-07-25 20:00 | 355 | 354
2016-07-25 20:30 | 352 | 350
2016-07-25 21:00 | 362 | 360
2016-07-25 21:30 | 368 | 366
2016-07-25 22:00 | 371 | 370
2016-07-25 22:30 | 359 | 357
2016-07-25 23:00 | 347 | 345
2016-07-25 23:30 | 340 | 338
2016-07-26 | 334 | 332
2016-07-26 00:30 | 314 | 311
2016-07-26 01:00 | 298 | 295
2016-07-26 01:30 | 284 | 279
2016-07-26 02:00 | 275 | 270
2016-07-26 02:30 | 271 | 266
2016-07-26 03:00 | 271 | 266
2016-07-26 03:30 | 267 | 261
2016-07-26 04:00 | 267 | 260
2016-07-26 04:30 | 268 | 262
2016-07-26 05:00 | 270 | 264
2016-07-26 05:30 | 280 | 274
2016-07-26 06:00 | 289 | 285
2016-07-26 06:30 | 312 | 307
2016-07-26 07:00 | 332 | 329
2016-07-26 07:30 | 354 | 352
2016-07-26 08:00 | 359 | 358
2016-07-26 08:30 | 364 | 362
2016-07-26 09:00 | 354 | 352
2016-07-26 09:30 | 347 | 345
2016-07-26 10:00 | 345 | 343
2016-07-26 10:30 | 343 | 341
2016-07-26 11:00 | 339 | 336
2016-07-26 11:30 | 341 | 338
2016-07-26 12:00 | 341 | 339
2016-07-26 12:30 | 342 | 339
2016-07-26 13:00 | 330 | 328
2016-07-26 13:30 | 330 | 327
2016-07-26 14:00 | 331 | 328
2016-07-26 14:30 | 327 | 325
2016-07-26 15:00 | 330 | 327
2016-07-26 15:30 | 330 | 327
2016-07-26 16:00 | 339 | 336
2016-07-26 16:30 | 347 | 344
2016-07-26 17:00 | 352 | 350
2016-07-26 17:30 | 356 | 354
2016-07-26 18:00 | 360 | 358
2016-07-26 18:30 | 367 | 365
2016-07-26 19:00 | 375 | 373
2016-07-26 19:30 | 366 | 365
2016-07-26 20:00 | 361 | 360
2016-07-26 20:30 | 357 | 355
2016-07-26 21:00 | 351 | 348
2016-07-26 21:30 | 351 | 348
2016-07-26 22:00 | 351 | 348
2016-07-26 22:30 | 371 | 369
2016-07-26 23:00 | 381 | 380
2016-07-26 23:30 | 375 | 373
2016-07-27 | 366 | 365
2016-07-27 00:30 | 349 | 347
2016-07-27 01:00 | 337 | 334
2016-07-27 01:30 | 323 | 320
2016-07-27 02:00 | 313 | 309
2016-07-27 02:30 | 307 | 303
2016-07-27 03:00 | 306 | 302
2016-07-27 03:30 | 302 | 298
2016-07-27 04:00 | 305 | 301
2016-07-27 04:30 | 307 | 302
2016-07-27 05:00 | 306 | 301
2016-07-27 05:30 | 305 | 301
2016-07-27 06:00 | 301 | 297
2016-07-27 06:30 | 323 | 320
2016-07-27 07:00 | 352 | 350
2016-07-27 07:30 | 376 | 375
2016-07-27 08:00 | 404 | 404
2016-07-27 08:30 | 399 | 399
2016-07-27 09:00 | 394 | 394
2016-07-27 09:30 | 386 | 385
2016-07-27 10:00 | 384 | 383
2016-07-27 10:30 | 378 | 378
2016-07-27 11:00 | 374 | 373
2016-07-27 11:30 | 375 | 374
2016-07-27 12:00 | 378 | 377
2016-07-27 12:30 | 366 | 365
2016-07-27 13:00 | 327 | 326
2016-07-27 13:30 | 324 | 322
2016-07-27 14:00 | 329 | 327
2016-07-27 14:30 | 326 | 323
2016-07-27 15:00 | 320 | 318
2016-07-27 15:30 | 328 | 326
2016-07-27 16:00 | 337 | 335
2016-07-27 16:30 | 313 | 311
2016-07-27 17:00 | 263 | 261
2016-07-27 17:30 | 212 | 206
2016-07-27 18:00 | 212 | 203
2016-07-27 18:30 | 220 | 212
2016-07-27 19:00 | 227 | 220
2016-07-27 19:30 | 213 | 207
2016-07-27 20:00 | 211 | 203
2016-07-27 20:30 | 206 | 198
2016-07-27 21:00 | 198 | 189
2016-07-27 21:30 | 209 | 199
2016-07-27 22:00 | 248 | 241
2016-07-27 22:30 | 269 | 264
2016-07-27 23:00 | 261 | 256
2016-07-27 23:30 | 253 | 249
2016-07-28 | 247 | 242
2016-07-28 00:30 | 231 | 224
2016-07-28 01:00 | 220 | 213
2016-07-28 01:30 | 207 | 199
2016-07-28 02:00 | 200 | 190
2016-07-28 02:30 | 194 | 183
2016-07-28 03:00 | 190 | 178
2016-07-28 03:30 | 189 | 178
2016-07-28 04:00 | 186 | 174
2016-07-28 04:30 | 190 | 178
2016-07-28 05:00 | 197 | 185
2016-07-28 05:30 | 203 | 193
2016-07-28 06:00 | 212 | 203
2016-07-28 06:30 | 233 | 225
2016-07-28 07:00 | 249 | 242
2016-07-28 07:30 | 261 | 256
2016-07-28 08:00 | 287 | 283
2016-07-28 08:30 | 288 | 285
2016-07-28 09:00 | 276 | 273
2016-07-28 09:30 | 273 | 269
2016-07-28 10:00 | 262 | 257
2016-07-28 10:30 | 262 | 256
2016-07-28 11:00 | 254 | 249
2016-07-28 11:30 | 254 | 249
2016-07-28 12:00 | 249 | 243
2016-07-28 12:30 | 246 | 239
2016-07-28 13:00 | 248 | 241
2016-07-28 13:30 | 248 | 241
2016-07-28 14:00 | 249 | 242
2016-07-28 14:30 | 243 | 237
2016-07-28 15:00 | 246 | 239
2016-07-28 15:30 | 251 | 245
2016-07-28 16:00 | 255 | 249
2016-07-28 16:30 | 263 | 257
2016-07-28 17:00 | 266 | 261
2016-07-28 17:30 | 217 | 211
2016-07-28 18:00 | 201 | 192
2016-07-28 18:30 | 195 | 184
2016-07-28 19:00 | 206 | 196
2016-07-28 19:30 | 195 | 185
2016-07-28 20:00 | 198 | 188
2016-07-28 20:30 | 213 | 203
2016-07-28 21:00 | 209 | 200
2016-07-28 21:30 | 208 | 198
2016-07-28 22:00 | 210 | 200
2016-07-28 22:30 | 250 | 242
2016-07-28 23:00 | 245 | 238
2016-07-28 23:30 | 247 | 240
2016-07-29 | 239 | 232
2016-07-29 00:30 | 226 | 218
2016-07-29 01:00 | 214 | 205
2016-07-29 01:30 | 198 | 187
2016-07-29 02:00 | 189 | 177
2016-07-29 02:30 | 187 | 173
2016-07-29 03:00 | 184 | 170
2016-07-29 03:30 | 181 | 167
2016-07-29 04:00 | 180 | 165
2016-07-29 04:30 | 185 | 171
2016-07-29 05:00 | 186 | 172
2016-07-29 05:30 | 195 | 181
2016-07-29 06:00 | 205 | 193
2016-07-29 06:30 | 228 | 217
2016-07-29 07:00 | 246 | 238
2016-07-29 07:30 | 262 | 256
2016-07-29 08:00 | 250 | 245
2016-07-29 08:30 | 266 | 261
2016-07-29 09:00 | 261 | 256
2016-07-29 09:30 | 260 | 254
2016-07-29 10:00 | 248 | 242
2016-07-29 10:30 | 242 | 234
2016-07-29 11:00 | 238 | 231
2016-07-29 11:30 | 233 | 225
2016-07-29 12:00 | 234 | 226
2016-07-29 12:30 | 233 | 225
2016-07-29 13:00 | 235 | 227
2016-07-29 13:30 | 236 | 228
2016-07-29 14:00 | 235 | 226
2016-07-29 14:30 | 231 | 222
2016-07-29 15:00 | 230 | 221
2016-07-29 15:30 | 231 | 223
2016-07-29 16:00 | 241 | 233
2016-07-29 16:30 | 250 | 243
2016-07-29 17:00 | 258 | 252
2016-07-29 17:30 | 206 | 199
2016-07-29 18:00 | 170 | 158
2016-07-29 18:30 | 188 | 175
2016-07-29 19:00 | 200 | 188
2016-07-29 19:30 | 188 | 176
2016-07-29 20:00 | 190 | 177
2016-07-29 20:30 | 206 | 195
2016-07-29 21:00 | 243 | 235
2016-07-29 21:30 | 262 | 255
2016-07-29 22:00 | 264 | 259
2016-07-29 22:30 | 253 | 248
2016-07-29 23:00 | 253 | 248
2016-07-29 23:30 | 282 | 277
2016-07-30 | 325 | 322
2016-07-30 00:30 | 308 | 305
2016-07-30 01:00 | 294 | 291
2016-07-30 01:30 | 281 | 277
2016-07-30 02:00 | 270 | 266
2016-07-30 02:30 | 263 | 258
2016-07-30 03:00 | 260 | 256
2016-07-30 03:30 | 259 | 255
2016-07-30 04:00 | 255 | 250
2016-07-30 04:30 | 258 | 252
2016-07-30 05:00 | 262 | 257
2016-07-30 05:30 | 266 | 261
2016-07-30 06:00 | 268 | 263
2016-07-30 06:30 | 274 | 269
2016-07-30 07:00 | 284 | 280
2016-07-30 07:30 | 299 | 295
2016-07-30 08:00 | 315 | 311
2016-07-30 08:30 | 316 | 313
2016-07-30 09:00 | 316 | 314
2016-07-30 09:30 | 319 | 317
2016-07-30 10:00 | 313 | 310
2016-07-30 10:30 | 311 | 308
2016-07-30 11:00 | 313 | 310
2016-07-30 11:30 | 308 | 306
2016-07-30 12:00 | 301 | 298
2016-07-30 12:30 | 299 | 296
2016-07-30 13:00 | 293 | 290
2016-07-30 13:30 | 291 | 288
2016-07-30 14:00 | 291 | 288
2016-07-30 14:30 | 280 | 277
2016-07-30 15:00 | 284 | 281
2016-07-30 15:30 | 289 | 285
2016-07-30 16:00 | 298 | 295
2016-07-30 16:30 | 309 | 306
2016-07-30 17:00 | 322 | 319
2016-07-30 17:30 | 332 | 329
2016-07-30 18:00 | 322 | 320
2016-07-30 18:30 | 332 | 330
2016-07-30 19:00 | 342 | 340
2016-07-30 19:30 | 344 | 342
2016-07-30 20:00 | 343 | 342
2016-07-30 20:30 | 351 | 350
2016-07-30 21:00 | 348 | 346
2016-07-30 21:30 | 335 | 333
2016-07-30 22:00 | 329 | 327
2016-07-30 22:30 | 322 | 319
2016-07-30 23:00 | 318 | 315
2016-07-30 23:30 | 313 | 310
2016-07-31 | 306 | 302
2016-07-31 00:30 | 294 | 290
2016-07-31 01:00 | 283 | 279
2016-07-31 01:30 | 272 | 267
2016-07-31 02:00 | 267 | 262
2016-07-31 02:30 | 260 | 254
2016-07-31 03:00 | 262 | 255
2016-07-31 03:30 | 257 | 250
2016-07-31 04:00 | 248 | 241
2016-07-31 04:30 | 253 | 246
2016-07-31 05:00 | 254 | 247
2016-07-31 05:30 | 257 | 251
2016-07-31 06:00 | 259 | 253
2016-07-31 06:30 | 273 | 267
2016-07-31 07:00 | 278 | 272
2016-07-31 07:30 | 286 | 281
2016-07-31 08:00 | 299 | 295
2016-07-31 08:30 | 307 | 303
2016-07-31 09:00 | 304 | 301
2016-07-31 09:30 | 306 | 303
2016-07-31 10:00 | 308 | 305
2016-07-31 10:30 | 309 | 306
2016-07-31 11:00 | 307 | 304
2016-07-31 11:30 | 303 | 300
2016-07-31 12:00 | 299 | 296
2016-07-31 12:30 | 297 | 293
2016-07-31 13:00 | 293 | 289
2016-07-31 13:30 | 293 | 290
2016-07-31 14:00 | 292 | 288
2016-07-31 14:30 | 288 | 284
2016-07-31 15:00 | 285 | 281
2016-07-31 15:30 | 290 | 286
2016-07-31 16:00 | 301 | 297
2016-07-31 16:30 | 307 | 304
2016-07-31 17:00 | 316 | 313
2016-07-31 17:30 | 325 | 323
2016-07-31 18:00 | 312 | 310
2016-07-31 18:30 | 330 | 328
2016-07-31 19:00 | 334 | 332
2016-07-31 19:30 | 324 | 322
2016-07-31 20:00 | 323 | 321
2016-07-31 20:30 | 341 | 339
2016-07-31 21:00 | 356 | 355
2016-07-31 21:30 | 345 | 344
2016-07-31 22:00 | 340 | 338
2016-07-31 22:30 | 327 | 324
2016-07-31 23:00 | 315 | 312
2016-07-31 23:30 | 305 | 302
2016-08-01 | 302 | 298
2016-08-01 00:30 | 293 | 290
2016-08-01 01:00 | 287 | 283
2016-08-01 01:30 | 276 | 272
2016-08-01 02:00 | 267 | 262
2016-08-01 02:30 | 260 | 255
2016-08-01 03:00 | 257 | 251
2016-08-01 03:30 | 258 | 252
2016-08-01 04:00 | 260 | 253
2016-08-01 04:30 | 256 | 249
2016-08-01 05:00 | 250 | 244
2016-08-01 05:30 | 260 | 254
2016-08-01 06:00 | 274 | 268
2016-08-01 06:30 | 296 | 291
2016-08-01 07:00 | 300 | 296
2016-08-01 07:30 | 325 | 322
2016-08-01 08:00 | 335 | 333
2016-08-01 08:30 | 344 | 342
2016-08-01 09:00 | 349 | 347
2016-08-01 09:30 | 349 | 348
2016-08-01 10:00 | 341 | 340
2016-08-01 10:30 | 338 | 336
2016-08-01 11:00 | 334 | 332
2016-08-01 11:30 | 345 | 344
2016-08-01 12:00 | 347 | 345
2016-08-01 12:30 | 347 | 346
2016-08-01 13:00 | 351 | 350
2016-08-01 13:30 | 351 | 350
2016-08-01 14:00 | 348 | 347
2016-08-01 14:30 | 338 | 337
2016-08-01 15:00 | 335 | 334
2016-08-01 15:30 | 334 | 332
2016-08-01 16:00 | 338 | 336
2016-08-01 16:30 | 340 | 338
2016-08-01 17:00 | 344 | 343
2016-08-01 17:30 | 331 | 329
2016-08-01 18:00 | 320 | 318
2016-08-01 18:30 | 331 | 330
2016-08-01 19:00 | 342 | 341
2016-08-01 19:30 | 355 | 354
2016-08-01 20:00 | 354 | 353
2016-08-01 20:30 | 372 | 371
2016-08-01 21:00 | 369 | 368
2016-08-01 21:30 | 355 | 354
2016-08-01 22:00 | 358 | 356
2016-08-01 22:30 | 351 | 350
2016-08-01 23:00 | 340 | 339
2016-08-01 23:30 | 330 | 328
2016-08-02 | 318 | 316
2016-08-02 00:30 | 300 | 297
2016-08-02 01:00 | 288 | 285
2016-08-02 01:30 | 278 | 274
2016-08-02 02:00 | 281 | 277
2016-08-02 02:30 | 277 | 273
2016-08-02 03:00 | 276 | 272
2016-08-02 03:30 | 273 | 268
2016-08-02 04:00 | 279 | 274
2016-08-02 04:30 | 276 | 271
2016-08-02 05:00 | 271 | 266
2016-08-02 05:30 | 284 | 279
2016-08-02 06:00 | 301 | 297
2016-08-02 06:30 | 320 | 317
2016-08-02 07:00 | 329 | 326
2016-08-02 07:30 | 336 | 334
2016-08-02 08:00 | 343 | 341
2016-08-02 08:30 | 336 | 334
2016-08-02 09:00 | 339 | 338
2016-08-02 09:30 | 343 | 342
2016-08-02 10:00 | 331 | 330
2016-08-02 10:30 | 334 | 332
2016-08-02 11:00 | 340 | 339
2016-08-02 11:30 | 344 | 343
2016-08-02 12:00 | 342 | 341
2016-08-02 12:30 | 339 | 337
2016-08-02 13:00 | 343 | 342
2016-08-02 13:30 | 345 | 344
2016-08-02 14:00 | 348 | 347
2016-08-02 14:30 | 342 | 340
2016-08-02 15:00 | 339 | 338
2016-08-02 15:30 | 341 | 339
2016-08-02 16:00 | 354 | 352
2016-08-02 16:30 | 356 | 355
2016-08-02 17:00 | 368 | 368
2016-08-02 17:30 | 350 | 349
2016-08-02 18:00 | 338 | 337
2016-08-02 18:30 | 347 | 346
2016-08-02 19:00 | 357 | 356
2016-08-02 19:30 | 343 | 343
2016-08-02 20:00 | 333 | 332
2016-08-02 20:30 | 324 | 323
2016-08-02 21:00 | 321 | 319
2016-08-02 21:30 | 340 | 339
2016-08-02 22:00 | 353 | 352
2016-08-02 22:30 | 348 | 347
2016-08-02 23:00 | 341 | 340
2016-08-02 23:30 | 335 | 334
2016-08-03 | 326 | 324
2016-08-03 00:30 | 304 | 302
2016-08-03 01:00 | 288 | 285
2016-08-03 01:30 | 269 | 266
2016-08-03 02:00 | 261 | 256
2016-08-03 02:30 | 258 | 253
2016-08-03 03:00 | 249 | 244
2016-08-03 03:30 | 250 | 244
2016-08-03 04:00 | 252 | 246
2016-08-03 04:30 | 246 | 239
2016-08-03 05:00 | 223 | 213
2016-08-03 05:30 | 232 | 221
2016-08-03 06:00 | 244 | 233
2016-08-03 06:30 | 260 | 251
2016-08-03 07:00 | 263 | 255
2016-08-03 07:30 | 281 | 274
2016-08-03 08:00 | 287 | 282
2016-08-03 08:30 | 279 | 275
2016-08-03 09:00 | 245 | 240
2016-08-03 09:30 | 240 | 232
2016-08-03 10:00 | 228 | 219
2016-08-03 10:30 | 228 | 218
2016-08-03 11:00 | 226 | 215
2016-08-03 11:30 | 218 | 207
2016-08-03 12:00 | 214 | 202
2016-08-03 12:30 | 215 | 202
2016-08-03 13:00 | 214 | 200
2016-08-03 13:30 | 215 | 201
2016-08-03 14:00 | 213 | 199
2016-08-03 14:30 | 209 | 194
2016-08-03 15:00 | 214 | 199
2016-08-03 15:30 | 222 | 208
2016-08-03 16:00 | 217 | 204
2016-08-03 16:30 | 226 | 214
2016-08-03 17:00 | 173 | 157
2016-08-03 17:30 | 167 | 145
2016-08-03 18:00 | 160 | 136
2016-08-03 18:30 | 172 | 150
2016-08-03 19:00 | 179 | 159
2016-08-03 19:30 | 170 | 149
2016-08-03 20:00 | 164 | 143
2016-08-03 20:30 | 163 | 140
2016-08-03 21:00 | 171 | 148
2016-08-03 21:30 | 166 | 146
2016-08-03 22:00 | 174 | 155
2016-08-03 22:30 | 186 | 170
2016-08-03 23:00 | 188 | 173
2016-08-03 23:30 | 224 | 212
2016-08-04 | 233 | 225
2016-08-04 00:30 | 219 | 209
2016-08-04 01:00 | 203 | 192
2016-08-04 01:30 | 194 | 181
2016-08-04 02:00 | 181 | 167
2016-08-04 02:30 | 183 | 166
2016-08-04 03:00 | 179 | 162
2016-08-04 03:30 | 181 | 164
2016-08-04 04:00 | 184 | 167
2016-08-04 04:30 | 184 | 168
2016-08-04 05:00 | 186 | 170
2016-08-04 05:30 | 189 | 173
2016-08-04 06:00 | 204 | 191
2016-08-04 06:30 | 230 | 219
2016-08-04 07:00 | 211 | 200
2016-08-04 07:30 | 203 | 192
2016-08-04 08:00 | 187 | 175
2016-08-04 08:30 | 196 | 184
2016-08-04 09:00 | 223 | 212
2016-08-04 09:30 | 240 | 232
2016-08-04 10:00 | 240 | 233
2016-08-04 10:30 | 224 | 216
2016-08-04 11:00 | 212 | 202
2016-08-04 11:30 | 206 | 195
2016-08-04 12:00 | 211 | 199
2016-08-04 12:30 | 207 | 195
2016-08-04 13:00 | 207 | 192
2016-08-04 13:30 | 208 | 193
2016-08-04 14:00 | 215 | 200
2016-08-04 14:30 | 204 | 189
2016-08-04 15:00 | 208 | 193
2016-08-04 15:30 | 213 | 198
2016-08-04 16:00 | 224 | 209
2016-08-04 16:30 | 229 | 211
2016-08-04 17:00 | 194 | 173
2016-08-04 17:30 | 197 | 172
2016-08-04 18:00 | 180 | 154
2016-08-04 18:30 | 192 | 166
2016-08-04 19:00 | 196 | 172
2016-08-04 19:30 | 204 | 182
2016-08-04 20:00 | 202 | 183
2016-08-04 20:30 | 206 | 187
2016-08-04 21:00 | 199 | 180
2016-08-04 21:30 | 235 | 216
2016-08-04 22:00 | 253 | 241
2016-08-04 22:30 | 252 | 241
2016-08-04 23:00 | 245 | 234
2016-08-04 23:30 | 258 | 248
2016-08-05 | 308 | 300
2016-08-05 00:30 | 304 | 299
2016-08-05 01:00 | 282 | 277
2016-08-05 01:30 | 263 | 255
2016-08-05 02:00 | 254 | 243
2016-08-05 02:30 | 252 | 239
2016-08-05 03:00 | 251 | 239
2016-08-05 03:30 | 243 | 230
2016-08-05 04:00 | 248 | 234
2016-08-05 04:30 | 254 | 240
2016-08-05 05:00 | 253 | 241
2016-08-05 05:30 | 259 | 248
2016-08-05 06:00 | 279 | 268
2016-08-05 06:30 | 286 | 278
2016-08-05 07:00 | 294 | 288
2016-08-05 07:30 | 306 | 301
2016-08-05 08:00 | 308 | 307
2016-08-05 08:30 | 306 | 305
2016-08-05 09:00 | 310 | 309
2016-08-05 09:30 | 304 | 303
2016-08-05 10:00 | 299 | 298
2016-08-05 10:30 | 286 | 285
2016-08-05 11:00 | 285 | 284
2016-08-05 11:30 | 281 | 279
2016-08-05 12:00 | 282 | 280
2016-08-05 12:30 | 285 | 283
2016-08-05 13:00 | 290 | 288
2016-08-05 13:30 | 289 | 287
2016-08-05 14:00 | 285 | 283
2016-08-05 14:30 | 273 | 272
2016-08-05 15:00 | 276 | 273
2016-08-05 15:30 | 280 | 278
2016-08-05 16:00 | 285 | 283
2016-08-05 16:30 | 296 | 294
2016-08-05 17:00 | 302 | 301
2016-08-05 17:30 | 298 | 297
2016-08-05 18:00 | 278 | 277
2016-08-05 18:30 | 281 | 280
2016-08-05 19:00 | 289 | 288
2016-08-05 19:30 | 292 | 291
2016-08-05 20:00 | 288 | 287
2016-08-05 20:30 | 277 | 276
2016-08-05 21:00 | 274 | 273
2016-08-05 21:30 | 272 | 271
2016-08-05 22:00 | 285 | 283
2016-08-05 22:30 | 273 | 272
2016-08-05 23:00 | 266 | 265
2016-08-05 23:30 | 270 | 269
2016-08-06 | 270 | 269
2016-08-06 00:30 | 269 | 267
2016-08-06 01:00 | 260 | 259
2016-08-06 01:30 | 254 | 252
2016-08-06 02:00 | 240 | 237
2016-08-06 02:30 | 235 | 230
2016-08-06 03:00 | 237 | 232
2016-08-06 03:30 | 231 | 227
2016-08-06 04:00 | 228 | 223
2016-08-06 04:30 | 229 | 224
2016-08-06 05:00 | 231 | 226
2016-08-06 05:30 | 233 | 228
2016-08-06 06:00 | 241 | 236
2016-08-06 06:30 | 254 | 249
2016-08-06 07:00 | 261 | 257
2016-08-06 07:30 | 275 | 271
2016-08-06 08:00 | 278 | 275
2016-08-06 08:30 | 288 | 285
2016-08-06 09:00 | 293 | 290
2016-08-06 09:30 | 274 | 271
2016-08-06 10:00 | 285 | 283
2016-08-06 10:30 | 298 | 296
2016-08-06 11:00 | 283 | 281
2016-08-06 11:30 | 284 | 281
2016-08-06 12:00 | 280 | 278
2016-08-06 12:30 | 276 | 273
2016-08-06 13:00 | 272 | 269
2016-08-06 13:30 | 277 | 273
2016-08-06 14:00 | 282 | 279
2016-08-06 14:30 | 273 | 269
2016-08-06 15:00 | 271 | 268
2016-08-06 15:30 | 265 | 261
2016-08-06 16:00 | 273 | 270
2016-08-06 16:30 | 287 | 284
2016-08-06 17:00 | 294 | 292
2016-08-06 17:30 | 304 | 302
2016-08-06 18:00 | 290 | 288
2016-08-06 18:30 | 293 | 290
2016-08-06 19:00 | 298 | 296
2016-08-06 19:30 | 318 | 316
2016-08-06 20:00 | 316 | 314
2016-08-06 20:30 | 333 | 331
2016-08-06 21:00 | 318 | 317
2016-08-06 21:30 | 317 | 316
2016-08-06 22:00 | 312 | 310
2016-08-06 22:30 | 305 | 303
2016-08-06 23:00 | 289 | 287
2016-08-06 23:30 | 283 | 280
2016-08-07 | 287 | 284
2016-08-07 00:30 | 277 | 274
2016-08-07 01:00 | 269 | 266
2016-08-07 01:30 | 262 | 259
2016-08-07 02:00 | 251 | 248
2016-08-07 02:30 | 241 | 236
2016-08-07 03:00 | 239 | 234
2016-08-07 03:30 | 235 | 230
2016-08-07 04:00 | 244 | 238
2016-08-07 04:30 | 252 | 247
2016-08-07 05:00 | 256 | 251
2016-08-07 05:30 | 260 | 254
2016-08-07 06:00 | 259 | 254
2016-08-07 06:30 | 271 | 267
2016-08-07 07:00 | 278 | 274
2016-08-07 07:30 | 296 | 293
2016-08-07 08:00 | 305 | 303
2016-08-07 08:30 | 314 | 312
2016-08-07 09:00 | 314 | 312
2016-08-07 09:30 | 309 | 306
2016-08-07 10:00 | 308 | 306
2016-08-07 10:30 | 310 | 308
2016-08-07 11:00 | 306 | 303
2016-08-07 11:30 | 299 | 296
2016-08-07 12:00 | 293 | 290
2016-08-07 12:30 | 285 | 282
2016-08-07 13:00 | 290 | 287
2016-08-07 13:30 | 293 | 290
2016-08-07 14:00 | 293 | 289
2016-08-07 14:30 | 270 | 267
2016-08-07 15:00 | 278 | 274
2016-08-07 15:30 | 280 | 277
2016-08-07 16:00 | 290 | 287
2016-08-07 16:30 | 302 | 299
2016-08-07 17:00 | 314 | 312
2016-08-07 17:30 | 322 | 320
2016-08-07 18:00 | 308 | 306
2016-08-07 18:30 | 327 | 325
2016-08-07 19:00 | 341 | 340
2016-08-07 19:30 | 341 | 340
2016-08-07 20:00 | 348 | 347
2016-08-07 20:30 | 358 | 357
2016-08-07 21:00 | 351 | 350
2016-08-07 21:30 | 347 | 346
2016-08-07 22:00 | 339 | 339
2016-08-07 22:30 | 325 | 324
2016-08-07 23:00 | 314 | 312
2016-08-07 23:30 | 300 | 298
2016-08-08 | 296 | 294
2016-08-08 00:30 | 289 | 287
2016-08-08 01:00 | 296 | 293
2016-08-08 01:30 | 286 | 283
2016-08-08 02:00 | 277 | 274
2016-08-08 02:30 | 271 | 268
2016-08-08 03:00 | 274 | 270
2016-08-08 03:30 | 269 | 265
2016-08-08 04:00 | 270 | 266
2016-08-08 04:30 | 265 | 261
2016-08-08 05:00 | 269 | 265
2016-08-08 05:30 | 287 | 283
2016-08-08 06:00 | 304 | 301
2016-08-08 06:30 | 331 | 329
2016-08-08 07:00 | 341 | 340
2016-08-08 07:30 | 372 | 371
2016-08-08 08:00 | 381 | 380
2016-08-08 08:30 | 380 | 379
2016-08-08 09:00 | 374 | 374
2016-08-08 09:30 | 371 | 371
2016-08-08 10:00 | 367 | 366
2016-08-08 10:30 | 352 | 351
2016-08-08 11:00 | 348 | 347
2016-08-08 11:30 | 347 | 346
2016-08-08 12:00 | 344 | 343
2016-08-08 12:30 | 356 | 354
2016-08-08 13:00 | 356 | 355
2016-08-08 13:30 | 363 | 362
2016-08-08 14:00 | 360 | 359
2016-08-08 14:30 | 351 | 350
2016-08-08 15:00 | 346 | 345
2016-08-08 15:30 | 351 | 350
2016-08-08 16:00 | 354 | 353
2016-08-08 16:30 | 360 | 359
2016-08-08 17:00 | 372 | 372
2016-08-08 17:30 | 361 | 361
2016-08-08 18:00 | 342 | 341
2016-08-08 18:30 | 350 | 349
2016-08-08 19:00 | 353 | 352
2016-08-08 19:30 | 335 | 335
2016-08-08 20:00 | 346 | 345
2016-08-08 20:30 | 336 | 336
2016-08-08 21:00 | 337 | 336
2016-08-08 21:30 | 332 | 331
2016-08-08 22:00 | 335 | 333
2016-08-08 22:30 | 343 | 342
2016-08-08 23:00 | 348 | 347
2016-08-08 23:30 | 339 | 338
2016-08-09 | 334 | 333
2016-08-09 00:30 | 323 | 322
2016-08-09 01:00 | 306 | 304
2016-08-09 01:30 | 289 | 286
2016-08-09 02:00 | 281 | 278
2016-08-09 02:30 | 273 | 270
2016-08-09 03:00 | 269 | 265
2016-08-09 03:30 | 266 | 262
2016-08-09 04:00 | 265 | 260
2016-08-09 04:30 | 265 | 261
2016-08-09 05:00 | 270 | 266
2016-08-09 05:30 | 282 | 278
2016-08-09 06:00 | 287 | 284
2016-08-09 06:30 | 310 | 306
2016-08-09 07:00 | 322 | 319
2016-08-09 07:30 | 332 | 329
2016-08-09 08:00 | 334 | 332
2016-08-09 08:30 | 343 | 342
2016-08-09 09:00 | 349 | 348
2016-08-09 09:30 | 344 | 342
2016-08-09 10:00 | 337 | 335
2016-08-09 10:30 | 334 | 332
2016-08-09 11:00 | 337 | 335
2016-08-09 11:30 | 339 | 337
2016-08-09 12:00 | 338 | 336
2016-08-09 12:30 | 341 | 339
2016-08-09 13:00 | 341 | 340
2016-08-09 13:30 | 346 | 344
2016-08-09 14:00 | 348 | 346
2016-08-09 14:30 | 333 | 331
2016-08-09 15:00 | 331 | 329
2016-08-09 15:30 | 346 | 345
2016-08-09 16:00 | 311 | 310
2016-08-09 16:30 | 334 | 332
2016-08-09 17:00 | 346 | 344
2016-08-09 17:30 | 359 | 357
2016-08-09 18:00 | 339 | 338
2016-08-09 18:30 | 339 | 337
2016-08-09 19:00 | 340 | 338
2016-08-09 19:30 | 348 | 346
2016-08-09 20:00 | 358 | 356
2016-08-09 20:30 | 365 | 364
2016-08-09 21:00 | 356 | 355
2016-08-09 21:30 | 344 | 342
2016-08-09 22:00 | 352 | 350
2016-08-09 22:30 | 349 | 348
2016-08-09 23:00 | 351 | 350
2016-08-09 23:30 | 346 | 344
2016-08-10 | 334 | 332
2016-08-10 00:30 | 324 | 322
2016-08-10 01:00 | 310 | 308
2016-08-10 01:30 | 289 | 285
2016-08-10 02:00 | 279 | 275
2016-08-10 02:30 | 275 | 271
2016-08-10 03:00 | 278 | 273
2016-08-10 03:30 | 285 | 280
2016-08-10 04:00 | 296 | 292
2016-08-10 04:30 | 296 | 293
2016-08-10 05:00 | 298 | 295
2016-08-10 05:30 | 309 | 306
2016-08-10 06:00 | 319 | 317
2016-08-10 06:30 | 335 | 333
2016-08-10 07:00 | 357 | 356
2016-08-10 07:30 | 369 | 367
2016-08-10 08:00 | 383 | 382
2016-08-10 08:30 | 375 | 374
2016-08-10 09:00 | 352 | 351
2016-08-10 09:30 | 350 | 349
2016-08-10 10:00 | 346 | 345
2016-08-10 10:30 | 339 | 338
2016-08-10 11:00 | 334 | 332
2016-08-10 11:30 | 326 | 324
2016-08-10 12:00 | 325 | 323
2016-08-10 12:30 | 325 | 322
2016-08-10 13:00 | 320 | 317
2016-08-10 13:30 | 318 | 316
2016-08-10 14:00 | 318 | 316
2016-08-10 14:30 | 333 | 331
2016-08-10 15:00 | 339 | 337
2016-08-10 15:30 | 340 | 338
2016-08-10 16:00 | 344 | 343
2016-08-10 16:30 | 343 | 342
2016-08-10 17:00 | 347 | 345
2016-08-10 17:30 | 346 | 345
2016-08-10 18:00 | 330 | 328
2016-08-10 18:30 | 332 | 330
2016-08-10 19:00 | 343 | 341
2016-08-10 19:30 | 340 | 338
2016-08-10 20:00 | 339 | 338
2016-08-10 20:30 | 344 | 342
2016-08-10 21:00 | 339 | 337
2016-08-10 21:30 | 329 | 327
2016-08-10 22:00 | 337 | 335
2016-08-10 22:30 | 357 | 355
2016-08-10 23:00 | 354 | 353
2016-08-10 23:30 | 343 | 341
2016-08-11 | 336 | 335
2016-08-11 00:30 | 322 | 320
2016-08-11 01:00 | 309 | 306
2016-08-11 01:30 | 291 | 288
2016-08-11 02:00 | 278 | 274
2016-08-11 02:30 | 273 | 269
2016-08-11 03:00 | 268 | 263
2016-08-11 03:30 | 264 | 259
2016-08-11 04:00 | 265 | 260
2016-08-11 04:30 | 270 | 265
2016-08-11 05:00 | 272 | 267
2016-08-11 05:30 | 281 | 277
2016-08-11 06:00 | 288 | 284
2016-08-11 06:30 | 309 | 306
2016-08-11 07:00 | 320 | 317
2016-08-11 07:30 | 312 | 310
2016-08-11 08:00 | 298 | 296
2016-08-11 08:30 | 293 | 290
2016-08-11 09:00 | 285 | 282
2016-08-11 09:30 | 288 | 284
2016-08-11 10:00 | 304 | 300
2016-08-11 10:30 | 324 | 321
2016-08-11 11:00 | 311 | 308
2016-08-11 11:30 | 304 | 301
2016-08-11 12:00 | 274 | 271
2016-08-11 12:30 | 271 | 267
2016-08-11 13:00 | 288 | 283
2016-08-11 13:30 | 289 | 285
2016-08-11 14:00 | 293 | 289
2016-08-11 14:30 | 286 | 282
2016-08-11 15:00 | 286 | 282
2016-08-11 15:30 | 273 | 269
2016-08-11 16:00 | 245 | 240
2016-08-11 16:30 | 239 | 234
2016-08-11 17:00 | 214 | 208
2016-08-11 17:30 | 205 | 198
2016-08-11 18:00 | 192 | 175
2016-08-11 18:30 | 195 | 178
2016-08-11 19:00 | 201 | 185
2016-08-11 19:30 | 198 | 183
2016-08-11 20:00 | 197 | 181
2016-08-11 20:30 | 187 | 171
2016-08-11 21:00 | 191 | 175
2016-08-11 21:30 | 194 | 178
2016-08-11 22:00 | 208 | 194
2016-08-11 22:30 | 207 | 193
2016-08-11 23:00 | 215 | 202
2016-08-11 23:30 | 251 | 241
2016-08-12 | 257 | 249
2016-08-12 00:30 | 245 | 238
2016-08-12 01:00 | 270 | 262
2016-08-12 01:30 | 288 | 282
2016-08-12 02:00 | 266 | 261
2016-08-12 02:30 | 267 | 260
2016-08-12 03:00 | 222 | 215
2016-08-12 03:30 | 198 | 185
2016-08-12 04:00 | 202 | 187
2016-08-12 04:30 | 198 | 183
2016-08-12 05:00 | 199 | 184
2016-08-12 05:30 | 212 | 198
2016-08-12 06:00 | 213 | 201
2016-08-12 06:30 | 224 | 213
2016-08-12 07:00 | 227 | 216
2016-08-12 07:30 | 248 | 238
2016-08-12 08:00 | 258 | 250
2016-08-12 08:30 | 260 | 252
2016-08-12 09:00 | 259 | 251
2016-08-12 09:30 | 253 | 245
2016-08-12 10:00 | 251 | 243
2016-08-12 10:30 | 253 | 244
2016-08-12 11:00 | 251 | 244
2016-08-12 11:30 | 250 | 245
2016-08-12 12:00 | 249 | 244
2016-08-12 12:30 | 247 | 241
2016-08-12 13:00 | 244 | 238
2016-08-12 13:30 | 247 | 241
2016-08-12 14:00 | 247 | 241
2016-08-12 14:30 | 236 | 230
2016-08-12 15:00 | 237 | 231
2016-08-12 15:30 | 254 | 248
2016-08-12 16:00 | 265 | 260
2016-08-12 16:30 | 273 | 268
2016-08-12 17:00 | 212 | 206
2016-08-12 17:30 | 184 | 175
2016-08-12 18:00 | 172 | 158
2016-08-12 18:30 | 179 | 164
2016-08-12 19:00 | 185 | 171
2016-08-12 19:30 | 170 | 155
2016-08-12 20:00 | 165 | 149
2016-08-12 20:30 | 170 | 152
2016-08-12 21:00 | 187 | 172
2016-08-12 21:30 | 241 | 230
2016-08-12 22:00 | 262 | 255
2016-08-12 22:30 | 273 | 267
2016-08-12 23:00 | 267 | 262
2016-08-12 23:30 | 282 | 278
2016-08-13 | 330 | 326
2016-08-13 00:30 | 319 | 316
2016-08-13 01:00 | 300 | 297
2016-08-13 01:30 | 287 | 283
2016-08-13 02:00 | 276 | 271
2016-08-13 02:30 | 269 | 264
2016-08-13 03:00 | 260 | 253
2016-08-13 03:30 | 259 | 252
2016-08-13 04:00 | 255 | 248
2016-08-13 04:30 | 258 | 251
2016-08-13 05:00 | 263 | 256
2016-08-13 05:30 | 276 | 270
2016-08-13 06:00 | 294 | 289
2016-08-13 06:30 | 299 | 295
2016-08-13 07:00 | 303 | 300
2016-08-13 07:30 | 311 | 307
2016-08-13 08:00 | 319 | 316
2016-08-13 08:30 | 324 | 321
2016-08-13 09:00 | 328 | 325
2016-08-13 09:30 | 335 | 332
2016-08-13 10:00 | 330 | 328
2016-08-13 10:30 | 327 | 325
2016-08-13 11:00 | 328 | 326
2016-08-13 11:30 | 318 | 316
2016-08-13 12:00 | 307 | 304
2016-08-13 12:30 | 308 | 305
2016-08-13 13:00 | 307 | 303
2016-08-13 13:30 | 312 | 309
2016-08-13 14:00 | 314 | 311
2016-08-13 14:30 | 298 | 295
2016-08-13 15:00 | 298 | 295
2016-08-13 15:30 | 308 | 305
2016-08-13 16:00 | 328 | 325
2016-08-13 16:30 | 333 | 331
2016-08-13 17:00 | 327 | 325
2016-08-13 17:30 | 330 | 328
2016-08-13 18:00 | 336 | 334
2016-08-13 18:30 | 308 | 306
2016-08-13 19:00 | 315 | 313
2016-08-13 19:30 | 319 | 317
2016-08-13 20:00 | 325 | 322
2016-08-13 20:30 | 311 | 309
2016-08-13 21:00 | 324 | 321
2016-08-13 21:30 | 333 | 330
2016-08-13 22:00 | 338 | 335
2016-08-13 22:30 | 330 | 327
2016-08-13 23:00 | 322 | 320
2016-08-13 23:30 | 313 | 310
2016-08-14 | 309 | 306
2016-08-14 00:30 | 295 | 292
2016-08-14 01:00 | 290 | 287
2016-08-14 01:30 | 272 | 268
2016-08-14 02:00 | 262 | 257
2016-08-14 02:30 | 261 | 255
2016-08-14 03:00 | 257 | 251
2016-08-14 03:30 | 250 | 244
2016-08-14 04:00 | 252 | 245
2016-08-14 04:30 | 251 | 245
2016-08-14 05:00 | 249 | 243
2016-08-14 05:30 | 256 | 250
2016-08-14 06:00 | 259 | 253
2016-08-14 06:30 | 265 | 260
2016-08-14 07:00 | 265 | 259
2016-08-14 07:30 | 276 | 271
2016-08-14 08:00 | 282 | 278
2016-08-14 08:30 | 287 | 283
2016-08-14 09:00 | 292 | 288
2016-08-14 09:30 | 295 | 292
2016-08-14 10:00 | 303 | 300
2016-08-14 10:30 | 301 | 297
2016-08-14 11:00 | 301 | 298
2016-08-14 11:30 | 297 | 294
2016-08-14 12:00 | 295 | 291
2016-08-14 12:30 | 298 | 294
2016-08-14 13:00 | 297 | 293
2016-08-14 13:30 | 299 | 296
2016-08-14 14:00 | 298 | 295
2016-08-14 14:30 | 289 | 286
2016-08-14 15:00 | 291 | 287
2016-08-14 15:30 | 294 | 290
2016-08-14 16:00 | 306 | 303
2016-08-14 16:30 | 304 | 301
2016-08-14 17:00 | 307 | 305
2016-08-14 17:30 | 309 | 307
2016-08-14 18:00 | 316 | 313
2016-08-14 18:30 | 325 | 323
2016-08-14 19:00 | 325 | 323
2016-08-14 19:30 | 330 | 328
2016-08-14 20:00 | 333 | 332
2016-08-14 20:30 | 326 | 325
2016-08-14 21:00 | 328 | 326
2016-08-14 21:30 | 333 | 331
2016-08-14 22:00 | 326 | 324
2016-08-14 22:30 | 312 | 310
2016-08-14 23:00 | 304 | 302
2016-08-14 23:30 | 304 | 301
2016-08-15 | 298 | 295
2016-08-15 00:30 | 291 | 288
2016-08-15 01:00 | 285 | 281
2016-08-15 01:30 | 269 | 265
2016-08-15 02:00 | 259 | 254
2016-08-15 02:30 | 256 | 250
2016-08-15 03:00 | 259 | 253
2016-08-15 03:30 | 261 | 255
2016-08-15 04:00 | 262 | 256
2016-08-15 04:30 | 265 | 260
2016-08-15 05:00 | 264 | 259
2016-08-15 05:30 | 268 | 263
2016-08-15 06:00 | 275 | 270
2016-08-15 06:30 | 307 | 303
2016-08-15 07:00 | 307 | 304
2016-08-15 07:30 | 323 | 321
2016-08-15 08:00 | 328 | 326
2016-08-15 08:30 | 340 | 339
2016-08-15 09:00 | 344 | 343
2016-08-15 09:30 | 361 | 360
2016-08-15 10:00 | 370 | 369
2016-08-15 10:30 | 361 | 360
2016-08-15 11:00 | 362 | 361
2016-08-15 11:30 | 352 | 351
2016-08-15 12:00 | 319 | 318
2016-08-15 12:30 | 308 | 305
2016-08-15 13:00 | 307 | 304
2016-08-15 13:30 | 315 | 313
2016-08-15 14:00 | 307 | 305
2016-08-15 14:30 | 313 | 310
2016-08-15 15:00 | 311 | 309
2016-08-15 15:30 | 286 | 284
2016-08-15 16:00 | 262 | 259
2016-08-15 16:30 | 274 | 270
2016-08-15 17:00 | 279 | 275
2016-08-15 17:30 | 230 | 225
2016-08-15 18:00 | 223 | 217
2016-08-15 18:30 | 216 | 209
2016-08-15 19:00 | 211 | 203
2016-08-15 19:30 | 208 | 200
2016-08-15 20:00 | 197 | 188
2016-08-15 20:30 | 207 | 197
2016-08-15 21:00 | 216 | 206
2016-08-15 21:30 | 252 | 245
2016-08-15 22:00 | 260 | 255
2016-08-15 22:30 | 263 | 258
2016-08-15 23:00 | 264 | 259
2016-08-15 23:30 | 262 | 257
2016-08-16 | 253 | 248
2016-08-16 00:30 | 242 | 236
2016-08-16 01:00 | 228 | 221
2016-08-16 01:30 | 213 | 205
2016-08-16 02:00 | 199 | 190
2016-08-16 02:30 | 191 | 179
2016-08-16 03:00 | 186 | 173
2016-08-16 03:30 | 191 | 178
2016-08-16 04:00 | 191 | 178
2016-08-16 04:30 | 191 | 179
2016-08-16 05:00 | 198 | 186
2016-08-16 05:30 | 201 | 191
2016-08-16 06:00 | 209 | 200
2016-08-16 06:30 | 228 | 220
2016-08-16 07:00 | 244 | 237
2016-08-16 07:30 | 274 | 268
2016-08-16 08:00 | 293 | 289
2016-08-16 08:30 | 302 | 298
2016-08-16 09:00 | 295 | 291
2016-08-16 09:30 | 296 | 292
2016-08-16 10:00 | 298 | 294
2016-08-16 10:30 | 290 | 286
2016-08-16 11:00 | 293 | 289
2016-08-16 11:30 | 272 | 268
2016-08-16 12:00 | 261 | 256
2016-08-16 12:30 | 250 | 244
2016-08-16 13:00 | 245 | 239
2016-08-16 13:30 | 246 | 240
2016-08-16 14:00 | 246 | 240
2016-08-16 14:30 | 234 | 228
2016-08-16 15:00 | 239 | 232
2016-08-16 15:30 | 257 | 251
2016-08-16 16:00 | 271 | 266
2016-08-16 16:30 | 274 | 270
2016-08-16 17:00 | 259 | 254
2016-08-16 17:30 | 197 | 190
2016-08-16 18:00 | 193 | 183
2016-08-16 18:30 | 204 | 194
2016-08-16 19:00 | 206 | 197
2016-08-16 19:30 | 190 | 181
2016-08-16 20:00 | 187 | 176
2016-08-16 20:30 | 204 | 193
2016-08-16 21:00 | 217 | 207
2016-08-16 21:30 | 260 | 253
2016-08-16 22:00 | 283 | 278
2016-08-16 22:30 | 276 | 272
2016-08-16 23:00 | 269 | 264
2016-08-16 23:30 | 263 | 259
2016-08-17 | 259 | 254
2016-08-17 00:30 | 240 | 235
2016-08-17 01:00 | 225 | 218
2016-08-17 01:30 | 208 | 200
2016-08-17 02:00 | 199 | 190
2016-08-17 02:30 | 191 | 180
2016-08-17 03:00 | 191 | 179
2016-08-17 03:30 | 192 | 180
2016-08-17 04:00 | 194 | 183
2016-08-17 04:30 | 213 | 203
2016-08-17 05:00 | 223 | 213
2016-08-17 05:30 | 231 | 222
2016-08-17 06:00 | 241 | 234
2016-08-17 06:30 | 265 | 259
2016-08-17 07:00 | 250 | 244
2016-08-17 07:30 | 282 | 277
2016-08-17 08:00 | 301 | 298
2016-08-17 08:30 | 305 | 302
2016-08-17 09:00 | 302 | 299
2016-08-17 09:30 | 303 | 300
2016-08-17 10:00 | 294 | 291
2016-08-17 10:30 | 293 | 289
2016-08-17 11:00 | 297 | 293
2016-08-17 11:30 | 297 | 293
2016-08-17 12:00 | 297 | 293
2016-08-17 12:30 | 300 | 296
2016-08-17 13:00 | 294 | 291
2016-08-17 13:30 | 292 | 288
2016-08-17 14:00 | 294 | 291
2016-08-17 14:30 | 236 | 232
2016-08-17 15:00 | 226 | 219
2016-08-17 15:30 | 231 | 222
2016-08-17 16:00 | 247 | 240
2016-08-17 16:30 | 249 | 243
2016-08-17 17:00 | 246 | 240
2016-08-17 17:30 | 238 | 231
2016-08-17 18:00 | 233 | 225
2016-08-17 18:30 | 230 | 222
2016-08-17 19:00 | 223 | 215
2016-08-17 19:30 | 218 | 210
2016-08-17 20:00 | 212 | 203
2016-08-17 20:30 | 207 | 197
2016-08-17 21:00 | 215 | 205
2016-08-17 21:30 | 223 | 213
2016-08-17 22:00 | 230 | 221
2016-08-17 22:30 | 214 | 206
2016-08-17 23:00 | 261 | 253
2016-08-17 23:30 | 300 | 295
2016-08-18 | 342 | 339
2016-08-18 00:30 | 332 | 330
2016-08-18 01:00 | 320 | 318
2016-08-18 01:30 | 297 | 294
2016-08-18 02:00 | 285 | 282
2016-08-18 02:30 | 272 | 268
2016-08-18 03:00 | 266 | 261
2016-08-18 03:30 | 264 | 259
2016-08-18 04:00 | 265 | 260
2016-08-18 04:30 | 273 | 268
2016-08-18 05:00 | 277 | 273
2016-08-18 05:30 | 286 | 282
2016-08-18 06:00 | 298 | 294
2016-08-18 06:30 | 318 | 315
2016-08-18 07:00 | 326 | 323
2016-08-18 07:30 | 344 | 342
2016-08-18 08:00 | 351 | 349
2016-08-18 08:30 | 355 | 354
2016-08-18 09:00 | 353 | 352
2016-08-18 09:30 | 355 | 354
2016-08-18 10:00 | 360 | 359
2016-08-18 10:30 | 351 | 350
2016-08-18 11:00 | 348 | 347
2016-08-18 11:30 | 351 | 350
2016-08-18 12:00 | 345 | 344
2016-08-18 12:30 | 342 | 340
2016-08-18 13:00 | 333 | 331
2016-08-18 13:30 | 338 | 336
2016-08-18 14:00 | 338 | 336
2016-08-18 14:30 | 332 | 330
2016-08-18 15:00 | 328 | 327
2016-08-18 15:30 | 336 | 334
2016-08-18 16:00 | 345 | 344
2016-08-18 16:30 | 349 | 348
2016-08-18 17:00 | 341 | 340
2016-08-18 17:30 | 333 | 332
2016-08-18 18:00 | 339 | 337
2016-08-18 18:30 | 347 | 346
2016-08-18 19:00 | 354 | 353
2016-08-18 19:30 | 344 | 343
2016-08-18 20:00 | 346 | 345
2016-08-18 20:30 | 355 | 354
2016-08-18 21:00 | 374 | 373
2016-08-18 21:30 | 359 | 358
2016-08-18 22:00 | 366 | 364
2016-08-18 22:30 | 349 | 348
2016-08-18 23:00 | 354 | 352
2016-08-18 23:30 | 348 | 346
2016-08-19 | 333 | 331
2016-08-19 00:30 | 320 | 318
2016-08-19 01:00 | 307 | 304
2016-08-19 01:30 | 297 | 294
2016-08-19 02:00 | 284 | 280
2016-08-19 02:30 | 271 | 267
2016-08-19 03:00 | 274 | 270
2016-08-19 03:30 | 269 | 265
2016-08-19 04:00 | 264 | 259
2016-08-19 04:30 | 271 | 265
2016-08-19 05:00 | 271 | 265
2016-08-19 05:30 | 279 | 274
2016-08-19 06:00 | 287 | 283
2016-08-19 06:30 | 305 | 301
2016-08-19 07:00 | 325 | 322
2016-08-19 07:30 | 346 | 345
2016-08-19 08:00 | 356 | 355
2016-08-19 08:30 | 368 | 368
2016-08-19 09:00 | 372 | 372
2016-08-19 09:30 | 361 | 361
2016-08-19 10:00 | 348 | 347
2016-08-19 10:30 | 345 | 345
2016-08-19 11:00 | 350 | 350
2016-08-19 11:30 | 352 | 351
2016-08-19 12:00 | 354 | 354
2016-08-19 12:30 | 355 | 354
2016-08-19 13:00 | 371 | 370
2016-08-19 13:30 | 349 | 349
2016-08-19 14:00 | 342 | 341
2016-08-19 14:30 | 335 | 334
2016-08-19 15:00 | 333 | 332
2016-08-19 15:30 | 335 | 334
2016-08-19 16:00 | 338 | 337
2016-08-19 16:30 | 344 | 343
2016-08-19 17:00 | 336 | 335
2016-08-19 17:30 | 329 | 328
2016-08-19 18:00 | 330 | 329
2016-08-19 18:30 | 334 | 333
2016-08-19 19:00 | 342 | 341
2016-08-19 19:30 | 329 | 328
2016-08-19 20:00 | 331 | 330
2016-08-19 20:30 | 316 | 315
2016-08-19 21:00 | 327 | 326
2016-08-19 21:30 | 339 | 338
2016-08-19 22:00 | 357 | 356
2016-08-19 22:30 | 358 | 357
2016-08-19 23:00 | 351 | 350
2016-08-19 23:30 | 346 | 345
2016-08-20 | 335 | 334
2016-08-20 00:30 | 319 | 318
2016-08-20 01:00 | 299 | 297
2016-08-20 01:30 | 288 | 285
2016-08-20 02:00 | 276 | 273
2016-08-20 02:30 | 266 | 261
2016-08-20 03:00 | 270 | 265
2016-08-20 03:30 | 271 | 267
2016-08-20 04:00 | 275 | 271
2016-08-20 04:30 | 281 | 277
2016-08-20 05:00 | 280 | 276
2016-08-20 05:30 | 268 | 264
2016-08-20 06:00 | 263 | 259
2016-08-20 06:30 | 273 | 269
2016-08-20 07:00 | 285 | 281
2016-08-20 07:30 | 301 | 298
2016-08-20 08:00 | 316 | 313
2016-08-20 08:30 | 327 | 325
2016-08-20 09:00 | 328 | 326
2016-08-20 09:30 | 327 | 326
2016-08-20 10:00 | 330 | 328
2016-08-20 10:30 | 332 | 331
2016-08-20 11:00 | 328 | 327
2016-08-20 11:30 | 328 | 326
2016-08-20 12:00 | 324 | 322
2016-08-20 12:30 | 323 | 321
2016-08-20 13:00 | 323 | 321
2016-08-20 13:30 | 314 | 312
2016-08-20 14:00 | 307 | 305
2016-08-20 14:30 | 294 | 291
2016-08-20 15:00 | 298 | 295
2016-08-20 15:30 | 310 | 308
2016-08-20 16:00 | 311 | 309
2016-08-20 16:30 | 321 | 319
2016-08-20 17:00 | 324 | 322
2016-08-20 17:30 | 331 | 330
2016-08-20 18:00 | 327 | 326
2016-08-20 18:30 | 331 | 329
2016-08-20 19:00 | 343 | 342
2016-08-20 19:30 | 345 | 344
2016-08-20 20:00 | 361 | 360
2016-08-20 20:30 | 355 | 354
2016-08-20 21:00 | 348 | 347
2016-08-20 21:30 | 338 | 336
2016-08-20 22:00 | 339 | 337
2016-08-20 22:30 | 334 | 332
2016-08-20 23:00 | 321 | 319
2016-08-20 23:30 | 312 | 310
2016-08-21 | 310 | 308
2016-08-21 00:30 | 300 | 297
2016-08-21 01:00 | 290 | 287
2016-08-21 01:30 | 279 | 275
2016-08-21 02:00 | 268 | 264
2016-08-21 02:30 | 258 | 253
2016-08-21 03:00 | 257 | 251
2016-08-21 03:30 | 254 | 248
2016-08-21 04:00 | 257 | 251
2016-08-21 04:30 | 254 | 248
2016-08-21 05:00 | 256 | 250
2016-08-21 05:30 | 256 | 250
2016-08-21 06:00 | 256 | 250
2016-08-21 06:30 | 257 | 251
2016-08-21 07:00 | 269 | 264
2016-08-21 07:30 | 273 | 268
2016-08-21 08:00 | 283 | 279
2016-08-21 08:30 | 293 | 289
2016-08-21 09:00 | 300 | 297
2016-08-21 09:30 | 301 | 298
2016-08-21 10:00 | 308 | 305
2016-08-21 10:30 | 302 | 300
2016-08-21 11:00 | 303 | 300
2016-08-21 11:30 | 302 | 299
2016-08-21 12:00 | 296 | 293
2016-08-21 12:30 | 289 | 285
2016-08-21 13:00 | 286 | 282
2016-08-21 13:30 | 285 | 282
2016-08-21 14:00 | 289 | 286
2016-08-21 14:30 | 284 | 281
2016-08-21 15:00 | 286 | 282
2016-08-21 15:30 | 295 | 291
2016-08-21 16:00 | 299 | 296
2016-08-21 16:30 | 298 | 295
2016-08-21 17:00 | 296 | 293
2016-08-21 17:30 | 304 | 301
2016-08-21 18:00 | 312 | 310
2016-08-21 18:30 | 321 | 319
2016-08-21 19:00 | 339 | 338
2016-08-21 19:30 | 333 | 332
2016-08-21 20:00 | 325 | 324
2016-08-21 20:30 | 319 | 317
2016-08-21 21:00 | 329 | 327
2016-08-21 21:30 | 352 | 350
2016-08-21 22:00 | 350 | 348
2016-08-21 22:30 | 338 | 337
2016-08-21 23:00 | 323 | 321
2016-08-21 23:30 | 314 | 312
2016-08-22 | 311 | 309
2016-08-22 00:30 | 300 | 297
2016-08-22 01:00 | 295 | 293
2016-08-22 01:30 | 284 | 281
2016-08-22 02:00 | 273 | 270
2016-08-22 02:30 | 272 | 268
2016-08-22 03:00 | 265 | 261
2016-08-22 03:30 | 267 | 263
2016-08-22 04:00 | 264 | 260
2016-08-22 04:30 | 271 | 266
2016-08-22 05:00 | 274 | 270
2016-08-22 05:30 | 280 | 276
2016-08-22 06:00 | 281 | 278
2016-08-22 06:30 | 301 | 297
2016-08-22 07:00 | 310 | 307
2016-08-22 07:30 | 321 | 319
2016-08-22 08:00 | 328 | 326
2016-08-22 08:30 | 334 | 333
2016-08-22 09:00 | 337 | 336
2016-08-22 09:30 | 331 | 330
2016-08-22 10:00 | 321 | 320
2016-08-22 10:30 | 320 | 319
2016-08-22 11:00 | 327 | 326
2016-08-22 11:30 | 329 | 327
2016-08-22 12:00 | 322 | 321
2016-08-22 12:30 | 284 | 283
2016-08-22 13:00 | 286 | 285
2016-08-22 13:30 | 284 | 283
2016-08-22 14:00 | 282 | 281
2016-08-22 14:30 | 278 | 277
2016-08-22 15:00 | 281 | 279
2016-08-22 15:30 | 281 | 279
2016-08-22 16:00 | 281 | 280
2016-08-22 16:30 | 290 | 289
2016-08-22 17:00 | 301 | 300
2016-08-22 17:30 | 306 | 305
2016-08-22 18:00 | 296 | 295
2016-08-22 18:30 | 293 | 292
2016-08-22 19:00 | 311 | 310
2016-08-22 19:30 | 304 | 303
2016-08-22 20:00 | 300 | 299
2016-08-22 20:30 | 290 | 289
2016-08-22 21:00 | 278 | 277
2016-08-22 21:30 | 272 | 270
2016-08-22 22:00 | 293 | 291
2016-08-22 22:30 | 292 | 290
2016-08-22 23:00 | 283 | 282
2016-08-22 23:30 | 278 | 276
2016-08-23 | 275 | 273
2016-08-23 00:30 | 268 | 266
2016-08-23 01:00 | 265 | 262
2016-08-23 01:30 | 249 | 246
2016-08-23 02:00 | 233 | 229
2016-08-23 02:30 | 231 | 227
2016-08-23 03:00 | 227 | 222
2016-08-23 03:30 | 226 | 222
2016-08-23 04:00 | 228 | 223
2016-08-23 04:30 | 230 | 226
2016-08-23 05:00 | 234 | 230
2016-08-23 05:30 | 227 | 223
2016-08-23 06:00 | 213 | 208
2016-08-23 06:30 | 215 | 210
2016-08-23 07:00 | 235 | 230
2016-08-23 07:30 | 253 | 249
2016-08-23 08:00 | 261 | 258
2016-08-23 08:30 | 269 | 266
2016-08-23 09:00 | 260 | 257
2016-08-23 09:30 | 257 | 255
2016-08-23 10:00 | 253 | 249
2016-08-23 10:30 | 251 | 248
2016-08-23 11:00 | 255 | 252
2016-08-23 11:30 | 255 | 252
2016-08-23 12:00 | 256 | 253
2016-08-23 12:30 | 251 | 248
2016-08-23 13:00 | 252 | 249
2016-08-23 13:30 | 261 | 258
2016-08-23 14:00 | 263 | 260
2016-08-23 14:30 | 251 | 248
2016-08-23 15:00 | 247 | 244
2016-08-23 15:30 | 246 | 242
2016-08-23 16:00 | 248 | 244
2016-08-23 16:30 | 253 | 249
2016-08-23 17:00 | 262 | 259
2016-08-23 17:30 | 263 | 261
2016-08-23 18:00 | 265 | 263
2016-08-23 18:30 | 287 | 286
2016-08-23 19:00 | 300 | 299
2016-08-23 19:30 | 300 | 299
2016-08-23 20:00 | 297 | 296
2016-08-23 20:30 | 285 | 284
2016-08-23 21:00 | 282 | 280
2016-08-23 21:30 | 274 | 272
2016-08-23 22:00 | 283 | 281
2016-08-23 22:30 | 300 | 298
2016-08-23 23:00 | 291 | 289
2016-08-23 23:30 | 281 | 280
2016-08-24 | 276 | 274
2016-08-24 00:30 | 261 | 259
2016-08-24 01:00 | 260 | 257
2016-08-24 01:30 | 246 | 243
2016-08-24 02:00 | 241 | 238
2016-08-24 02:30 | 235 | 231
2016-08-24 03:00 | 233 | 229
2016-08-24 03:30 | 233 | 229
2016-08-24 04:00 | 228 | 224
2016-08-24 04:30 | 227 | 222
2016-08-24 05:00 | 231 | 226
2016-08-24 05:30 | 240 | 236
2016-08-24 06:00 | 245 | 241
2016-08-24 06:30 | 265 | 262
2016-08-24 07:00 | 264 | 262
2016-08-24 07:30 | 281 | 279
2016-08-24 08:00 | 283 | 281
2016-08-24 08:30 | 281 | 279
2016-08-24 09:00 | 284 | 282
2016-08-24 09:30 | 272 | 270
2016-08-24 10:00 | 268 | 265
2016-08-24 10:30 | 266 | 263
2016-08-24 11:00 | 275 | 273
2016-08-24 11:30 | 265 | 262
2016-08-24 12:00 | 262 | 259
2016-08-24 12:30 | 267 | 264
2016-08-24 13:00 | 273 | 269
2016-08-24 13:30 | 271 | 267
2016-08-24 14:00 | 270 | 266
2016-08-24 14:30 | 274 | 270
2016-08-24 15:00 | 271 | 267
2016-08-24 15:30 | 265 | 261
2016-08-24 16:00 | 270 | 266
2016-08-24 16:30 | 282 | 278
2016-08-24 17:00 | 287 | 284
2016-08-24 17:30 | 300 | 298
2016-08-24 18:00 | 268 | 265
2016-08-24 18:30 | 230 | 226
2016-08-24 19:00 | 241 | 236
2016-08-24 19:30 | 268 | 263
2016-08-24 20:00 | 276 | 272
2016-08-24 20:30 | 234 | 229
2016-08-24 21:00 | 261 | 255
2016-08-24 21:30 | 281 | 277
2016-08-24 22:00 | 288 | 285
2016-08-24 22:30 | 282 | 279
2016-08-24 23:00 | 286 | 282
2016-08-24 23:30 | 287 | 284
2016-08-25 | 278 | 274
2016-08-25 00:30 | 269 | 265
2016-08-25 01:00 | 256 | 252
2016-08-25 01:30 | 243 | 237
2016-08-25 02:00 | 235 | 229
2016-08-25 02:30 | 229 | 223
2016-08-25 03:00 | 224 | 216
2016-08-25 03:30 | 225 | 218
2016-08-25 04:00 | 228 | 220
2016-08-25 04:30 | 227 | 220
2016-08-25 05:00 | 235 | 229
2016-08-25 05:30 | 236 | 230
2016-08-25 06:00 | 231 | 225
2016-08-25 06:30 | 250 | 244
2016-08-25 07:00 | 268 | 263
2016-08-25 07:30 | 296 | 292
2016-08-25 08:00 | 308 | 305
2016-08-25 08:30 | 313 | 310
2016-08-25 09:00 | 318 | 316
2016-08-25 09:30 | 315 | 313
2016-08-25 10:00 | 320 | 318
2016-08-25 10:30 | 327 | 325
2016-08-25 11:00 | 330 | 328
2016-08-25 11:30 | 328 | 326
2016-08-25 12:00 | 327 | 325
2016-08-25 12:30 | 324 | 322
2016-08-25 13:00 | 325 | 323
2016-08-25 13:30 | 325 | 323
2016-08-25 14:00 | 324 | 322
2016-08-25 14:30 | 318 | 316
2016-08-25 15:00 | 318 | 315
2016-08-25 15:30 | 314 | 312
2016-08-25 16:00 | 309 | 306
2016-08-25 16:30 | 308 | 305
2016-08-25 17:00 | 309 | 307
2016-08-25 17:30 | 313 | 311
2016-08-25 18:00 | 308 | 306
2016-08-25 18:30 | 307 | 305
2016-08-25 19:00 | 317 | 314
2016-08-25 19:30 | 309 | 307
2016-08-25 20:00 | 304 | 301
2016-08-25 20:30 | 293 | 290
2016-08-25 21:00 | 285 | 282
2016-08-25 21:30 | 276 | 273
2016-08-25 22:00 | 289 | 285
2016-08-25 22:30 | 286 | 283
2016-08-25 23:00 | 293 | 290
2016-08-25 23:30 | 281 | 278
2016-08-26 | 252 | 249
2016-08-26 00:30 | 254 | 249
2016-08-26 01:00 | 247 | 241
2016-08-26 01:30 | 237 | 231
2016-08-26 02:00 | 238 | 232
2016-08-26 02:30 | 233 | 227
2016-08-26 03:00 | 230 | 223
2016-08-26 03:30 | 229 | 223
2016-08-26 04:00 | 223 | 215
2016-08-26 04:30 | 222 | 214
2016-08-26 05:00 | 221 | 214
2016-08-26 05:30 | 226 | 218
2016-08-26 06:00 | 232 | 225
2016-08-26 06:30 | 248 | 242
2016-08-26 07:00 | 257 | 251
2016-08-26 07:30 | 278 | 274
2016-08-26 08:00 | 299 | 296
2016-08-26 08:30 | 310 | 308
2016-08-26 09:00 | 318 | 316
2016-08-26 09:30 | 311 | 309
2016-08-26 10:00 | 302 | 300
2016-08-26 10:30 | 311 | 308
2016-08-26 11:00 | 313 | 311
2016-08-26 11:30 | 315 | 312
2016-08-26 12:00 | 329 | 327
2016-08-26 12:30 | 329 | 327
2016-08-26 13:00 | 323 | 320
2016-08-26 13:30 | 322 | 319
2016-08-26 14:00 | 315 | 313
2016-08-26 14:30 | 307 | 304
2016-08-26 15:00 | 304 | 301
2016-08-26 15:30 | 306 | 303
2016-08-26 16:00 | 316 | 313
2016-08-26 16:30 | 287 | 285
2016-08-26 17:00 | 237 | 233
2016-08-26 17:30 | 239 | 232
2016-08-26 18:00 | 229 | 222
2016-08-26 18:30 | 227 | 221
2016-08-26 19:00 | 241 | 234
2016-08-26 19:30 | 232 | 226
2016-08-26 20:00 | 231 | 224
2016-08-26 20:30 | 228 | 221
2016-08-26 21:00 | 224 | 217
2016-08-26 21:30 | 215 | 207
2016-08-26 22:00 | 225 | 217
2016-08-26 22:30 | 291 | 285
2016-08-26 23:00 | 308 | 304
2016-08-26 23:30 | 306 | 304
2016-08-27 | 287 | 284
2016-08-27 00:30 | 282 | 278
2016-08-27 01:00 | 273 | 269
2016-08-27 01:30 | 261 | 256
2016-08-27 02:00 | 252 | 246
2016-08-27 02:30 | 247 | 240
2016-08-27 03:00 | 241 | 234
2016-08-27 03:30 | 238 | 230
2016-08-27 04:00 | 235 | 227
2016-08-27 04:30 | 233 | 225
2016-08-27 05:00 | 233 | 226
2016-08-27 05:30 | 239 | 231
2016-08-27 06:00 | 238 | 231
2016-08-27 06:30 | 244 | 237
2016-08-27 07:00 | 253 | 246
2016-08-27 07:30 | 264 | 257
2016-08-27 08:00 | 275 | 269
2016-08-27 08:30 | 281 | 276
2016-08-27 09:00 | 279 | 274
2016-08-27 09:30 | 275 | 270
2016-08-27 10:00 | 270 | 264
2016-08-27 10:30 | 268 | 262
2016-08-27 11:00 | 259 | 254
2016-08-27 11:30 | 260 | 254
2016-08-27 12:00 | 261 | 256
2016-08-27 12:30 | 260 | 255
2016-08-27 13:00 | 256 | 251
2016-08-27 13:30 | 257 | 251
2016-08-27 14:00 | 251 | 246
2016-08-27 14:30 | 248 | 242
2016-08-27 15:00 | 245 | 239
2016-08-27 15:30 | 251 | 245
2016-08-27 16:00 | 258 | 253
2016-08-27 16:30 | 266 | 261
2016-08-27 17:00 | 277 | 272
2016-08-27 17:30 | 287 | 282
2016-08-27 18:00 | 284 | 281
2016-08-27 18:30 | 282 | 279
2016-08-27 19:00 | 292 | 289
2016-08-27 19:30 | 290 | 287
2016-08-27 20:00 | 297 | 295
2016-08-27 20:30 | 290 | 287
2016-08-27 21:00 | 286 | 282
2016-08-27 21:30 | 280 | 276
2016-08-27 22:00 | 277 | 273
2016-08-27 22:30 | 277 | 273
2016-08-27 23:00 | 263 | 258
2016-08-27 23:30 | 251 | 246
2016-08-28 | 251 | 245
2016-08-28 00:30 | 238 | 232
2016-08-28 01:00 | 230 | 223
2016-08-28 01:30 | 222 | 214
2016-08-28 02:00 | 222 | 213
2016-08-28 02:30 | 225 | 216
2016-08-28 03:00 | 228 | 220
2016-08-28 03:30 | 230 | 221
2016-08-28 04:00 | 228 | 220
2016-08-28 04:30 | 228 | 219
2016-08-28 05:00 | 226 | 217
2016-08-28 05:30 | 233 | 225
2016-08-28 06:00 | 239 | 231
2016-08-28 06:30 | 240 | 233
2016-08-28 07:00 | 245 | 237
2016-08-28 07:30 | 249 | 241
2016-08-28 08:00 | 254 | 247
2016-08-28 08:30 | 258 | 251
2016-08-28 09:00 | 259 | 253
2016-08-28 09:30 | 257 | 250
2016-08-28 10:00 | 254 | 248
2016-08-28 10:30 | 256 | 250
2016-08-28 11:00 | 255 | 249
2016-08-28 11:30 | 266 | 261
2016-08-28 12:00 | 295 | 290
2016-08-28 12:30 | 292 | 288
2016-08-28 13:00 | 295 | 291
2016-08-28 13:30 | 286 | 282
2016-08-28 14:00 | 287 | 283
2016-08-28 14:30 | 281 | 276
2016-08-28 15:00 | 278 | 274
2016-08-28 15:30 | 278 | 274
2016-08-28 16:00 | 281 | 276
2016-08-28 16:30 | 292 | 288
2016-08-28 17:00 | 303 | 300
2016-08-28 17:30 | 324 | 321
2016-08-28 18:00 | 322 | 319
2016-08-28 18:30 | 323 | 321
2016-08-28 19:00 | 337 | 335
2016-08-28 19:30 | 329 | 327
2016-08-28 20:00 | 328 | 325
2016-08-28 20:30 | 328 | 326
2016-08-28 21:00 | 324 | 321
2016-08-28 21:30 | 310 | 308
2016-08-28 22:00 | 305 | 302
2016-08-28 22:30 | 303 | 300
2016-08-28 23:00 | 298 | 294
2016-08-28 23:30 | 284 | 281
2016-08-29 | 287 | 283
2016-08-29 00:30 | 282 | 278
2016-08-29 01:00 | 278 | 273
2016-08-29 01:30 | 270 | 265
2016-08-29 02:00 | 258 | 253
2016-08-29 02:30 | 252 | 246
2016-08-29 03:00 | 249 | 241
2016-08-29 03:30 | 246 | 237
2016-08-29 04:00 | 248 | 239
2016-08-29 04:30 | 248 | 239
2016-08-29 05:00 | 246 | 237
2016-08-29 05:30 | 255 | 246
2016-08-29 06:00 | 264 | 255
2016-08-29 06:30 | 287 | 280
2016-08-29 07:00 | 292 | 287
2016-08-29 07:30 | 296 | 291
2016-08-29 08:00 | 309 | 304
2016-08-29 08:30 | 313 | 309
2016-08-29 09:00 | 318 | 315
2016-08-29 09:30 | 320 | 317
2016-08-29 10:00 | 321 | 318
2016-08-29 10:30 | 313 | 309
2016-08-29 11:00 | 308 | 304
2016-08-29 11:30 | 314 | 310
2016-08-29 12:00 | 313 | 309
2016-08-29 12:30 | 317 | 313
2016-08-29 13:00 | 320 | 316
2016-08-29 13:30 | 326 | 323
2016-08-29 14:00 | 323 | 320
2016-08-29 14:30 | 311 | 308
2016-08-29 15:00 | 314 | 310
2016-08-29 15:30 | 317 | 313
2016-08-29 16:00 | 323 | 320
2016-08-29 16:30 | 336 | 333
2016-08-29 17:00 | 340 | 338
2016-08-29 17:30 | 336 | 334
2016-08-29 18:00 | 337 | 335
2016-08-29 18:30 | 335 | 332
2016-08-29 19:00 | 329 | 327
2016-08-29 19:30 | 329 | 327
2016-08-29 20:00 | 331 | 329
2016-08-29 20:30 | 307 | 304
2016-08-29 21:00 | 322 | 318
2016-08-29 21:30 | 319 | 316
2016-08-29 22:00 | 327 | 322
2016-08-29 22:30 | 320 | 315
2016-08-29 23:00 | 316 | 311
2016-08-29 23:30 | 318 | 313
2016-08-30 | 320 | 315
2016-08-30 00:30 | 311 | 307
2016-08-30 01:00 | 297 | 293
2016-08-30 01:30 | 278 | 273
2016-08-30 02:00 | 269 | 263
2016-08-30 02:30 | 259 | 253
2016-08-30 03:00 | 257 | 249
2016-08-30 03:30 | 254 | 246
2016-08-30 04:00 | 255 | 247
2016-08-30 04:30 | 256 | 248
2016-08-30 05:00 | 259 | 252
2016-08-30 05:30 | 267 | 260
2016-08-30 06:00 | 275 | 268
2016-08-30 06:30 | 288 | 282
2016-08-30 07:00 | 294 | 290
2016-08-30 07:30 | 334 | 331
2016-08-30 08:00 | 338 | 336
2016-08-30 08:30 | 336 | 335
2016-08-30 09:00 | 327 | 326
2016-08-30 09:30 | 323 | 322
2016-08-30 10:00 | 321 | 320
2016-08-30 10:30 | 317 | 315
2016-08-30 11:00 | 315 | 313
2016-08-30 11:30 | 325 | 323
2016-08-30 12:00 | 343 | 341
2016-08-30 12:30 | 342 | 341
2016-08-30 13:00 | 336 | 334
2016-08-30 13:30 | 331 | 329
2016-08-30 14:00 | 333 | 331
2016-08-30 14:30 | 336 | 335
2016-08-30 15:00 | 323 | 321
2016-08-30 15:30 | 315 | 313
2016-08-30 16:00 | 324 | 322
2016-08-30 16:30 | 330 | 329
2016-08-30 17:00 | 337 | 336
2016-08-30 17:30 | 335 | 334
2016-08-30 18:00 | 329 | 328
2016-08-30 18:30 | 334 | 333
2016-08-30 19:00 | 343 | 341
2016-08-30 19:30 | 339 | 338
2016-08-30 20:00 | 334 | 333
2016-08-30 20:30 | 329 | 327
2016-08-30 21:00 | 329 | 327
2016-08-30 21:30 | 321 | 320
2016-08-30 22:00 | 329 | 328
2016-08-30 22:30 | 350 | 349
2016-08-30 23:00 | 350 | 349
2016-08-30 23:30 | 338 | 337
2016-08-31 | 325 | 324
2016-08-31 00:30 | 310 | 309
2016-08-31 01:00 | 300 | 298
2016-08-31 01:30 | 280 | 277
2016-08-31 02:00 | 270 | 266
2016-08-31 02:30 | 269 | 264
2016-08-31 03:00 | 261 | 256
2016-08-31 03:30 | 260 | 255
2016-08-31 04:00 | 263 | 258
2016-08-31 04:30 | 268 | 264
2016-08-31 05:00 | 267 | 263
2016-08-31 05:30 | 272 | 268
2016-08-31 06:00 | 286 | 282
2016-08-31 06:30 | 318 | 315
2016-08-31 07:00 | 336 | 334
2016-08-31 07:30 | 359 | 357
2016-08-31 08:00 | 369 | 369
2016-08-31 08:30 | 371 | 371
2016-08-31 09:00 | 372 | 372
2016-08-31 09:30 | 370 | 369
2016-08-31 10:00 | 365 | 364
2016-08-31 10:30 | 350 | 349
2016-08-31 11:00 | 369 | 368
2016-08-31 11:30 | 357 | 356
2016-08-31 12:00 | 322 | 321
2016-08-31 12:30 | 308 | 306
2016-08-31 13:00 | 316 | 314
2016-08-31 13:30 | 313 | 311
2016-08-31 14:00 | 312 | 311
2016-08-31 14:30 | 297 | 295
2016-08-31 15:00 | 298 | 296
2016-08-31 15:30 | 304 | 302
2016-08-31 16:00 | 293 | 291
2016-08-31 16:30 | 259 | 257
2016-08-31 17:00 | 248 | 244
2016-08-31 17:30 | 234 | 230
2016-08-31 18:00 | 229 | 223
2016-08-31 18:30 | 233 | 228
2016-08-31 19:00 | 233 | 227
2016-08-31 19:30 | 226 | 221
2016-08-31 20:00 | 223 | 218
2016-08-31 20:30 | 213 | 206
2016-08-31 21:00 | 225 | 218
2016-08-31 21:30 | 220 | 213
2016-08-31 22:00 | 268 | 262
2016-08-31 22:30 | 208 | 202
2016-08-31 23:00 | 198 | 189
2016-08-31 23:30 | 252 | 242
2016-09-01 | 236 | 228
2016-09-01 00:30 | 230 | 221
2016-09-01 01:00 | 200 | 189
2016-09-01 01:30 | 206 | 194
2016-09-01 02:00 | 199 | 185
2016-09-01 02:30 | 195 | 180
2016-09-01 03:00 | 193 | 178
2016-09-01 03:30 | 191 | 176
2016-09-01 04:00 | 189 | 174
2016-09-01 04:30 | 192 | 177
2016-09-01 05:00 | 201 | 187
2016-09-01 05:30 | 180 | 165
2016-09-01 06:00 | 196 | 180
2016-09-01 06:30 | 162 | 143
2016-09-01 07:00 | 167 | 145
2016-09-01 07:30 | 198 | 182
2016-09-01 08:00 | 213 | 201
2016-09-01 08:30 | 228 | 218
2016-09-01 09:00 | 222 | 212
2016-09-01 09:30 | 215 | 205
2016-09-01 10:00 | 215 | 205
2016-09-01 10:30 | 223 | 212
2016-09-01 11:00 | 211 | 200
2016-09-01 11:30 | 210 | 199
2016-09-01 12:00 | 205 | 196
2016-09-01 12:30 | 193 | 183
2016-09-01 13:00 | 192 | 182
2016-09-01 13:30 | 187 | 176
2016-09-01 14:00 | 186 | 175
2016-09-01 14:30 | 185 | 173
2016-09-01 15:00 | 175 | 165
2016-09-01 15:30 | 195 | 183
2016-09-01 16:00 | 199 | 188
2016-09-01 16:30 | 199 | 190
2016-09-01 17:00 | 206 | 197
2016-09-01 17:30 | 211 | 203
2016-09-01 18:00 | 218 | 210
2016-09-01 18:30 | 231 | 224
2016-09-01 19:00 | 250 | 245
2016-09-01 19:30 | 247 | 242
2016-09-01 20:00 | 227 | 221
2016-09-01 20:30 | 214 | 210
2016-09-01 21:00 | 215 | 211
2016-09-01 21:30 | 231 | 227
2016-09-01 22:00 | 253 | 249
2016-09-01 22:30 | 202 | 198
2016-09-01 23:00 | 184 | 177
2016-09-01 23:30 | 169 | 159
2016-09-02 | 178 | 167
2016-09-02 00:30 | 210 | 202
2016-09-02 01:00 | 210 | 204
2016-09-02 01:30 | 205 | 200
2016-09-02 02:00 | 198 | 191
2016-09-02 02:30 | 201 | 194
2016-09-02 03:00 | 202 | 195
2016-09-02 03:30 | 198 | 192
2016-09-02 04:00 | 196 | 189
2016-09-02 04:30 | 198 | 191
2016-09-02 05:00 | 201 | 194
2016-09-02 05:30 | 208 | 202
2016-09-02 06:00 | 214 | 209
2016-09-02 06:30 | 184 | 178
2016-09-02 07:00 | 184 | 176
2016-09-02 07:30 | 209 | 202
2016-09-02 08:00 | 214 | 208
2016-09-02 08:30 | 211 | 206
2016-09-02 09:00 | 213 | 208
2016-09-02 09:30 | 207 | 201
2016-09-02 10:00 | 213 | 206
2016-09-02 10:30 | 211 | 204
2016-09-02 11:00 | 210 | 204
2016-09-02 11:30 | 216 | 210
2016-09-02 12:00 | 215 | 210
2016-09-02 12:30 | 212 | 207
2016-09-02 13:00 | 207 | 201
2016-09-02 13:30 | 208 | 202
2016-09-02 14:00 | 215 | 209
2016-09-02 14:30 | 209 | 204
2016-09-02 15:00 | 202 | 195
2016-09-02 15:30 | 198 | 190
2016-09-02 16:00 | 208 | 201
2016-09-02 16:30 | 217 | 212
2016-09-02 17:00 | 217 | 212
2016-09-02 17:30 | 221 | 217
2016-09-02 18:00 | 224 | 219
2016-09-02 18:30 | 226 | 221
2016-09-02 19:00 | 236 | 232
2016-09-02 19:30 | 234 | 232
2016-09-02 20:00 | 226 | 223
2016-09-02 20:30 | 216 | 212
2016-09-02 21:00 | 206 | 202
2016-09-02 21:30 | 197 | 192
2016-09-02 22:00 | 193 | 187
2016-09-02 22:30 | 188 | 181
2016-09-02 23:00 | 192 | 184
2016-09-02 23:30 | 180 | 172
2016-09-03 | 166 | 157
2016-09-03 00:30 | 190 | 182
2016-09-03 01:00 | 207 | 200
2016-09-03 01:30 | 199 | 194
2016-09-03 02:00 | 224 | 219
2016-09-03 02:30 | 277 | 274
2016-09-03 03:00 | 273 | 271
2016-09-03 03:30 | 269 | 267
2016-09-03 04:00 | 270 | 268
2016-09-03 04:30 | 270 | 268
2016-09-03 05:00 | 273 | 271
2016-09-03 05:30 | 273 | 271
2016-09-03 06:00 | 278 | 276
2016-09-03 06:30 | 285 | 283
2016-09-03 07:00 | 288 | 287
2016-09-03 07:30 | 302 | 301
2016-09-03 08:00 | 318 | 317
2016-09-03 08:30 | 317 | 316
2016-09-03 09:00 | 318 | 318
2016-09-03 09:30 | 320 | 319
2016-09-03 10:00 | 328 | 327
2016-09-03 10:30 | 331 | 330
2016-09-03 11:00 | 325 | 324
2016-09-03 11:30 | 323 | 322
2016-09-03 12:00 | 327 | 326
2016-09-03 12:30 | 324 | 323
2016-09-03 13:00 | 326 | 325
2016-09-03 13:30 | 327 | 327
2016-09-03 14:00 | 314 | 313
2016-09-03 14:30 | 298 | 297
2016-09-03 15:00 | 303 | 302
2016-09-03 15:30 | 311 | 310
2016-09-03 16:00 | 318 | 317
2016-09-03 16:30 | 324 | 323
2016-09-03 17:00 | 335 | 335
2016-09-03 17:30 | 345 | 344
2016-09-03 18:00 | 336 | 335
2016-09-03 18:30 | 328 | 328
2016-09-03 19:00 | 339 | 339
2016-09-03 19:30 | 350 | 350
2016-09-03 20:00 | 344 | 344
2016-09-03 20:30 | 344 | 343
2016-09-03 21:00 | 349 | 349
2016-09-03 21:30 | 342 | 342
2016-09-03 22:00 | 330 | 330
2016-09-03 22:30 | 321 | 320
2016-09-03 23:00 | 308 | 307
2016-09-03 23:30 | 295 | 294
2016-09-04 | 287 | 286
2016-09-04 00:30 | 276 | 275
2016-09-04 01:00 | 271 | 269
2016-09-04 01:30 | 263 | 261
2016-09-04 02:00 | 262 | 260
2016-09-04 02:30 | 261 | 259
2016-09-04 03:00 | 254 | 251
2016-09-04 03:30 | 256 | 254
2016-09-04 04:00 | 255 | 253
2016-09-04 04:30 | 254 | 252
2016-09-04 05:00 | 258 | 255
2016-09-04 05:30 | 266 | 264
2016-09-04 06:00 | 263 | 261
2016-09-04 06:30 | 266 | 263
2016-09-04 07:00 | 274 | 272
2016-09-04 07:30 | 281 | 279
2016-09-04 08:00 | 291 | 289
2016-09-04 08:30 | 301 | 300
2016-09-04 09:00 | 313 | 312
2016-09-04 09:30 | 317 | 317
2016-09-04 10:00 | 314 | 313
2016-09-04 10:30 | 316 | 315
2016-09-04 11:00 | 309 | 308
2016-09-04 11:30 | 311 | 310
2016-09-04 12:00 | 310 | 310
2016-09-04 12:30 | 307 | 306
2016-09-04 13:00 | 305 | 304
2016-09-04 13:30 | 310 | 309
2016-09-04 14:00 | 311 | 310
2016-09-04 14:30 | 297 | 296
2016-09-04 15:00 | 296 | 295
2016-09-04 15:30 | 298 | 297
2016-09-04 16:00 | 308 | 307
2016-09-04 16:30 | 326 | 325
2016-09-04 17:00 | 343 | 342
2016-09-04 17:30 | 362 | 362
2016-09-04 18:00 | 364 | 364
2016-09-04 18:30 | 366 | 366
2016-09-04 19:00 | 370 | 370
2016-09-04 19:30 | 368 | 368
2016-09-04 20:00 | 354 | 354
2016-09-04 20:30 | 353 | 353
2016-09-04 21:00 | 345 | 345
2016-09-04 21:30 | 334 | 333
2016-09-04 22:00 | 320 | 319
2016-09-04 22:30 | 300 | 299
2016-09-04 23:00 | 297 | 296
2016-09-04 23:30 | 290 | 288
2016-09-05 | 283 | 281
2016-09-05 00:30 | 275 | 273
2016-09-05 01:00 | 266 | 264
2016-09-05 01:30 | 260 | 257
2016-09-05 02:00 | 264 | 262
2016-09-05 02:30 | 260 | 257
2016-09-05 03:00 | 256 | 252
2016-09-05 03:30 | 256 | 251
2016-09-05 04:00 | 256 | 251
2016-09-05 04:30 | 251 | 247
2016-09-05 05:00 | 257 | 252
2016-09-05 05:30 | 265 | 261
2016-09-05 06:00 | 268 | 264
2016-09-05 06:30 | 289 | 285
2016-09-05 07:00 | 295 | 292
2016-09-05 07:30 | 329 | 326
2016-09-05 08:00 | 343 | 341
2016-09-05 08:30 | 339 | 337
2016-09-05 09:00 | 346 | 345
2016-09-05 09:30 | 350 | 348
2016-09-05 10:00 | 345 | 344
2016-09-05 10:30 | 347 | 346
2016-09-05 11:00 | 340 | 339
2016-09-05 11:30 | 345 | 344
2016-09-05 12:00 | 355 | 354
2016-09-05 12:30 | 345 | 344
2016-09-05 13:00 | 346 | 345
2016-09-05 13:30 | 345 | 344
2016-09-05 14:00 | 342 | 341
2016-09-05 14:30 | 342 | 341
2016-09-05 15:00 | 338 | 337
2016-09-05 15:30 | 338 | 337
2016-09-05 16:00 | 343 | 342
2016-09-05 16:30 | 297 | 295
2016-09-05 17:00 | 256 | 253
2016-09-05 17:30 | 258 | 251
2016-09-05 18:00 | 266 | 260
2016-09-05 18:30 | 267 | 262
2016-09-05 19:00 | 282 | 277
2016-09-05 19:30 | 281 | 277
2016-09-05 20:00 | 269 | 264
2016-09-05 20:30 | 270 | 264
2016-09-05 21:00 | 291 | 285
2016-09-05 21:30 | 293 | 288
2016-09-05 22:00 | 298 | 293
2016-09-05 22:30 | 231 | 225
2016-09-05 23:00 | 229 | 219
2016-09-05 23:30 | 297 | 290
2016-09-06 | 299 | 295
2016-09-06 00:30 | 290 | 286
2016-09-06 01:00 | 281 | 276
2016-09-06 01:30 | 277 | 271
2016-09-06 02:00 | 273 | 267
2016-09-06 02:30 | 271 | 265
2016-09-06 03:00 | 264 | 258
2016-09-06 03:30 | 269 | 262
2016-09-06 04:00 | 271 | 265
2016-09-06 04:30 | 271 | 265
2016-09-06 05:00 | 274 | 268
2016-09-06 05:30 | 285 | 279
2016-09-06 06:00 | 298 | 293
2016-09-06 06:30 | 309 | 305
2016-09-06 07:00 | 326 | 322
2016-09-06 07:30 | 345 | 342
2016-09-06 08:00 | 353 | 350
2016-09-06 08:30 | 344 | 341
2016-09-06 09:00 | 340 | 337
2016-09-06 09:30 | 338 | 335
2016-09-06 10:00 | 346 | 343
2016-09-06 10:30 | 346 | 344
2016-09-06 11:00 | 343 | 341
2016-09-06 11:30 | 347 | 344
2016-09-06 12:00 | 343 | 340
2016-09-06 12:30 | 350 | 348
2016-09-06 13:00 | 359 | 357
2016-09-06 13:30 | 364 | 362
2016-09-06 14:00 | 363 | 361
2016-09-06 14:30 | 357 | 355
2016-09-06 15:00 | 359 | 358
2016-09-06 15:30 | 361 | 359
2016-09-06 16:00 | 355 | 353
2016-09-06 16:30 | 363 | 361
2016-09-06 17:00 | 278 | 276
2016-09-06 17:30 | 269 | 264
2016-09-06 18:00 | 268 | 263
2016-09-06 18:30 | 287 | 282
2016-09-06 19:00 | 300 | 296
2016-09-06 19:30 | 327 | 323
2016-09-06 20:00 | 319 | 317
2016-09-06 20:30 | 302 | 299
2016-09-06 21:00 | 293 | 289
2016-09-06 21:30 | 284 | 280
2016-09-06 22:00 | 307 | 302
2016-09-06 22:30 | 244 | 239
2016-09-06 23:00 | 225 | 215
2016-09-06 23:30 | 291 | 280
2016-09-07 | 300 | 293
2016-09-07 00:30 | 294 | 288
2016-09-07 01:00 | 285 | 278
2016-09-07 01:30 | 279 | 272
2016-09-07 02:00 | 276 | 268
2016-09-07 02:30 | 271 | 263
2016-09-07 03:00 | 277 | 269
2016-09-07 03:30 | 277 | 268
2016-09-07 04:00 | 274 | 265
2016-09-07 04:30 | 277 | 268
2016-09-07 05:00 | 274 | 266
2016-09-07 05:30 | 278 | 270
2016-09-07 06:00 | 293 | 285
2016-09-07 06:30 | 306 | 299
2016-09-07 07:00 | 323 | 320
2016-09-07 07:30 | 343 | 340
2016-09-07 08:00 | 351 | 349
2016-09-07 08:30 | 347 | 345
2016-09-07 09:00 | 335 | 333
2016-09-07 09:30 | 346 | 343
2016-09-07 10:00 | 342 | 339
2016-09-07 10:30 | 337 | 334
2016-09-07 11:00 | 342 | 340
2016-09-07 11:30 | 355 | 353
2016-09-07 12:00 | 350 | 347
2016-09-07 12:30 | 344 | 341
2016-09-07 13:00 | 342 | 339
2016-09-07 13:30 | 349 | 346
2016-09-07 14:00 | 343 | 341
2016-09-07 14:30 | 331 | 328
2016-09-07 15:00 | 336 | 333
2016-09-07 15:30 | 337 | 334
2016-09-07 16:00 | 338 | 335
2016-09-07 16:30 | 295 | 292
2016-09-07 17:00 | 253 | 248
2016-09-07 17:30 | 263 | 255
2016-09-07 18:00 | 271 | 265
2016-09-07 18:30 | 289 | 283
2016-09-07 19:00 | 332 | 327
2016-09-07 19:30 | 341 | 338
2016-09-07 20:00 | 318 | 315
2016-09-07 20:30 | 301 | 297
2016-09-07 21:00 | 305 | 300
2016-09-07 21:30 | 300 | 296
2016-09-07 22:00 | 287 | 282
2016-09-07 22:30 | 248 | 242
2016-09-07 23:00 | 231 | 221
2016-09-07 23:30 | 286 | 277
2016-09-08 | 301 | 295
2016-09-08 00:30 | 296 | 292
2016-09-08 01:00 | 284 | 279
2016-09-08 01:30 | 279 | 273
2016-09-08 02:00 | 278 | 271
2016-09-08 02:30 | 270 | 264
2016-09-08 03:00 | 272 | 266
2016-09-08 03:30 | 268 | 261
2016-09-08 04:00 | 272 | 266
2016-09-08 04:30 | 269 | 263
2016-09-08 05:00 | 278 | 271
2016-09-08 05:30 | 286 | 280
2016-09-08 06:00 | 290 | 284
2016-09-08 06:30 | 310 | 306
2016-09-08 07:00 | 324 | 321
2016-09-08 07:30 | 347 | 345
2016-09-08 08:00 | 350 | 349
2016-09-08 08:30 | 355 | 353
2016-09-08 09:00 | 351 | 350
2016-09-08 09:30 | 349 | 347
2016-09-08 10:00 | 348 | 347
2016-09-08 10:30 | 348 | 347
2016-09-08 11:00 | 346 | 345
2016-09-08 11:30 | 340 | 338
2016-09-08 12:00 | 352 | 351
2016-09-08 12:30 | 354 | 353
2016-09-08 13:00 | 354 | 353
2016-09-08 13:30 | 364 | 362
2016-09-08 14:00 | 372 | 371
2016-09-08 14:30 | 365 | 364
2016-09-08 15:00 | 366 | 365
2016-09-08 15:30 | 367 | 365
2016-09-08 16:00 | 376 | 375
2016-09-08 16:30 | 377 | 376
2016-09-08 17:00 | 374 | 374
2016-09-08 17:30 | 379 | 378
2016-09-08 18:00 | 388 | 387
2016-09-08 18:30 | 393 | 392
2016-09-08 19:00 | 357 | 357
2016-09-08 19:30 | 358 | 357
2016-09-08 20:00 | 361 | 360
2016-09-08 20:30 | 319 | 317
2016-09-08 21:00 | 309 | 306
2016-09-08 21:30 | 285 | 282
2016-09-08 22:00 | 300 | 297
2016-09-08 22:30 | 255 | 251
2016-09-08 23:00 | 226 | 220
2016-09-08 23:30 | 294 | 288
2016-09-09 | 306 | 303
2016-09-09 00:30 | 299 | 296
2016-09-09 01:00 | 290 | 287
2016-09-09 01:30 | 280 | 277
2016-09-09 02:00 | 278 | 274
2016-09-09 02:30 | 274 | 271
2016-09-09 03:00 | 273 | 269
2016-09-09 03:30 | 278 | 274
2016-09-09 04:00 | 276 | 272
2016-09-09 04:30 | 274 | 270
2016-09-09 05:00 | 277 | 273
2016-09-09 05:30 | 282 | 279
2016-09-09 06:00 | 296 | 293
2016-09-09 06:30 | 311 | 309
2016-09-09 07:00 | 340 | 338
2016-09-09 07:30 | 366 | 365
2016-09-09 08:00 | 374 | 373
2016-09-09 08:30 | 373 | 373
2016-09-09 09:00 | 367 | 367
2016-09-09 09:30 | 365 | 364
2016-09-09 10:00 | 362 | 361
2016-09-09 10:30 | 360 | 359
2016-09-09 11:00 | 358 | 356
2016-09-09 11:30 | 359 | 357
2016-09-09 12:00 | 354 | 352
2016-09-09 12:30 | 351 | 349
2016-09-09 13:00 | 349 | 348
2016-09-09 13:30 | 344 | 342
2016-09-09 14:00 | 345 | 343
2016-09-09 14:30 | 332 | 329
2016-09-09 15:00 | 324 | 322
2016-09-09 15:30 | 338 | 336
2016-09-09 16:00 | 336 | 333
2016-09-09 16:30 | 345 | 343
2016-09-09 17:00 | 350 | 349
2016-09-09 17:30 | 362 | 361
2016-09-09 18:00 | 360 | 359
2016-09-09 18:30 | 369 | 368
2016-09-09 19:00 | 381 | 380
2016-09-09 19:30 | 378 | 377
2016-09-09 20:00 | 367 | 365
2016-09-09 20:30 | 360 | 359
2016-09-09 21:00 | 350 | 348
2016-09-09 21:30 | 364 | 362
2016-09-09 22:00 | 353 | 352
2016-09-09 22:30 | 332 | 331
2016-09-09 23:00 | 321 | 319
2016-09-09 23:30 | 322 | 320
2016-09-10 | 315 | 312
2016-09-10 00:30 | 307 | 304
2016-09-10 01:00 | 297 | 294
2016-09-10 01:30 | 295 | 292
2016-09-10 02:00 | 291 | 287
2016-09-10 02:30 | 286 | 282
2016-09-10 03:00 | 282 | 277
2016-09-10 03:30 | 278 | 273
2016-09-10 04:00 | 271 | 266
2016-09-10 04:30 | 273 | 268
2016-09-10 05:00 | 273 | 268
2016-09-10 05:30 | 274 | 268
2016-09-10 06:00 | 277 | 271
2016-09-10 06:30 | 374 | 370
2016-09-10 07:00 | 420 | 418
2016-09-10 07:30 | 451 | 451
2016-09-10 08:00 | 477 | 476
2016-09-10 08:30 | 490 | 490
2016-09-10 09:00 | 489 | 489
2016-09-10 09:30 | 501 | 501
2016-09-10 10:00 | 513 | 513
2016-09-10 10:30 | 508 | 508
2016-09-10 11:00 | 480 | 480
2016-09-10 11:30 | 337 | 337
2016-09-10 12:00 | 328 | 327
2016-09-10 12:30 | 325 | 324
2016-09-10 13:00 | 324 | 322
2016-09-10 13:30 | 330 | 328
2016-09-10 14:00 | 328 | 327
2016-09-10 14:30 | 319 | 317
2016-09-10 15:00 | 322 | 320
2016-09-10 15:30 | 329 | 327
2016-09-10 16:00 | 321 | 319
2016-09-10 16:30 | 323 | 321
2016-09-10 17:00 | 326 | 324
2016-09-10 17:30 | 342 | 341
2016-09-10 18:00 | 345 | 343
2016-09-10 18:30 | 355 | 354
2016-09-10 19:00 | 361 | 360
2016-09-10 19:30 | 366 | 365
2016-09-10 20:00 | 358 | 357
2016-09-10 20:30 | 348 | 347
2016-09-10 21:00 | 344 | 343
2016-09-10 21:30 | 342 | 341
2016-09-10 22:00 | 333 | 331
2016-09-10 22:30 | 324 | 322
2016-09-10 23:00 | 311 | 309
2016-09-10 23:30 | 306 | 304
2016-09-11 | 308 | 305
2016-09-11 00:30 | 304 | 301
2016-09-11 01:00 | 299 | 296
2016-09-11 01:30 | 293 | 290
2016-09-11 02:00 | 285 | 282
2016-09-11 02:30 | 283 | 280
2016-09-11 03:00 | 278 | 275
2016-09-11 03:30 | 275 | 272
2016-09-11 04:00 | 274 | 269
2016-09-11 04:30 | 272 | 268
2016-09-11 05:00 | 255 | 251
2016-09-11 05:30 | 252 | 247
2016-09-11 06:00 | 257 | 251
2016-09-11 06:30 | 271 | 264
2016-09-11 07:00 | 282 | 276
2016-09-11 07:30 | 287 | 282
2016-09-11 08:00 | 296 | 292
2016-09-11 08:30 | 305 | 301
2016-09-11 09:00 | 309 | 305
2016-09-11 09:30 | 319 | 316
2016-09-11 10:00 | 323 | 320
2016-09-11 10:30 | 325 | 322
2016-09-11 11:00 | 319 | 317
2016-09-11 11:30 | 315 | 313
2016-09-11 12:00 | 315 | 312
2016-09-11 12:30 | 319 | 316
2016-09-11 13:00 | 318 | 316
2016-09-11 13:30 | 328 | 325
2016-09-11 14:00 | 337 | 336
2016-09-11 14:30 | 320 | 318
2016-09-11 15:00 | 326 | 324
2016-09-11 15:30 | 338 | 336
2016-09-11 16:00 | 331 | 329
2016-09-11 16:30 | 343 | 341
2016-09-11 17:00 | 352 | 350
2016-09-11 17:30 | 373 | 372
2016-09-11 18:00 | 379 | 379
2016-09-11 18:30 | 371 | 370
2016-09-11 19:00 | 401 | 400
2016-09-11 19:30 | 403 | 403
2016-09-11 20:00 | 395 | 395
2016-09-11 20:30 | 383 | 382
2016-09-11 21:00 | 383 | 382
2016-09-11 21:30 | 365 | 364
2016-09-11 22:00 | 353 | 352
2016-09-11 22:30 | 333 | 331
2016-09-11 23:00 | 320 | 318
2016-09-11 23:30 | 305 | 302
2016-09-12 | 311 | 307
2016-09-12 00:30 | 311 | 307
2016-09-12 01:00 | 296 | 292
2016-09-12 01:30 | 290 | 286
2016-09-12 02:00 | 288 | 283
2016-09-12 02:30 | 286 | 281
2016-09-12 03:00 | 282 | 277
2016-09-12 03:30 | 281 | 276
2016-09-12 04:00 | 279 | 273
2016-09-12 04:30 | 283 | 278
2016-09-12 05:00 | 289 | 283
2016-09-12 05:30 | 296 | 291
2016-09-12 06:00 | 307 | 303
2016-09-12 06:30 | 324 | 321
2016-09-12 07:00 | 339 | 336
2016-09-12 07:30 | 375 | 373
2016-09-12 08:00 | 386 | 385
2016-09-12 08:30 | 388 | 387
2016-09-12 09:00 | 391 | 390
2016-09-12 09:30 | 386 | 386
2016-09-12 10:00 | 394 | 394
2016-09-12 10:30 | 387 | 387
2016-09-12 11:00 | 387 | 387
2016-09-12 11:30 | 384 | 384
2016-09-12 12:00 | 364 | 363
2016-09-12 12:30 | 355 | 354
2016-09-12 13:00 | 348 | 347
2016-09-12 13:30 | 352 | 351
2016-09-12 14:00 | 353 | 352
2016-09-12 14:30 | 362 | 360
2016-09-12 15:00 | 365 | 365
2016-09-12 15:30 | 338 | 337
2016-09-12 16:00 | 286 | 285
2016-09-12 16:30 | 237 | 234
2016-09-12 17:00 | 232 | 226
2016-09-12 17:30 | 235 | 228
2016-09-12 18:00 | 241 | 235
2016-09-12 18:30 | 251 | 245
2016-09-12 19:00 | 282 | 278
2016-09-12 19:30 | 279 | 275
2016-09-12 20:00 | 270 | 265
2016-09-12 20:30 | 254 | 249
2016-09-12 21:00 | 260 | 254
2016-09-12 21:30 | 299 | 295
2016-09-12 22:00 | 282 | 279
2016-09-12 22:30 | 228 | 222
2016-09-12 23:00 | 248 | 240
2016-09-12 23:30 | 224 | 216
2016-09-13 | 240 | 232
2016-09-13 00:30 | 234 | 226
2016-09-13 01:00 | 220 | 212
2016-09-13 01:30 | 220 | 211
2016-09-13 02:00 | 218 | 209
2016-09-13 02:30 | 207 | 198
2016-09-13 03:00 | 207 | 198
2016-09-13 03:30 | 211 | 201
2016-09-13 04:00 | 214 | 204
2016-09-13 04:30 | 217 | 206
2016-09-13 05:00 | 226 | 216
2016-09-13 05:30 | 239 | 229
2016-09-13 06:00 | 246 | 238
2016-09-13 06:30 | 237 | 229
2016-09-13 07:00 | 222 | 213
2016-09-13 07:30 | 240 | 232
2016-09-13 08:00 | 249 | 243
2016-09-13 08:30 | 265 | 259
2016-09-13 09:00 | 276 | 270
2016-09-13 09:30 | 272 | 266
2016-09-13 10:00 | 260 | 254
2016-09-13 10:30 | 262 | 256
2016-09-13 11:00 | 282 | 276
2016-09-13 11:30 | 269 | 264
2016-09-13 12:00 | 263 | 257
2016-09-13 12:30 | 267 | 261
2016-09-13 13:00 | 267 | 262
2016-09-13 13:30 | 257 | 251
2016-09-13 14:00 | 252 | 246
2016-09-13 14:30 | 237 | 230
2016-09-13 15:00 | 234 | 227
2016-09-13 15:30 | 237 | 233
2016-09-13 16:00 | 241 | 238
2016-09-13 16:30 | 244 | 242
2016-09-13 17:00 | 255 | 253
2016-09-13 17:30 | 276 | 274
2016-09-13 18:00 | 279 | 277
2016-09-13 18:30 | 276 | 272
2016-09-13 19:00 | 291 | 285
2016-09-13 19:30 | 279 | 273
2016-09-13 20:00 | 263 | 257
2016-09-13 20:30 | 254 | 246
2016-09-13 21:00 | 257 | 248
2016-09-13 21:30 | 301 | 292
2016-09-13 22:00 | 291 | 284
2016-09-13 22:30 | 245 | 237
2016-09-13 23:00 | 253 | 242
2016-09-13 23:30 | 276 | 267
2016-09-14 | 317 | 310
2016-09-14 00:30 | 312 | 307
2016-09-14 01:00 | 299 | 293
2016-09-14 01:30 | 293 | 287
2016-09-14 02:00 | 280 | 274
2016-09-14 02:30 | 280 | 273
2016-09-14 03:00 | 273 | 266
2016-09-14 03:30 | 272 | 265
2016-09-14 04:00 | 271 | 264
2016-09-14 04:30 | 276 | 269
2016-09-14 05:00 | 276 | 269
2016-09-14 05:30 | 282 | 275
2016-09-14 06:00 | 297 | 290
2016-09-14 06:30 | 306 | 301
2016-09-14 07:00 | 324 | 319
2016-09-14 07:30 | 358 | 354
2016-09-14 08:00 | 362 | 359
2016-09-14 08:30 | 358 | 355
2016-09-14 09:00 | 361 | 357
2016-09-14 09:30 | 368 | 364
2016-09-14 10:00 | 361 | 357
2016-09-14 10:30 | 366 | 362
2016-09-14 11:00 | 365 | 361
2016-09-14 11:30 | 367 | 363
2016-09-14 12:00 | 371 | 367
2016-09-14 12:30 | 378 | 374
2016-09-14 13:00 | 361 | 357
2016-09-14 13:30 | 357 | 353
2016-09-14 14:00 | 356 | 353
2016-09-14 14:30 | 359 | 355
2016-09-14 15:00 | 351 | 347
2016-09-14 15:30 | 358 | 354
2016-09-14 16:00 | 373 | 369
2016-09-14 16:30 | 360 | 356
2016-09-14 17:00 | 371 | 368
2016-09-14 17:30 | 379 | 376
2016-09-14 18:00 | 368 | 364
2016-09-14 18:30 | 384 | 380
2016-09-14 19:00 | 404 | 401
2016-09-14 19:30 | 406 | 403
2016-09-14 20:00 | 396 | 393
2016-09-14 20:30 | 384 | 380
2016-09-14 21:00 | 375 | 371
2016-09-14 21:30 | 358 | 354
2016-09-14 22:00 | 341 | 337
2016-09-14 22:30 | 321 | 316
2016-09-14 23:00 | 324 | 319
2016-09-14 23:30 | 311 | 304
2016-09-15 | 298 | 290
2016-09-15 00:30 | 299 | 290
2016-09-15 01:00 | 294 | 285
2016-09-15 01:30 | 286 | 278
2016-09-15 02:00 | 281 | 273
2016-09-15 02:30 | 273 | 264
2016-09-15 03:00 | 276 | 267
2016-09-15 03:30 | 279 | 270
2016-09-15 04:00 | 285 | 276
2016-09-15 04:30 | 292 | 284
2016-09-15 05:00 | 298 | 289
2016-09-15 05:30 | 307 | 300
2016-09-15 06:00 | 313 | 305
2016-09-15 06:30 | 336 | 329
2016-09-15 07:00 | 346 | 340
2016-09-15 07:30 | 360 | 354
2016-09-15 08:00 | 367 | 362
2016-09-15 08:30 | 371 | 365
2016-09-15 09:00 | 363 | 358
2016-09-15 09:30 | 364 | 359
2016-09-15 10:00 | 372 | 368
2016-09-15 10:30 | 368 | 364
2016-09-15 11:00 | 367 | 363
2016-09-15 11:30 | 366 | 362
2016-09-15 12:00 | 367 | 363
2016-09-15 12:30 | 382 | 378
2016-09-15 13:00 | 384 | 380
2016-09-15 13:30 | 383 | 379
2016-09-15 14:00 | 384 | 380
2016-09-15 14:30 | 376 | 372
2016-09-15 15:00 | 375 | 371
2016-09-15 15:30 | 369 | 366
2016-09-15 16:00 | 372 | 368
2016-09-15 16:30 | 386 | 382
2016-09-15 17:00 | 382 | 379
2016-09-15 17:30 | 393 | 391
2016-09-15 18:00 | 394 | 392
2016-09-15 18:30 | 413 | 411
2016-09-15 19:00 | 422 | 420
2016-09-15 19:30 | 415 | 412
2016-09-15 20:00 | 402 | 399
2016-09-15 20:30 | 397 | 394
2016-09-15 21:00 | 393 | 390
2016-09-15 21:30 | 370 | 367
2016-09-15 22:00 | 352 | 349
2016-09-15 22:30 | 348 | 345
2016-09-15 23:00 | 338 | 334
2016-09-15 23:30 | 330 | 326
2016-09-16 | 321 | 316
2016-09-16 00:30 | 318 | 313
2016-09-16 01:00 | 305 | 302
2016-09-16 01:30 | 291 | 287
2016-09-16 02:00 | 286 | 282
2016-09-16 02:30 | 282 | 277
2016-09-16 03:00 | 278 | 273
2016-09-16 03:30 | 280 | 276
2016-09-16 04:00 | 278 | 273
2016-09-16 04:30 | 278 | 272
2016-09-16 05:00 | 286 | 280
2016-09-16 05:30 | 297 | 290
2016-09-16 06:00 | 296 | 290
2016-09-16 06:30 | 303 | 298
2016-09-16 07:00 | 325 | 321
2016-09-16 07:30 | 357 | 354
2016-09-16 08:00 | 355 | 352
2016-09-16 08:30 | 371 | 369
2016-09-16 09:00 | 373 | 371
2016-09-16 09:30 | 377 | 375
2016-09-16 10:00 | 396 | 395
2016-09-16 10:30 | 397 | 396
2016-09-16 11:00 | 391 | 390
2016-09-16 11:30 | 386 | 385
2016-09-16 12:00 | 393 | 391
2016-09-16 12:30 | 380 | 379
2016-09-16 13:00 | 373 | 371
2016-09-16 13:30 | 374 | 373
2016-09-16 14:00 | 392 | 391
2016-09-16 14:30 | 376 | 374
2016-09-16 15:00 | 363 | 362
2016-09-16 15:30 | 364 | 362
2016-09-16 16:00 | 371 | 369
2016-09-16 16:30 | 377 | 376
2016-09-16 17:00 | 381 | 379
2016-09-16 17:30 | 369 | 367
2016-09-16 18:00 | 362 | 361
2016-09-16 18:30 | 372 | 371
2016-09-16 19:00 | 381 | 379
2016-09-16 19:30 | 370 | 369
2016-09-16 20:00 | 373 | 372
2016-09-16 20:30 | 366 | 364
2016-09-16 21:00 | 351 | 348
2016-09-16 21:30 | 336 | 333
2016-09-16 22:00 | 324 | 321
2016-09-16 22:30 | 327 | 324
2016-09-16 23:00 | 319 | 316
2016-09-16 23:30 | 319 | 317
2016-09-17 | 312 | 309
2016-09-17 00:30 | 306 | 303
2016-09-17 01:00 | 290 | 287
2016-09-17 01:30 | 285 | 280
2016-09-17 02:00 | 277 | 273
2016-09-17 02:30 | 270 | 266
2016-09-17 03:00 | 268 | 264
2016-09-17 03:30 | 269 | 264
2016-09-17 04:00 | 263 | 258
2016-09-17 04:30 | 266 | 261
2016-09-17 05:00 | 269 | 264
2016-09-17 05:30 | 266 | 261
2016-09-17 06:00 | 267 | 262
2016-09-17 06:30 | 274 | 269
2016-09-17 07:00 | 285 | 280
2016-09-17 07:30 | 294 | 289
2016-09-17 08:00 | 306 | 302
2016-09-17 08:30 | 338 | 334
2016-09-17 09:00 | 351 | 347
2016-09-17 09:30 | 355 | 351
2016-09-17 10:00 | 355 | 352
2016-09-17 10:30 | 354 | 351
2016-09-17 11:00 | 355 | 351
2016-09-17 11:30 | 355 | 352
2016-09-17 12:00 | 350 | 348
2016-09-17 12:30 | 355 | 352
2016-09-17 13:00 | 348 | 346
2016-09-17 13:30 | 354 | 352
2016-09-17 14:00 | 360 | 358
2016-09-17 14:30 | 348 | 346
2016-09-17 15:00 | 338 | 336
2016-09-17 15:30 | 341 | 338
2016-09-17 16:00 | 347 | 345
2016-09-17 16:30 | 353 | 351
2016-09-17 17:00 | 353 | 350
2016-09-17 17:30 | 362 | 360
2016-09-17 18:00 | 363 | 361
2016-09-17 18:30 | 364 | 362
2016-09-17 19:00 | 377 | 375
2016-09-17 19:30 | 382 | 380
2016-09-17 20:00 | 380 | 377
2016-09-17 20:30 | 366 | 363
2016-09-17 21:00 | 355 | 352
2016-09-17 21:30 | 342 | 339
2016-09-17 22:00 | 334 | 331
2016-09-17 22:30 | 336 | 333
2016-09-17 23:00 | 322 | 319
2016-09-17 23:30 | 312 | 310
2016-09-18 | 307 | 304
2016-09-18 00:30 | 297 | 294
2016-09-18 01:00 | 284 | 281
2016-09-18 01:30 | 278 | 274
2016-09-18 02:00 | 280 | 275
2016-09-18 02:30 | 270 | 265
2016-09-18 03:00 | 267 | 261
2016-09-18 03:30 | 274 | 268
2016-09-18 04:00 | 269 | 263
2016-09-18 04:30 | 271 | 265
2016-09-18 05:00 | 268 | 263
2016-09-18 05:30 | 262 | 255
2016-09-18 06:00 | 260 | 253
2016-09-18 06:30 | 266 | 259
2016-09-18 07:00 | 270 | 264
2016-09-18 07:30 | 277 | 271
2016-09-18 08:00 | 290 | 284
2016-09-18 08:30 | 304 | 299
2016-09-18 09:00 | 307 | 302
2016-09-18 09:30 | 302 | 296
2016-09-18 10:00 | 316 | 311
2016-09-18 10:30 | 324 | 319
2016-09-18 11:00 | 321 | 316
2016-09-18 11:30 | 323 | 319
2016-09-18 12:00 | 313 | 309
2016-09-18 12:30 | 313 | 308
2016-09-18 13:00 | 320 | 317
2016-09-18 13:30 | 329 | 325
2016-09-18 14:00 | 324 | 319
2016-09-18 14:30 | 315 | 311
2016-09-18 15:00 | 317 | 314
2016-09-18 15:30 | 322 | 317
2016-09-18 16:00 | 330 | 326
2016-09-18 16:30 | 332 | 328
2016-09-18 17:00 | 329 | 325
2016-09-18 17:30 | 346 | 343
2016-09-18 18:00 | 363 | 360
2016-09-18 18:30 | 374 | 371
2016-09-18 19:00 | 385 | 383
2016-09-18 19:30 | 379 | 377
2016-09-18 20:00 | 363 | 361
2016-09-18 20:30 | 358 | 355
2016-09-18 21:00 | 347 | 345
2016-09-18 21:30 | 340 | 338
2016-09-18 22:00 | 339 | 336
2016-09-18 22:30 | 342 | 339
2016-09-18 23:00 | 334 | 332
2016-09-18 23:30 | 321 | 319
2016-09-19 | 309 | 306
2016-09-19 00:30 | 301 | 298
2016-09-19 01:00 | 292 | 289
2016-09-19 01:30 | 286 | 283
2016-09-19 02:00 | 287 | 284
2016-09-19 02:30 | 280 | 277
2016-09-19 03:00 | 282 | 278
2016-09-19 03:30 | 274 | 270
2016-09-19 04:00 | 276 | 272
2016-09-19 04:30 | 279 | 275
2016-09-19 05:00 | 284 | 281
2016-09-19 05:30 | 292 | 288
2016-09-19 06:00 | 299 | 296
2016-09-19 06:30 | 317 | 314
2016-09-19 07:00 | 324 | 321
2016-09-19 07:30 | 361 | 358
2016-09-19 08:00 | 369 | 366
2016-09-19 08:30 | 371 | 369
2016-09-19 09:00 | 368 | 365
2016-09-19 09:30 | 375 | 372
2016-09-19 10:00 | 378 | 375
2016-09-19 10:30 | 387 | 385
2016-09-19 11:00 | 386 | 383
2016-09-19 11:30 | 386 | 382
2016-09-19 12:00 | 386 | 382
2016-09-19 12:30 | 398 | 395
2016-09-19 13:00 | 391 | 388
2016-09-19 13:30 | 387 | 384
2016-09-19 14:00 | 383 | 379
2016-09-19 14:30 | 386 | 382
2016-09-19 15:00 | 384 | 381
2016-09-19 15:30 | 383 | 380
2016-09-19 16:00 | 390 | 387
2016-09-19 16:30 | 395 | 392
2016-09-19 17:00 | 389 | 385
2016-09-19 17:30 | 387 | 384
2016-09-19 18:00 | 397 | 394
2016-09-19 18:30 | 418 | 415
2016-09-19 19:00 | 427 | 425
2016-09-19 19:30 | 426 | 423
2016-09-19 20:00 | 411 | 409
2016-09-19 20:30 | 399 | 396
2016-09-19 21:00 | 388 | 385
2016-09-19 21:30 | 376 | 373
2016-09-19 22:00 | 361 | 358
2016-09-19 22:30 | 343 | 340
2016-09-19 23:00 | 330 | 327
2016-09-19 23:30 | 322 | 319
2016-09-20 | 308 | 304
2016-09-20 00:30 | 296 | 292
2016-09-20 01:00 | 303 | 299
2016-09-20 01:30 | 300 | 296
2016-09-20 02:00 | 293 | 289
2016-09-20 02:30 | 288 | 284
2016-09-20 03:00 | 279 | 275
2016-09-20 03:30 | 269 | 265
2016-09-20 04:00 | 269 | 264
2016-09-20 04:30 | 276 | 271
2016-09-20 05:00 | 275 | 270
2016-09-20 05:30 | 281 | 277
2016-09-20 06:00 | 298 | 294
2016-09-20 06:30 | 314 | 310
2016-09-20 07:00 | 319 | 315
2016-09-20 07:30 | 344 | 340
2016-09-20 08:00 | 357 | 353
2016-09-20 08:30 | 389 | 386
2016-09-20 09:00 | 394 | 390
2016-09-20 09:30 | 396 | 394
2016-09-20 10:00 | 392 | 389
2016-09-20 10:30 | 386 | 384
2016-09-20 11:00 | 386 | 384
2016-09-20 11:30 | 380 | 378
2016-09-20 12:00 | 358 | 355
2016-09-20 12:30 | 351 | 348
2016-09-20 13:00 | 352 | 349
2016-09-20 13:30 | 356 | 353
2016-09-20 14:00 | 350 | 347
2016-09-20 14:30 | 336 | 333
2016-09-20 15:00 | 334 | 331
2016-09-20 15:30 | 325 | 321
2016-09-20 16:00 | 301 | 298
2016-09-20 16:30 | 280 | 277
2016-09-20 17:00 | 260 | 255
2016-09-20 17:30 | 277 | 271
2016-09-20 18:00 | 251 | 245
2016-09-20 18:30 | 252 | 246
2016-09-20 19:00 | 260 | 253
2016-09-20 19:30 | 262 | 255
2016-09-20 20:00 | 254 | 247
2016-09-20 20:30 | 255 | 248
2016-09-20 21:00 | 264 | 257
2016-09-20 21:30 | 281 | 274
2016-09-20 22:00 | 289 | 283
2016-09-20 22:30 | 232 | 225
2016-09-20 23:00 | 265 | 257
2016-09-20 23:30 | 255 | 247
2016-09-21 | 250 | 241
2016-09-21 00:30 | 239 | 230
2016-09-21 01:00 | 225 | 215
2016-09-21 01:30 | 220 | 210
2016-09-21 02:00 | 225 | 215
2016-09-21 02:30 | 216 | 206
2016-09-21 03:00 | 218 | 208
2016-09-21 03:30 | 215 | 204
2016-09-21 04:00 | 209 | 198
2016-09-21 04:30 | 210 | 199
2016-09-21 05:00 | 209 | 198
2016-09-21 05:30 | 217 | 206
2016-09-21 06:00 | 223 | 213
2016-09-21 06:30 | 236 | 227
2016-09-21 07:00 | 235 | 227
2016-09-21 07:30 | 262 | 254
2016-09-21 08:00 | 249 | 240
2016-09-21 08:30 | 249 | 240
2016-09-21 09:00 | 249 | 239
2016-09-21 09:30 | 228 | 218
2016-09-21 10:00 | 228 | 216
2016-09-21 10:30 | 226 | 214
2016-09-21 11:00 | 233 | 222
2016-09-21 11:30 | 241 | 230
2016-09-21 12:00 | 302 | 294
2016-09-21 12:30 | 296 | 290
2016-09-21 13:00 | 297 | 290
2016-09-21 13:30 | 300 | 293
2016-09-21 14:00 | 279 | 272
2016-09-21 14:30 | 236 | 226
2016-09-21 15:00 | 279 | 269
2016-09-21 15:30 | 252 | 243
2016-09-21 16:00 | 233 | 223
2016-09-21 16:30 | 242 | 231
2016-09-21 17:00 | 241 | 231
2016-09-21 17:30 | 304 | 297
2016-09-21 18:00 | 291 | 284
2016-09-21 18:30 | 265 | 258
2016-09-21 19:00 | 270 | 262
2016-09-21 19:30 | 262 | 254
2016-09-21 20:00 | 253 | 245
2016-09-21 20:30 | 258 | 248
2016-09-21 21:00 | 249 | 239
2016-09-21 21:30 | 244 | 235
2016-09-21 22:00 | 268 | 259
2016-09-21 22:30 | 232 | 222
2016-09-21 23:00 | 228 | 216
2016-09-21 23:30 | 211 | 199
2016-09-22 | 215 | 203
2016-09-22 00:30 | 245 | 234
2016-09-22 01:00 | 228 | 218
2016-09-22 01:30 | 229 | 219
2016-09-22 02:00 | 219 | 207
2016-09-22 02:30 | 219 | 208
2016-09-22 03:00 | 216 | 204
2016-09-22 03:30 | 219 | 208
2016-09-22 04:00 | 221 | 210
2016-09-22 04:30 | 218 | 207
2016-09-22 05:00 | 222 | 211
2016-09-22 05:30 | 228 | 218
2016-09-22 06:00 | 235 | 225
2016-09-22 06:30 | 186 | 173
2016-09-22 07:00 | 197 | 184
2016-09-22 07:30 | 265 | 255
2016-09-22 08:00 | 254 | 245
2016-09-22 08:30 | 261 | 254
2016-09-22 09:00 | 260 | 251
2016-09-22 09:30 | 291 | 282
2016-09-22 10:00 | 265 | 256
2016-09-22 10:30 | 276 | 268
2016-09-22 11:00 | 268 | 260
2016-09-22 11:30 | 254 | 246
2016-09-22 12:00 | 255 | 247
2016-09-22 12:30 | 257 | 249
2016-09-22 13:00 | 266 | 259
2016-09-22 13:30 | 301 | 294
2016-09-22 14:00 | 306 | 301
2016-09-22 14:30 | 301 | 296
2016-09-22 15:00 | 314 | 309
2016-09-22 15:30 | 319 | 314
2016-09-22 16:00 | 278 | 272
2016-09-22 16:30 | 272 | 266
2016-09-22 17:00 | 266 | 260
2016-09-22 17:30 | 273 | 266
2016-09-22 18:00 | 280 | 273
2016-09-22 18:30 | 271 | 265
2016-09-22 19:00 | 258 | 251
2016-09-22 19:30 | 290 | 284
2016-09-22 20:00 | 311 | 306
2016-09-22 20:30 | 273 | 268
2016-09-22 21:00 | 267 | 261
2016-09-22 21:30 | 260 | 253
2016-09-22 22:00 | 285 | 279
2016-09-22 22:30 | 238 | 231
2016-09-22 23:00 | 215 | 207
2016-09-22 23:30 | 268 | 260
2016-09-23 | 323 | 318
2016-09-23 00:30 | 308 | 304
2016-09-23 01:00 | 296 | 292
2016-09-23 01:30 | 293 | 289
2016-09-23 02:00 | 286 | 281
2016-09-23 02:30 | 288 | 282
2016-09-23 03:00 | 289 | 283
2016-09-23 03:30 | 286 | 280
2016-09-23 04:00 | 283 | 277
2016-09-23 04:30 | 290 | 283
2016-09-23 05:00 | 294 | 288
2016-09-23 05:30 | 298 | 292
2016-09-23 06:00 | 302 | 296
2016-09-23 06:30 | 311 | 306
2016-09-23 07:00 | 320 | 316
2016-09-23 07:30 | 337 | 334
2016-09-23 08:00 | 351 | 349
2016-09-23 08:30 | 362 | 359
2016-09-23 09:00 | 359 | 357
2016-09-23 09:30 | 368 | 366
2016-09-23 10:00 | 369 | 367
2016-09-23 10:30 | 365 | 363
2016-09-23 11:00 | 363 | 361
2016-09-23 11:30 | 366 | 365
2016-09-23 12:00 | 370 | 369
2016-09-23 12:30 | 370 | 370
2016-09-23 13:00 | 366 | 365
2016-09-23 13:30 | 371 | 369
2016-09-23 14:00 | 365 | 364
2016-09-23 14:30 | 368 | 368
2016-09-23 15:00 | 369 | 368
2016-09-23 15:30 | 371 | 370
2016-09-23 16:00 | 384 | 384
2016-09-23 16:30 | 389 | 388
2016-09-23 17:00 | 394 | 393
2016-09-23 17:30 | 401 | 401
2016-09-23 18:00 | 401 | 400
2016-09-23 18:30 | 403 | 403
2016-09-23 19:00 | 410 | 410
2016-09-23 19:30 | 416 | 416
2016-09-23 20:00 | 404 | 404
2016-09-23 20:30 | 406 | 406
2016-09-23 21:00 | 399 | 398
2016-09-23 21:30 | 386 | 384
2016-09-23 22:00 | 371 | 369
2016-09-23 22:30 | 365 | 362
2016-09-23 23:00 | 355 | 352
2016-09-23 23:30 | 337 | 334
2016-09-24 | 325 | 320
2016-09-24 00:30 | 317 | 312
2016-09-24 01:00 | 307 | 302
2016-09-24 01:30 | 296 | 291
2016-09-24 02:00 | 291 | 285
2016-09-24 02:30 | 290 | 283
2016-09-24 03:00 | 285 | 278
2016-09-24 03:30 | 283 | 275
2016-09-24 04:00 | 283 | 275
2016-09-24 04:30 | 290 | 282
2016-09-24 05:00 | 286 | 278
2016-09-24 05:30 | 296 | 288
2016-09-24 06:00 | 293 | 286
2016-09-24 06:30 | 289 | 281
2016-09-24 07:00 | 305 | 297
2016-09-24 07:30 | 315 | 308
2016-09-24 08:00 | 330 | 324
2016-09-24 08:30 | 352 | 348
2016-09-24 09:00 | 370 | 366
2016-09-24 09:30 | 365 | 361
2016-09-24 10:00 | 350 | 346
2016-09-24 10:30 | 344 | 340
2016-09-24 11:00 | 346 | 341
2016-09-24 11:30 | 343 | 338
2016-09-24 12:00 | 339 | 335
2016-09-24 12:30 | 341 | 336
2016-09-24 13:00 | 341 | 337
2016-09-24 13:30 | 345 | 340
2016-09-24 14:00 | 342 | 338
2016-09-24 14:30 | 338 | 333
2016-09-24 15:00 | 344 | 341
2016-09-24 15:30 | 355 | 351
2016-09-24 16:00 | 351 | 348
2016-09-24 16:30 | 358 | 355
2016-09-24 17:00 | 375 | 372
2016-09-24 17:30 | 386 | 384
2016-09-24 18:00 | 400 | 398
2016-09-24 18:30 | 401 | 400
2016-09-24 19:00 | 408 | 406
2016-09-24 19:30 | 412 | 411
2016-09-24 20:00 | 404 | 403
2016-09-24 20:30 | 392 | 391
2016-09-24 21:00 | 379 | 377
2016-09-24 21:30 | 373 | 371
2016-09-24 22:00 | 360 | 357
2016-09-24 22:30 | 350 | 347
2016-09-24 23:00 | 335 | 332
2016-09-24 23:30 | 320 | 316
2016-09-25 | 310 | 305
2016-09-25 00:30 | 304 | 298
2016-09-25 01:00 | 296 | 290
2016-09-25 01:30 | 295 | 288
2016-09-25 02:00 | 288 | 281
2016-09-25 02:30 | 285 | 278
2016-09-25 03:00 | 287 | 281
2016-09-25 03:30 | 283 | 276
2016-09-25 04:00 | 279 | 272
2016-09-25 04:30 | 286 | 279
2016-09-25 05:00 | 291 | 284
2016-09-25 05:30 | 287 | 280
2016-09-25 06:00 | 280 | 273
2016-09-25 06:30 | 278 | 271
2016-09-25 07:00 | 289 | 281
2016-09-25 07:30 | 297 | 290
2016-09-25 08:00 | 303 | 297
2016-09-25 08:30 | 309 | 303
2016-09-25 09:00 | 306 | 301
2016-09-25 09:30 | 312 | 307
2016-09-25 10:00 | 316 | 311
2016-09-25 10:30 | 320 | 315
2016-09-25 11:00 | 313 | 309
2016-09-25 11:30 | 322 | 317
2016-09-25 12:00 | 326 | 321
2016-09-25 12:30 | 328 | 323
2016-09-25 13:00 | 342 | 338
2016-09-25 13:30 | 343 | 340
2016-09-25 14:00 | 342 | 339
2016-09-25 14:30 | 336 | 333
2016-09-25 15:00 | 337 | 334
2016-09-25 15:30 | 349 | 346
2016-09-25 16:00 | 362 | 359
2016-09-25 16:30 | 368 | 366
2016-09-25 17:00 | 379 | 377
2016-09-25 17:30 | 389 | 388
2016-09-25 18:00 | 396 | 395
2016-09-25 18:30 | 404 | 403
2016-09-25 19:00 | 413 | 412
2016-09-25 19:30 | 419 | 418
2016-09-25 20:00 | 414 | 414
2016-09-25 20:30 | 426 | 425
2016-09-25 21:00 | 419 | 419
2016-09-25 21:30 | 392 | 391
2016-09-25 22:00 | 378 | 376
2016-09-25 22:30 | 362 | 359
2016-09-25 23:00 | 348 | 346
2016-09-25 23:30 | 336 | 333
2016-09-26 | 323 | 319
2016-09-26 00:30 | 322 | 318
2016-09-26 01:00 | 305 | 301
2016-09-26 01:30 | 300 | 294
2016-09-26 02:00 | 302 | 296
2016-09-26 02:30 | 301 | 296
2016-09-26 03:00 | 296 | 290
2016-09-26 03:30 | 295 | 290
2016-09-26 04:00 | 287 | 281
2016-09-26 04:30 | 281 | 274
2016-09-26 05:00 | 285 | 278
2016-09-26 05:30 | 292 | 285
2016-09-26 06:00 | 298 | 292
2016-09-26 06:30 | 315 | 310
2016-09-26 07:00 | 331 | 326
2016-09-26 07:30 | 343 | 339
2016-09-26 08:00 | 361 | 358
2016-09-26 08:30 | 370 | 367
2016-09-26 09:00 | 370 | 367
2016-09-26 09:30 | 374 | 371
2016-09-26 10:00 | 375 | 373
2016-09-26 10:30 | 374 | 372
2016-09-26 11:00 | 376 | 373
2016-09-26 11:30 | 379 | 377
2016-09-26 12:00 | 385 | 383
2016-09-26 12:30 | 396 | 394
2016-09-26 13:00 | 409 | 408
2016-09-26 13:30 | 414 | 413
2016-09-26 14:00 | 400 | 399
2016-09-26 14:30 | 405 | 404
2016-09-26 15:00 | 408 | 407
2016-09-26 15:30 | 409 | 408
2016-09-26 16:00 | 417 | 416
2016-09-26 16:30 | 420 | 420
2016-09-26 17:00 | 415 | 415
2016-09-26 17:30 | 424 | 423
2016-09-26 18:00 | 420 | 420
2016-09-26 18:30 | 438 | 437
2016-09-26 19:00 | 453 | 452
2016-09-26 19:30 | 459 | 459
2016-09-26 20:00 | 443 | 443
2016-09-26 20:30 | 425 | 425
2016-09-26 21:00 | 411 | 411
2016-09-26 21:30 | 404 | 404
2016-09-26 22:00 | 395 | 395
2016-09-26 22:30 | 378 | 378
2016-09-26 23:00 | 355 | 354
2016-09-26 23:30 | 341 | 340
2016-09-27 | 328 | 327
2016-09-27 00:30 | 322 | 320
2016-09-27 01:00 | 315 | 313
2016-09-27 01:30 | 306 | 304
2016-09-27 02:00 | 304 | 302
2016-09-27 02:30 | 299 | 296
2016-09-27 03:00 | 303 | 298
2016-09-27 03:30 | 300 | 295
2016-09-27 04:00 | 295 | 290
2016-09-27 04:30 | 293 | 287
2016-09-27 05:00 | 298 | 292
2016-09-27 05:30 | 301 | 296
2016-09-27 06:00 | 306 | 301
2016-09-27 06:30 | 309 | 304
2016-09-27 07:00 | 323 | 319
2016-09-27 07:30 | 360 | 356
2016-09-27 08:00 | 366 | 364
2016-09-27 08:30 | 379 | 377
2016-09-27 09:00 | 384 | 383
2016-09-27 09:30 | 384 | 383
2016-09-27 10:00 | 381 | 380
2016-09-27 10:30 | 377 | 376
2016-09-27 11:00 | 382 | 380
2016-09-27 11:30 | 401 | 400
2016-09-27 12:00 | 415 | 414
2016-09-27 12:30 | 416 | 415
2016-09-27 13:00 | 420 | 419
2016-09-27 13:30 | 423 | 423
2016-09-27 14:00 | 422 | 422
2016-09-27 14:30 | 403 | 403
2016-09-27 15:00 | 407 | 407
2016-09-27 15:30 | 415 | 414
2016-09-27 16:00 | 425 | 424
2016-09-27 16:30 | 431 | 431
2016-09-27 17:00 | 434 | 433
2016-09-27 17:30 | 431 | 431
2016-09-27 18:00 | 428 | 428
2016-09-27 18:30 | 434 | 434
2016-09-27 19:00 | 438 | 438
2016-09-27 19:30 | 458 | 458
2016-09-27 20:00 | 449 | 449
2016-09-27 20:30 | 431 | 431
2016-09-27 21:00 | 422 | 422
2016-09-27 21:30 | 403 | 402
2016-09-27 22:00 | 389 | 388
2016-09-27 22:30 | 370 | 369
2016-09-27 23:00 | 352 | 350
2016-09-27 23:30 | 335 | 332
2016-09-28 | 327 | 324
2016-09-28 00:30 | 316 | 312
2016-09-28 01:00 | 307 | 304
2016-09-28 01:30 | 300 | 297
2016-09-28 02:00 | 302 | 298
2016-09-28 02:30 | 299 | 295
2016-09-28 03:00 | 299 | 295
2016-09-28 03:30 | 299 | 296
2016-09-28 04:00 | 290 | 286
2016-09-28 04:30 | 297 | 293
2016-09-28 05:00 | 306 | 303
2016-09-28 05:30 | 313 | 310
2016-09-28 06:00 | 313 | 310
2016-09-28 06:30 | 319 | 316
2016-09-28 07:00 | 331 | 327
2016-09-28 07:30 | 357 | 354
2016-09-28 08:00 | 367 | 365
2016-09-28 08:30 | 376 | 375
2016-09-28 09:00 | 383 | 382
2016-09-28 09:30 | 383 | 382
2016-09-28 10:00 | 384 | 383
2016-09-28 10:30 | 385 | 384
2016-09-28 11:00 | 381 | 380
2016-09-28 11:30 | 380 | 379
2016-09-28 12:00 | 379 | 377
2016-09-28 12:30 | 383 | 381
2016-09-28 13:00 | 384 | 383
2016-09-28 13:30 | 387 | 386
2016-09-28 14:00 | 380 | 379
2016-09-28 14:30 | 388 | 387
2016-09-28 15:00 | 392 | 391
2016-09-28 15:30 | 392 | 391
2016-09-28 16:00 | 404 | 403
2016-09-28 16:30 | 411 | 411
2016-09-28 17:00 | 415 | 414
2016-09-28 17:30 | 410 | 410
2016-09-28 18:00 | 409 | 408
2016-09-28 18:30 | 438 | 437
2016-09-28 19:00 | 458 | 458
2016-09-28 19:30 | 449 | 449
2016-09-28 20:00 | 438 | 438
2016-09-28 20:30 | 429 | 429
2016-09-28 21:00 | 415 | 415
2016-09-28 21:30 | 403 | 403
2016-09-28 22:00 | 389 | 388
2016-09-28 22:30 | 356 | 355
2016-09-28 23:00 | 361 | 359
2016-09-28 23:30 | 353 | 351
2016-09-29 | 335 | 333
2016-09-29 00:30 | 322 | 319
2016-09-29 01:00 | 288 | 285
2016-09-29 01:30 | 278 | 274
2016-09-29 02:00 | 270 | 265
2016-09-29 02:30 | 263 | 257
2016-09-29 03:00 | 272 | 266
2016-09-29 03:30 | 277 | 272
2016-09-29 04:00 | 277 | 272
2016-09-29 04:30 | 266 | 260
2016-09-29 05:00 | 228 | 221
2016-09-29 05:30 | 242 | 233
2016-09-29 06:00 | 254 | 246
2016-09-29 06:30 | 258 | 251
2016-09-29 07:00 | 230 | 222
2016-09-29 07:30 | 250 | 241
2016-09-29 08:00 | 261 | 254
2016-09-29 08:30 | 275 | 269
2016-09-29 09:00 | 284 | 279
2016-09-29 09:30 | 275 | 270
2016-09-29 10:00 | 282 | 274
2016-09-29 10:30 | 281 | 273
2016-09-29 11:00 | 262 | 254
2016-09-29 11:30 | 259 | 249
2016-09-29 12:00 | 259 | 251
2016-09-29 12:30 | 263 | 256
2016-09-29 13:00 | 265 | 257
2016-09-29 13:30 | 271 | 265
2016-09-29 14:00 | 269 | 262
2016-09-29 14:30 | 255 | 248
2016-09-29 15:00 | 253 | 246
2016-09-29 15:30 | 260 | 252
2016-09-29 16:00 | 261 | 254
2016-09-29 16:30 | 265 | 258
2016-09-29 17:00 | 270 | 264
2016-09-29 17:30 | 268 | 261
2016-09-29 18:00 | 279 | 273
2016-09-29 18:30 | 310 | 305
2016-09-29 19:00 | 323 | 320
2016-09-29 19:30 | 317 | 315
2016-09-29 20:00 | 307 | 305
2016-09-29 20:30 | 296 | 293
2016-09-29 21:00 | 281 | 277
2016-09-29 21:30 | 253 | 248
2016-09-29 22:00 | 236 | 228
2016-09-29 22:30 | 221 | 211
2016-09-29 23:00 | 211 | 199
2016-09-29 23:30 | 201 | 188
2016-09-30 | 197 | 183
2016-09-30 00:30 | 233 | 220
2016-09-30 01:00 | 223 | 215
2016-09-30 01:30 | 221 | 212
2016-09-30 02:00 | 214 | 205
2016-09-30 02:30 | 213 | 203
2016-09-30 03:00 | 213 | 204
2016-09-30 03:30 | 219 | 209
2016-09-30 04:00 | 221 | 213
2016-09-30 04:30 | 219 | 211
2016-09-30 05:00 | 219 | 211
2016-09-30 05:30 | 212 | 203
2016-09-30 06:00 | 228 | 220
2016-09-30 06:30 | 240 | 233
2016-09-30 07:00 | 253 | 246
2016-09-30 07:30 | 275 | 269
2016-09-30 08:00 | 289 | 285
2016-09-30 08:30 | 297 | 294
2016-09-30 09:00 | 307 | 304
2016-09-30 09:30 | 311 | 308
2016-09-30 10:00 | 317 | 315
2016-09-30 10:30 | 319 | 316
2016-09-30 11:00 | 311 | 309
2016-09-30 11:30 | 307 | 304
2016-09-30 12:00 | 310 | 307
2016-09-30 12:30 | 314 | 311
2016-09-30 13:00 | 314 | 311
2016-09-30 13:30 | 316 | 313
2016-09-30 14:00 | 308 | 305
2016-09-30 14:30 | 305 | 301
2016-09-30 15:00 | 311 | 308
2016-09-30 15:30 | 319 | 316
2016-09-30 16:00 | 324 | 322
2016-09-30 16:30 | 276 | 272
2016-09-30 17:00 | 284 | 280
2016-09-30 17:30 | 293 | 289
2016-09-30 18:00 | 294 | 290
2016-09-30 18:30 | 296 | 292
2016-09-30 19:00 | 281 | 278
2016-09-30 19:30 | 301 | 298
2016-09-30 20:00 | 294 | 291
2016-09-30 20:30 | 282 | 278
2016-09-30 21:00 | 272 | 267
2016-09-30 21:30 | 258 | 252
2016-09-30 22:00 | 246 | 239
2016-09-30 22:30 | 232 | 224
2016-09-30 23:00 | 224 | 215
2016-09-30 23:30 | 210 | 200
2016-10-01 | 197 | 185
2016-10-01 00:30 | 233 | 222
2016-10-01 01:00 | 317 | 311
2016-10-01 01:30 | 319 | 316
2016-10-01 02:00 | 304 | 300
2016-10-01 02:30 | 306 | 302
2016-10-01 03:00 | 301 | 297
2016-10-01 03:30 | 300 | 296
2016-10-01 04:00 | 302 | 298
2016-10-01 04:30 | 302 | 298
2016-10-01 05:00 | 302 | 299
2016-10-01 05:30 | 305 | 301
2016-10-01 06:00 | 302 | 298
2016-10-01 06:30 | 311 | 307
2016-10-01 07:00 | 322 | 319
2016-10-01 07:30 | 338 | 335
2016-10-01 08:00 | 350 | 348
2016-10-01 08:30 | 360 | 358
2016-10-01 09:00 | 367 | 365
2016-10-01 09:30 | 364 | 362
2016-10-01 10:00 | 363 | 361
2016-10-01 10:30 | 364 | 362
2016-10-01 11:00 | 352 | 350
2016-10-01 11:30 | 343 | 341
2016-10-01 12:00 | 351 | 349
2016-10-01 12:30 | 339 | 337
2016-10-01 13:00 | 340 | 337
2016-10-01 13:30 | 341 | 339
2016-10-01 14:00 | 342 | 340
2016-10-01 14:30 | 347 | 345
2016-10-01 15:00 | 356 | 354
2016-10-01 15:30 | 360 | 358
2016-10-01 16:00 | 369 | 367
2016-10-01 16:30 | 369 | 368
2016-10-01 17:00 | 372 | 371
2016-10-01 17:30 | 369 | 368
2016-10-01 18:00 | 375 | 373
2016-10-01 18:30 | 381 | 380
2016-10-01 19:00 | 394 | 393
2016-10-01 19:30 | 387 | 386
2016-10-01 20:00 | 371 | 370
2016-10-01 20:30 | 356 | 355
2016-10-01 21:00 | 360 | 358
2016-10-01 21:30 | 358 | 356
2016-10-01 22:00 | 341 | 339
2016-10-01 22:30 | 336 | 334
2016-10-01 23:00 | 332 | 330
2016-10-01 23:30 | 319 | 317
2016-10-02 | 291 | 288
2016-10-02 00:30 | 301 | 297
2016-10-02 01:00 | 297 | 293
2016-10-02 01:30 | 285 | 282
2016-10-02 02:00 | 283 | 279
2016-10-02 02:30 | 283 | 279
2016-10-02 03:00 | 275 | 270
2016-10-02 03:30 | 272 | 268
2016-10-02 04:00 | 273 | 268
2016-10-02 04:30 | 271 | 266
2016-10-02 05:00 | 269 | 264
2016-10-02 05:30 | 272 | 267
2016-10-02 06:00 | 273 | 268
2016-10-02 06:30 | 272 | 268
2016-10-02 07:00 | 285 | 280
2016-10-02 07:30 | 291 | 287
2016-10-02 08:00 | 294 | 291
2016-10-02 08:30 | 311 | 307
2016-10-02 09:00 | 314 | 311
2016-10-02 09:30 | 321 | 319
2016-10-02 10:00 | 321 | 318
2016-10-02 10:30 | 326 | 324
2016-10-02 11:00 | 331 | 329
2016-10-02 11:30 | 325 | 323
2016-10-02 12:00 | 321 | 319
2016-10-02 12:30 | 316 | 314
2016-10-02 13:00 | 303 | 300
2016-10-02 13:30 | 303 | 300
2016-10-02 14:00 | 306 | 303
2016-10-02 14:30 | 314 | 312
2016-10-02 15:00 | 321 | 318
2016-10-02 15:30 | 324 | 322
2016-10-02 16:00 | 333 | 330
2016-10-02 16:30 | 342 | 339
2016-10-02 17:00 | 346 | 344
2016-10-02 17:30 | 365 | 363
2016-10-02 18:00 | 383 | 382
2016-10-02 18:30 | 395 | 394
2016-10-02 19:00 | 408 | 408
2016-10-02 19:30 | 405 | 404
2016-10-02 20:00 | 390 | 389
2016-10-02 20:30 | 375 | 374
2016-10-02 21:00 | 368 | 367
2016-10-02 21:30 | 358 | 357
2016-10-02 22:00 | 346 | 345
2016-10-02 22:30 | 332 | 331
2016-10-02 23:00 | 319 | 316
2016-10-02 23:30 | 303 | 301
2016-10-03 | 297 | 293
2016-10-03 00:30 | 291 | 288
2016-10-03 01:00 | 280 | 276
2016-10-03 01:30 | 275 | 270
2016-10-03 02:00 | 274 | 269
2016-10-03 02:30 | 269 | 265
2016-10-03 03:00 | 267 | 262
2016-10-03 03:30 | 264 | 259
2016-10-03 04:00 | 269 | 263
2016-10-03 04:30 | 269 | 264
2016-10-03 05:00 | 274 | 269
2016-10-03 05:30 | 274 | 269
2016-10-03 06:00 | 269 | 264
2016-10-03 06:30 | 273 | 268
2016-10-03 07:00 | 279 | 274
2016-10-03 07:30 | 287 | 282
2016-10-03 08:00 | 292 | 288
2016-10-03 08:30 | 304 | 300
2016-10-03 09:00 | 303 | 299
2016-10-03 09:30 | 305 | 301
2016-10-03 10:00 | 303 | 300
2016-10-03 10:30 | 304 | 300
2016-10-03 11:00 | 312 | 309
2016-10-03 11:30 | 314 | 311
2016-10-03 12:00 | 321 | 318
2016-10-03 12:30 | 324 | 321
2016-10-03 13:00 | 321 | 318
2016-10-03 13:30 | 314 | 311
2016-10-03 14:00 | 329 | 326
2016-10-03 14:30 | 328 | 325
2016-10-03 15:00 | 338 | 336
2016-10-03 15:30 | 350 | 348
2016-10-03 16:00 | 356 | 354
2016-10-03 16:30 | 358 | 356
2016-10-03 17:00 | 383 | 382
2016-10-03 17:30 | 403 | 402
2016-10-03 18:00 | 389 | 388
2016-10-03 18:30 | 397 | 396
2016-10-03 19:00 | 437 | 436
2016-10-03 19:30 | 437 | 437
2016-10-03 20:00 | 424 | 424
2016-10-03 20:30 | 392 | 391
2016-10-03 21:00 | 394 | 393
2016-10-03 21:30 | 373 | 371
2016-10-03 22:00 | 363 | 361
2016-10-03 22:30 | 325 | 323
2016-10-03 23:00 | 325 | 322
2016-10-03 23:30 | 314 | 311
2016-10-04 | 306 | 302
2016-10-04 00:30 | 299 | 295
2016-10-04 01:00 | 293 | 288
2016-10-04 01:30 | 285 | 280
2016-10-04 02:00 | 279 | 274
2016-10-04 02:30 | 276 | 271
2016-10-04 03:00 | 279 | 274
2016-10-04 03:30 | 282 | 277
2016-10-04 04:00 | 281 | 275
2016-10-04 04:30 | 285 | 280
2016-10-04 05:00 | 293 | 288
2016-10-04 05:30 | 292 | 288
2016-10-04 06:00 | 289 | 285
2016-10-04 06:30 | 303 | 298
2016-10-04 07:00 | 305 | 301
2016-10-04 07:30 | 346 | 343
2016-10-04 08:00 | 356 | 354
2016-10-04 08:30 | 362 | 360
2016-10-04 09:00 | 364 | 362
2016-10-04 09:30 | 369 | 367
2016-10-04 10:00 | 365 | 363
2016-10-04 10:30 | 351 | 349
2016-10-04 11:00 | 351 | 348
2016-10-04 11:30 | 351 | 349
2016-10-04 12:00 | 360 | 358
2016-10-04 12:30 | 359 | 357
2016-10-04 13:00 | 355 | 353
2016-10-04 13:30 | 346 | 344
2016-10-04 14:00 | 349 | 346
2016-10-04 14:30 | 354 | 352
2016-10-04 15:00 | 362 | 360
2016-10-04 15:30 | 365 | 363
2016-10-04 16:00 | 380 | 379
2016-10-04 16:30 | 395 | 393
2016-10-04 17:00 | 398 | 397
2016-10-04 17:30 | 392 | 392
2016-10-04 18:00 | 385 | 384
2016-10-04 18:30 | 400 | 399
2016-10-04 19:00 | 414 | 414
2016-10-04 19:30 | 407 | 407
2016-10-04 20:00 | 396 | 395
2016-10-04 20:30 | 384 | 383
2016-10-04 21:00 | 392 | 391
2016-10-04 21:30 | 386 | 385
2016-10-04 22:00 | 361 | 360
2016-10-04 22:30 | 342 | 340
2016-10-04 23:00 | 330 | 327
2016-10-04 23:30 | 318 | 315
2016-10-05 | 310 | 307
2016-10-05 00:30 | 313 | 310
2016-10-05 01:00 | 311 | 308
2016-10-05 01:30 | 297 | 294
2016-10-05 02:00 | 283 | 279
2016-10-05 02:30 | 276 | 271
2016-10-05 03:00 | 273 | 268
2016-10-05 03:30 | 264 | 258
2016-10-05 04:00 | 266 | 261
2016-10-05 04:30 | 260 | 254
2016-10-05 05:00 | 268 | 262
2016-10-05 05:30 | 276 | 271
2016-10-05 06:00 | 281 | 276
2016-10-05 06:30 | 301 | 297
2016-10-05 07:00 | 298 | 295
2016-10-05 07:30 | 332 | 328
2016-10-05 08:00 | 344 | 342
2016-10-05 08:30 | 350 | 348
2016-10-05 09:00 | 353 | 351
2016-10-05 09:30 | 349 | 347
2016-10-05 10:00 | 341 | 339
2016-10-05 10:30 | 336 | 334
2016-10-05 11:00 | 337 | 335
2016-10-05 11:30 | 335 | 333
2016-10-05 12:00 | 336 | 333
2016-10-05 12:30 | 339 | 337
2016-10-05 13:00 | 343 | 340
2016-10-05 13:30 | 331 | 329
2016-10-05 14:00 | 332 | 330
2016-10-05 14:30 | 330 | 328
2016-10-05 15:00 | 330 | 328
2016-10-05 15:30 | 324 | 322
2016-10-05 16:00 | 268 | 264
2016-10-05 16:30 | 236 | 230
2016-10-05 17:00 | 227 | 220
2016-10-05 17:30 | 245 | 237
2016-10-05 18:00 | 245 | 239
2016-10-05 18:30 | 258 | 252
2016-10-05 19:00 | 265 | 260
2016-10-05 19:30 | 258 | 253
2016-10-05 20:00 | 252 | 247
2016-10-05 20:30 | 265 | 260
2016-10-05 21:00 | 277 | 272
2016-10-05 21:30 | 267 | 263
2016-10-05 22:00 | 289 | 284
2016-10-05 22:30 | 219 | 213
2016-10-05 23:00 | 214 | 205
2016-10-05 23:30 | 194 | 183
2016-10-06 | 190 | 178
2016-10-06 00:30 | 193 | 179
2016-10-06 01:00 | 194 | 181
2016-10-06 01:30 | 265 | 255
2016-10-06 02:00 | 264 | 257
2016-10-06 02:30 | 255 | 249
2016-10-06 03:00 | 251 | 245
2016-10-06 03:30 | 257 | 251
2016-10-06 04:00 | 248 | 241
2016-10-06 04:30 | 251 | 244
2016-10-06 05:00 | 244 | 237
2016-10-06 05:30 | 229 | 222
2016-10-06 06:00 | 240 | 232
2016-10-06 06:30 | 260 | 253
2016-10-06 07:00 | 283 | 277
2016-10-06 07:30 | 321 | 317
2016-10-06 08:00 | 327 | 324
2016-10-06 08:30 | 329 | 327
2016-10-06 09:00 | 328 | 325
2016-10-06 09:30 | 308 | 305
2016-10-06 10:00 | 311 | 308
2016-10-06 10:30 | 318 | 314
2016-10-06 11:00 | 315 | 312
2016-10-06 11:30 | 321 | 318
2016-10-06 12:00 | 326 | 323
2016-10-06 12:30 | 313 | 310
2016-10-06 13:00 | 324 | 321
2016-10-06 13:30 | 317 | 314
2016-10-06 14:00 | 316 | 313
2016-10-06 14:30 | 325 | 322
2016-10-06 15:00 | 328 | 325
2016-10-06 15:30 | 330 | 327
2016-10-06 16:00 | 335 | 332
2016-10-06 16:30 | 338 | 335
2016-10-06 17:00 | 351 | 348
2016-10-06 17:30 | 351 | 349
2016-10-06 18:00 | 379 | 378
2016-10-06 18:30 | 408 | 407
2016-10-06 19:00 | 428 | 428
2016-10-06 19:30 | 424 | 424
2016-10-06 20:00 | 398 | 398
2016-10-06 20:30 | 388 | 387
2016-10-06 21:00 | 375 | 374
2016-10-06 21:30 | 354 | 353
2016-10-06 22:00 | 350 | 348
2016-10-06 22:30 | 320 | 318
2016-10-06 23:00 | 301 | 299
2016-10-06 23:30 | 283 | 279
2016-10-07 | 282 | 277
2016-10-07 00:30 | 273 | 268
2016-10-07 01:00 | 264 | 259
2016-10-07 01:30 | 259 | 252
2016-10-07 02:00 | 260 | 254
2016-10-07 02:30 | 251 | 244
2016-10-07 03:00 | 251 | 244
2016-10-07 03:30 | 248 | 241
2016-10-07 04:00 | 248 | 241
2016-10-07 04:30 | 258 | 251
2016-10-07 05:00 | 260 | 254
2016-10-07 05:30 | 270 | 264
2016-10-07 06:00 | 272 | 267
2016-10-07 06:30 | 290 | 286
2016-10-07 07:00 | 305 | 300
2016-10-07 07:30 | 319 | 316
2016-10-07 08:00 | 328 | 324
2016-10-07 08:30 | 331 | 328
2016-10-07 09:00 | 334 | 332
2016-10-07 09:30 | 330 | 327
2016-10-07 10:00 | 324 | 321
2016-10-07 10:30 | 323 | 320
2016-10-07 11:00 | 316 | 314
2016-10-07 11:30 | 317 | 314
2016-10-07 12:00 | 322 | 319
2016-10-07 12:30 | 325 | 322
2016-10-07 13:00 | 320 | 318
2016-10-07 13:30 | 308 | 305
2016-10-07 14:00 | 310 | 306
2016-10-07 14:30 | 312 | 308
2016-10-07 15:00 | 277 | 274
2016-10-07 15:30 | 224 | 219
2016-10-07 16:00 | 236 | 229
2016-10-07 16:30 | 247 | 241
2016-10-07 17:00 | 255 | 250
2016-10-07 17:30 | 262 | 257
2016-10-07 18:00 | 260 | 256
2016-10-07 18:30 | 277 | 273
2016-10-07 19:00 | 292 | 289
2016-10-07 19:30 | 276 | 273
2016-10-07 20:00 | 262 | 259
2016-10-07 20:30 | 265 | 261
2016-10-07 21:00 | 258 | 254
2016-10-07 21:30 | 244 | 240
2016-10-07 22:00 | 233 | 228
2016-10-07 22:30 | 218 | 212
2016-10-07 23:00 | 209 | 203
2016-10-07 23:30 | 197 | 188
2016-10-08 | 187 | 177
2016-10-08 00:30 | 227 | 218
2016-10-08 01:00 | 255 | 249
2016-10-08 01:30 | 257 | 252
2016-10-08 02:00 | 254 | 250
2016-10-08 02:30 | 234 | 228
2016-10-08 03:00 | 226 | 219
2016-10-08 03:30 | 233 | 226
2016-10-08 04:00 | 227 | 221
2016-10-08 04:30 | 219 | 211
2016-10-08 05:00 | 227 | 219
2016-10-08 05:30 | 238 | 231
2016-10-08 06:00 | 238 | 232
2016-10-08 06:30 | 240 | 233
2016-10-08 07:00 | 248 | 242
2016-10-08 07:30 | 260 | 255
2016-10-08 08:00 | 267 | 262
2016-10-08 08:30 | 279 | 275
2016-10-08 09:00 | 286 | 282
2016-10-08 09:30 | 298 | 295
2016-10-08 10:00 | 290 | 287
2016-10-08 10:30 | 293 | 289
2016-10-08 11:00 | 294 | 291
2016-10-08 11:30 | 292 | 289
2016-10-08 12:00 | 293 | 290
2016-10-08 12:30 | 294 | 291
2016-10-08 13:00 | 298 | 295
2016-10-08 13:30 | 294 | 291
2016-10-08 14:00 | 291 | 288
2016-10-08 14:30 | 295 | 292
2016-10-08 15:00 | 288 | 285
2016-10-08 15:30 | 294 | 291
2016-10-08 16:00 | 302 | 299
2016-10-08 16:30 | 313 | 311
2016-10-08 17:00 | 328 | 326
2016-10-08 17:30 | 339 | 337
2016-10-08 18:00 | 356 | 354
2016-10-08 18:30 | 370 | 369
2016-10-08 19:00 | 379 | 378
2016-10-08 19:30 | 374 | 373
2016-10-08 20:00 | 363 | 362
2016-10-08 20:30 | 363 | 362
2016-10-08 21:00 | 359 | 357
2016-10-08 21:30 | 344 | 343
2016-10-08 22:00 | 325 | 323
2016-10-08 22:30 | 312 | 310
2016-10-08 23:00 | 304 | 302
2016-10-08 23:30 | 295 | 293
2016-10-09 | 281 | 277
2016-10-09 00:30 | 278 | 274
2016-10-09 01:00 | 268 | 263
2016-10-09 01:30 | 257 | 253
2016-10-09 02:00 | 254 | 249
2016-10-09 02:30 | 253 | 247
2016-10-09 03:00 | 252 | 247
2016-10-09 03:30 | 251 | 245
2016-10-09 04:00 | 246 | 240
2016-10-09 04:30 | 244 | 238
2016-10-09 05:00 | 249 | 242
2016-10-09 05:30 | 249 | 243
2016-10-09 06:00 | 250 | 244
2016-10-09 06:30 | 251 | 245
2016-10-09 07:00 | 253 | 246
2016-10-09 07:30 | 258 | 252
2016-10-09 08:00 | 267 | 262
2016-10-09 08:30 | 273 | 269
2016-10-09 09:00 | 278 | 274
2016-10-09 09:30 | 287 | 283
2016-10-09 10:00 | 287 | 283
2016-10-09 10:30 | 282 | 278
2016-10-09 11:00 | 285 | 281
2016-10-09 11:30 | 286 | 282
2016-10-09 12:00 | 284 | 281
2016-10-09 12:30 | 290 | 286
2016-10-09 13:00 | 294 | 291
2016-10-09 13:30 | 286 | 283
2016-10-09 14:00 | 279 | 276
2016-10-09 14:30 | 284 | 280
2016-10-09 15:00 | 288 | 285
2016-10-09 15:30 | 298 | 295
2016-10-09 16:00 | 311 | 308
2016-10-09 16:30 | 322 | 320
2016-10-09 17:00 | 333 | 332
2016-10-09 17:30 | 346 | 344
2016-10-09 18:00 | 356 | 355
2016-10-09 18:30 | 386 | 385
2016-10-09 19:00 | 407 | 406
2016-10-09 19:30 | 405 | 405
2016-10-09 20:00 | 393 | 393
2016-10-09 20:30 | 375 | 375
2016-10-09 21:00 | 363 | 362
2016-10-09 21:30 | 344 | 343
2016-10-09 22:00 | 324 | 322
2016-10-09 22:30 | 309 | 306
2016-10-09 23:00 | 295 | 293
2016-10-09 23:30 | 285 | 282
2016-10-10 | 277 | 273
2016-10-10 00:30 | 268 | 264
2016-10-10 01:00 | 228 | 223
2016-10-10 01:30 | 218 | 211
2016-10-10 02:00 | 215 | 207
2016-10-10 02:30 | 217 | 209
2016-10-10 03:00 | 210 | 203
2016-10-10 03:30 | 212 | 204
2016-10-10 04:00 | 215 | 207
2016-10-10 04:30 | 205 | 196
2016-10-10 05:00 | 161 | 149
2016-10-10 05:30 | 169 | 154
2016-10-10 06:00 | 185 | 171
2016-10-10 06:30 | 196 | 184
2016-10-10 07:00 | 174 | 161
2016-10-10 07:30 | 228 | 217
2016-10-10 08:00 | 230 | 222
2016-10-10 08:30 | 250 | 243
2016-10-10 09:00 | 248 | 242
2016-10-10 09:30 | 276 | 271
2016-10-10 10:00 | 335 | 331
2016-10-10 10:30 | 332 | 331
2016-10-10 11:00 | 318 | 317
2016-10-10 11:30 | 329 | 327
2016-10-10 12:00 | 344 | 342
2016-10-10 12:30 | 338 | 336
2016-10-10 13:00 | 326 | 325
2016-10-10 13:30 | 328 | 326
2016-10-10 14:00 | 255 | 253
2016-10-10 14:30 | 276 | 273
2016-10-10 15:00 | 236 | 233
2016-10-10 15:30 | 245 | 241
2016-10-10 16:00 | 263 | 259
2016-10-10 16:30 | 278 | 275
2016-10-10 17:00 | 291 | 288
2016-10-10 17:30 | 287 | 285
2016-10-10 18:00 | 295 | 293
2016-10-10 18:30 | 307 | 305
2016-10-10 19:00 | 338 | 336
2016-10-10 19:30 | 330 | 329
2016-10-10 20:00 | 299 | 297
2016-10-10 20:30 | 306 | 304
2016-10-10 21:00 | 290 | 288
2016-10-10 21:30 | 265 | 262
2016-10-10 22:00 | 332 | 329
2016-10-10 22:30 | 231 | 228
2016-10-10 23:00 | 200 | 193
2016-10-10 23:30 | 189 | 180
2016-10-11 | 203 | 193
2016-10-11 00:30 | 267 | 260
2016-10-11 01:00 | 250 | 246
2016-10-11 01:30 | 239 | 234
2016-10-11 02:00 | 237 | 232
2016-10-11 02:30 | 242 | 236
2016-10-11 03:00 | 229 | 223
2016-10-11 03:30 | 229 | 222
2016-10-11 04:00 | 225 | 218
2016-10-11 04:30 | 226 | 219
2016-10-11 05:00 | 205 | 197
2016-10-11 05:30 | 154 | 142
2016-10-11 06:00 | 129 | 109
2016-10-11 06:30 | 131 | 112
2016-10-11 07:00 | 155 | 138
2016-10-11 07:30 | 197 | 185
2016-10-11 08:00 | 195 | 187
2016-10-11 08:30 | 218 | 212
2016-10-11 09:00 | 193 | 186
2016-10-11 09:30 | 181 | 173
2016-10-11 10:00 | 188 | 180
2016-10-11 10:30 | 250 | 244
2016-10-11 11:00 | 272 | 269
2016-10-11 11:30 | 273 | 270
2016-10-11 12:00 | 281 | 278
2016-10-11 12:30 | 287 | 284
2016-10-11 13:00 | 282 | 280
2016-10-11 13:30 | 268 | 265
2016-10-11 14:00 | 267 | 264
2016-10-11 14:30 | 276 | 273
2016-10-11 15:00 | 291 | 288
2016-10-11 15:30 | 296 | 294
2016-10-11 16:00 | 308 | 305
2016-10-11 16:30 | 321 | 320
2016-10-11 17:00 | 345 | 343
2016-10-11 17:30 | 341 | 340
2016-10-11 18:00 | 332 | 331
2016-10-11 18:30 | 315 | 314
2016-10-11 19:00 | 308 | 306
2016-10-11 19:30 | 301 | 299
2016-10-11 20:00 | 360 | 358
2016-10-11 20:30 | 433 | 432
2016-10-11 21:00 | 417 | 417
2016-10-11 21:30 | 409 | 409
2016-10-11 22:00 | 390 | 390
2016-10-11 22:30 | 314 | 314
2016-10-11 23:00 | 306 | 304
2016-10-11 23:30 | 295 | 293
2016-10-12 | 298 | 296
2016-10-12 00:30 | 292 | 290
2016-10-12 01:00 | 282 | 280
2016-10-12 01:30 | 271 | 268
2016-10-12 02:00 | 266 | 263
2016-10-12 02:30 | 258 | 254
2016-10-12 03:00 | 257 | 252
2016-10-12 03:30 | 252 | 247
2016-10-12 04:00 | 251 | 246
2016-10-12 04:30 | 252 | 247
2016-10-12 05:00 | 264 | 259
2016-10-12 05:30 | 280 | 276
2016-10-12 06:00 | 271 | 268
2016-10-12 06:30 | 287 | 284
2016-10-12 07:00 | 269 | 266
2016-10-12 07:30 | 317 | 315
2016-10-12 08:00 | 358 | 356
2016-10-12 08:30 | 360 | 359
2016-10-12 09:00 | 349 | 348
2016-10-12 09:30 | 347 | 346
2016-10-12 10:00 | 339 | 337
2016-10-12 10:30 | 343 | 341
2016-10-12 11:00 | 355 | 353
2016-10-12 11:30 | 362 | 361
2016-10-12 12:00 | 372 | 371
2016-10-12 12:30 | 390 | 389
2016-10-12 13:00 | 392 | 392
2016-10-12 13:30 | 369 | 369
2016-10-12 14:00 | 367 | 366
2016-10-12 14:30 | 368 | 367
2016-10-12 15:00 | 377 | 376
2016-10-12 15:30 | 374 | 374
2016-10-12 16:00 | 394 | 393
2016-10-12 16:30 | 402 | 402
2016-10-12 17:00 | 411 | 411
2016-10-12 17:30 | 403 | 402
2016-10-12 18:00 | 325 | 325
2016-10-12 18:30 | 315 | 314
2016-10-12 19:00 | 334 | 331
2016-10-12 19:30 | 345 | 343
2016-10-12 20:00 | 360 | 358
2016-10-12 20:30 | 367 | 366
2016-10-12 21:00 | 429 | 428
2016-10-12 21:30 | 408 | 408
2016-10-12 22:00 | 377 | 376
2016-10-12 22:30 | 348 | 347
2016-10-12 23:00 | 310 | 308
2016-10-12 23:30 | 293 | 290
2016-10-13 | 280 | 275
2016-10-13 00:30 | 279 | 274
2016-10-13 01:00 | 269 | 263
2016-10-13 01:30 | 260 | 252
2016-10-13 02:00 | 257 | 249
2016-10-13 02:30 | 257 | 248
2016-10-13 03:00 | 251 | 242
2016-10-13 03:30 | 254 | 245
2016-10-13 04:00 | 258 | 249
2016-10-13 04:30 | 272 | 264
2016-10-13 05:00 | 265 | 257
2016-10-13 05:30 | 263 | 255
2016-10-13 06:00 | 262 | 255
2016-10-13 06:30 | 295 | 289
2016-10-13 07:00 | 248 | 242
2016-10-13 07:30 | 327 | 321
2016-10-13 08:00 | 388 | 385
2016-10-13 08:30 | 387 | 385
2016-10-13 09:00 | 391 | 389
2016-10-13 09:30 | 379 | 377
2016-10-13 10:00 | 386 | 384
2016-10-13 10:30 | 409 | 408
2016-10-13 11:00 | 407 | 406
2016-10-13 11:30 | 401 | 400
2016-10-13 12:00 | 413 | 412
2016-10-13 12:30 | 414 | 413
2016-10-13 13:00 | 406 | 404
2016-10-13 13:30 | 394 | 392
2016-10-13 14:00 | 397 | 395
2016-10-13 14:30 | 425 | 423
2016-10-13 15:00 | 420 | 419
2016-10-13 15:30 | 407 | 406
2016-10-13 16:00 | 402 | 401
2016-10-13 16:30 | 398 | 396
2016-10-13 17:00 | 420 | 418
2016-10-13 17:30 | 351 | 349
2016-10-13 18:00 | 326 | 323
2016-10-13 18:30 | 339 | 335
2016-10-13 19:00 | 365 | 362
2016-10-13 19:30 | 354 | 351
2016-10-13 20:00 | 358 | 355
2016-10-13 20:30 | 347 | 344
2016-10-13 21:00 | 414 | 411
2016-10-13 21:30 | 406 | 404
2016-10-13 22:00 | 380 | 378
2016-10-13 22:30 | 314 | 311
2016-10-13 23:00 | 291 | 286
2016-10-13 23:30 | 278 | 271
2016-10-14 | 255 | 247
2016-10-14 00:30 | 254 | 245
2016-10-14 01:00 | 251 | 241
2016-10-14 01:30 | 257 | 246
2016-10-14 02:00 | 250 | 239
2016-10-14 02:30 | 241 | 230
2016-10-14 03:00 | 252 | 241
2016-10-14 03:30 | 256 | 245
2016-10-14 04:00 | 252 | 241
2016-10-14 04:30 | 257 | 247
2016-10-14 05:00 | 254 | 244
2016-10-14 05:30 | 241 | 231
2016-10-14 06:00 | 237 | 226
2016-10-14 06:30 | 232 | 220
2016-10-14 07:00 | 247 | 236
2016-10-14 07:30 | 315 | 307
2016-10-14 08:00 | 355 | 350
2016-10-14 08:30 | 356 | 353
2016-10-14 09:00 | 359 | 356
2016-10-14 09:30 | 369 | 365
2016-10-14 10:00 | 361 | 358
2016-10-14 10:30 | 409 | 406
2016-10-14 11:00 | 482 | 480
2016-10-14 11:30 | 496 | 496
2016-10-14 12:00 | 495 | 494
2016-10-14 12:30 | 523 | 522
2016-10-14 13:00 | 526 | 523
2016-10-14 13:30 | 512 | 509
2016-10-14 14:00 | 512 | 508
2016-10-14 14:30 | 523 | 520
2016-10-14 15:00 | 532 | 528
2016-10-14 15:30 | 535 | 532
2016-10-14 16:00 | 525 | 523
2016-10-14 16:30 | 523 | 520
2016-10-14 17:00 | 518 | 515
2016-10-14 17:30 | 517 | 514
2016-10-14 18:00 | 518 | 514
2016-10-14 18:30 | 540 | 537
2016-10-14 19:00 | 569 | 566
2016-10-14 19:30 | 565 | 563
2016-10-14 20:00 | 577 | 574
2016-10-14 20:30 | 553 | 551
2016-10-14 21:00 | 554 | 551
2016-10-14 21:30 | 542 | 539
2016-10-14 22:00 | 523 | 520
2016-10-14 22:30 | 446 | 442
2016-10-14 23:00 | 429 | 423
2016-10-14 23:30 | 425 | 418
2016-10-15 | 431 | 423
2016-10-15 00:30 | 436 | 429
2016-10-15 01:00 | 414 | 406
2016-10-15 01:30 | 413 | 405
2016-10-15 02:00 | 415 | 408
2016-10-15 02:30 | 413 | 405
2016-10-15 03:00 | 401 | 393
2016-10-15 03:30 | 400 | 391
2016-10-15 04:00 | 402 | 393
2016-10-15 04:30 | 416 | 408
2016-10-15 05:00 | 423 | 416
2016-10-15 05:30 | 429 | 421
2016-10-15 06:00 | 437 | 430
2016-10-15 06:30 | 448 | 442
2016-10-15 07:00 | 435 | 429
2016-10-15 07:30 | 463 | 457
2016-10-15 08:00 | 508 | 504
2016-10-15 08:30 | 525 | 522
2016-10-15 09:00 | 542 | 539
2016-10-15 09:30 | 538 | 536
2016-10-15 10:00 | 532 | 529
2016-10-15 10:30 | 524 | 520
2016-10-15 11:00 | 513 | 510
2016-10-15 11:30 | 515 | 511
2016-10-15 12:00 | 511 | 507
2016-10-15 12:30 | 517 | 514
2016-10-15 13:00 | 527 | 524
2016-10-15 13:30 | 510 | 507
2016-10-15 14:00 | 498 | 495
2016-10-15 14:30 | 495 | 492
2016-10-15 15:00 | 495 | 491
2016-10-15 15:30 | 501 | 497
2016-10-15 16:00 | 501 | 498
2016-10-15 16:30 | 514 | 511
2016-10-15 17:00 | 560 | 557
2016-10-15 17:30 | 587 | 585
2016-10-15 18:00 | 590 | 589
2016-10-15 18:30 | 594 | 593
2016-10-15 19:00 | 555 | 554
2016-10-15 19:30 | 564 | 562
2016-10-15 20:00 | 583 | 581
2016-10-15 20:30 | 587 | 586
2016-10-15 21:00 | 578 | 577
2016-10-15 21:30 | 560 | 559
2016-10-15 22:00 | 549 | 547
2016-10-15 22:30 | 524 | 522
2016-10-15 23:00 | 504 | 501
2016-10-15 23:30 | 484 | 481
2016-10-16 | 472 | 468
2016-10-16 00:30 | 458 | 453
2016-10-16 01:00 | 450 | 445
2016-10-16 01:30 | 446 | 441
2016-10-16 02:00 | 437 | 431
2016-10-16 02:30 | 434 | 429
2016-10-16 03:00 | 434 | 428
2016-10-16 03:30 | 420 | 414
2016-10-16 04:00 | 405 | 398
2016-10-16 04:30 | 403 | 395
2016-10-16 05:00 | 404 | 397
2016-10-16 05:30 | 419 | 412
2016-10-16 06:00 | 416 | 409
2016-10-16 06:30 | 422 | 416
2016-10-16 07:00 | 434 | 427
2016-10-16 07:30 | 446 | 440
2016-10-16 08:00 | 451 | 446
2016-10-16 08:30 | 491 | 486
2016-10-16 09:00 | 511 | 507
2016-10-16 09:30 | 501 | 497
2016-10-16 10:00 | 500 | 496
2016-10-16 10:30 | 506 | 503
2016-10-16 11:00 | 501 | 497
2016-10-16 11:30 | 489 | 486
2016-10-16 12:00 | 493 | 489
2016-10-16 12:30 | 480 | 476
2016-10-16 13:00 | 449 | 445
2016-10-16 13:30 | 461 | 456
2016-10-16 14:00 | 466 | 461
2016-10-16 14:30 | 481 | 477
2016-10-16 15:00 | 477 | 473
2016-10-16 15:30 | 490 | 486
2016-10-16 16:00 | 495 | 492
2016-10-16 16:30 | 496 | 493
2016-10-16 17:00 | 520 | 517
2016-10-16 17:30 | 534 | 532
2016-10-16 18:00 | 553 | 551
2016-10-16 18:30 | 539 | 536
2016-10-16 19:00 | 589 | 587
2016-10-16 19:30 | 603 | 602
2016-10-16 20:00 | 606 | 605
2016-10-16 20:30 | 579 | 579
2016-10-16 21:00 | 568 | 567
2016-10-16 21:30 | 546 | 545
2016-10-16 22:00 | 531 | 530
2016-10-16 22:30 | 501 | 500
2016-10-16 23:00 | 477 | 475
2016-10-16 23:30 | 459 | 456
2016-10-17 | 437 | 434
2016-10-17 00:30 | 428 | 425
2016-10-17 01:00 | 410 | 405
2016-10-17 01:30 | 397 | 392
2016-10-17 02:00 | 390 | 385
2016-10-17 02:30 | 385 | 379
2016-10-17 03:00 | 384 | 378
2016-10-17 03:30 | 379 | 373
2016-10-17 04:00 | 388 | 382
2016-10-17 04:30 | 392 | 387
2016-10-17 05:00 | 400 | 395
2016-10-17 05:30 | 405 | 401
2016-10-17 06:00 | 420 | 415
2016-10-17 06:30 | 439 | 435
2016-10-17 07:00 | 458 | 455
2016-10-17 07:30 | 500 | 497
2016-10-17 08:00 | 524 | 522
2016-10-17 08:30 | 537 | 535
2016-10-17 09:00 | 538 | 537
2016-10-17 09:30 | 547 | 546
2016-10-17 10:00 | 534 | 533
2016-10-17 10:30 | 519 | 518
2016-10-17 11:00 | 519 | 518
2016-10-17 11:30 | 525 | 524
2016-10-17 12:00 | 519 | 518
2016-10-17 12:30 | 540 | 539
2016-10-17 13:00 | 546 | 546
2016-10-17 13:30 | 517 | 517
2016-10-17 14:00 | 503 | 502
2016-10-17 14:30 | 516 | 516
2016-10-17 15:00 | 534 | 533
2016-10-17 15:30 | 540 | 540
2016-10-17 16:00 | 558 | 558
2016-10-17 16:30 | 572 | 572
2016-10-17 17:00 | 572 | 572
2016-10-17 17:30 | 569 | 569
2016-10-17 18:00 | 570 | 570
2016-10-17 18:30 | 587 | 587
2016-10-17 19:00 | 597 | 596
2016-10-17 19:30 | 620 | 620
2016-10-17 20:00 | 623 | 623
2016-10-17 20:30 | 593 | 593
2016-10-17 21:00 | 571 | 571
2016-10-17 21:30 | 552 | 552
2016-10-17 22:00 | 527 | 527
2016-10-17 22:30 | 479 | 478
2016-10-17 23:00 | 461 | 460
2016-10-17 23:30 | 441 | 439
2016-10-18 | 438 | 435
2016-10-18 00:30 | 421 | 418
2016-10-18 01:00 | 416 | 413
2016-10-18 01:30 | 409 | 405
2016-10-18 02:00 | 405 | 401
2016-10-18 02:30 | 396 | 392
2016-10-18 03:00 | 399 | 394
2016-10-18 03:30 | 398 | 394
2016-10-18 04:00 | 401 | 396
2016-10-18 04:30 | 404 | 400
2016-10-18 05:00 | 409 | 405
2016-10-18 05:30 | 413 | 409
2016-10-18 06:00 | 414 | 410
2016-10-18 06:30 | 449 | 446
2016-10-18 07:00 | 462 | 460
2016-10-18 07:30 | 506 | 504
2016-10-18 08:00 | 524 | 523
2016-10-18 08:30 | 534 | 533
2016-10-18 09:00 | 534 | 533
2016-10-18 09:30 | 534 | 533
2016-10-18 10:00 | 523 | 522
2016-10-18 10:30 | 523 | 522
2016-10-18 11:00 | 524 | 523
2016-10-18 11:30 | 537 | 536
2016-10-18 12:00 | 548 | 547
2016-10-18 12:30 | 546 | 546
2016-10-18 13:00 | 559 | 559
2016-10-18 13:30 | 546 | 546
2016-10-18 14:00 | 538 | 538
2016-10-18 14:30 | 548 | 548
2016-10-18 15:00 | 553 | 552
2016-10-18 15:30 | 564 | 564
2016-10-18 16:00 | 575 | 574
2016-10-18 16:30 | 592 | 592
2016-10-18 17:00 | 582 | 582
2016-10-18 17:30 | 571 | 571
2016-10-18 18:00 | 570 | 570
2016-10-18 18:30 | 577 | 577
2016-10-18 19:00 | 596 | 596
2016-10-18 19:30 | 590 | 590
2016-10-18 20:00 | 608 | 608
2016-10-18 20:30 | 593 | 593
2016-10-18 21:00 | 568 | 568
2016-10-18 21:30 | 560 | 560
2016-10-18 22:00 | 536 | 536
2016-10-18 22:30 | 481 | 480
2016-10-18 23:00 | 456 | 455
2016-10-18 23:30 | 446 | 444
2016-10-19 | 444 | 442
2016-10-19 00:30 | 437 | 435
2016-10-19 01:00 | 438 | 436
2016-10-19 01:30 | 441 | 438
2016-10-19 02:00 | 452 | 449
2016-10-19 02:30 | 445 | 442
2016-10-19 03:00 | 447 | 444
2016-10-19 03:30 | 451 | 448
2016-10-19 04:00 | 448 | 446
2016-10-19 04:30 | 439 | 437
2016-10-19 05:00 | 439 | 437
2016-10-19 05:30 | 422 | 420
2016-10-19 06:00 | 423 | 421
2016-10-19 06:30 | 451 | 449
2016-10-19 07:00 | 490 | 488
2016-10-19 07:30 | 561 | 560
2016-10-19 08:00 | 572 | 572
2016-10-19 08:30 | 593 | 593
2016-10-19 09:00 | 604 | 604
2016-10-19 09:30 | 616 | 616
2016-10-19 10:00 | 622 | 622
2016-10-19 10:30 | 621 | 621
2016-10-19 11:00 | 619 | 619
2016-10-19 11:30 | 608 | 608
2016-10-19 12:00 | 587 | 587
2016-10-19 12:30 | 569 | 569
2016-10-19 13:00 | 560 | 560
2016-10-19 13:30 | 543 | 543
2016-10-19 14:00 | 537 | 536
2016-10-19 14:30 | 559 | 558
2016-10-19 15:00 | 574 | 574
2016-10-19 15:30 | 572 | 572
2016-10-19 16:00 | 520 | 520
2016-10-19 16:30 | 511 | 511
2016-10-19 17:00 | 535 | 535
2016-10-19 17:30 | 535 | 535
2016-10-19 18:00 | 527 | 527
2016-10-19 18:30 | 522 | 522
2016-10-19 19:00 | 487 | 487
2016-10-19 19:30 | 487 | 486
2016-10-19 20:00 | 480 | 479
2016-10-19 20:30 | 494 | 493
2016-10-19 21:00 | 528 | 527
2016-10-19 21:30 | 517 | 516
2016-10-19 22:00 | 499 | 498
2016-10-19 22:30 | 382 | 381
2016-10-19 23:00 | 349 | 345
2016-10-19 23:30 | 347 | 342
2016-10-20 | 368 | 363
2016-10-20 00:30 | 331 | 326
2016-10-20 01:00 | 355 | 349
2016-10-20 01:30 | 355 | 350
2016-10-20 02:00 | 358 | 352
2016-10-20 02:30 | 354 | 348
2016-10-20 03:00 | 348 | 341
2016-10-20 03:30 | 338 | 331
2016-10-20 04:00 | 336 | 329
2016-10-20 04:30 | 345 | 338
2016-10-20 05:00 | 349 | 343
2016-10-20 05:30 | 355 | 349
2016-10-20 06:00 | 376 | 370
2016-10-20 06:30 | 401 | 396
2016-10-20 07:00 | 425 | 421
2016-10-20 07:30 | 452 | 448
2016-10-20 08:00 | 482 | 480
2016-10-20 08:30 | 485 | 483
2016-10-20 09:00 | 481 | 480
2016-10-20 09:30 | 487 | 486
2016-10-20 10:00 | 474 | 473
2016-10-20 10:30 | 470 | 468
2016-10-20 11:00 | 468 | 467
2016-10-20 11:30 | 474 | 473
2016-10-20 12:00 | 484 | 483
2016-10-20 12:30 | 491 | 490
2016-10-20 13:00 | 489 | 488
2016-10-20 13:30 | 467 | 466
2016-10-20 14:00 | 471 | 469
2016-10-20 14:30 | 489 | 488
2016-10-20 15:00 | 495 | 495
2016-10-20 15:30 | 486 | 485
2016-10-20 16:00 | 499 | 499
2016-10-20 16:30 | 435 | 434
2016-10-20 17:00 | 408 | 406
2016-10-20 17:30 | 420 | 418
2016-10-20 18:00 | 446 | 444
2016-10-20 18:30 | 425 | 423
2016-10-20 19:00 | 403 | 401
2016-10-20 19:30 | 426 | 423
2016-10-20 20:00 | 455 | 453
2016-10-20 20:30 | 457 | 455
2016-10-20 21:00 | 447 | 446
2016-10-20 21:30 | 409 | 407
2016-10-20 22:00 | 453 | 451
2016-10-20 22:30 | 304 | 301
2016-10-20 23:00 | 280 | 272
2016-10-20 23:30 | 264 | 253
2016-10-21 | 314 | 305
2016-10-21 00:30 | 348 | 342
2016-10-21 01:00 | 328 | 323
2016-10-21 01:30 | 320 | 313
2016-10-21 02:00 | 316 | 308
2016-10-21 02:30 | 302 | 294
2016-10-21 03:00 | 298 | 290
2016-10-21 03:30 | 298 | 289
2016-10-21 04:00 | 289 | 280
2016-10-21 04:30 | 291 | 281
2016-10-21 05:00 | 292 | 283
2016-10-21 05:30 | 305 | 296
2016-10-21 06:00 | 285 | 276
2016-10-21 06:30 | 312 | 304
2016-10-21 07:00 | 349 | 343
2016-10-21 07:30 | 415 | 411
2016-10-21 08:00 | 450 | 448
2016-10-21 08:30 | 425 | 423
2016-10-21 09:00 | 436 | 434
2016-10-21 09:30 | 437 | 435
2016-10-21 10:00 | 428 | 426
2016-10-21 10:30 | 429 | 427
2016-10-21 11:00 | 422 | 420
2016-10-21 11:30 | 417 | 415
2016-10-21 12:00 | 412 | 410
2016-10-21 12:30 | 427 | 425
2016-10-21 13:00 | 436 | 434
2016-10-21 13:30 | 435 | 432
2016-10-21 14:00 | 409 | 407
2016-10-21 14:30 | 402 | 399
2016-10-21 15:00 | 408 | 405
2016-10-21 15:30 | 408 | 405
2016-10-21 16:00 | 420 | 418
2016-10-21 16:30 | 430 | 428
2016-10-21 17:00 | 451 | 449
2016-10-21 17:30 | 450 | 449
2016-10-21 18:00 | 452 | 450
2016-10-21 18:30 | 460 | 459
2016-10-21 19:00 | 458 | 457
2016-10-21 19:30 | 380 | 378
2016-10-21 20:00 | 387 | 384
2016-10-21 20:30 | 372 | 369
2016-10-21 21:00 | 352 | 348
2016-10-21 21:30 | 335 | 330
2016-10-21 22:00 | 299 | 293
2016-10-21 22:30 | 287 | 279
2016-10-21 23:00 | 272 | 262
2016-10-21 23:30 | 251 | 240
2016-10-22 | 237 | 224
2016-10-22 00:30 | 300 | 288
2016-10-22 01:00 | 416 | 410
2016-10-22 01:30 | 436 | 433
2016-10-22 02:00 | 430 | 427
2016-10-22 02:30 | 432 | 430
2016-10-22 03:00 | 432 | 429
2016-10-22 03:30 | 434 | 431
2016-10-22 04:00 | 413 | 410
2016-10-22 04:30 | 416 | 413
2016-10-22 05:00 | 420 | 417
2016-10-22 05:30 | 425 | 422
2016-10-22 06:00 | 421 | 418
2016-10-22 06:30 | 413 | 410
2016-10-22 07:00 | 421 | 418
2016-10-22 07:30 | 437 | 434
2016-10-22 08:00 | 458 | 455
2016-10-22 08:30 | 470 | 468
2016-10-22 09:00 | 486 | 484
2016-10-22 09:30 | 495 | 493
2016-10-22 10:00 | 507 | 506
2016-10-22 10:30 | 515 | 514
2016-10-22 11:00 | 502 | 501
2016-10-22 11:30 | 503 | 502
2016-10-22 12:00 | 506 | 506
2016-10-22 12:30 | 504 | 503
2016-10-22 13:00 | 506 | 505
2016-10-22 13:30 | 508 | 508
2016-10-22 14:00 | 501 | 500
2016-10-22 14:30 | 504 | 503
2016-10-22 15:00 | 503 | 502
2016-10-22 15:30 | 527 | 527
2016-10-22 16:00 | 545 | 544
2016-10-22 16:30 | 554 | 554
2016-10-22 17:00 | 541 | 541
2016-10-22 17:30 | 571 | 571
2016-10-22 18:00 | 570 | 570
2016-10-22 18:30 | 585 | 585
2016-10-22 19:00 | 588 | 588
2016-10-22 19:30 | 581 | 581
2016-10-22 20:00 | 595 | 595
2016-10-22 20:30 | 594 | 594
2016-10-22 21:00 | 581 | 581
2016-10-22 21:30 | 559 | 559
2016-10-22 22:00 | 540 | 540
2016-10-22 22:30 | 517 | 517
2016-10-22 23:00 | 501 | 500
2016-10-22 23:30 | 482 | 481
2016-10-23 | 465 | 464
2016-10-23 00:30 | 459 | 458
2016-10-23 01:00 | 448 | 447
2016-10-23 01:30 | 447 | 445
2016-10-23 02:00 | 433 | 432
2016-10-23 02:30 | 435 | 434
2016-10-23 03:00 | 434 | 433
2016-10-23 03:30 | 429 | 427
2016-10-23 04:00 | 423 | 421
2016-10-23 04:30 | 419 | 416
2016-10-23 05:00 | 411 | 408
2016-10-23 05:30 | 410 | 407
2016-10-23 06:00 | 404 | 401
2016-10-23 06:30 | 413 | 410
2016-10-23 07:00 | 418 | 415
2016-10-23 07:30 | 435 | 433
2016-10-23 08:00 | 447 | 445
2016-10-23 08:30 | 463 | 461
2016-10-23 09:00 | 468 | 467
2016-10-23 09:30 | 480 | 479
2016-10-23 10:00 | 489 | 487
2016-10-23 10:30 | 496 | 495
2016-10-23 11:00 | 492 | 491
2016-10-23 11:30 | 498 | 496
2016-10-23 12:00 | 502 | 500
2016-10-23 12:30 | 502 | 500
2016-10-23 13:00 | 506 | 505
2016-10-23 13:30 | 502 | 501
2016-10-23 14:00 | 500 | 499
2016-10-23 14:30 | 514 | 513
2016-10-23 15:00 | 523 | 521
2016-10-23 15:30 | 534 | 533
2016-10-23 16:00 | 543 | 542
2016-10-23 16:30 | 543 | 542
2016-10-23 17:00 | 547 | 547
2016-10-23 17:30 | 562 | 562
2016-10-23 18:00 | 549 | 549
2016-10-23 18:30 | 555 | 554
2016-10-23 19:00 | 533 | 532
2016-10-23 19:30 | 542 | 542
2016-10-23 20:00 | 530 | 529
2016-10-23 20:30 | 536 | 536
2016-10-23 21:00 | 530 | 529
2016-10-23 21:30 | 550 | 549
2016-10-23 22:00 | 453 | 452
2016-10-23 22:30 | 413 | 411
2016-10-23 23:00 | 431 | 428
2016-10-23 23:30 | 452 | 450
2016-10-24 | 435 | 433
2016-10-24 00:30 | 431 | 428
2016-10-24 01:00 | 428 | 425
2016-10-24 01:30 | 431 | 428
2016-10-24 02:00 | 428 | 425
2016-10-24 02:30 | 430 | 426
2016-10-24 03:00 | 427 | 423
2016-10-24 03:30 | 424 | 421
2016-10-24 04:00 | 428 | 424
2016-10-24 04:30 | 429 | 425
2016-10-24 05:00 | 438 | 435
2016-10-24 05:30 | 431 | 429
2016-10-24 06:00 | 426 | 423
2016-10-24 06:30 | 427 | 423
2016-10-24 07:00 | 445 | 441
2016-10-24 07:30 | 513 | 510
2016-10-24 08:00 | 545 | 544
2016-10-24 08:30 | 561 | 560
2016-10-24 09:00 | 556 | 555
2016-10-24 09:30 | 556 | 555
2016-10-24 10:00 | 555 | 555
2016-10-24 10:30 | 562 | 561
2016-10-24 11:00 | 566 | 566
2016-10-24 11:30 | 563 | 562
2016-10-24 12:00 | 573 | 572
2016-10-24 12:30 | 589 | 588
2016-10-24 13:00 | 590 | 590
2016-10-24 13:30 | 579 | 578
2016-10-24 14:00 | 562 | 562
2016-10-24 14:30 | 572 | 572
2016-10-24 15:00 | 575 | 574
2016-10-24 15:30 | 573 | 573
2016-10-24 16:00 | 570 | 570
2016-10-24 16:30 | 577 | 576
2016-10-24 17:00 | 595 | 595
2016-10-24 17:30 | 603 | 603
2016-10-24 18:00 | 615 | 615
2016-10-24 18:30 | 630 | 629
2016-10-24 19:00 | 649 | 649
2016-10-24 19:30 | 643 | 643
2016-10-24 20:00 | 645 | 645
2016-10-24 20:30 | 636 | 636
2016-10-24 21:00 | 618 | 618
2016-10-24 21:30 | 596 | 596
2016-10-24 22:00 | 574 | 574
2016-10-24 22:30 | 527 | 527
2016-10-24 23:00 | 497 | 496
2016-10-24 23:30 | 471 | 469
2016-10-25 | 460 | 458
2016-10-25 00:30 | 485 | 483
2016-10-25 01:00 | 468 | 467
2016-10-25 01:30 | 460 | 458
2016-10-25 02:00 | 457 | 455
2016-10-25 02:30 | 447 | 445
2016-10-25 03:00 | 443 | 440
2016-10-25 03:30 | 440 | 438
2016-10-25 04:00 | 437 | 434
2016-10-25 04:30 | 436 | 434
2016-10-25 05:00 | 445 | 442
2016-10-25 05:30 | 452 | 450
2016-10-25 06:00 | 459 | 457
2016-10-25 06:30 | 503 | 501
2016-10-25 07:00 | 530 | 528
2016-10-25 07:30 | 547 | 546
2016-10-25 08:00 | 539 | 538
2016-10-25 08:30 | 540 | 539
2016-10-25 09:00 | 543 | 542
2016-10-25 09:30 | 534 | 533
2016-10-25 10:00 | 528 | 527
2016-10-25 10:30 | 524 | 523
2016-10-25 11:00 | 532 | 531
2016-10-25 11:30 | 536 | 535
2016-10-25 12:00 | 551 | 550
2016-10-25 12:30 | 551 | 551
2016-10-25 13:00 | 551 | 551
2016-10-25 13:30 | 538 | 537
2016-10-25 14:00 | 531 | 531
2016-10-25 14:30 | 538 | 537
2016-10-25 15:00 | 539 | 538
2016-10-25 15:30 | 513 | 512
2016-10-25 16:00 | 551 | 551
2016-10-25 16:30 | 602 | 601
2016-10-25 17:00 | 621 | 621
2016-10-25 17:30 | 628 | 628
2016-10-25 18:00 | 627 | 627
2016-10-25 18:30 | 621 | 621
2016-10-25 19:00 | 638 | 638
2016-10-25 19:30 | 646 | 645
2016-10-25 20:00 | 644 | 644
2016-10-25 20:30 | 621 | 621
2016-10-25 21:00 | 600 | 600
2016-10-25 21:30 | 570 | 570
2016-10-25 22:00 | 551 | 550
2016-10-25 22:30 | 524 | 523
2016-10-25 23:00 | 488 | 487
2016-10-25 23:30 | 467 | 465
2016-10-26 | 462 | 460
2016-10-26 00:30 | 450 | 447
2016-10-26 01:00 | 387 | 384
2016-10-26 01:30 | 373 | 369
2016-10-26 02:00 | 368 | 363
2016-10-26 02:30 | 364 | 360
2016-10-26 03:00 | 358 | 353
2016-10-26 03:30 | 360 | 355
2016-10-26 04:00 | 355 | 350
2016-10-26 04:30 | 347 | 342
2016-10-26 05:00 | 293 | 286
2016-10-26 05:30 | 273 | 264
2016-10-26 06:00 | 220 | 207
2016-10-26 06:30 | 240 | 224
2016-10-26 07:00 | 269 | 252
2016-10-26 07:30 | 388 | 377
2016-10-26 08:00 | 421 | 415
2016-10-26 08:30 | 402 | 397
2016-10-26 09:00 | 399 | 394
2016-10-26 09:30 | 405 | 399
2016-10-26 10:00 | 398 | 393
2016-10-26 10:30 | 400 | 395
2016-10-26 11:00 | 416 | 410
2016-10-26 11:30 | 420 | 415
2016-10-26 12:00 | 428 | 423
2016-10-26 12:30 | 442 | 438
2016-10-26 13:00 | 433 | 429
2016-10-26 13:30 | 424 | 420
2016-10-26 14:00 | 424 | 419
2016-10-26 14:30 | 438 | 434
2016-10-26 15:00 | 440 | 436
2016-10-26 15:30 | 454 | 450
2016-10-26 16:00 | 469 | 466
2016-10-26 16:30 | 489 | 486
2016-10-26 17:00 | 500 | 497
2016-10-26 17:30 | 500 | 498
2016-10-26 18:00 | 495 | 493
2016-10-26 18:30 | 514 | 512
2016-10-26 19:00 | 526 | 525
2016-10-26 19:30 | 525 | 524
2016-10-26 20:00 | 519 | 517
2016-10-26 20:30 | 505 | 504
2016-10-26 21:00 | 503 | 501
2016-10-26 21:30 | 498 | 496
2016-10-26 22:00 | 478 | 476
2016-10-26 22:30 | 394 | 391
2016-10-26 23:00 | 409 | 404
2016-10-26 23:30 | 401 | 396
2016-10-27 | 379 | 374
2016-10-27 00:30 | 375 | 368
2016-10-27 01:00 | 356 | 349
2016-10-27 01:30 | 348 | 340
2016-10-27 02:00 | 345 | 337
2016-10-27 02:30 | 342 | 333
2016-10-27 03:00 | 337 | 328
2016-10-27 03:30 | 335 | 325
2016-10-27 04:00 | 331 | 321
2016-10-27 04:30 | 333 | 322
2016-10-27 05:00 | 339 | 329
2016-10-27 05:30 | 356 | 347
2016-10-27 06:00 | 342 | 334
2016-10-27 06:30 | 377 | 369
2016-10-27 07:00 | 399 | 392
2016-10-27 07:30 | 436 | 430
2016-10-27 08:00 | 453 | 449
2016-10-27 08:30 | 448 | 445
2016-10-27 09:00 | 452 | 449
2016-10-27 09:30 | 446 | 442
2016-10-27 10:00 | 461 | 459
2016-10-27 10:30 | 465 | 462
2016-10-27 11:00 | 462 | 460
2016-10-27 11:30 | 469 | 466
2016-10-27 12:00 | 485 | 483
2016-10-27 12:30 | 490 | 488
2016-10-27 13:00 | 464 | 462
2016-10-27 13:30 | 466 | 464
2016-10-27 14:00 | 475 | 473
2016-10-27 14:30 | 487 | 486
2016-10-27 15:00 | 496 | 495
2016-10-27 15:30 | 507 | 506
2016-10-27 16:00 | 524 | 523
2016-10-27 16:30 | 551 | 550
2016-10-27 17:00 | 541 | 541
2016-10-27 17:30 | 558 | 558
2016-10-27 18:00 | 573 | 573
2016-10-27 18:30 | 579 | 579
2016-10-27 19:00 | 575 | 575
2016-10-27 19:30 | 580 | 580
2016-10-27 20:00 | 586 | 585
2016-10-27 20:30 | 575 | 574
2016-10-27 21:00 | 549 | 548
2016-10-27 21:30 | 519 | 519
2016-10-27 22:00 | 496 | 495
2016-10-27 22:30 | 430 | 429
2016-10-27 23:00 | 439 | 436
2016-10-27 23:30 | 424 | 422
2016-10-28 | 413 | 410
2016-10-28 00:30 | 392 | 389
2016-10-28 01:00 | 375 | 371
2016-10-28 01:30 | 372 | 366
2016-10-28 02:00 | 360 | 354
2016-10-28 02:30 | 360 | 354
2016-10-28 03:00 | 352 | 346
2016-10-28 03:30 | 356 | 349
2016-10-28 04:00 | 356 | 349
2016-10-28 04:30 | 362 | 356
2016-10-28 05:00 | 357 | 351
2016-10-28 05:30 | 347 | 341
2016-10-28 06:00 | 287 | 278
2016-10-28 06:30 | 309 | 299
2016-10-28 07:00 | 265 | 254
2016-10-28 07:30 | 381 | 372
2016-10-28 08:00 | 445 | 441
2016-10-28 08:30 | 428 | 425
2016-10-28 09:00 | 407 | 404
2016-10-28 09:30 | 428 | 425
2016-10-28 10:00 | 425 | 422
2016-10-28 10:30 | 486 | 483
2016-10-28 11:00 | 584 | 583
2016-10-28 11:30 | 590 | 590
2016-10-28 12:00 | 593 | 593
2016-10-28 12:30 | 592 | 592
2016-10-28 13:00 | 578 | 577
2016-10-28 13:30 | 561 | 561
2016-10-28 14:00 | 558 | 558
2016-10-28 14:30 | 577 | 577
2016-10-28 15:00 | 585 | 585
2016-10-28 15:30 | 569 | 569
2016-10-28 16:00 | 585 | 585
2016-10-28 16:30 | 617 | 616
2016-10-28 17:00 | 638 | 638
2016-10-28 17:30 | 617 | 617
2016-10-28 18:00 | 633 | 633
2016-10-28 18:30 | 662 | 662
2016-10-28 19:00 | 684 | 684
2016-10-28 19:30 | 679 | 679
2016-10-28 20:00 | 662 | 662
2016-10-28 20:30 | 646 | 646
2016-10-28 21:00 | 632 | 632
2016-10-28 21:30 | 612 | 612
2016-10-28 22:00 | 600 | 600
2016-10-28 22:30 | 536 | 536
2016-10-28 23:00 | 527 | 527
2016-10-28 23:30 | 531 | 530
2016-10-29 | 517 | 516
2016-10-29 00:30 | 504 | 503
2016-10-29 01:00 | 490 | 488
2016-10-29 01:30 | 478 | 477
2016-10-29 02:00 | 466 | 464
2016-10-29 02:30 | 460 | 458
2016-10-29 03:00 | 458 | 456
2016-10-29 03:30 | 455 | 453
2016-10-29 04:00 | 450 | 448
2016-10-29 04:30 | 449 | 447
2016-10-29 05:00 | 453 | 451
2016-10-29 05:30 | 460 | 458
2016-10-29 06:00 | 449 | 447
2016-10-29 06:30 | 463 | 461
2016-10-29 07:00 | 469 | 467
2016-10-29 07:30 | 484 | 482
2016-10-29 08:00 | 485 | 483
2016-10-29 08:30 | 485 | 483
2016-10-29 09:00 | 508 | 507
2016-10-29 09:30 | 518 | 517
2016-10-29 10:00 | 498 | 497
2016-10-29 10:30 | 473 | 472
2016-10-29 11:00 | 469 | 468
2016-10-29 11:30 | 468 | 467
2016-10-29 12:00 | 501 | 500
2016-10-29 12:30 | 510 | 509
2016-10-29 13:00 | 519 | 518
2016-10-29 13:30 | 508 | 507
2016-10-29 14:00 | 520 | 519
2016-10-29 14:30 | 528 | 527
2016-10-29 15:00 | 546 | 545
2016-10-29 15:30 | 558 | 558
2016-10-29 16:00 | 575 | 575
2016-10-29 16:30 | 584 | 583
2016-10-29 17:00 | 595 | 595
2016-10-29 17:30 | 602 | 602
2016-10-29 18:00 | 606 | 606
2016-10-29 18:30 | 616 | 616
2016-10-29 19:00 | 635 | 635
2016-10-29 19:30 | 654 | 654
2016-10-29 20:00 | 644 | 644
2016-10-29 20:30 | 637 | 637
2016-10-29 21:00 | 613 | 613
2016-10-29 21:30 | 599 | 599
2016-10-29 22:00 | 596 | 596
2016-10-29 22:30 | 553 | 552
2016-10-29 23:00 | 545 | 544
2016-10-29 23:30 | 527 | 526
2016-10-30 | 513 | 513
2016-10-30 00:30 | 497 | 496
2016-10-30 01:00 | 479 | 478
2016-10-30 01:30 | 477 | 475
2016-10-30 02:00 | 463 | 462
2016-10-30 02:30 | 459 | 457
2016-10-30 03:00 | 450 | 448
2016-10-30 03:30 | 452 | 450
2016-10-30 04:00 | 442 | 440
2016-10-30 04:30 | 446 | 443
2016-10-30 05:00 | 445 | 443
2016-10-30 05:30 | 439 | 437
2016-10-30 06:00 | 427 | 425
2016-10-30 06:30 | 432 | 429
2016-10-30 07:00 | 446 | 444
2016-10-30 07:30 | 462 | 460
2016-10-30 08:00 | 481 | 480
2016-10-30 08:30 | 495 | 493
2016-10-30 09:00 | 504 | 503
2016-10-30 09:30 | 488 | 487
2016-10-30 10:00 | 490 | 489
2016-10-30 10:30 | 520 | 519
2016-10-30 11:00 | 478 | 477
2016-10-30 11:30 | 417 | 415
2016-10-30 12:00 | 518 | 516
2016-10-30 12:30 | 527 | 526
2016-10-30 13:00 | 520 | 519
2016-10-30 13:30 | 506 | 505
2016-10-30 14:00 | 507 | 507
2016-10-30 14:30 | 513 | 513
2016-10-30 15:00 | 529 | 529
2016-10-30 15:30 | 541 | 540
2016-10-30 16:00 | 563 | 563
2016-10-30 16:30 | 586 | 586
2016-10-30 17:00 | 608 | 608
2016-10-30 17:30 | 615 | 615
2016-10-30 18:00 | 633 | 633
2016-10-30 18:30 | 648 | 648
2016-10-30 19:00 | 674 | 674
2016-10-30 19:30 | 706 | 706
2016-10-30 20:00 | 694 | 694
2016-10-30 20:30 | 661 | 661
2016-10-30 21:00 | 643 | 643
2016-10-30 21:30 | 621 | 621
2016-10-30 22:00 | 600 | 600
2016-10-30 22:30 | 567 | 566
2016-10-30 23:00 | 542 | 541
2016-10-30 23:30 | 523 | 522
2016-10-31 | 507 | 505
2016-10-31 00:30 | 483 | 481
2016-10-31 01:00 | 468 | 466
2016-10-31 01:30 | 463 | 462
2016-10-31 02:00 | 471 | 469
2016-10-31 02:30 | 468 | 466
2016-10-31 03:00 | 458 | 456
2016-10-31 03:30 | 457 | 455
2016-10-31 04:00 | 452 | 450
2016-10-31 04:30 | 452 | 449
2016-10-31 05:00 | 462 | 460
2016-10-31 05:30 | 480 | 477
2016-10-31 06:00 | 482 | 480
2016-10-31 06:30 | 513 | 511
2016-10-31 07:00 | 524 | 522
2016-10-31 07:30 | 575 | 574
2016-10-31 08:00 | 585 | 585
2016-10-31 08:30 | 581 | 581
2016-10-31 09:00 | 592 | 591
2016-10-31 09:30 | 578 | 578
2016-10-31 10:00 | 557 | 556
2016-10-31 10:30 | 545 | 544
2016-10-31 11:00 | 547 | 546
2016-10-31 11:30 | 549 | 549
2016-10-31 12:00 | 560 | 560
2016-10-31 12:30 | 567 | 566
2016-10-31 13:00 | 572 | 571
2016-10-31 13:30 | 569 | 568
2016-10-31 14:00 | 572 | 572
2016-10-31 14:30 | 575 | 575
2016-10-31 15:00 | 579 | 578
2016-10-31 15:30 | 584 | 584
2016-10-31 16:00 | 600 | 600
2016-10-31 16:30 | 632 | 632
2016-10-31 17:00 | 650 | 650
2016-10-31 17:30 | 655 | 655
2016-10-31 18:00 | 655 | 655
2016-10-31 18:30 | 659 | 659
2016-10-31 19:00 | 673 | 673
2016-10-31 19:30 | 676 | 676
2016-10-31 20:00 | 655 | 655
2016-10-31 20:30 | 627 | 627
2016-10-31 21:00 | 611 | 611
2016-10-31 21:30 | 594 | 594
2016-10-31 22:00 | 561 | 561
2016-10-31 22:30 | 490 | 490
2016-10-31 23:00 | 479 | 477
2016-10-31 23:30 | 462 | 460
2016-11-01 | 468 | 466
2016-11-01 00:30 | 458 | 455
2016-11-01 01:00 | 438 | 435
2016-11-01 01:30 | 424 | 421
2016-11-01 02:00 | 421 | 417
2016-11-01 02:30 | 442 | 438
2016-11-01 03:00 | 444 | 441
2016-11-01 03:30 | 435 | 432
2016-11-01 04:00 | 437 | 433
2016-11-01 04:30 | 431 | 428
2016-11-01 05:00 | 431 | 428
2016-11-01 05:30 | 442 | 439
2016-11-01 06:00 | 436 | 433
2016-11-01 06:30 | 473 | 471
2016-11-01 07:00 | 500 | 498
2016-11-01 07:30 | 523 | 522
2016-11-01 08:00 | 542 | 541
2016-11-01 08:30 | 509 | 509
2016-11-01 09:00 | 489 | 488
2016-11-01 09:30 | 481 | 480
2016-11-01 10:00 | 512 | 510
2016-11-01 10:30 | 533 | 531
2016-11-01 11:00 | 550 | 549
2016-11-01 11:30 | 556 | 555
2016-11-01 12:00 | 560 | 559
2016-11-01 12:30 | 566 | 566
2016-11-01 13:00 | 565 | 564
2016-11-01 13:30 | 559 | 559
2016-11-01 14:00 | 570 | 569
2016-11-01 14:30 | 587 | 587
2016-11-01 15:00 | 569 | 569
2016-11-01 15:30 | 561 | 561
2016-11-01 16:00 | 583 | 583
2016-11-01 16:30 | 591 | 590
2016-11-01 17:00 | 625 | 625
2016-11-01 17:30 | 635 | 635
2016-11-01 18:00 | 644 | 644
2016-11-01 18:30 | 657 | 657
2016-11-01 19:00 | 666 | 666
2016-11-01 19:30 | 670 | 670
2016-11-01 20:00 | 665 | 665
2016-11-01 20:30 | 650 | 650
2016-11-01 21:00 | 629 | 629
2016-11-01 21:30 | 606 | 605
2016-11-01 22:00 | 577 | 577
2016-11-01 22:30 | 540 | 540
2016-11-01 23:00 | 511 | 510
2016-11-01 23:30 | 498 | 496
2016-11-02 | 484 | 483
2016-11-02 00:30 | 475 | 473
2016-11-02 01:00 | 452 | 450
2016-11-02 01:30 | 445 | 442
2016-11-02 02:00 | 432 | 429
2016-11-02 02:30 | 428 | 425
2016-11-02 03:00 | 428 | 425
2016-11-02 03:30 | 428 | 424
2016-11-02 04:00 | 427 | 423
2016-11-02 04:30 | 426 | 423
2016-11-02 05:00 | 429 | 426
2016-11-02 05:30 | 441 | 437
2016-11-02 06:00 | 450 | 446
2016-11-02 06:30 | 485 | 482
2016-11-02 07:00 | 508 | 506
2016-11-02 07:30 | 533 | 532
2016-11-02 08:00 | 551 | 550
2016-11-02 08:30 | 559 | 558
2016-11-02 09:00 | 562 | 562
2016-11-02 09:30 | 563 | 563
2016-11-02 10:00 | 566 | 565
2016-11-02 10:30 | 568 | 567
2016-11-02 11:00 | 569 | 568
2016-11-02 11:30 | 566 | 566
2016-11-02 12:00 | 530 | 529
2016-11-02 12:30 | 529 | 527
2016-11-02 13:00 | 532 | 531
2016-11-02 13:30 | 532 | 531
2016-11-02 14:00 | 512 | 511
2016-11-02 14:30 | 526 | 525
2016-11-02 15:00 | 535 | 534
2016-11-02 15:30 | 485 | 484
2016-11-02 16:00 | 474 | 473
2016-11-02 16:30 | 475 | 473
2016-11-02 17:00 | 548 | 547
2016-11-02 17:30 | 548 | 547
2016-11-02 18:00 | 547 | 546
2016-11-02 18:30 | 572 | 571
2016-11-02 19:00 | 579 | 579
2016-11-02 19:30 | 529 | 529
2016-11-02 20:00 | 531 | 530
2016-11-02 20:30 | 533 | 532
2016-11-02 21:00 | 516 | 515
2016-11-02 21:30 | 486 | 485
2016-11-02 22:00 | 467 | 465
2016-11-02 22:30 | 436 | 433
2016-11-02 23:00 | 390 | 387
2016-11-02 23:30 | 380 | 375
2016-11-03 | 375 | 369
2016-11-03 00:30 | 367 | 361
2016-11-03 01:00 | 344 | 337
2016-11-03 01:30 | 340 | 332
2016-11-03 02:00 | 331 | 323
2016-11-03 02:30 | 330 | 322
2016-11-03 03:00 | 321 | 312
2016-11-03 03:30 | 320 | 310
2016-11-03 04:00 | 312 | 302
2016-11-03 04:30 | 306 | 295
2016-11-03 05:00 | 309 | 298
2016-11-03 05:30 | 318 | 308
2016-11-03 06:00 | 257 | 246
2016-11-03 06:30 | 281 | 267
2016-11-03 07:00 | 290 | 277
2016-11-03 07:30 | 326 | 316
2016-11-03 08:00 | 346 | 338
2016-11-03 08:30 | 347 | 341
2016-11-03 09:00 | 355 | 348
2016-11-03 09:30 | 359 | 353
2016-11-03 10:00 | 356 | 350
2016-11-03 10:30 | 436 | 431
2016-11-03 11:00 | 454 | 452
2016-11-03 11:30 | 462 | 460
2016-11-03 12:00 | 463 | 460
2016-11-03 12:30 | 466 | 464
2016-11-03 13:00 | 461 | 459
2016-11-03 13:30 | 475 | 473
2016-11-03 14:00 | 475 | 474
2016-11-03 14:30 | 486 | 485
2016-11-03 15:00 | 497 | 496
2016-11-03 15:30 | 498 | 497
2016-11-03 16:00 | 504 | 503
2016-11-03 16:30 | 453 | 452
2016-11-03 17:00 | 446 | 444
2016-11-03 17:30 | 438 | 436
2016-11-03 18:00 | 455 | 452
2016-11-03 18:30 | 462 | 461
2016-11-03 19:00 | 482 | 480
2016-11-03 19:30 | 430 | 429
2016-11-03 20:00 | 416 | 413
2016-11-03 20:30 | 432 | 429
2016-11-03 21:00 | 432 | 429
2016-11-03 21:30 | 410 | 407
2016-11-03 22:00 | 390 | 386
2016-11-03 22:30 | 353 | 348
2016-11-03 23:00 | 326 | 320
2016-11-03 23:30 | 381 | 374
2016-11-04 | 381 | 376
2016-11-04 00:30 | 364 | 359
2016-11-04 01:00 | 350 | 344
2016-11-04 01:30 | 334 | 327
2016-11-04 02:00 | 324 | 315
2016-11-04 02:30 | 327 | 318
2016-11-04 03:00 | 342 | 333
2016-11-04 03:30 | 337 | 329
2016-11-04 04:00 | 330 | 322
2016-11-04 04:30 | 330 | 321
2016-11-04 05:00 | 262 | 251
2016-11-04 05:30 | 268 | 254
2016-11-04 06:00 | 270 | 255
2016-11-04 06:30 | 293 | 282
2016-11-04 07:00 | 321 | 311
2016-11-04 07:30 | 344 | 336
2016-11-04 08:00 | 356 | 349
2016-11-04 08:30 | 368 | 362
2016-11-04 09:00 | 381 | 376
2016-11-04 09:30 | 376 | 372
2016-11-04 10:00 | 367 | 364
2016-11-04 10:30 | 372 | 370
2016-11-04 11:00 | 421 | 419
2016-11-04 11:30 | 514 | 513
2016-11-04 12:00 | 604 | 604
2016-11-04 12:30 | 610 | 610
2016-11-04 13:00 | 609 | 609
2016-11-04 13:30 | 601 | 601
2016-11-04 14:00 | 605 | 605
2016-11-04 14:30 | 614 | 614
2016-11-04 15:00 | 622 | 622
2016-11-04 15:30 | 585 | 585
2016-11-04 16:00 | 602 | 602
2016-11-04 16:30 | 607 | 607
2016-11-04 17:00 | 658 | 658
2016-11-04 17:30 | 658 | 657
2016-11-04 18:00 | 649 | 649
2016-11-04 18:30 | 656 | 656
2016-11-04 19:00 | 659 | 659
2016-11-04 19:30 | 657 | 657
2016-11-04 20:00 | 644 | 644
2016-11-04 20:30 | 634 | 634
2016-11-04 21:00 | 608 | 608
2016-11-04 21:30 | 581 | 581
2016-11-04 22:00 | 563 | 563
2016-11-04 22:30 | 551 | 551
2016-11-04 23:00 | 523 | 523
2016-11-04 23:30 | 512 | 511
2016-11-05 | 498 | 497
2016-11-05 00:30 | 473 | 471
2016-11-05 01:00 | 455 | 453
2016-11-05 01:30 | 449 | 447
2016-11-05 02:00 | 443 | 441
2016-11-05 02:30 | 441 | 439
2016-11-05 03:00 | 446 | 444
2016-11-05 03:30 | 452 | 450
2016-11-05 04:00 | 438 | 436
2016-11-05 04:30 | 437 | 435
2016-11-05 05:00 | 437 | 434
2016-11-05 05:30 | 430 | 427
2016-11-05 06:00 | 421 | 418
2016-11-05 06:30 | 430 | 427
2016-11-05 07:00 | 455 | 452
2016-11-05 07:30 | 479 | 477
2016-11-05 08:00 | 502 | 500
2016-11-05 08:30 | 519 | 518
2016-11-05 09:00 | 535 | 534
2016-11-05 09:30 | 558 | 558
2016-11-05 10:00 | 551 | 550
2016-11-05 10:30 | 547 | 546
2016-11-05 11:00 | 550 | 550
2016-11-05 11:30 | 563 | 562
2016-11-05 12:00 | 562 | 561
2016-11-05 12:30 | 576 | 576
2016-11-05 13:00 | 566 | 566
2016-11-05 13:30 | 557 | 557
2016-11-05 14:00 | 567 | 566
2016-11-05 14:30 | 576 | 576
2016-11-05 15:00 | 573 | 573
2016-11-05 15:30 | 588 | 588
2016-11-05 16:00 | 603 | 603
2016-11-05 16:30 | 628 | 628
2016-11-05 17:00 | 630 | 630
2016-11-05 17:30 | 600 | 600
2016-11-05 18:00 | 638 | 638
2016-11-05 18:30 | 647 | 647
2016-11-05 19:00 | 620 | 620
2016-11-05 19:30 | 629 | 629
2016-11-05 20:00 | 633 | 633
2016-11-05 20:30 | 616 | 616
2016-11-05 21:00 | 605 | 605
2016-11-05 21:30 | 594 | 594
2016-11-05 22:00 | 579 | 579
2016-11-05 22:30 | 555 | 555
2016-11-05 23:00 | 540 | 540
2016-11-05 23:30 | 522 | 522
2016-11-06 | 506 | 505
2016-11-06 00:30 | 487 | 486
2016-11-06 01:00 | 467 | 466
2016-11-06 01:30 | 467 | 465
2016-11-06 02:00 | 459 | 457
2016-11-06 02:30 | 457 | 455
2016-11-06 03:00 | 450 | 448
2016-11-06 03:30 | 438 | 436
2016-11-06 04:00 | 436 | 434
2016-11-06 04:30 | 441 | 439
2016-11-06 05:00 | 437 | 435
2016-11-06 05:30 | 435 | 432
2016-11-06 06:00 | 435 | 432
2016-11-06 06:30 | 427 | 424
2016-11-06 07:00 | 439 | 437
2016-11-06 07:30 | 462 | 460
2016-11-06 08:00 | 472 | 470
2016-11-06 08:30 | 484 | 483
2016-11-06 09:00 | 501 | 500
2016-11-06 09:30 | 518 | 517
2016-11-06 10:00 | 530 | 530
2016-11-06 10:30 | 542 | 541
2016-11-06 11:00 | 545 | 545
2016-11-06 11:30 | 544 | 544
2016-11-06 12:00 | 541 | 541
2016-11-06 12:30 | 560 | 560
2016-11-06 13:00 | 569 | 569
2016-11-06 13:30 | 559 | 559
2016-11-06 14:00 | 569 | 569
2016-11-06 14:30 | 588 | 588
2016-11-06 15:00 | 598 | 598
2016-11-06 15:30 | 607 | 607
2016-11-06 16:00 | 608 | 608
2016-11-06 16:30 | 629 | 629
2016-11-06 17:00 | 652 | 652
2016-11-06 17:30 | 663 | 663
2016-11-06 18:00 | 674 | 674
2016-11-06 18:30 | 672 | 672
2016-11-06 19:00 | 646 | 646
2016-11-06 19:30 | 645 | 645
2016-11-06 20:00 | 657 | 657
2016-11-06 20:30 | 654 | 654
2016-11-06 21:00 | 641 | 641
2016-11-06 21:30 | 616 | 616
2016-11-06 22:00 | 581 | 581
2016-11-06 22:30 | 552 | 552
2016-11-06 23:00 | 522 | 521
2016-11-06 23:30 | 507 | 507
2016-11-07 | 494 | 493
2016-11-07 00:30 | 482 | 481
2016-11-07 01:00 | 463 | 461
2016-11-07 01:30 | 447 | 445
2016-11-07 02:00 | 455 | 453
2016-11-07 02:30 | 463 | 461
2016-11-07 03:00 | 455 | 453
2016-11-07 03:30 | 447 | 445
2016-11-07 04:00 | 456 | 454
2016-11-07 04:30 | 443 | 441
2016-11-07 05:00 | 400 | 398
2016-11-07 05:30 | 399 | 396
2016-11-07 06:00 | 407 | 404
2016-11-07 06:30 | 441 | 437
2016-11-07 07:00 | 474 | 471
2016-11-07 07:30 | 498 | 497
2016-11-07 08:00 | 504 | 503
2016-11-07 08:30 | 450 | 450
2016-11-07 09:00 | 457 | 456
2016-11-07 09:30 | 464 | 462
2016-11-07 10:00 | 457 | 455
2016-11-07 10:30 | 474 | 472
2016-11-07 11:00 | 462 | 460
2016-11-07 11:30 | 471 | 469
2016-11-07 12:00 | 479 | 478
2016-11-07 12:30 | 488 | 487
2016-11-07 13:00 | 486 | 485
2016-11-07 13:30 | 473 | 471
2016-11-07 14:00 | 426 | 425
2016-11-07 14:30 | 458 | 457
2016-11-07 15:00 | 456 | 455
2016-11-07 15:30 | 421 | 420
2016-11-07 16:00 | 411 | 409
2016-11-07 16:30 | 431 | 429
2016-11-07 17:00 | 398 | 396
2016-11-07 17:30 | 496 | 494
2016-11-07 18:00 | 522 | 521
2016-11-07 18:30 | 557 | 557
2016-11-07 19:00 | 580 | 580
2016-11-07 19:30 | 548 | 548
2016-11-07 20:00 | 535 | 535
2016-11-07 20:30 | 502 | 502
2016-11-07 21:00 | 510 | 509
2016-11-07 21:30 | 481 | 481
2016-11-07 22:00 | 465 | 464
2016-11-07 22:30 | 364 | 362
2016-11-07 23:00 | 352 | 348
2016-11-07 23:30 | 362 | 357
2016-11-08 | 356 | 352
2016-11-08 00:30 | 349 | 344
2016-11-08 01:00 | 336 | 330
2016-11-08 01:30 | 331 | 325
2016-11-08 02:00 | 335 | 329
2016-11-08 02:30 | 328 | 321
2016-11-08 03:00 | 317 | 310
2016-11-08 03:30 | 321 | 314
2016-11-08 04:00 | 317 | 309
2016-11-08 04:30 | 315 | 307
2016-11-08 05:00 | 320 | 313
2016-11-08 05:30 | 310 | 302
2016-11-08 06:00 | 283 | 275
2016-11-08 06:30 | 324 | 317
2016-11-08 07:00 | 343 | 337
2016-11-08 07:30 | 399 | 395
2016-11-08 08:00 | 404 | 402
2016-11-08 08:30 | 407 | 405
2016-11-08 09:00 | 430 | 428
2016-11-08 09:30 | 410 | 409
2016-11-08 10:00 | 408 | 406
2016-11-08 10:30 | 418 | 416
2016-11-08 11:00 | 428 | 427
2016-11-08 11:30 | 427 | 425
2016-11-08 12:00 | 412 | 410
2016-11-08 12:30 | 418 | 417
2016-11-08 13:00 | 411 | 409
2016-11-08 13:30 | 410 | 408
2016-11-08 14:00 | 426 | 425
2016-11-08 14:30 | 419 | 418
2016-11-08 15:00 | 302 | 300
2016-11-08 15:30 | 198 | 190
2016-11-08 16:00 | 223 | 209
2016-11-08 16:30 | 271 | 255
2016-11-08 17:00 | 294 | 282
2016-11-08 17:30 | 277 | 264
2016-11-08 18:00 | 280 | 265
2016-11-08 18:30 | 453 | 444
2016-11-08 19:00 | 521 | 518
2016-11-08 19:30 | 539 | 538
2016-11-08 20:00 | 532 | 531
2016-11-08 20:30 | 512 | 511
2016-11-08 21:00 | 497 | 496
2016-11-08 21:30 | 536 | 534
2016-11-08 22:00 | 594 | 593
2016-11-08 22:30 | 567 | 567
2016-11-08 23:00 | 549 | 548
2016-11-08 23:30 | 526 | 525
2016-11-09 | 509 | 508
2016-11-09 00:30 | 483 | 482
2016-11-09 01:00 | 473 | 471
2016-11-09 01:30 | 461 | 459
2016-11-09 02:00 | 461 | 458
2016-11-09 02:30 | 463 | 460
2016-11-09 03:00 | 460 | 457
2016-11-09 03:30 | 465 | 462
2016-11-09 04:00 | 459 | 456
2016-11-09 04:30 | 462 | 458
2016-11-09 05:00 | 469 | 466
2016-11-09 05:30 | 453 | 450
2016-11-09 06:00 | 455 | 452
2016-11-09 06:30 | 452 | 449
2016-11-09 07:00 | 474 | 471
2016-11-09 07:30 | 534 | 532
2016-11-09 08:00 | 558 | 557
2016-11-09 08:30 | 567 | 566
2016-11-09 09:00 | 555 | 554
2016-11-09 09:30 | 574 | 573
2016-11-09 10:00 | 552 | 551
2016-11-09 10:30 | 498 | 497
2016-11-09 11:00 | 536 | 535
2016-11-09 11:30 | 569 | 568
2016-11-09 12:00 | 578 | 577
2016-11-09 12:30 | 529 | 528
2016-11-09 13:00 | 507 | 506
2016-11-09 13:30 | 507 | 506
2016-11-09 14:00 | 511 | 510
2016-11-09 14:30 | 506 | 505
2016-11-09 15:00 | 494 | 493
2016-11-09 15:30 | 489 | 488
2016-11-09 16:00 | 450 | 448
2016-11-09 16:30 | 518 | 517
2016-11-09 17:00 | 526 | 526
2016-11-09 17:30 | 556 | 555
2016-11-09 18:00 | 579 | 578
2016-11-09 18:30 | 573 | 573
2016-11-09 19:00 | 563 | 562
2016-11-09 19:30 | 572 | 572
2016-11-09 20:00 | 547 | 546
2016-11-09 20:30 | 533 | 533
2016-11-09 21:00 | 536 | 535
2016-11-09 21:30 | 581 | 580
2016-11-09 22:00 | 655 | 655
2016-11-09 22:30 | 598 | 598
2016-11-09 23:00 | 576 | 575
2016-11-09 23:30 | 572 | 572
2016-11-10 | 555 | 554
2016-11-10 00:30 | 521 | 520
2016-11-10 01:00 | 504 | 502
2016-11-10 01:30 | 487 | 486
2016-11-10 02:00 | 469 | 466
2016-11-10 02:30 | 470 | 467
2016-11-10 03:00 | 465 | 462
2016-11-10 03:30 | 464 | 461
2016-11-10 04:00 | 457 | 454
2016-11-10 04:30 | 467 | 464
2016-11-10 05:00 | 487 | 484
2016-11-10 05:30 | 470 | 468
2016-11-10 06:00 | 440 | 437
2016-11-10 06:30 | 442 | 439
2016-11-10 07:00 | 467 | 465
2016-11-10 07:30 | 486 | 484
2016-11-10 08:00 | 487 | 486
2016-11-10 08:30 | 500 | 498
2016-11-10 09:00 | 506 | 505
2016-11-10 09:30 | 491 | 490
2016-11-10 10:00 | 459 | 457
2016-11-10 10:30 | 455 | 454
2016-11-10 11:00 | 469 | 468
2016-11-10 11:30 | 434 | 432
2016-11-10 12:00 | 393 | 391
2016-11-10 12:30 | 416 | 413
2016-11-10 13:00 | 428 | 426
2016-11-10 13:30 | 447 | 445
2016-11-10 14:00 | 458 | 456
2016-11-10 14:30 | 450 | 449
2016-11-10 15:00 | 443 | 441
2016-11-10 15:30 | 392 | 390
2016-11-10 16:00 | 407 | 404
2016-11-10 16:30 | 414 | 412
2016-11-10 17:00 | 419 | 417
2016-11-10 17:30 | 411 | 410
2016-11-10 18:00 | 410 | 408
2016-11-10 18:30 | 487 | 485
2016-11-10 19:00 | 505 | 505
2016-11-10 19:30 | 455 | 455
2016-11-10 20:00 | 452 | 451
2016-11-10 20:30 | 454 | 453
2016-11-10 21:00 | 521 | 520
2016-11-10 21:30 | 509 | 508
2016-11-10 22:00 | 502 | 502
2016-11-10 22:30 | 451 | 450
2016-11-10 23:00 | 440 | 438
2016-11-10 23:30 | 438 | 436
2016-11-11 | 459 | 457
2016-11-11 00:30 | 517 | 515
2016-11-11 01:00 | 498 | 497
2016-11-11 01:30 | 486 | 484
2016-11-11 02:00 | 482 | 480
2016-11-11 02:30 | 475 | 473
2016-11-11 03:00 | 470 | 468
2016-11-11 03:30 | 469 | 467
2016-11-11 04:00 | 470 | 468
2016-11-11 04:30 | 468 | 466
2016-11-11 05:00 | 477 | 475
2016-11-11 05:30 | 481 | 479
2016-11-11 06:00 | 486 | 485
2016-11-11 06:30 | 519 | 518
2016-11-11 07:00 | 521 | 520
2016-11-11 07:30 | 560 | 559
2016-11-11 08:00 | 582 | 582
2016-11-11 08:30 | 583 | 583
2016-11-11 09:00 | 586 | 586
2016-11-11 09:30 | 594 | 594
2016-11-11 10:00 | 594 | 594
2016-11-11 10:30 | 602 | 602
2016-11-11 11:00 | 581 | 581
2016-11-11 11:30 | 622 | 622
2016-11-11 12:00 | 635 | 635
2016-11-11 12:30 | 648 | 648
2016-11-11 13:00 | 558 | 557
2016-11-11 13:30 | 503 | 503
2016-11-11 14:00 | 496 | 496
2016-11-11 14:30 | 476 | 476
2016-11-11 15:00 | 489 | 489
2016-11-11 15:30 | 509 | 509
2016-11-11 16:00 | 517 | 517
2016-11-11 16:30 | 543 | 542
2016-11-11 17:00 | 534 | 534
2016-11-11 17:30 | 598 | 598
2016-11-11 18:00 | 603 | 603
2016-11-11 18:30 | 591 | 591
2016-11-11 19:00 | 545 | 545
2016-11-11 19:30 | 554 | 554
2016-11-11 20:00 | 569 | 569
2016-11-11 20:30 | 560 | 559
2016-11-11 21:00 | 606 | 606
2016-11-11 21:30 | 533 | 533
2016-11-11 22:00 | 522 | 522
2016-11-11 22:30 | 556 | 555
2016-11-11 23:00 | 532 | 531
2016-11-11 23:30 | 520 | 519
2016-11-12 | 536 | 535
2016-11-12 00:30 | 536 | 536
2016-11-12 01:00 | 511 | 511
2016-11-12 01:30 | 505 | 504
2016-11-12 02:00 | 496 | 495
2016-11-12 02:30 | 488 | 487
2016-11-12 03:00 | 474 | 473
2016-11-12 03:30 | 478 | 476
2016-11-12 04:00 | 478 | 476
2016-11-12 04:30 | 484 | 482
2016-11-12 05:00 | 501 | 499
2016-11-12 05:30 | 510 | 508
2016-11-12 06:00 | 506 | 504
2016-11-12 06:30 | 512 | 511
2016-11-12 07:00 | 518 | 516
2016-11-12 07:30 | 551 | 550
2016-11-12 08:00 | 568 | 568
2016-11-12 08:30 | 595 | 594
2016-11-12 09:00 | 605 | 605
2016-11-12 09:30 | 609 | 609
2016-11-12 10:00 | 597 | 597
2016-11-12 10:30 | 617 | 617
2016-11-12 11:00 | 627 | 627
2016-11-12 11:30 | 615 | 615
2016-11-12 12:00 | 623 | 623
2016-11-12 12:30 | 643 | 643
2016-11-12 13:00 | 649 | 649
2016-11-12 13:30 | 609 | 609
2016-11-12 14:00 | 611 | 611
2016-11-12 14:30 | 612 | 612
2016-11-12 15:00 | 588 | 588
2016-11-12 15:30 | 621 | 621
2016-11-12 16:00 | 572 | 572
2016-11-12 16:30 | 590 | 590
2016-11-12 17:00 | 600 | 600
2016-11-12 17:30 | 541 | 541
2016-11-12 18:00 | 571 | 571
2016-11-12 18:30 | 616 | 616
2016-11-12 19:00 | 651 | 651
2016-11-12 19:30 | 646 | 646
2016-11-12 20:00 | 622 | 622
2016-11-12 20:30 | 599 | 599
2016-11-12 21:00 | 648 | 648
2016-11-12 21:30 | 627 | 627
2016-11-12 22:00 | 609 | 609
2016-11-12 22:30 | 589 | 589
2016-11-12 23:00 | 543 | 543
2016-11-12 23:30 | 553 | 553
2016-11-13 | 540 | 539
2016-11-13 00:30 | 530 | 530
2016-11-13 01:00 | 504 | 503
2016-11-13 01:30 | 486 | 485
2016-11-13 02:00 | 475 | 474
2016-11-13 02:30 | 463 | 462
2016-11-13 03:00 | 454 | 452
2016-11-13 03:30 | 446 | 444
2016-11-13 04:00 | 449 | 447
2016-11-13 04:30 | 445 | 443
2016-11-13 05:00 | 432 | 429
2016-11-13 05:30 | 431 | 428
2016-11-13 06:00 | 431 | 428
2016-11-13 06:30 | 435 | 432
2016-11-13 07:00 | 453 | 449
2016-11-13 07:30 | 470 | 467
2016-11-13 08:00 | 476 | 474
2016-11-13 08:30 | 497 | 495
2016-11-13 09:00 | 515 | 514
2016-11-13 09:30 | 538 | 537
2016-11-13 10:00 | 564 | 564
2016-11-13 10:30 | 581 | 581
2016-11-13 11:00 | 578 | 577
2016-11-13 11:30 | 537 | 537
2016-11-13 12:00 | 550 | 549
2016-11-13 12:30 | 556 | 556
2016-11-13 13:00 | 573 | 573
2016-11-13 13:30 | 567 | 567
2016-11-13 14:00 | 575 | 575
2016-11-13 14:30 | 541 | 541
2016-11-13 15:00 | 463 | 462
2016-11-13 15:30 | 453 | 452
2016-11-13 16:00 | 402 | 401
2016-11-13 16:30 | 407 | 405
2016-11-13 17:00 | 480 | 478
2016-11-13 17:30 | 480 | 479
2016-11-13 18:00 | 524 | 523
2016-11-13 18:30 | 532 | 531
2016-11-13 19:00 | 514 | 514
2016-11-13 19:30 | 530 | 529
2016-11-13 20:00 | 527 | 526
2016-11-13 20:30 | 512 | 511
2016-11-13 21:00 | 498 | 497
2016-11-13 21:30 | 473 | 472
2016-11-13 22:00 | 490 | 489
2016-11-13 22:30 | 521 | 520
2016-11-13 23:00 | 515 | 514
2016-11-13 23:30 | 492 | 491
2016-11-14 | 426 | 425
2016-11-14 00:30 | 443 | 440
2016-11-14 01:00 | 439 | 436
2016-11-14 01:30 | 424 | 421
2016-11-14 02:00 | 417 | 413
2016-11-14 02:30 | 412 | 408
2016-11-14 03:00 | 413 | 409
2016-11-14 03:30 | 415 | 411
2016-11-14 04:00 | 411 | 407
2016-11-14 04:30 | 417 | 413
2016-11-14 05:00 | 429 | 425
2016-11-14 05:30 | 430 | 426
2016-11-14 06:00 | 432 | 428
2016-11-14 06:30 | 445 | 441
2016-11-14 07:00 | 477 | 474
2016-11-14 07:30 | 531 | 529
2016-11-14 08:00 | 561 | 560
2016-11-14 08:30 | 570 | 570
2016-11-14 09:00 | 581 | 581
2016-11-14 09:30 | 564 | 563
2016-11-14 10:00 | 538 | 538
2016-11-14 10:30 | 550 | 549
2016-11-14 11:00 | 549 | 549
2016-11-14 11:30 | 516 | 515
2016-11-14 12:00 | 468 | 467
2016-11-14 12:30 | 438 | 436
2016-11-14 13:00 | 476 | 474
2016-11-14 13:30 | 475 | 473
2016-11-14 14:00 | 497 | 495
2016-11-14 14:30 | 498 | 497
2016-11-14 15:00 | 539 | 538
2016-11-14 15:30 | 535 | 534
2016-11-14 16:00 | 523 | 523
2016-11-14 16:30 | 503 | 502
2016-11-14 17:00 | 502 | 501
2016-11-14 17:30 | 561 | 560
2016-11-14 18:00 | 587 | 587
2016-11-14 18:30 | 623 | 623
2016-11-14 19:00 | 541 | 541
2016-11-14 19:30 | 575 | 574
2016-11-14 20:00 | 520 | 520
2016-11-14 20:30 | 477 | 477
2016-11-14 21:00 | 533 | 532
2016-11-14 21:30 | 505 | 505
2016-11-14 22:00 | 475 | 473
2016-11-14 22:30 | 317 | 315
2016-11-14 23:00 | 328 | 320
2016-11-14 23:30 | 351 | 344
2016-11-15 | 435 | 429
2016-11-15 00:30 | 472 | 469
2016-11-15 01:00 | 450 | 448
2016-11-15 01:30 | 443 | 441
2016-11-15 02:00 | 443 | 440
2016-11-15 02:30 | 445 | 442
2016-11-15 03:00 | 425 | 422
2016-11-15 03:30 | 416 | 412
2016-11-15 04:00 | 414 | 410
2016-11-15 04:30 | 410 | 406
2016-11-15 05:00 | 406 | 402
2016-11-15 05:30 | 419 | 415
2016-11-15 06:00 | 427 | 423
2016-11-15 06:30 | 459 | 456
2016-11-15 07:00 | 479 | 477
2016-11-15 07:30 | 488 | 486
2016-11-15 08:00 | 500 | 498
2016-11-15 08:30 | 503 | 501
2016-11-15 09:00 | 500 | 499
2016-11-15 09:30 | 510 | 508
2016-11-15 10:00 | 510 | 509
2016-11-15 10:30 | 525 | 524
2016-11-15 11:00 | 537 | 536
2016-11-15 11:30 | 523 | 522
2016-11-15 12:00 | 526 | 526
2016-11-15 12:30 | 536 | 536
2016-11-15 13:00 | 541 | 541
2016-11-15 13:30 | 514 | 513
2016-11-15 14:00 | 492 | 492
2016-11-15 14:30 | 494 | 493
2016-11-15 15:00 | 498 | 498
2016-11-15 15:30 | 513 | 512
2016-11-15 16:00 | 522 | 522
2016-11-15 16:30 | 537 | 537
2016-11-15 17:00 | 566 | 565
2016-11-15 17:30 | 603 | 603
2016-11-15 18:00 | 605 | 605
2016-11-15 18:30 | 634 | 634
2016-11-15 19:00 | 651 | 651
2016-11-15 19:30 | 621 | 621
2016-11-15 20:00 | 633 | 633
2016-11-15 20:30 | 623 | 623
2016-11-15 21:00 | 596 | 596
2016-11-15 21:30 | 573 | 573
2016-11-15 22:00 | 547 | 547
2016-11-15 22:30 | 499 | 499
2016-11-15 23:00 | 483 | 481
2016-11-15 23:30 | 465 | 464
2016-11-16 | 450 | 448
2016-11-16 00:30 | 438 | 436
2016-11-16 01:00 | 425 | 422
2016-11-16 01:30 | 418 | 416
2016-11-16 02:00 | 406 | 403
2016-11-16 02:30 | 400 | 396
2016-11-16 03:00 | 404 | 400
2016-11-16 03:30 | 392 | 388
2016-11-16 04:00 | 386 | 382
2016-11-16 04:30 | 392 | 388
2016-11-16 05:00 | 402 | 398
2016-11-16 05:30 | 407 | 404
2016-11-16 06:00 | 411 | 409
2016-11-16 06:30 | 459 | 456
2016-11-16 07:00 | 492 | 490
2016-11-16 07:30 | 505 | 504
2016-11-16 08:00 | 524 | 523
2016-11-16 08:30 | 539 | 538
2016-11-16 09:00 | 540 | 540
2016-11-16 09:30 | 545 | 545
2016-11-16 10:00 | 546 | 545
2016-11-16 10:30 | 555 | 555
2016-11-16 11:00 | 548 | 548
2016-11-16 11:30 | 549 | 548
2016-11-16 12:00 | 557 | 557
2016-11-16 12:30 | 563 | 563
2016-11-16 13:00 | 574 | 574
2016-11-16 13:30 | 572 | 572
2016-11-16 14:00 | 581 | 581
2016-11-16 14:30 | 588 | 588
2016-11-16 15:00 | 609 | 609
2016-11-16 15:30 | 600 | 600
2016-11-16 16:00 | 610 | 609
2016-11-16 16:30 | 617 | 617
2016-11-16 17:00 | 620 | 620
2016-11-16 17:30 | 622 | 622
2016-11-16 18:00 | 618 | 618
2016-11-16 18:30 | 626 | 626
2016-11-16 19:00 | 645 | 645
2016-11-16 19:30 | 656 | 656
2016-11-16 20:00 | 646 | 646
2016-11-16 20:30 | 625 | 625
2016-11-16 21:00 | 597 | 597
2016-11-16 21:30 | 583 | 583
2016-11-16 22:00 | 546 | 546
2016-11-16 22:30 | 521 | 520
2016-11-16 23:00 | 502 | 501
2016-11-16 23:30 | 480 | 479
2016-11-17 | 465 | 464
2016-11-17 00:30 | 456 | 455
2016-11-17 01:00 | 439 | 437
2016-11-17 01:30 | 428 | 425
2016-11-17 02:00 | 423 | 420
2016-11-17 02:30 | 420 | 416
2016-11-17 03:00 | 416 | 412
2016-11-17 03:30 | 416 | 412
2016-11-17 04:00 | 416 | 412
2016-11-17 04:30 | 424 | 421
2016-11-17 05:00 | 428 | 426
2016-11-17 05:30 | 438 | 435
2016-11-17 06:00 | 447 | 444
2016-11-17 06:30 | 477 | 475
2016-11-17 07:00 | 483 | 481
2016-11-17 07:30 | 531 | 529
2016-11-17 08:00 | 553 | 552
2016-11-17 08:30 | 554 | 554
2016-11-17 09:00 | 561 | 561
2016-11-17 09:30 | 556 | 556
2016-11-17 10:00 | 551 | 551
2016-11-17 10:30 | 550 | 549
2016-11-17 11:00 | 551 | 550
2016-11-17 11:30 | 542 | 541
2016-11-17 12:00 | 569 | 569
2016-11-17 12:30 | 579 | 578
2016-11-17 13:00 | 567 | 567
2016-11-17 13:30 | 563 | 563
2016-11-17 14:00 | 558 | 557
2016-11-17 14:30 | 569 | 569
2016-11-17 15:00 | 570 | 570
2016-11-17 15:30 | 585 | 585
2016-11-17 16:00 | 606 | 605
2016-11-17 16:30 | 616 | 616
2016-11-17 17:00 | 611 | 611
2016-11-17 17:30 | 608 | 608
2016-11-17 18:00 | 612 | 612
2016-11-17 18:30 | 617 | 617
2016-11-17 19:00 | 642 | 642
2016-11-17 19:30 | 641 | 641
2016-11-17 20:00 | 623 | 623
2016-11-17 20:30 | 605 | 605
2016-11-17 21:00 | 593 | 593
2016-11-17 21:30 | 570 | 570
2016-11-17 22:00 | 555 | 555
2016-11-17 22:30 | 531 | 531
2016-11-17 23:00 | 494 | 494
2016-11-17 23:30 | 475 | 474
2016-11-18 | 462 | 461
2016-11-18 00:30 | 453 | 451
2016-11-18 01:00 | 433 | 431
2016-11-18 01:30 | 422 | 420
2016-11-18 02:00 | 425 | 422
2016-11-18 02:30 | 411 | 408
2016-11-18 03:00 | 402 | 399
2016-11-18 03:30 | 396 | 393
2016-11-18 04:00 | 395 | 392
2016-11-18 04:30 | 390 | 386
2016-11-18 05:00 | 399 | 395
2016-11-18 05:30 | 404 | 400
2016-11-18 06:00 | 412 | 409
2016-11-18 06:30 | 445 | 442
2016-11-18 07:00 | 431 | 428
2016-11-18 07:30 | 484 | 482
2016-11-18 08:00 | 516 | 514
2016-11-18 08:30 | 553 | 552
2016-11-18 09:00 | 554 | 553
2016-11-18 09:30 | 539 | 538
2016-11-18 10:00 | 440 | 439
2016-11-18 10:30 | 439 | 437
2016-11-18 11:00 | 443 | 441
2016-11-18 11:30 | 445 | 442
2016-11-18 12:00 | 443 | 441
2016-11-18 12:30 | 443 | 440
2016-11-18 13:00 | 460 | 458
2016-11-18 13:30 | 401 | 399
2016-11-18 14:00 | 349 | 345
2016-11-18 14:30 | 307 | 300
2016-11-18 15:00 | 332 | 324
2016-11-18 15:30 | 315 | 308
2016-11-18 16:00 | 317 | 309
2016-11-18 16:30 | 352 | 345
2016-11-18 17:00 | 378 | 373
2016-11-18 17:30 | 468 | 464
2016-11-18 18:00 | 481 | 479
2016-11-18 18:30 | 496 | 495
2016-11-18 19:00 | 474 | 473
2016-11-18 19:30 | 476 | 475
2016-11-18 20:00 | 471 | 470
2016-11-18 20:30 | 470 | 468
2016-11-18 21:00 | 456 | 454
2016-11-18 21:30 | 471 | 469
2016-11-18 22:00 | 544 | 542
2016-11-18 22:30 | 508 | 507
2016-11-18 23:00 | 496 | 495
2016-11-18 23:30 | 478 | 477
2016-11-19 | 465 | 463
2016-11-19 00:30 | 454 | 452
2016-11-19 01:00 | 432 | 429
2016-11-19 01:30 | 428 | 425
2016-11-19 02:00 | 418 | 414
2016-11-19 02:30 | 405 | 400
2016-11-19 03:00 | 399 | 394
2016-11-19 03:30 | 402 | 397
2016-11-19 04:00 | 395 | 390
2016-11-19 04:30 | 387 | 382
2016-11-19 05:00 | 390 | 384
2016-11-19 05:30 | 388 | 382
2016-11-19 06:00 | 390 | 383
2016-11-19 06:30 | 399 | 394
2016-11-19 07:00 | 428 | 422
2016-11-19 07:30 | 441 | 437
2016-11-19 08:00 | 446 | 442
2016-11-19 08:30 | 464 | 461
2016-11-19 09:00 | 485 | 482
2016-11-19 09:30 | 491 | 488
2016-11-19 10:00 | 490 | 488
2016-11-19 10:30 | 500 | 498
2016-11-19 11:00 | 490 | 489
2016-11-19 11:30 | 479 | 477
2016-11-19 12:00 | 477 | 475
2016-11-19 12:30 | 492 | 490
2016-11-19 13:00 | 491 | 489
2016-11-19 13:30 | 490 | 488
2016-11-19 14:00 | 499 | 497
2016-11-19 14:30 | 506 | 504
2016-11-19 15:00 | 499 | 497
2016-11-19 15:30 | 514 | 513
2016-11-19 16:00 | 529 | 528
2016-11-19 16:30 | 539 | 537
2016-11-19 17:00 | 553 | 553
2016-11-19 17:30 | 562 | 562
2016-11-19 18:00 | 563 | 563
2016-11-19 18:30 | 573 | 573
2016-11-19 19:00 | 589 | 589
2016-11-19 19:30 | 590 | 590
2016-11-19 20:00 | 572 | 572
2016-11-19 20:30 | 564 | 563
2016-11-19 21:00 | 547 | 547
2016-11-19 21:30 | 526 | 526
2016-11-19 22:00 | 513 | 513
2016-11-19 22:30 | 506 | 505
2016-11-19 23:00 | 482 | 481
2016-11-19 23:30 | 471 | 469
2016-11-20 | 458 | 455
2016-11-20 00:30 | 456 | 453
2016-11-20 01:00 | 434 | 431
2016-11-20 01:30 | 430 | 427
2016-11-20 02:00 | 416 | 412
2016-11-20 02:30 | 400 | 396
2016-11-20 03:00 | 394 | 390
2016-11-20 03:30 | 393 | 388
2016-11-20 04:00 | 389 | 383
2016-11-20 04:30 | 389 | 383
2016-11-20 05:00 | 391 | 386
2016-11-20 05:30 | 387 | 381
2016-11-20 06:00 | 381 | 375
2016-11-20 06:30 | 394 | 389
2016-11-20 07:00 | 411 | 406
2016-11-20 07:30 | 419 | 415
2016-11-20 08:00 | 433 | 429
2016-11-20 08:30 | 448 | 445
2016-11-20 09:00 | 463 | 460
2016-11-20 09:30 | 472 | 469
2016-11-20 10:00 | 479 | 477
2016-11-20 10:30 | 482 | 479
2016-11-20 11:00 | 471 | 469
2016-11-20 11:30 | 476 | 474
2016-11-20 12:00 | 482 | 480
2016-11-20 12:30 | 482 | 479
2016-11-20 13:00 | 495 | 493
2016-11-20 13:30 | 496 | 494
2016-11-20 14:00 | 502 | 501
2016-11-20 14:30 | 511 | 509
2016-11-20 15:00 | 519 | 517
2016-11-20 15:30 | 533 | 532
2016-11-20 16:00 | 541 | 540
2016-11-20 16:30 | 549 | 548
2016-11-20 17:00 | 559 | 559
2016-11-20 17:30 | 574 | 574
2016-11-20 18:00 | 583 | 582
2016-11-20 18:30 | 598 | 598
2016-11-20 19:00 | 608 | 607
2016-11-20 19:30 | 607 | 606
2016-11-20 20:00 | 595 | 595
2016-11-20 20:30 | 571 | 571
2016-11-20 21:00 | 570 | 570
2016-11-20 21:30 | 552 | 551
2016-11-20 22:00 | 533 | 532
2016-11-20 22:30 | 515 | 514
2016-11-20 23:00 | 485 | 483
2016-11-20 23:30 | 471 | 469
2016-11-21 | 456 | 453
2016-11-21 00:30 | 453 | 450
2016-11-21 01:00 | 434 | 431
2016-11-21 01:30 | 429 | 425
2016-11-21 02:00 | 412 | 407
2016-11-21 02:30 | 404 | 398
2016-11-21 03:00 | 403 | 397
2016-11-21 03:30 | 402 | 396
2016-11-21 04:00 | 402 | 396
2016-11-21 04:30 | 397 | 391
2016-11-21 05:00 | 359 | 352
2016-11-21 05:30 | 366 | 358
2016-11-21 06:00 | 363 | 355
2016-11-21 06:30 | 393 | 386
2016-11-21 07:00 | 436 | 431
2016-11-21 07:30 | 467 | 464
2016-11-21 08:00 | 485 | 483
2016-11-21 08:30 | 457 | 455
2016-11-21 09:00 | 410 | 408
2016-11-21 09:30 | 429 | 426
2016-11-21 10:00 | 426 | 423
2016-11-21 10:30 | 426 | 423
2016-11-21 11:00 | 426 | 423
2016-11-21 11:30 | 428 | 425
2016-11-21 12:00 | 431 | 428
2016-11-21 12:30 | 429 | 426
2016-11-21 13:00 | 428 | 425
2016-11-21 13:30 | 430 | 427
2016-11-21 14:00 | 435 | 432
2016-11-21 14:30 | 427 | 424
2016-11-21 15:00 | 427 | 424
2016-11-21 15:30 | 430 | 427
2016-11-21 16:00 | 432 | 429
2016-11-21 16:30 | 462 | 460
2016-11-21 17:00 | 478 | 476
2016-11-21 17:30 | 484 | 482
2016-11-21 18:00 | 482 | 480
2016-11-21 18:30 | 487 | 486
2016-11-21 19:00 | 515 | 514
2016-11-21 19:30 | 517 | 516
2016-11-21 20:00 | 492 | 491
2016-11-21 20:30 | 477 | 476
2016-11-21 21:00 | 454 | 452
2016-11-21 21:30 | 426 | 423
2016-11-21 22:00 | 399 | 396
2016-11-21 22:30 | 380 | 376
2016-11-21 23:00 | 343 | 338
2016-11-21 23:30 | 330 | 323
2016-11-22 | 320 | 311
2016-11-22 00:30 | 328 | 319
2016-11-22 01:00 | 307 | 297
2016-11-22 01:30 | 298 | 287
2016-11-22 02:00 | 290 | 278
2016-11-22 02:30 | 283 | 269
2016-11-22 03:00 | 285 | 272
2016-11-22 03:30 | 294 | 281
2016-11-22 04:00 | 305 | 293
2016-11-22 04:30 | 310 | 299
2016-11-22 05:00 | 313 | 302
2016-11-22 05:30 | 322 | 311
2016-11-22 06:00 | 331 | 321
2016-11-22 06:30 | 356 | 348
2016-11-22 07:00 | 396 | 390
2016-11-22 07:30 | 418 | 413
2016-11-22 08:00 | 427 | 424
2016-11-22 08:30 | 430 | 427
2016-11-22 09:00 | 430 | 427
2016-11-22 09:30 | 436 | 432
2016-11-22 10:00 | 439 | 436
2016-11-22 10:30 | 439 | 436
2016-11-22 11:00 | 438 | 435
2016-11-22 11:30 | 427 | 424
2016-11-22 12:00 | 449 | 446
2016-11-22 12:30 | 453 | 451
2016-11-22 13:00 | 454 | 452
2016-11-22 13:30 | 475 | 473
2016-11-22 14:00 | 488 | 486
2016-11-22 14:30 | 496 | 495
2016-11-22 15:00 | 422 | 421
2016-11-22 15:30 | 424 | 422
2016-11-22 16:00 | 401 | 398
2016-11-22 16:30 | 401 | 398
2016-11-22 17:00 | 451 | 448
2016-11-22 17:30 | 469 | 467
2016-11-22 18:00 | 458 | 456
2016-11-22 18:30 | 460 | 458
2016-11-22 19:00 | 482 | 480
2016-11-22 19:30 | 489 | 488
2016-11-22 20:00 | 480 | 478
2016-11-22 20:30 | 460 | 459
2016-11-22 21:00 | 436 | 434
2016-11-22 21:30 | 475 | 473
2016-11-22 22:00 | 594 | 593
2016-11-22 22:30 | 572 | 571
2016-11-22 23:00 | 523 | 523
2016-11-22 23:30 | 518 | 517
2016-11-23 | 504 | 503
2016-11-23 00:30 | 492 | 491
2016-11-23 01:00 | 483 | 481
2016-11-23 01:30 | 475 | 473
2016-11-23 02:00 | 465 | 463
2016-11-23 02:30 | 455 | 453
2016-11-23 03:00 | 457 | 454
2016-11-23 03:30 | 464 | 461
2016-11-23 04:00 | 450 | 448
2016-11-23 04:30 | 450 | 447
2016-11-23 05:00 | 456 | 453
2016-11-23 05:30 | 462 | 460
2016-11-23 06:00 | 474 | 471
2016-11-23 06:30 | 506 | 504
2016-11-23 07:00 | 534 | 533
2016-11-23 07:30 | 562 | 561
2016-11-23 08:00 | 580 | 580
2016-11-23 08:30 | 598 | 598
2016-11-23 09:00 | 596 | 596
2016-11-23 09:30 | 571 | 570
2016-11-23 10:00 | 590 | 589
2016-11-23 10:30 | 547 | 547
2016-11-23 11:00 | 554 | 553
2016-11-23 11:30 | 588 | 587
2016-11-23 12:00 | 594 | 594
2016-11-23 12:30 | 607 | 607
2016-11-23 13:00 | 547 | 547
2016-11-23 13:30 | 567 | 567
2016-11-23 14:00 | 649 | 648
2016-11-23 14:30 | 652 | 652
2016-11-23 15:00 | 651 | 651
2016-11-23 15:30 | 652 | 652
2016-11-23 16:00 | 638 | 638
2016-11-23 16:30 | 611 | 611
2016-11-23 17:00 | 634 | 634
2016-11-23 17:30 | 634 | 634
2016-11-23 18:00 | 693 | 692
2016-11-23 18:30 | 699 | 699
2016-11-23 19:00 | 717 | 717
2016-11-23 19:30 | 727 | 727
2016-11-23 20:00 | 720 | 720
2016-11-23 20:30 | 700 | 700
2016-11-23 21:00 | 670 | 670
2016-11-23 21:30 | 651 | 651
2016-11-23 22:00 | 627 | 627
2016-11-23 22:30 | 593 | 592
2016-11-23 23:00 | 563 | 563
2016-11-23 23:30 | 541 | 540
2016-11-24 | 527 | 525
2016-11-24 00:30 | 514 | 513
2016-11-24 01:00 | 503 | 502
2016-11-24 01:30 | 490 | 488
2016-11-24 02:00 | 476 | 474
2016-11-24 02:30 | 459 | 456
2016-11-24 03:00 | 457 | 454
2016-11-24 03:30 | 455 | 451
2016-11-24 04:00 | 455 | 451
2016-11-24 04:30 | 454 | 451
2016-11-24 05:00 | 455 | 452
2016-11-24 05:30 | 459 | 456
2016-11-24 06:00 | 479 | 476
2016-11-24 06:30 | 516 | 513
2016-11-24 07:00 | 542 | 540
2016-11-24 07:30 | 580 | 579
2016-11-24 08:00 | 616 | 615
2016-11-24 08:30 | 634 | 634
2016-11-24 09:00 | 640 | 640
2016-11-24 09:30 | 634 | 634
2016-11-24 10:00 | 622 | 622
2016-11-24 10:30 | 604 | 604
2016-11-24 11:00 | 602 | 602
2016-11-24 11:30 | 605 | 605
2016-11-24 12:00 | 616 | 616
2016-11-24 12:30 | 616 | 616
2016-11-24 13:00 | 622 | 622
2016-11-24 13:30 | 589 | 589
2016-11-24 14:00 | 587 | 587
2016-11-24 14:30 | 588 | 588
2016-11-24 15:00 | 566 | 566
2016-11-24 15:30 | 471 | 471
2016-11-24 16:00 | 481 | 480
2016-11-24 16:30 | 495 | 493
2016-11-24 17:00 | 533 | 532
2016-11-24 17:30 | 570 | 569
2016-11-24 18:00 | 573 | 572
2016-11-24 18:30 | 577 | 577
2016-11-24 19:00 | 536 | 536
2016-11-24 19:30 | 542 | 542
2016-11-24 20:00 | 526 | 526
2016-11-24 20:30 | 582 | 582
2016-11-24 21:00 | 660 | 660
2016-11-24 21:30 | 655 | 655
2016-11-24 22:00 | 638 | 638
2016-11-24 22:30 | 593 | 593
2016-11-24 23:00 | 569 | 569
2016-11-24 23:30 | 548 | 548
2016-11-25 | 532 | 531
2016-11-25 00:30 | 511 | 510
2016-11-25 01:00 | 499 | 497
2016-11-25 01:30 | 496 | 494
2016-11-25 02:00 | 485 | 482
2016-11-25 02:30 | 478 | 475
2016-11-25 03:00 | 466 | 464
2016-11-25 03:30 | 462 | 459
2016-11-25 04:00 | 454 | 451
2016-11-25 04:30 | 460 | 457
2016-11-25 05:00 | 466 | 463
2016-11-25 05:30 | 469 | 467
2016-11-25 06:00 | 479 | 476
2016-11-25 06:30 | 512 | 510
2016-11-25 07:00 | 547 | 546
2016-11-25 07:30 | 571 | 570
2016-11-25 08:00 | 594 | 594
2016-11-25 08:30 | 605 | 605
2016-11-25 09:00 | 604 | 604
2016-11-25 09:30 | 612 | 612
2016-11-25 10:00 | 608 | 608
2016-11-25 10:30 | 593 | 593
2016-11-25 11:00 | 582 | 582
2016-11-25 11:30 | 590 | 590
2016-11-25 12:00 | 604 | 603
2016-11-25 12:30 | 605 | 605
2016-11-25 13:00 | 603 | 603
2016-11-25 13:30 | 629 | 629
2016-11-25 14:00 | 663 | 663
2016-11-25 14:30 | 667 | 667
2016-11-25 15:00 | 662 | 662
2016-11-25 15:30 | 668 | 667
2016-11-25 16:00 | 678 | 678
2016-11-25 16:30 | 690 | 690
2016-11-25 17:00 | 709 | 709
2016-11-25 17:30 | 674 | 673
2016-11-25 18:00 | 671 | 671
2016-11-25 18:30 | 662 | 662
2016-11-25 19:00 | 658 | 658
2016-11-25 19:30 | 669 | 669
2016-11-25 20:00 | 657 | 657
2016-11-25 20:30 | 638 | 638
2016-11-25 21:00 | 624 | 624
2016-11-25 21:30 | 597 | 597
2016-11-25 22:00 | 585 | 585
2016-11-25 22:30 | 569 | 568
2016-11-25 23:00 | 537 | 537
2016-11-25 23:30 | 509 | 508
2016-11-26 | 494 | 493
2016-11-26 00:30 | 483 | 481
2016-11-26 01:00 | 460 | 458
2016-11-26 01:30 | 451 | 448
2016-11-26 02:00 | 442 | 439
2016-11-26 02:30 | 435 | 432
2016-11-26 03:00 | 428 | 424
2016-11-26 03:30 | 431 | 427
2016-11-26 04:00 | 423 | 419
2016-11-26 04:30 | 415 | 411
2016-11-26 05:00 | 419 | 415
2016-11-26 05:30 | 421 | 417
2016-11-26 06:00 | 418 | 414
2016-11-26 06:30 | 434 | 430
2016-11-26 07:00 | 454 | 451
2016-11-26 07:30 | 482 | 479
2016-11-26 08:00 | 491 | 489
2016-11-26 08:30 | 517 | 515
2016-11-26 09:00 | 537 | 536
2016-11-26 09:30 | 552 | 552
2016-11-26 10:00 | 535 | 534
2016-11-26 10:30 | 533 | 532
2016-11-26 11:00 | 528 | 527
2016-11-26 11:30 | 528 | 528
2016-11-26 12:00 | 532 | 532
2016-11-26 12:30 | 534 | 534
2016-11-26 13:00 | 535 | 535
2016-11-26 13:30 | 541 | 540
2016-11-26 14:00 | 550 | 550
2016-11-26 14:30 | 561 | 561
2016-11-26 15:00 | 558 | 558
2016-11-26 15:30 | 567 | 567
2016-11-26 16:00 | 587 | 586
2016-11-26 16:30 | 596 | 595
2016-11-26 17:00 | 625 | 625
2016-11-26 17:30 | 634 | 634
2016-11-26 18:00 | 642 | 642
2016-11-26 18:30 | 652 | 652
2016-11-26 19:00 | 668 | 668
2016-11-26 19:30 | 666 | 666
2016-11-26 20:00 | 647 | 647
2016-11-26 20:30 | 629 | 629
2016-11-26 21:00 | 612 | 612
2016-11-26 21:30 | 603 | 602
2016-11-26 22:00 | 589 | 588
2016-11-26 22:30 | 564 | 563
2016-11-26 23:00 | 537 | 536
2016-11-26 23:30 | 509 | 507
2016-11-27 | 493 | 490
2016-11-27 00:30 | 477 | 474
2016-11-27 01:00 | 459 | 455
2016-11-27 01:30 | 443 | 440
2016-11-27 02:00 | 432 | 429
2016-11-27 02:30 | 424 | 420
2016-11-27 03:00 | 418 | 414
2016-11-27 03:30 | 415 | 411
2016-11-27 04:00 | 411 | 406
2016-11-27 04:30 | 417 | 412
2016-11-27 05:00 | 416 | 411
2016-11-27 05:30 | 410 | 405
2016-11-27 06:00 | 409 | 404
2016-11-27 06:30 | 424 | 419
2016-11-27 07:00 | 436 | 432
2016-11-27 07:30 | 454 | 450
2016-11-27 08:00 | 466 | 463
2016-11-27 08:30 | 483 | 480
2016-11-27 09:00 | 511 | 509
2016-11-27 09:30 | 529 | 527
2016-11-27 10:00 | 509 | 507
2016-11-27 10:30 | 512 | 511
2016-11-27 11:00 | 517 | 515
2016-11-27 11:30 | 519 | 518
2016-11-27 12:00 | 532 | 531
2016-11-27 12:30 | 547 | 546
2016-11-27 13:00 | 555 | 554
2016-11-27 13:30 | 564 | 563
2016-11-27 14:00 | 558 | 557
2016-11-27 14:30 | 563 | 562
2016-11-27 15:00 | 563 | 563
2016-11-27 15:30 | 574 | 574
2016-11-27 16:00 | 587 | 587
2016-11-27 16:30 | 595 | 595
2016-11-27 17:00 | 625 | 625
2016-11-27 17:30 | 635 | 635
2016-11-27 18:00 | 640 | 640
2016-11-27 18:30 | 642 | 642
2016-11-27 19:00 | 654 | 654
2016-11-27 19:30 | 666 | 666
2016-11-27 20:00 | 647 | 647
2016-11-27 20:30 | 634 | 634
2016-11-27 21:00 | 619 | 619
2016-11-27 21:30 | 591 | 591
2016-11-27 22:00 | 565 | 565
2016-11-27 22:30 | 537 | 537
2016-11-27 23:00 | 521 | 520
2016-11-27 23:30 | 502 | 501
2016-11-28 | 481 | 479
2016-11-28 00:30 | 472 | 469
2016-11-28 01:00 | 460 | 458
2016-11-28 01:30 | 451 | 448
2016-11-28 02:00 | 440 | 436
2016-11-28 02:30 | 437 | 432
2016-11-28 03:00 | 429 | 424
2016-11-28 03:30 | 415 | 410
2016-11-28 04:00 | 424 | 418
2016-11-28 04:30 | 427 | 421
2016-11-28 05:00 | 424 | 419
2016-11-28 05:30 | 434 | 429
2016-11-28 06:00 | 450 | 445
2016-11-28 06:30 | 486 | 482
2016-11-28 07:00 | 488 | 485
2016-11-28 07:30 | 539 | 537
2016-11-28 08:00 | 558 | 557
2016-11-28 08:30 | 578 | 577
2016-11-28 09:00 | 582 | 581
2016-11-28 09:30 | 570 | 569
2016-11-28 10:00 | 578 | 577
2016-11-28 10:30 | 585 | 584
2016-11-28 11:00 | 584 | 584
2016-11-28 11:30 | 589 | 588
2016-11-28 12:00 | 594 | 593
2016-11-28 12:30 | 607 | 606
2016-11-28 13:00 | 625 | 625
2016-11-28 13:30 | 629 | 629
2016-11-28 14:00 | 634 | 633
2016-11-28 14:30 | 640 | 640
2016-11-28 15:00 | 627 | 627
2016-11-28 15:30 | 612 | 612
2016-11-28 16:00 | 636 | 635
2016-11-28 16:30 | 623 | 623
2016-11-28 17:00 | 649 | 649
2016-11-28 17:30 | 656 | 656
2016-11-28 18:00 | 655 | 654
2016-11-28 18:30 | 664 | 663
2016-11-28 19:00 | 681 | 680
2016-11-28 19:30 | 673 | 672
2016-11-28 20:00 | 646 | 645
2016-11-28 20:30 | 644 | 643
2016-11-28 21:00 | 623 | 622
2016-11-28 21:30 | 618 | 617
2016-11-28 22:00 | 593 | 592
2016-11-28 22:30 | 564 | 563
2016-11-28 23:00 | 537 | 535
2016-11-28 23:30 | 510 | 508
2016-11-29 | 498 | 495
2016-11-29 00:30 | 483 | 480
2016-11-29 01:00 | 466 | 463
2016-11-29 01:30 | 457 | 454
2016-11-29 02:00 | 451 | 447
2016-11-29 02:30 | 440 | 436
2016-11-29 03:00 | 436 | 431
2016-11-29 03:30 | 435 | 430
2016-11-29 04:00 | 431 | 426
2016-11-29 04:30 | 437 | 431
2016-11-29 05:00 | 440 | 435
2016-11-29 05:30 | 454 | 449
2016-11-29 06:00 | 445 | 440
2016-11-29 06:30 | 479 | 475
2016-11-29 07:00 | 505 | 501
2016-11-29 07:30 | 531 | 528
2016-11-29 08:00 | 548 | 546
2016-11-29 08:30 | 566 | 564
2016-11-29 09:00 | 578 | 577
2016-11-29 09:30 | 584 | 583
2016-11-29 10:00 | 577 | 576
2016-11-29 10:30 | 566 | 565
2016-11-29 11:00 | 561 | 559
2016-11-29 11:30 | 572 | 571
2016-11-29 12:00 | 575 | 574
2016-11-29 12:30 | 555 | 554
2016-11-29 13:00 | 556 | 555
2016-11-29 13:30 | 558 | 557
2016-11-29 14:00 | 572 | 571
2016-11-29 14:30 | 596 | 595
2016-11-29 15:00 | 607 | 607
2016-11-29 15:30 | 625 | 625
2016-11-29 16:00 | 636 | 636
2016-11-29 16:30 | 662 | 662
2016-11-29 17:00 | 672 | 672
2016-11-29 17:30 | 667 | 667
2016-11-29 18:00 | 672 | 671
2016-11-29 18:30 | 672 | 672
2016-11-29 19:00 | 678 | 678
2016-11-29 19:30 | 684 | 684
2016-11-29 20:00 | 673 | 673
2016-11-29 20:30 | 666 | 666
2016-11-29 21:00 | 636 | 636
2016-11-29 21:30 | 608 | 608
2016-11-29 22:00 | 581 | 580
2016-11-29 22:30 | 534 | 533
2016-11-29 23:00 | 527 | 525
2016-11-29 23:30 | 507 | 505
2016-11-30 | 493 | 490
2016-11-30 00:30 | 474 | 471
2016-11-30 01:00 | 461 | 458
2016-11-30 01:30 | 455 | 452
2016-11-30 02:00 | 443 | 439
2016-11-30 02:30 | 441 | 437
2016-11-30 03:00 | 440 | 435
2016-11-30 03:30 | 436 | 431
2016-11-30 04:00 | 430 | 425
2016-11-30 04:30 | 431 | 425
2016-11-30 05:00 | 437 | 432
2016-11-30 05:30 | 432 | 427
2016-11-30 06:00 | 438 | 433
2016-11-30 06:30 | 467 | 462
2016-11-30 07:00 | 505 | 502
2016-11-30 07:30 | 529 | 526
2016-11-30 08:00 | 538 | 536
2016-11-30 08:30 | 557 | 556
2016-11-30 09:00 | 527 | 526
2016-11-30 09:30 | 526 | 525
2016-11-30 10:00 | 543 | 542
2016-11-30 10:30 | 566 | 565
2016-11-30 11:00 | 564 | 563
2016-11-30 11:30 | 557 | 556
2016-11-30 12:00 | 577 | 576
2016-11-30 12:30 | 570 | 569
2016-11-30 13:00 | 557 | 556
2016-11-30 13:30 | 530 | 529
2016-11-30 14:00 | 545 | 544
2016-11-30 14:30 | 574 | 573
2016-11-30 15:00 | 613 | 613
2016-11-30 15:30 | 581 | 581
2016-11-30 16:00 | 594 | 594
2016-11-30 16:30 | 572 | 572
2016-11-30 17:00 | 574 | 574
2016-11-30 17:30 | 577 | 576
2016-11-30 18:00 | 574 | 574
2016-11-30 18:30 | 577 | 577
2016-11-30 19:00 | 597 | 596
2016-11-30 19:30 | 612 | 611
2016-11-30 20:00 | 601 | 600
2016-11-30 20:30 | 648 | 648
2016-11-30 21:00 | 639 | 639
2016-11-30 21:30 | 622 | 622
2016-11-30 22:00 | 590 | 589
2016-11-30 22:30 | 556 | 555
2016-11-30 23:00 | 528 | 527
2016-11-30 23:30 | 508 | 506
2016-12-01 | 486 | 484
2016-12-01 00:30 | 476 | 473
2016-12-01 01:00 | 459 | 456
2016-12-01 01:30 | 452 | 449
2016-12-01 02:00 | 444 | 440
2016-12-01 02:30 | 437 | 433
2016-12-01 03:00 | 433 | 429
2016-12-01 03:30 | 424 | 419
2016-12-01 04:00 | 415 | 410
2016-12-01 04:30 | 416 | 410
2016-12-01 05:00 | 420 | 414
2016-12-01 05:30 | 442 | 436
2016-12-01 06:00 | 449 | 444
2016-12-01 06:30 | 473 | 469
2016-12-01 07:00 | 500 | 496
2016-12-01 07:30 | 536 | 534
2016-12-01 08:00 | 552 | 550
2016-12-01 08:30 | 563 | 561
2016-12-01 09:00 | 550 | 549
2016-12-01 09:30 | 503 | 501
2016-12-01 10:00 | 507 | 505
2016-12-01 10:30 | 506 | 504
2016-12-01 11:00 | 508 | 507
2016-12-01 11:30 | 520 | 519
2016-12-01 12:00 | 523 | 522
2016-12-01 12:30 | 533 | 532
2016-12-01 13:00 | 559 | 558
2016-12-01 13:30 | 527 | 527
2016-12-01 14:00 | 578 | 577
2016-12-01 14:30 | 566 | 566
2016-12-01 15:00 | 579 | 579
2016-12-01 15:30 | 607 | 607
2016-12-01 16:00 | 612 | 612
2016-12-01 16:30 | 584 | 584
2016-12-01 17:00 | 613 | 612
2016-12-01 17:30 | 648 | 648
2016-12-01 18:00 | 655 | 655
2016-12-01 18:30 | 636 | 636
2016-12-01 19:00 | 646 | 645
2016-12-01 19:30 | 657 | 657
2016-12-01 20:00 | 647 | 647
2016-12-01 20:30 | 621 | 621
2016-12-01 21:00 | 605 | 605
2016-12-01 21:30 | 646 | 646
2016-12-01 22:00 | 632 | 632
2016-12-01 22:30 | 605 | 605
2016-12-01 23:00 | 582 | 581
2016-12-01 23:30 | 552 | 551
2016-12-02 | 507 | 505
2016-12-02 00:30 | 482 | 479
2016-12-02 01:00 | 470 | 466
2016-12-02 01:30 | 464 | 460
2016-12-02 02:00 | 452 | 448
2016-12-02 02:30 | 453 | 448
2016-12-02 03:00 | 447 | 442
2016-12-02 03:30 | 438 | 432
2016-12-02 04:00 | 435 | 429
2016-12-02 04:30 | 437 | 431
2016-12-02 05:00 | 440 | 434
2016-12-02 05:30 | 446 | 441
2016-12-02 06:00 | 451 | 446
2016-12-02 06:30 | 480 | 476
2016-12-02 07:00 | 507 | 504
2016-12-02 07:30 | 528 | 525
2016-12-02 08:00 | 528 | 526
2016-12-02 08:30 | 507 | 506
2016-12-02 09:00 | 506 | 505
2016-12-02 09:30 | 528 | 527
2016-12-02 10:00 | 536 | 535
2016-12-02 10:30 | 550 | 549
2016-12-02 11:00 | 557 | 556
2016-12-02 11:30 | 552 | 551
2016-12-02 12:00 | 489 | 488
2016-12-02 12:30 | 512 | 511
2016-12-02 13:00 | 526 | 525
2016-12-02 13:30 | 538 | 537
2016-12-02 14:00 | 549 | 548
2016-12-02 14:30 | 558 | 558
2016-12-02 15:00 | 536 | 536
2016-12-02 15:30 | 533 | 532
2016-12-02 16:00 | 492 | 491
2016-12-02 16:30 | 470 | 469
2016-12-02 17:00 | 524 | 523
2016-12-02 17:30 | 547 | 546
2016-12-02 18:00 | 553 | 553
2016-12-02 18:30 | 544 | 544
2016-12-02 19:00 | 552 | 552
2016-12-02 19:30 | 574 | 574
2016-12-02 20:00 | 566 | 566
2016-12-02 20:30 | 549 | 549
2016-12-02 21:00 | 529 | 528
2016-12-02 21:30 | 514 | 513
2016-12-02 22:00 | 488 | 487
2016-12-02 22:30 | 414 | 412
2016-12-02 23:00 | 456 | 453
2016-12-02 23:30 | 456 | 453
2016-12-03 | 439 | 436
2016-12-03 00:30 | 417 | 414
2016-12-03 01:00 | 403 | 399
2016-12-03 01:30 | 379 | 374
2016-12-03 02:00 | 372 | 366
2016-12-03 02:30 | 364 | 358
2016-12-03 03:00 | 364 | 358
2016-12-03 03:30 | 359 | 353
2016-12-03 04:00 | 355 | 348
2016-12-03 04:30 | 344 | 338
2016-12-03 05:00 | 345 | 339
2016-12-03 05:30 | 345 | 338
2016-12-03 06:00 | 344 | 337
2016-12-03 06:30 | 354 | 347
2016-12-03 07:00 | 369 | 363
2016-12-03 07:30 | 383 | 378
2016-12-03 08:00 | 397 | 393
2016-12-03 08:30 | 427 | 423
2016-12-03 09:00 | 442 | 439
2016-12-03 09:30 | 431 | 429
2016-12-03 10:00 | 437 | 434
2016-12-03 10:30 | 443 | 441
2016-12-03 11:00 | 448 | 446
2016-12-03 11:30 | 448 | 447
2016-12-03 12:00 | 466 | 465
2016-12-03 12:30 | 478 | 476
2016-12-03 13:00 | 486 | 485
2016-12-03 13:30 | 492 | 491
2016-12-03 14:00 | 504 | 503
2016-12-03 14:30 | 504 | 503
2016-12-03 15:00 | 513 | 512
2016-12-03 15:30 | 521 | 520
2016-12-03 16:00 | 495 | 495
2016-12-03 16:30 | 504 | 503
2016-12-03 17:00 | 519 | 518
2016-12-03 17:30 | 537 | 536
2016-12-03 18:00 | 538 | 538
2016-12-03 18:30 | 536 | 535
2016-12-03 19:00 | 541 | 541
2016-12-03 19:30 | 551 | 551
2016-12-03 20:00 | 542 | 541
2016-12-03 20:30 | 546 | 546
2016-12-03 21:00 | 615 | 614
2016-12-03 21:30 | 674 | 674
2016-12-03 22:00 | 655 | 655
2016-12-03 22:30 | 623 | 623
2016-12-03 23:00 | 609 | 609
2016-12-03 23:30 | 594 | 594
2016-12-04 | 562 | 562
2016-12-04 00:30 | 535 | 534
2016-12-04 01:00 | 521 | 520
2016-12-04 01:30 | 509 | 508
2016-12-04 02:00 | 494 | 492
2016-12-04 02:30 | 488 | 486
2016-12-04 03:00 | 483 | 480
2016-12-04 03:30 | 481 | 478
2016-12-04 04:00 | 477 | 475
2016-12-04 04:30 | 479 | 477
2016-12-04 05:00 | 475 | 473
2016-12-04 05:30 | 467 | 465
2016-12-04 06:00 | 460 | 457
2016-12-04 06:30 | 468 | 466
2016-12-04 07:00 | 477 | 475
2016-12-04 07:30 | 493 | 491
2016-12-04 08:00 | 511 | 509
2016-12-04 08:30 | 535 | 534
2016-12-04 09:00 | 540 | 539
2016-12-04 09:30 | 532 | 531
2016-12-04 10:00 | 526 | 525
2016-12-04 10:30 | 534 | 533
2016-12-04 11:00 | 535 | 534
2016-12-04 11:30 | 538 | 538
2016-12-04 12:00 | 545 | 545
2016-12-04 12:30 | 551 | 551
2016-12-04 13:00 | 558 | 558
2016-12-04 13:30 | 552 | 552
2016-12-04 14:00 | 561 | 561
2016-12-04 14:30 | 575 | 575
2016-12-04 15:00 | 532 | 532
2016-12-04 15:30 | 526 | 526
2016-12-04 16:00 | 508 | 508
2016-12-04 16:30 | 530 | 530
2016-12-04 17:00 | 539 | 538
2016-12-04 17:30 | 429 | 429
2016-12-04 18:00 | 444 | 442
2016-12-04 18:30 | 452 | 451
2016-12-04 19:00 | 493 | 492
2016-12-04 19:30 | 550 | 550
2016-12-04 20:00 | 581 | 581
2016-12-04 20:30 | 603 | 603
2016-12-04 21:00 | 622 | 621
2016-12-04 21:30 | 600 | 600
2016-12-04 22:00 | 567 | 567
2016-12-04 22:30 | 524 | 524
2016-12-04 23:00 | 510 | 509
2016-12-04 23:30 | 474 | 473
2016-12-05 | 525 | 523
2016-12-05 00:30 | 522 | 521
2016-12-05 01:00 | 515 | 513
2016-12-05 01:30 | 493 | 492
2016-12-05 02:00 | 483 | 481
2016-12-05 02:30 | 472 | 470
2016-12-05 03:00 | 470 | 468
2016-12-05 03:30 | 471 | 470
2016-12-05 04:00 | 472 | 470
2016-12-05 04:30 | 483 | 481
2016-12-05 05:00 | 483 | 481
2016-12-05 05:30 | 489 | 487
2016-12-05 06:00 | 492 | 490
2016-12-05 06:30 | 515 | 513
2016-12-05 07:00 | 472 | 470
2016-12-05 07:30 | 539 | 537
2016-12-05 08:00 | 546 | 545
2016-12-05 08:30 | 534 | 533
2016-12-05 09:00 | 543 | 543
2016-12-05 09:30 | 562 | 562
2016-12-05 10:00 | 555 | 555
2016-12-05 10:30 | 529 | 529
2016-12-05 11:00 | 518 | 518
2016-12-05 11:30 | 424 | 424
2016-12-05 12:00 | 426 | 423
2016-12-05 12:30 | 429 | 426
2016-12-05 13:00 | 399 | 396
2016-12-05 13:30 | 437 | 434
2016-12-05 14:00 | 393 | 390
2016-12-05 14:30 | 382 | 378
2016-12-05 15:00 | 349 | 345
2016-12-05 15:30 | 348 | 343
2016-12-05 16:00 | 308 | 302
2016-12-05 16:30 | 340 | 333
2016-12-05 17:00 | 398 | 393
2016-12-05 17:30 | 411 | 408
2016-12-05 18:00 | 475 | 473
2016-12-05 18:30 | 497 | 495
2016-12-05 19:00 | 457 | 456
2016-12-05 19:30 | 479 | 477
2016-12-05 20:00 | 498 | 497
2016-12-05 20:30 | 506 | 505
2016-12-05 21:00 | 585 | 584
2016-12-05 21:30 | 576 | 576
2016-12-05 22:00 | 553 | 553
2016-12-05 22:30 | 496 | 495
2016-12-05 23:00 | 500 | 498
2016-12-05 23:30 | 475 | 473
2016-12-06 | 455 | 452
2016-12-06 00:30 | 438 | 435
2016-12-06 01:00 | 419 | 416
2016-12-06 01:30 | 411 | 407
2016-12-06 02:00 | 400 | 396
2016-12-06 02:30 | 401 | 397
2016-12-06 03:00 | 397 | 393
2016-12-06 03:30 | 385 | 381
2016-12-06 04:00 | 383 | 379
2016-12-06 04:30 | 396 | 392
2016-12-06 05:00 | 402 | 398
2016-12-06 05:30 | 413 | 409
2016-12-06 06:00 | 425 | 422
2016-12-06 06:30 | 460 | 458
2016-12-06 07:00 | 438 | 436
2016-12-06 07:30 | 504 | 502
2016-12-06 08:00 | 577 | 577
2016-12-06 08:30 | 615 | 615
2016-12-06 09:00 | 619 | 619
2016-12-06 09:30 | 605 | 605
2016-12-06 10:00 | 568 | 568
2016-12-06 10:30 | 508 | 507
2016-12-06 11:00 | 488 | 487
2016-12-06 11:30 | 603 | 602
2016-12-06 12:00 | 617 | 617
2016-12-06 12:30 | 623 | 623
2016-12-06 13:00 | 627 | 627
2016-12-06 13:30 | 553 | 553
2016-12-06 14:00 | 540 | 539
2016-12-06 14:30 | 552 | 551
2016-12-06 15:00 | 514 | 514
2016-12-06 15:30 | 510 | 509
2016-12-06 16:00 | 481 | 480
2016-12-06 16:30 | 487 | 485
2016-12-06 17:00 | 503 | 501
2016-12-06 17:30 | 501 | 500
2016-12-06 18:00 | 484 | 483
2016-12-06 18:30 | 454 | 453
2016-12-06 19:00 | 469 | 466
2016-12-06 19:30 | 518 | 516
2016-12-06 20:00 | 543 | 541
2016-12-06 20:30 | 576 | 576
2016-12-06 21:00 | 611 | 610
2016-12-06 21:30 | 575 | 575
2016-12-06 22:00 | 535 | 535
2016-12-06 22:30 | 490 | 489
2016-12-06 23:00 | 480 | 478
2016-12-06 23:30 | 567 | 565
2016-12-07 | 563 | 562
2016-12-07 00:30 | 543 | 543
2016-12-07 01:00 | 522 | 520
2016-12-07 01:30 | 502 | 500
2016-12-07 02:00 | 502 | 500
2016-12-07 02:30 | 498 | 495
2016-12-07 03:00 | 491 | 488
2016-12-07 03:30 | 486 | 483
2016-12-07 04:00 | 484 | 480
2016-12-07 04:30 | 486 | 482
2016-12-07 05:00 | 492 | 488
2016-12-07 05:30 | 504 | 501
2016-12-07 06:00 | 509 | 506
2016-12-07 06:30 | 533 | 530
2016-12-07 07:00 | 560 | 558
2016-12-07 07:30 | 583 | 582
2016-12-07 08:00 | 605 | 604
2016-12-07 08:30 | 614 | 614
2016-12-07 09:00 | 621 | 621
2016-12-07 09:30 | 620 | 619
2016-12-07 10:00 | 611 | 610
2016-12-07 10:30 | 608 | 607
2016-12-07 11:00 | 549 | 547
2016-12-07 11:30 | 557 | 555
2016-12-07 12:00 | 561 | 560
2016-12-07 12:30 | 577 | 575
2016-12-07 13:00 | 584 | 583
2016-12-07 13:30 | 598 | 597
2016-12-07 14:00 | 547 | 546
2016-12-07 14:30 | 528 | 527
2016-12-07 15:00 | 529 | 527
2016-12-07 15:30 | 546 | 545
2016-12-07 16:00 | 518 | 516
2016-12-07 16:30 | 497 | 495
2016-12-07 17:00 | 523 | 521
2016-12-07 17:30 | 572 | 570
2016-12-07 18:00 | 544 | 543
2016-12-07 18:30 | 595 | 594
2016-12-07 19:00 | 609 | 609
2016-12-07 19:30 | 587 | 586
2016-12-07 20:00 | 552 | 551
2016-12-07 20:30 | 584 | 583
2016-12-07 21:00 | 644 | 643
2016-12-07 21:30 | 627 | 626
2016-12-07 22:00 | 603 | 602
2016-12-07 22:30 | 574 | 573
2016-12-07 23:00 | 544 | 543
2016-12-07 23:30 | 594 | 593
2016-12-08 | 585 | 584
2016-12-08 00:30 | 562 | 561
2016-12-08 01:00 | 543 | 541
2016-12-08 01:30 | 539 | 537
2016-12-08 02:00 | 534 | 532
2016-12-08 02:30 | 535 | 533
2016-12-08 03:00 | 534 | 531
2016-12-08 03:30 | 529 | 527
2016-12-08 04:00 | 524 | 522
2016-12-08 04:30 | 534 | 531
2016-12-08 05:00 | 541 | 538
2016-12-08 05:30 | 542 | 539
2016-12-08 06:00 | 535 | 532
2016-12-08 06:30 | 560 | 558
2016-12-08 07:00 | 590 | 588
2016-12-08 07:30 | 624 | 623
2016-12-08 08:00 | 633 | 632
2016-12-08 08:30 | 631 | 630
2016-12-08 09:00 | 617 | 617
2016-12-08 09:30 | 604 | 603
2016-12-08 10:00 | 577 | 576
2016-12-08 10:30 | 531 | 530
2016-12-08 11:00 | 488 | 486
2016-12-08 11:30 | 522 | 520
2016-12-08 12:00 | 620 | 618
2016-12-08 12:30 | 641 | 640
2016-12-08 13:00 | 653 | 652
2016-12-08 13:30 | 625 | 625
2016-12-08 14:00 | 594 | 593
2016-12-08 14:30 | 617 | 616
2016-12-08 15:00 | 645 | 645
2016-12-08 15:30 | 657 | 656
2016-12-08 16:00 | 669 | 669
2016-12-08 16:30 | 702 | 702
2016-12-08 17:00 | 693 | 693
2016-12-08 17:30 | 700 | 700
2016-12-08 18:00 | 710 | 710
2016-12-08 18:30 | 717 | 717
2016-12-08 19:00 | 714 | 714
2016-12-08 19:30 | 723 | 723
2016-12-08 20:00 | 715 | 715
2016-12-08 20:30 | 721 | 721
2016-12-08 21:00 | 738 | 738
2016-12-08 21:30 | 702 | 702
2016-12-08 22:00 | 674 | 674
2016-12-08 22:30 | 646 | 646
2016-12-08 23:00 | 617 | 617
2016-12-08 23:30 | 592 | 591
2016-12-09 | 561 | 560
2016-12-09 00:30 | 546 | 544
2016-12-09 01:00 | 531 | 530
2016-12-09 01:30 | 517 | 515
2016-12-09 02:00 | 515 | 514
2016-12-09 02:30 | 512 | 511
2016-12-09 03:00 | 517 | 515
2016-12-09 03:30 | 509 | 508
2016-12-09 04:00 | 510 | 508
2016-12-09 04:30 | 504 | 503
2016-12-09 05:00 | 507 | 505
2016-12-09 05:30 | 519 | 518
2016-12-09 06:00 | 515 | 514
2016-12-09 06:30 | 544 | 542
2016-12-09 07:00 | 569 | 568
2016-12-09 07:30 | 613 | 612
2016-12-09 08:00 | 629 | 629
2016-12-09 08:30 | 654 | 654
2016-12-09 09:00 | 645 | 645
2016-12-09 09:30 | 625 | 625
2016-12-09 10:00 | 615 | 614
2016-12-09 10:30 | 615 | 615
2016-12-09 11:00 | 629 | 628
2016-12-09 11:30 | 633 | 633
2016-12-09 12:00 | 593 | 593
2016-12-09 12:30 | 564 | 564
2016-12-09 13:00 | 528 | 527
2016-12-09 13:30 | 561 | 560
2016-12-09 14:00 | 591 | 591
2016-12-09 14:30 | 597 | 597
2016-12-09 15:00 | 607 | 607
2016-12-09 15:30 | 618 | 618
2016-12-09 16:00 | 606 | 606
2016-12-09 16:30 | 613 | 613
2016-12-09 17:00 | 612 | 612
2016-12-09 17:30 | 618 | 618
2016-12-09 18:00 | 600 | 600
2016-12-09 18:30 | 591 | 591
2016-12-09 19:00 | 603 | 603
2016-12-09 19:30 | 603 | 603
2016-12-09 20:00 | 589 | 589
2016-12-09 20:30 | 597 | 597
2016-12-09 21:00 | 612 | 612
2016-12-09 21:30 | 587 | 587
2016-12-09 22:00 | 566 | 566
2016-12-09 22:30 | 543 | 543
2016-12-09 23:00 | 517 | 517
2016-12-09 23:30 | 498 | 497
2016-12-10 | 477 | 476
2016-12-10 00:30 | 532 | 531
2016-12-10 01:00 | 523 | 523
2016-12-10 01:30 | 517 | 516
2016-12-10 02:00 | 506 | 506
2016-12-10 02:30 | 500 | 499
2016-12-10 03:00 | 491 | 490
2016-12-10 03:30 | 486 | 485
2016-12-10 04:00 | 483 | 482
2016-12-10 04:30 | 480 | 479
2016-12-10 05:00 | 482 | 481
2016-12-10 05:30 | 487 | 485
2016-12-10 06:00 | 481 | 480
2016-12-10 06:30 | 485 | 483
2016-12-10 07:00 | 522 | 521
2016-12-10 07:30 | 562 | 561
2016-12-10 08:00 | 571 | 570
2016-12-10 08:30 | 581 | 581
2016-12-10 09:00 | 590 | 590
2016-12-10 09:30 | 585 | 585
2016-12-10 10:00 | 559 | 559
2016-12-10 10:30 | 556 | 556
2016-12-10 11:00 | 562 | 561
2016-12-10 11:30 | 575 | 575
2016-12-10 12:00 | 583 | 583
2016-12-10 12:30 | 578 | 578
2016-12-10 13:00 | 584 | 584
2016-12-10 13:30 | 598 | 598
2016-12-10 14:00 | 608 | 608
2016-12-10 14:30 | 612 | 612
2016-12-10 15:00 | 615 | 615
2016-12-10 15:30 | 614 | 614
2016-12-10 16:00 | 590 | 590
2016-12-10 16:30 | 610 | 610
2016-12-10 17:00 | 620 | 620
2016-12-10 17:30 | 618 | 618
2016-12-10 18:00 | 614 | 614
2016-12-10 18:30 | 615 | 615
2016-12-10 19:00 | 619 | 619
2016-12-10 19:30 | 629 | 629
2016-12-10 20:00 | 617 | 617
2016-12-10 20:30 | 628 | 627
2016-12-10 21:00 | 647 | 647
2016-12-10 21:30 | 633 | 633
2016-12-10 22:00 | 623 | 623
2016-12-10 22:30 | 600 | 600
2016-12-10 23:00 | 579 | 579
2016-12-10 23:30 | 558 | 558
2016-12-11 | 535 | 535
2016-12-11 00:30 | 526 | 525
2016-12-11 01:00 | 516 | 514
2016-12-11 01:30 | 510 | 508
2016-12-11 02:00 | 493 | 491
2016-12-11 02:30 | 489 | 488
2016-12-11 03:00 | 488 | 486
2016-12-11 03:30 | 483 | 481
2016-12-11 04:00 | 475 | 473
2016-12-11 04:30 | 475 | 473
2016-12-11 05:00 | 472 | 470
2016-12-11 05:30 | 477 | 475
2016-12-11 06:00 | 467 | 465
2016-12-11 06:30 | 468 | 466
2016-12-11 07:00 | 472 | 470
2016-12-11 07:30 | 493 | 491
2016-12-11 08:00 | 505 | 504
2016-12-11 08:30 | 514 | 513
2016-12-11 09:00 | 520 | 519
2016-12-11 09:30 | 529 | 528
2016-12-11 10:00 | 524 | 524
2016-12-11 10:30 | 527 | 526
2016-12-11 11:00 | 522 | 522
2016-12-11 11:30 | 525 | 524
2016-12-11 12:00 | 528 | 527
2016-12-11 12:30 | 529 | 528
2016-12-11 13:00 | 527 | 527
2016-12-11 13:30 | 505 | 504
2016-12-11 14:00 | 508 | 507
2016-12-11 14:30 | 507 | 506
2016-12-11 15:00 | 516 | 516
2016-12-11 15:30 | 531 | 530
2016-12-11 16:00 | 502 | 501
2016-12-11 16:30 | 518 | 517
2016-12-11 17:00 | 538 | 537
2016-12-11 17:30 | 556 | 556
2016-12-11 18:00 | 569 | 568
2016-12-11 18:30 | 576 | 576
2016-12-11 19:00 | 581 | 581
2016-12-11 19:30 | 586 | 586
2016-12-11 20:00 | 581 | 581
2016-12-11 20:30 | 600 | 600
2016-12-11 21:00 | 621 | 621
2016-12-11 21:30 | 608 | 607
2016-12-11 22:00 | 588 | 587
2016-12-11 22:30 | 566 | 566
2016-12-11 23:00 | 547 | 547
2016-12-11 23:30 | 530 | 529
2016-12-12 | 502 | 501
2016-12-12 00:30 | 477 | 475
2016-12-12 01:00 | 468 | 466
2016-12-12 01:30 | 464 | 462
2016-12-12 02:00 | 459 | 457
2016-12-12 02:30 | 448 | 446
2016-12-12 03:00 | 448 | 446
2016-12-12 03:30 | 441 | 439
2016-12-12 04:00 | 445 | 442
2016-12-12 04:30 | 444 | 441
2016-12-12 05:00 | 455 | 453
2016-12-12 05:30 | 464 | 462
2016-12-12 06:00 | 479 | 477
2016-12-12 06:30 | 494 | 492
2016-12-12 07:00 | 477 | 475
2016-12-12 07:30 | 503 | 501
2016-12-12 08:00 | 533 | 532
2016-12-12 08:30 | 553 | 552
2016-12-12 09:00 | 554 | 554
2016-12-12 09:30 | 548 | 548
2016-12-12 10:00 | 531 | 531
2016-12-12 10:30 | 501 | 501
2016-12-12 11:00 | 433 | 432
2016-12-12 11:30 | 455 | 453
2016-12-12 12:00 | 461 | 459
2016-12-12 12:30 | 453 | 452
2016-12-12 13:00 | 463 | 461
2016-12-12 13:30 | 443 | 441
2016-12-12 14:00 | 438 | 436
2016-12-12 14:30 | 433 | 430
2016-12-12 15:00 | 436 | 433
2016-12-12 15:30 | 375 | 372
2016-12-12 16:00 | 339 | 334
2016-12-12 16:30 | 367 | 362
2016-12-12 17:00 | 371 | 367
2016-12-12 17:30 | 372 | 368
2016-12-12 18:00 | 369 | 365
2016-12-12 18:30 | 376 | 372
2016-12-12 19:00 | 396 | 392
2016-12-12 19:30 | 414 | 410
2016-12-12 20:00 | 407 | 404
2016-12-12 20:30 | 420 | 417
2016-12-12 21:00 | 496 | 494
2016-12-12 21:30 | 494 | 493
2016-12-12 22:00 | 468 | 467
2016-12-12 22:30 | 442 | 440
2016-12-12 23:00 | 415 | 413
2016-12-12 23:30 | 401 | 398
2016-12-13 | 383 | 379
2016-12-13 00:30 | 364 | 359
2016-12-13 01:00 | 350 | 344
2016-12-13 01:30 | 344 | 337
2016-12-13 02:00 | 341 | 334
2016-12-13 02:30 | 342 | 335
2016-12-13 03:00 | 392 | 386
2016-12-13 03:30 | 396 | 392
2016-12-13 04:00 | 392 | 387
2016-12-13 04:30 | 392 | 387
2016-12-13 05:00 | 400 | 395
2016-12-13 05:30 | 406 | 402
2016-12-13 06:00 | 404 | 400
2016-12-13 06:30 | 426 | 422
2016-12-13 07:00 | 463 | 460
2016-12-13 07:30 | 494 | 491
2016-12-13 08:00 | 513 | 511
2016-12-13 08:30 | 524 | 523
2016-12-13 09:00 | 542 | 541
2016-12-13 09:30 | 531 | 529
2016-12-13 10:00 | 519 | 517
2016-12-13 10:30 | 520 | 518
2016-12-13 11:00 | 515 | 513
2016-12-13 11:30 | 521 | 519
2016-12-13 12:00 | 527 | 526
2016-12-13 12:30 | 531 | 529
2016-12-13 13:00 | 529 | 528
2016-12-13 13:30 | 536 | 535
2016-12-13 14:00 | 513 | 512
2016-12-13 14:30 | 507 | 505
2016-12-13 15:00 | 520 | 518
2016-12-13 15:30 | 524 | 522
2016-12-13 16:00 | 487 | 486
2016-12-13 16:30 | 495 | 493
2016-12-13 17:00 | 495 | 493
2016-12-13 17:30 | 492 | 490
2016-12-13 18:00 | 506 | 505
2016-12-13 18:30 | 513 | 512
2016-12-13 19:00 | 521 | 519
2016-12-13 19:30 | 489 | 487
2016-12-13 20:00 | 490 | 489
2016-12-13 20:30 | 501 | 500
2016-12-13 21:00 | 521 | 520
2016-12-13 21:30 | 495 | 493
2016-12-13 22:00 | 469 | 467
2016-12-13 22:30 | 363 | 361
2016-12-13 23:00 | 402 | 397
2016-12-13 23:30 | 397 | 392
2016-12-14 | 382 | 378
2016-12-14 00:30 | 363 | 358
2016-12-14 01:00 | 352 | 346
2016-12-14 01:30 | 352 | 345
2016-12-14 02:00 | 349 | 342
2016-12-14 02:30 | 346 | 339
2016-12-14 03:00 | 335 | 328
2016-12-14 03:30 | 333 | 325
2016-12-14 04:00 | 338 | 330
2016-12-14 04:30 | 340 | 332
2016-12-14 05:00 | 340 | 332
2016-12-14 05:30 | 352 | 345
2016-12-14 06:00 | 359 | 353
2016-12-14 06:30 | 399 | 393
2016-12-14 07:00 | 414 | 409
2016-12-14 07:30 | 447 | 443
2016-12-14 08:00 | 468 | 465
2016-12-14 08:30 | 476 | 473
2016-12-14 09:00 | 493 | 491
2016-12-14 09:30 | 480 | 478
2016-12-14 10:00 | 468 | 466
2016-12-14 10:30 | 467 | 464
2016-12-14 11:00 | 470 | 467
2016-12-14 11:30 | 482 | 479
2016-12-14 12:00 | 486 | 484
2016-12-14 12:30 | 471 | 469
2016-12-14 13:00 | 469 | 467
2016-12-14 13:30 | 492 | 490
2016-12-14 14:00 | 506 | 504
2016-12-14 14:30 | 507 | 506
2016-12-14 15:00 | 502 | 500
2016-12-14 15:30 | 504 | 502
2016-12-14 16:00 | 481 | 479
2016-12-14 16:30 | 448 | 446
2016-12-14 17:00 | 461 | 459
2016-12-14 17:30 | 454 | 452
2016-12-14 18:00 | 506 | 504
2016-12-14 18:30 | 504 | 503
2016-12-14 19:00 | 474 | 472
2016-12-14 19:30 | 495 | 493
2016-12-14 20:00 | 505 | 502
2016-12-14 20:30 | 522 | 520
2016-12-14 21:00 | 538 | 537
2016-12-14 21:30 | 518 | 517
2016-12-14 22:00 | 499 | 498
2016-12-14 22:30 | 465 | 464
2016-12-14 23:00 | 453 | 451
2016-12-14 23:30 | 419 | 417
2016-12-15 | 401 | 398
2016-12-15 00:30 | 389 | 385
2016-12-15 01:00 | 386 | 381
2016-12-15 01:30 | 378 | 373
2016-12-15 02:00 | 371 | 365
2016-12-15 02:30 | 366 | 360
2016-12-15 03:00 | 359 | 353
2016-12-15 03:30 | 368 | 362
2016-12-15 04:00 | 365 | 358
2016-12-15 04:30 | 366 | 359
2016-12-15 05:00 | 372 | 366
2016-12-15 05:30 | 377 | 370
2016-12-15 06:00 | 385 | 379
2016-12-15 06:30 | 409 | 404
2016-12-15 07:00 | 440 | 436
2016-12-15 07:30 | 473 | 469
2016-12-15 08:00 | 498 | 495
2016-12-15 08:30 | 504 | 503
2016-12-15 09:00 | 517 | 517
2016-12-15 09:30 | 501 | 501
2016-12-15 10:00 | 487 | 487
2016-12-15 10:30 | 493 | 492
2016-12-15 11:00 | 496 | 495
2016-12-15 11:30 | 502 | 501
2016-12-15 12:00 | 504 | 503
2016-12-15 12:30 | 413 | 412
2016-12-15 13:00 | 431 | 429
2016-12-15 13:30 | 441 | 439
2016-12-15 14:00 | 433 | 432
2016-12-15 14:30 | 439 | 438
2016-12-15 15:00 | 473 | 472
2016-12-15 15:30 | 435 | 435
2016-12-15 16:00 | 467 | 465
2016-12-15 16:30 | 485 | 484
2016-12-15 17:00 | 445 | 445
2016-12-15 17:30 | 436 | 435
2016-12-15 18:00 | 477 | 476
2016-12-15 18:30 | 514 | 513
2016-12-15 19:00 | 471 | 471
2016-12-15 19:30 | 462 | 461
2016-12-15 20:00 | 516 | 516
2016-12-15 20:30 | 486 | 486
2016-12-15 21:00 | 517 | 517
2016-12-15 21:30 | 523 | 523
2016-12-15 22:00 | 502 | 502
2016-12-15 22:30 | 467 | 466
2016-12-15 23:00 | 398 | 397
2016-12-15 23:30 | 366 | 363
2016-12-16 | 418 | 415
2016-12-16 00:30 | 400 | 398
2016-12-16 01:00 | 383 | 380
2016-12-16 01:30 | 373 | 369
2016-12-16 02:00 | 370 | 366
2016-12-16 02:30 | 359 | 355
2016-12-16 03:00 | 358 | 354
2016-12-16 03:30 | 356 | 352
2016-12-16 04:00 | 359 | 354
2016-12-16 04:30 | 356 | 351
2016-12-16 05:00 | 351 | 347
2016-12-16 05:30 | 353 | 349
2016-12-16 06:00 | 362 | 357
2016-12-16 06:30 | 334 | 329
2016-12-16 07:00 | 250 | 244
2016-12-16 07:30 | 300 | 291
2016-12-16 08:00 | 348 | 342
2016-12-16 08:30 | 331 | 326
2016-12-16 09:00 | 370 | 365
2016-12-16 09:30 | 378 | 375
2016-12-16 10:00 | 377 | 374
2016-12-16 10:30 | 377 | 374
2016-12-16 11:00 | 407 | 404
2016-12-16 11:30 | 417 | 414
2016-12-16 12:00 | 409 | 407
2016-12-16 12:30 | 390 | 387
2016-12-16 13:00 | 427 | 424
2016-12-16 13:30 | 448 | 447
2016-12-16 14:00 | 454 | 453
2016-12-16 14:30 | 440 | 439
2016-12-16 15:00 | 510 | 509
2016-12-16 15:30 | 552 | 552
2016-12-16 16:00 | 519 | 519
2016-12-16 16:30 | 476 | 476
2016-12-16 17:00 | 497 | 496
2016-12-16 17:30 | 509 | 509
2016-12-16 18:00 | 551 | 550
2016-12-16 18:30 | 543 | 543
2016-12-16 19:00 | 558 | 558
2016-12-16 19:30 | 581 | 580
2016-12-16 20:00 | 535 | 535
2016-12-16 20:30 | 493 | 493
2016-12-16 21:00 | 494 | 493
2016-12-16 21:30 | 495 | 494
2016-12-16 22:00 | 493 | 492
2016-12-16 22:30 | 458 | 457
2016-12-16 23:00 | 425 | 424
2016-12-16 23:30 | 452 | 450
2016-12-17 | 510 | 509
2016-12-17 00:30 | 537 | 536
2016-12-17 01:00 | 532 | 531
2016-12-17 01:30 | 519 | 518
2016-12-17 02:00 | 509 | 508
2016-12-17 02:30 | 505 | 504
2016-12-17 03:00 | 501 | 500
2016-12-17 03:30 | 499 | 498
2016-12-17 04:00 | 506 | 505
2016-12-17 04:30 | 503 | 502
2016-12-17 05:00 | 500 | 499
2016-12-17 05:30 | 501 | 500
2016-12-17 06:00 | 498 | 497
2016-12-17 06:30 | 507 | 506
2016-12-17 07:00 | 517 | 516
2016-12-17 07:30 | 543 | 542
2016-12-17 08:00 | 571 | 571
2016-12-17 08:30 | 584 | 584
2016-12-17 09:00 | 601 | 600
2016-12-17 09:30 | 602 | 602
2016-12-17 10:00 | 591 | 591
2016-12-17 10:30 | 591 | 590
2016-12-17 11:00 | 592 | 592
2016-12-17 11:30 | 596 | 596
2016-12-17 12:00 | 584 | 583
2016-12-17 12:30 | 584 | 584
2016-12-17 13:00 | 601 | 601
2016-12-17 13:30 | 549 | 549
2016-12-17 14:00 | 532 | 531
2016-12-17 14:30 | 531 | 530
2016-12-17 15:00 | 524 | 523
2016-12-17 15:30 | 531 | 529
2016-12-17 16:00 | 509 | 508
2016-12-17 16:30 | 454 | 453
2016-12-17 17:00 | 486 | 484
2016-12-17 17:30 | 509 | 507
2016-12-17 18:00 | 545 | 545
2016-12-17 18:30 | 561 | 560
2016-12-17 19:00 | 552 | 552
2016-12-17 19:30 | 567 | 566
2016-12-17 20:00 | 575 | 575
2016-12-17 20:30 | 559 | 559
2016-12-17 21:00 | 575 | 575
2016-12-17 21:30 | 574 | 574
2016-12-17 22:00 | 553 | 553
2016-12-17 22:30 | 467 | 466
2016-12-17 23:00 | 511 | 509
2016-12-17 23:30 | 462 | 461
2016-12-18 | 473 | 471
2016-12-18 00:30 | 465 | 463
2016-12-18 01:00 | 524 | 522
2016-12-18 01:30 | 520 | 519
2016-12-18 02:00 | 514 | 512
2016-12-18 02:30 | 500 | 499
2016-12-18 03:00 | 498 | 497
2016-12-18 03:30 | 500 | 499
2016-12-18 04:00 | 497 | 496
2016-12-18 04:30 | 502 | 501
2016-12-18 05:00 | 508 | 507
2016-12-18 05:30 | 521 | 520
2016-12-18 06:00 | 512 | 510
2016-12-18 06:30 | 504 | 502
2016-12-18 07:00 | 504 | 503
2016-12-18 07:30 | 520 | 518
2016-12-18 08:00 | 535 | 534
2016-12-18 08:30 | 554 | 553
2016-12-18 09:00 | 559 | 558
2016-12-18 09:30 | 522 | 522
2016-12-18 10:00 | 574 | 573
2016-12-18 10:30 | 573 | 573
2016-12-18 11:00 | 561 | 560
2016-12-18 11:30 | 525 | 525
2016-12-18 12:00 | 537 | 536
2016-12-18 12:30 | 536 | 536
2016-12-18 13:00 | 545 | 545
2016-12-18 13:30 | 546 | 546
2016-12-18 14:00 | 565 | 565
2016-12-18 14:30 | 561 | 561
2016-12-18 15:00 | 548 | 548
2016-12-18 15:30 | 544 | 544
2016-12-18 16:00 | 548 | 548
2016-12-18 16:30 | 591 | 590
2016-12-18 17:00 | 635 | 635
2016-12-18 17:30 | 659 | 659
2016-12-18 18:00 | 664 | 664
2016-12-18 18:30 | 665 | 665
2016-12-18 19:00 | 665 | 665
2016-12-18 19:30 | 673 | 673
2016-12-18 20:00 | 660 | 660
2016-12-18 20:30 | 665 | 665
2016-12-18 21:00 | 685 | 685
2016-12-18 21:30 | 687 | 687
2016-12-18 22:00 | 666 | 666
2016-12-18 22:30 | 596 | 596
2016-12-18 23:00 | 549 | 549
2016-12-18 23:30 | 572 | 571
2016-12-19 | 574 | 573
2016-12-19 00:30 | 562 | 561
2016-12-19 01:00 | 551 | 550
2016-12-19 01:30 | 537 | 536
2016-12-19 02:00 | 539 | 538
2016-12-19 02:30 | 528 | 527
2016-12-19 03:00 | 520 | 519
2016-12-19 03:30 | 518 | 516
2016-12-19 04:00 | 515 | 513
2016-12-19 04:30 | 512 | 510
2016-12-19 05:00 | 513 | 512
2016-12-19 05:30 | 525 | 524
2016-12-19 06:00 | 524 | 523
2016-12-19 06:30 | 549 | 548
2016-12-19 07:00 | 570 | 569
2016-12-19 07:30 | 615 | 615
2016-12-19 08:00 | 632 | 632
2016-12-19 08:30 | 650 | 650
2016-12-19 09:00 | 653 | 653
2016-12-19 09:30 | 641 | 641
2016-12-19 10:00 | 628 | 628
2016-12-19 10:30 | 630 | 630
2016-12-19 11:00 | 634 | 634
2016-12-19 11:30 | 639 | 639
2016-12-19 12:00 | 644 | 644
2016-12-19 12:30 | 655 | 655
2016-12-19 13:00 | 661 | 661
2016-12-19 13:30 | 666 | 666
2016-12-19 14:00 | 686 | 686
2016-12-19 14:30 | 694 | 694
2016-12-19 15:00 | 696 | 696
2016-12-19 15:30 | 707 | 707
2016-12-19 16:00 | 684 | 684
2016-12-19 16:30 | 725 | 725
2016-12-19 17:00 | 724 | 724
2016-12-19 17:30 | 738 | 738
2016-12-19 18:00 | 750 | 750
2016-12-19 18:30 | 758 | 757
2016-12-19 19:00 | 765 | 765
2016-12-19 19:30 | 784 | 784
2016-12-19 20:00 | 776 | 776
2016-12-19 20:30 | 754 | 754
2016-12-19 21:00 | 744 | 744
2016-12-19 21:30 | 720 | 720
2016-12-19 22:00 | 689 | 689
2016-12-19 22:30 | 609 | 609
2016-12-19 23:00 | 571 | 570
2016-12-19 23:30 | 594 | 593
2016-12-20 | 584 | 583
2016-12-20 00:30 | 569 | 568
2016-12-20 01:00 | 552 | 551
2016-12-20 01:30 | 541 | 539
2016-12-20 02:00 | 538 | 537
2016-12-20 02:30 | 526 | 524
2016-12-20 03:00 | 522 | 521
2016-12-20 03:30 | 519 | 517
2016-12-20 04:00 | 524 | 523
2016-12-20 04:30 | 519 | 518
2016-12-20 05:00 | 519 | 518
2016-12-20 05:30 | 509 | 507
2016-12-20 06:00 | 469 | 468
2016-12-20 06:30 | 448 | 446
2016-12-20 07:00 | 427 | 425
2016-12-20 07:30 | 460 | 457
2016-12-20 08:00 | 479 | 477
2016-12-20 08:30 | 487 | 485
2016-12-20 09:00 | 507 | 506
2016-12-20 09:30 | 491 | 489
2016-12-20 10:00 | 465 | 463
2016-12-20 10:30 | 399 | 396
2016-12-20 11:00 | 408 | 404
2016-12-20 11:30 | 421 | 418
2016-12-20 12:00 | 426 | 423
2016-12-20 12:30 | 435 | 432
2016-12-20 13:00 | 421 | 419
2016-12-20 13:30 | 426 | 423
2016-12-20 14:00 | 451 | 449
2016-12-20 14:30 | 462 | 460
2016-12-20 15:00 | 475 | 473
2016-12-20 15:30 | 412 | 410
2016-12-20 16:00 | 408 | 405
2016-12-20 16:30 | 426 | 423
2016-12-20 17:00 | 456 | 454
2016-12-20 17:30 | 454 | 452
2016-12-20 18:00 | 455 | 453
2016-12-20 18:30 | 464 | 463
2016-12-20 19:00 | 480 | 478
2016-12-20 19:30 | 511 | 510
2016-12-20 20:00 | 541 | 540
2016-12-20 20:30 | 532 | 531
2016-12-20 21:00 | 521 | 521
2016-12-20 21:30 | 541 | 540
2016-12-20 22:00 | 562 | 561
2016-12-20 22:30 | 502 | 501
2016-12-20 23:00 | 523 | 522
2016-12-20 23:30 | 495 | 494
2016-12-21 | 467 | 465
2016-12-21 00:30 | 458 | 456
2016-12-21 01:00 | 436 | 433
2016-12-21 01:30 | 424 | 421
2016-12-21 02:00 | 423 | 419
2016-12-21 02:30 | 417 | 414
2016-12-21 03:00 | 412 | 408
2016-12-21 03:30 | 408 | 404
2016-12-21 04:00 | 400 | 396
2016-12-21 04:30 | 402 | 398
2016-12-21 05:00 | 410 | 406
2016-12-21 05:30 | 422 | 418
2016-12-21 06:00 | 405 | 401
2016-12-21 06:30 | 402 | 398
2016-12-21 07:00 | 444 | 440
2016-12-21 07:30 | 478 | 475
2016-12-21 08:00 | 505 | 503
2016-12-21 08:30 | 520 | 519
2016-12-21 09:00 | 532 | 531
2016-12-21 09:30 | 520 | 519
2016-12-21 10:00 | 506 | 506
2016-12-21 10:30 | 516 | 515
2016-12-21 11:00 | 518 | 517
2016-12-21 11:30 | 519 | 518
2016-12-21 12:00 | 462 | 462
2016-12-21 12:30 | 455 | 454
2016-12-21 13:00 | 458 | 456
2016-12-21 13:30 | 457 | 456
2016-12-21 14:00 | 450 | 449
2016-12-21 14:30 | 452 | 451
2016-12-21 15:00 | 417 | 416
2016-12-21 15:30 | 426 | 424
2016-12-21 16:00 | 447 | 446
2016-12-21 16:30 | 458 | 457
2016-12-21 17:00 | 471 | 470
2016-12-21 17:30 | 503 | 502
2016-12-21 18:00 | 521 | 520
2016-12-21 18:30 | 542 | 541
2016-12-21 19:00 | 549 | 549
2016-12-21 19:30 | 565 | 565
2016-12-21 20:00 | 557 | 557
2016-12-21 20:30 | 554 | 554
2016-12-21 21:00 | 549 | 549
2016-12-21 21:30 | 596 | 595
2016-12-21 22:00 | 579 | 579
2016-12-21 22:30 | 527 | 527
2016-12-21 23:00 | 522 | 521
2016-12-21 23:30 | 493 | 492
2016-12-22 | 516 | 516
2016-12-22 00:30 | 580 | 580
2016-12-22 01:00 | 567 | 567
2016-12-22 01:30 | 549 | 549
2016-12-22 02:00 | 548 | 548
2016-12-22 02:30 | 543 | 543
2016-12-22 03:00 | 535 | 534
2016-12-22 03:30 | 528 | 528
2016-12-22 04:00 | 519 | 519
2016-12-22 04:30 | 517 | 516
2016-12-22 05:00 | 523 | 523
2016-12-22 05:30 | 526 | 526
2016-12-22 06:00 | 538 | 537
2016-12-22 06:30 | 560 | 560
2016-12-22 07:00 | 581 | 580
2016-12-22 07:30 | 620 | 619
2016-12-22 08:00 | 642 | 642
2016-12-22 08:30 | 663 | 663
2016-12-22 09:00 | 669 | 669
2016-12-22 09:30 | 661 | 661
2016-12-22 10:00 | 640 | 640
2016-12-22 10:30 | 645 | 645
2016-12-22 11:00 | 635 | 635
2016-12-22 11:30 | 646 | 646
2016-12-22 12:00 | 657 | 657
2016-12-22 12:30 | 660 | 660
2016-12-22 13:00 | 661 | 661
2016-12-22 13:30 | 606 | 606
2016-12-22 14:00 | 688 | 688
2016-12-22 14:30 | 699 | 699
2016-12-22 15:00 | 699 | 698
2016-12-22 15:30 | 719 | 719
2016-12-22 16:00 | 724 | 724
2016-12-22 16:30 | 759 | 759
2016-12-22 17:00 | 783 | 783
2016-12-22 17:30 | 786 | 786
2016-12-22 18:00 | 777 | 777
2016-12-22 18:30 | 778 | 778
2016-12-22 19:00 | 785 | 784
2016-12-22 19:30 | 799 | 798
2016-12-22 20:00 | 795 | 795
2016-12-22 20:30 | 778 | 777
2016-12-22 21:00 | 753 | 752
2016-12-22 21:30 | 730 | 730
2016-12-22 22:00 | 706 | 706
2016-12-22 22:30 | 666 | 666
2016-12-22 23:00 | 650 | 650
2016-12-22 23:30 | 627 | 627
2016-12-23 | 611 | 611
2016-12-23 00:30 | 599 | 599
2016-12-23 01:00 | 579 | 579
2016-12-23 01:30 | 572 | 571
2016-12-23 02:00 | 562 | 562
2016-12-23 02:30 | 547 | 546
2016-12-23 03:00 | 541 | 540
2016-12-23 03:30 | 541 | 540
2016-12-23 04:00 | 536 | 535
2016-12-23 04:30 | 539 | 538
2016-12-23 05:00 | 542 | 542
2016-12-23 05:30 | 551 | 550
2016-12-23 06:00 | 554 | 553
2016-12-23 06:30 | 574 | 573
2016-12-23 07:00 | 602 | 601
2016-12-23 07:30 | 622 | 621
2016-12-23 08:00 | 650 | 650
2016-12-23 08:30 | 664 | 664
2016-12-23 09:00 | 666 | 666
2016-12-23 09:30 | 651 | 651
2016-12-23 10:00 | 646 | 646
2016-12-23 10:30 | 650 | 650
2016-12-23 11:00 | 586 | 586
2016-12-23 11:30 | 556 | 556
2016-12-23 12:00 | 555 | 555
2016-12-23 12:30 | 567 | 567
2016-12-23 13:00 | 572 | 571
2016-12-23 13:30 | 580 | 580
2016-12-23 14:00 | 611 | 611
2016-12-23 14:30 | 607 | 607
2016-12-23 15:00 | 612 | 612
2016-12-23 15:30 | 614 | 614
2016-12-23 16:00 | 564 | 564
2016-12-23 16:30 | 567 | 567
2016-12-23 17:00 | 578 | 578
2016-12-23 17:30 | 570 | 570
2016-12-23 18:00 | 575 | 575
2016-12-23 18:30 | 579 | 579
2016-12-23 19:00 | 584 | 584
2016-12-23 19:30 | 601 | 601
2016-12-23 20:00 | 605 | 605
2016-12-23 20:30 | 597 | 597
2016-12-23 21:00 | 641 | 641
2016-12-23 21:30 | 638 | 638
2016-12-23 22:00 | 617 | 617
2016-12-23 22:30 | 553 | 553
2016-12-23 23:00 | 561 | 560
2016-12-23 23:30 | 618 | 618
2016-12-24 | 608 | 608
2016-12-24 00:30 | 599 | 599
2016-12-24 01:00 | 575 | 575
2016-12-24 01:30 | 564 | 564
2016-12-24 02:00 | 552 | 551
2016-12-24 02:30 | 546 | 545
2016-12-24 03:00 | 546 | 546
2016-12-24 03:30 | 545 | 544
2016-12-24 04:00 | 550 | 550
2016-12-24 04:30 | 539 | 539
2016-12-24 05:00 | 545 | 544
2016-12-24 05:30 | 549 | 548
2016-12-24 06:00 | 559 | 558
2016-12-24 06:30 | 565 | 564
2016-12-24 07:00 | 575 | 575
2016-12-24 07:30 | 593 | 593
2016-12-24 08:00 | 609 | 609
2016-12-24 08:30 | 626 | 626
2016-12-24 09:00 | 641 | 641
2016-12-24 09:30 | 584 | 584
2016-12-24 10:00 | 628 | 628
2016-12-24 10:30 | 629 | 629
2016-12-24 11:00 | 621 | 621
2016-12-24 11:30 | 644 | 644
2016-12-24 12:00 | 659 | 659
2016-12-24 12:30 | 664 | 664
2016-12-24 13:00 | 667 | 666
2016-12-24 13:30 | 676 | 676
2016-12-24 14:00 | 700 | 700
2016-12-24 14:30 | 704 | 703
2016-12-24 15:00 | 716 | 716
2016-12-24 15:30 | 730 | 730
2016-12-24 16:00 | 740 | 740
2016-12-24 16:30 | 739 | 739
2016-12-24 17:00 | 742 | 741
2016-12-24 17:30 | 740 | 740
2016-12-24 18:00 | 741 | 741
2016-12-24 18:30 | 742 | 742
2016-12-24 19:00 | 740 | 740
2016-12-24 19:30 | 746 | 746
2016-12-24 20:00 | 736 | 736
2016-12-24 20:30 | 730 | 730
2016-12-24 21:00 | 710 | 710
2016-12-24 21:30 | 696 | 696
2016-12-24 22:00 | 682 | 682
2016-12-24 22:30 | 670 | 670
2016-12-24 23:00 | 655 | 655
2016-12-24 23:30 | 626 | 626
2016-12-25 | 599 | 598
2016-12-25 00:30 | 592 | 590
2016-12-25 01:00 | 572 | 568
2016-12-25 01:30 | 562 | 558
2016-12-25 02:00 | 548 | 543
2016-12-25 02:30 | 537 | 532
2016-12-25 03:00 | 534 | 528
2016-12-25 03:30 | 532 | 526
2016-12-25 04:00 | 521 | 515
2016-12-25 04:30 | 517 | 512
2016-12-25 05:00 | 515 | 510
2016-12-25 05:30 | 515 | 510
2016-12-25 06:00 | 510 | 505
2016-12-25 06:30 | 517 | 513
2016-12-25 07:00 | 529 | 524
2016-12-25 07:30 | 547 | 544
2016-12-25 08:00 | 560 | 558
2016-12-25 08:30 | 571 | 569
2016-12-25 09:00 | 571 | 569
2016-12-25 09:30 | 566 | 565
2016-12-25 10:00 | 562 | 561
2016-12-25 10:30 | 569 | 568
2016-12-25 11:00 | 577 | 576
2016-12-25 11:30 | 573 | 572
2016-12-25 12:00 | 567 | 566
2016-12-25 12:30 | 567 | 566
2016-12-25 13:00 | 557 | 556
2016-12-25 13:30 | 548 | 547
2016-12-25 14:00 | 565 | 564
2016-12-25 14:30 | 559 | 559
2016-12-25 15:00 | 562 | 562
2016-12-25 15:30 | 571 | 571
2016-12-25 16:00 | 582 | 582
2016-12-25 16:30 | 618 | 618
2016-12-25 17:00 | 632 | 632
2016-12-25 17:30 | 641 | 641
2016-12-25 18:00 | 644 | 643
2016-12-25 18:30 | 654 | 654
2016-12-25 19:00 | 663 | 662
2016-12-25 19:30 | 678 | 678
2016-12-25 20:00 | 685 | 685
2016-12-25 20:30 | 679 | 678
2016-12-25 21:00 | 673 | 672
2016-12-25 21:30 | 662 | 661
2016-12-25 22:00 | 647 | 647
2016-12-25 22:30 | 628 | 628
2016-12-25 23:00 | 609 | 609
2016-12-25 23:30 | 588 | 588
2016-12-26 | 571 | 570
2016-12-26 00:30 | 564 | 564
2016-12-26 01:00 | 548 | 547
2016-12-26 01:30 | 534 | 533
2016-12-26 02:00 | 534 | 532
2016-12-26 02:30 | 521 | 519
2016-12-26 03:00 | 513 | 510
2016-12-26 03:30 | 513 | 511
2016-12-26 04:00 | 514 | 511
2016-12-26 04:30 | 510 | 507
2016-12-26 05:00 | 517 | 514
2016-12-26 05:30 | 521 | 519
2016-12-26 06:00 | 519 | 517
2016-12-26 06:30 | 531 | 528
2016-12-26 07:00 | 547 | 545
2016-12-26 07:30 | 559 | 558
2016-12-26 08:00 | 578 | 577
2016-12-26 08:30 | 589 | 588
2016-12-26 09:00 | 595 | 595
2016-12-26 09:30 | 588 | 588
2016-12-26 10:00 | 571 | 570
2016-12-26 10:30 | 577 | 576
2016-12-26 11:00 | 580 | 580
2016-12-26 11:30 | 582 | 582
2016-12-26 12:00 | 580 | 579
2016-12-26 12:30 | 592 | 591
2016-12-26 13:00 | 621 | 620
2016-12-26 13:30 | 620 | 620
2016-12-26 14:00 | 636 | 636
2016-12-26 14:30 | 646 | 646
2016-12-26 15:00 | 661 | 661
2016-12-26 15:30 | 682 | 682
2016-12-26 16:00 | 691 | 691
2016-12-26 16:30 | 727 | 727
2016-12-26 17:00 | 743 | 742
2016-12-26 17:30 | 750 | 750
2016-12-26 18:00 | 755 | 754
2016-12-26 18:30 | 758 | 756
2016-12-26 19:00 | 765 | 763
2016-12-26 19:30 | 782 | 780
2016-12-26 20:00 | 786 | 783
2016-12-26 20:30 | 774 | 771
2016-12-26 21:00 | 759 | 756
2016-12-26 21:30 | 739 | 737
2016-12-26 22:00 | 720 | 718
2016-12-26 22:30 | 691 | 690
2016-12-26 23:00 | 665 | 665
2016-12-26 23:30 | 639 | 639
2016-12-27 | 618 | 618
2016-12-27 00:30 | 604 | 603
2016-12-27 01:00 | 591 | 590
2016-12-27 01:30 | 584 | 583
2016-12-27 02:00 | 573 | 572
2016-12-27 02:30 | 562 | 561
2016-12-27 03:00 | 557 | 555
2016-12-27 03:30 | 551 | 550
2016-12-27 04:00 | 551 | 550
2016-12-27 04:30 | 553 | 552
2016-12-27 05:00 | 551 | 550
2016-12-27 05:30 | 554 | 553
2016-12-27 06:00 | 554 | 553
2016-12-27 06:30 | 564 | 563
2016-12-27 07:00 | 583 | 583
2016-12-27 07:30 | 598 | 597
2016-12-27 08:00 | 608 | 608
2016-12-27 08:30 | 623 | 622
2016-12-27 09:00 | 634 | 634
2016-12-27 09:30 | 622 | 622
2016-12-27 10:00 | 612 | 611
2016-12-27 10:30 | 614 | 614
2016-12-27 11:00 | 624 | 624
2016-12-27 11:30 | 632 | 632
2016-12-27 12:00 | 641 | 641
2016-12-27 12:30 | 654 | 654
2016-12-27 13:00 | 653 | 653
2016-12-27 13:30 | 640 | 640
2016-12-27 14:00 | 671 | 671
2016-12-27 14:30 | 685 | 684
2016-12-27 15:00 | 691 | 691
2016-12-27 15:30 | 693 | 693
2016-12-27 16:00 | 704 | 704
2016-12-27 16:30 | 731 | 731
2016-12-27 17:00 | 741 | 741
2016-12-27 17:30 | 762 | 761
2016-12-27 18:00 | 771 | 771
2016-12-27 18:30 | 777 | 777
2016-12-27 19:00 | 786 | 785
2016-12-27 19:30 | 788 | 787
2016-12-27 20:00 | 788 | 787
2016-12-27 20:30 | 780 | 779
2016-12-27 21:00 | 763 | 762
2016-12-27 21:30 | 745 | 744
2016-12-27 22:00 | 723 | 723
2016-12-27 22:30 | 695 | 695
2016-12-27 23:00 | 671 | 670
2016-12-27 23:30 | 652 | 652
2016-12-28 | 632 | 632
2016-12-28 00:30 | 620 | 620
2016-12-28 01:00 | 609 | 609
2016-12-28 01:30 | 596 | 596
2016-12-28 02:00 | 586 | 585
2016-12-28 02:30 | 583 | 583
2016-12-28 03:00 | 574 | 574
2016-12-28 03:30 | 572 | 572
2016-12-28 04:00 | 568 | 567
2016-12-28 04:30 | 567 | 566
2016-12-28 05:00 | 565 | 565
2016-12-28 05:30 | 573 | 573
2016-12-28 06:00 | 575 | 575
2016-12-28 06:30 | 593 | 593
2016-12-28 07:00 | 610 | 610
2016-12-28 07:30 | 634 | 634
2016-12-28 08:00 | 599 | 599
2016-12-28 08:30 | 589 | 589
2016-12-28 09:00 | 604 | 604
2016-12-28 09:30 | 588 | 588
2016-12-28 10:00 | 574 | 574
2016-12-28 10:30 | 565 | 564
2016-12-28 11:00 | 519 | 519
2016-12-28 11:30 | 524 | 523
2016-12-28 12:00 | 538 | 537
2016-12-28 12:30 | 544 | 543
2016-12-28 13:00 | 544 | 544
2016-12-28 13:30 | 556 | 555
2016-12-28 14:00 | 584 | 583
2016-12-28 14:30 | 596 | 596
2016-12-28 15:00 | 602 | 602
2016-12-28 15:30 | 613 | 613
2016-12-28 16:00 | 638 | 638
2016-12-28 16:30 | 646 | 646
2016-12-28 17:00 | 625 | 625
2016-12-28 17:30 | 596 | 596
2016-12-28 18:00 | 615 | 615
2016-12-28 18:30 | 637 | 637
2016-12-28 19:00 | 647 | 647
2016-12-28 19:30 | 662 | 662
2016-12-28 20:00 | 663 | 663
2016-12-28 20:30 | 647 | 647
2016-12-28 21:00 | 632 | 632
2016-12-28 21:30 | 612 | 612
2016-12-28 22:00 | 592 | 591
2016-12-28 22:30 | 611 | 611
2016-12-28 23:00 | 681 | 681
2016-12-28 23:30 | 661 | 661
2016-12-29 | 645 | 645
2016-12-29 00:30 | 632 | 632
2016-12-29 01:00 | 617 | 617
2016-12-29 01:30 | 600 | 600
2016-12-29 02:00 | 584 | 584
2016-12-29 02:30 | 579 | 579
2016-12-29 03:00 | 581 | 580
2016-12-29 03:30 | 574 | 574
2016-12-29 04:00 | 571 | 571
2016-12-29 04:30 | 568 | 568
2016-12-29 05:00 | 578 | 577
2016-12-29 05:30 | 585 | 585
2016-12-29 06:00 | 582 | 582
2016-12-29 06:30 | 583 | 582
2016-12-29 07:00 | 556 | 556
2016-12-29 07:30 | 574 | 573
2016-12-29 08:00 | 595 | 595
2016-12-29 08:30 | 618 | 618
2016-12-29 09:00 | 635 | 635
2016-12-29 09:30 | 630 | 630
2016-12-29 10:00 | 621 | 621
2016-12-29 10:30 | 581 | 580
2016-12-29 11:00 | 517 | 517
2016-12-29 11:30 | 472 | 471
2016-12-29 12:00 | 476 | 475
2016-12-29 12:30 | 486 | 486
2016-12-29 13:00 | 484 | 483
2016-12-29 13:30 | 481 | 480
2016-12-29 14:00 | 506 | 505
2016-12-29 14:30 | 521 | 520
2016-12-29 15:00 | 535 | 535
2016-12-29 15:30 | 534 | 533
2016-12-29 16:00 | 537 | 537
2016-12-29 16:30 | 551 | 551
2016-12-29 17:00 | 572 | 572
2016-12-29 17:30 | 588 | 588
2016-12-29 18:00 | 598 | 598
2016-12-29 18:30 | 594 | 594
2016-12-29 19:00 | 598 | 598
2016-12-29 19:30 | 608 | 608
2016-12-29 20:00 | 606 | 606
2016-12-29 20:30 | 591 | 591
2016-12-29 21:00 | 573 | 573
2016-12-29 21:30 | 613 | 613
2016-12-29 22:00 | 605 | 605
2016-12-29 22:30 | 510 | 510
2016-12-29 23:00 | 543 | 543
2016-12-29 23:30 | 539 | 539
2016-12-30 | 523 | 523
2016-12-30 00:30 | 511 | 511
2016-12-30 01:00 | 491 | 491
2016-12-30 01:30 | 476 | 475
2016-12-30 02:00 | 466 | 466
2016-12-30 02:30 | 461 | 460
2016-12-30 03:00 | 455 | 454
2016-12-30 03:30 | 448 | 447
2016-12-30 04:00 | 443 | 442
2016-12-30 04:30 | 441 | 440
2016-12-30 05:00 | 442 | 441
2016-12-30 05:30 | 450 | 449
2016-12-30 06:00 | 453 | 452
2016-12-30 06:30 | 466 | 465
2016-12-30 07:00 | 485 | 484
2016-12-30 07:30 | 501 | 500
2016-12-30 08:00 | 522 | 521
2016-12-30 08:30 | 542 | 542
2016-12-30 09:00 | 557 | 557
2016-12-30 09:30 | 539 | 539
2016-12-30 10:00 | 528 | 528
2016-12-30 10:30 | 492 | 491
2016-12-30 11:00 | 455 | 455
2016-12-30 11:30 | 461 | 460
2016-12-30 12:00 | 465 | 463
2016-12-30 12:30 | 472 | 471
2016-12-30 13:00 | 483 | 482
2016-12-30 13:30 | 505 | 504
2016-12-30 14:00 | 532 | 532
2016-12-30 14:30 | 541 | 541
2016-12-30 15:00 | 538 | 538
2016-12-30 15:30 | 552 | 552
2016-12-30 16:00 | 543 | 543
2016-12-30 16:30 | 516 | 516
2016-12-30 17:00 | 527 | 526
2016-12-30 17:30 | 564 | 564
2016-12-30 18:00 | 581 | 581
2016-12-30 18:30 | 587 | 587
2016-12-30 19:00 | 592 | 592
2016-12-30 19:30 | 614 | 614
2016-12-30 20:00 | 619 | 619
2016-12-30 20:30 | 602 | 602
2016-12-30 21:00 | 584 | 584
2016-12-30 21:30 | 558 | 558
2016-12-30 22:00 | 539 | 539
2016-12-30 22:30 | 491 | 491
2016-12-30 23:00 | 536 | 536
2016-12-30 23:30 | 544 | 543
2016-12-31 | 529 | 529
2016-12-31 00:30 | 518 | 518
2016-12-31 01:00 | 501 | 501
2016-12-31 01:30 | 481 | 480
2016-12-31 02:00 | 472 | 470
2016-12-31 02:30 | 467 | 465
2016-12-31 03:00 | 461 | 460
2016-12-31 03:30 | 460 | 458
2016-12-31 04:00 | 456 | 454
2016-12-31 04:30 | 460 | 458
2016-12-31 05:00 | 456 | 454
2016-12-31 05:30 | 459 | 457
2016-12-31 06:00 | 457 | 455
2016-12-31 06:30 | 459 | 458
2016-12-31 07:00 | 473 | 472
2016-12-31 07:30 | 489 | 488
2016-12-31 08:00 | 510 | 509
2016-12-31 08:30 | 524 | 524
2016-12-31 09:00 | 534 | 533
2016-12-31 09:30 | 529 | 528
2016-12-31 10:00 | 525 | 524
2016-12-31 10:30 | 535 | 535
2016-12-31 11:00 | 542 | 541
2016-12-31 11:30 | 505 | 505
2016-12-31 12:00 | 478 | 477
2016-12-31 12:30 | 487 | 486
2016-12-31 13:00 | 480 | 479
2016-12-31 13:30 | 517 | 516
2016-12-31 14:00 | 458 | 457
2016-12-31 14:30 | 484 | 483
2016-12-31 15:00 | 516 | 515
2016-12-31 15:30 | 535 | 535
2016-12-31 16:00 | 530 | 530
2016-12-31 16:30 | 508 | 508
2016-12-31 17:00 | 534 | 534
2016-12-31 17:30 | 532 | 531
2016-12-31 18:00 | 546 | 546
2016-12-31 18:30 | 554 | 553
2016-12-31 19:00 | 571 | 570
2016-12-31 19:30 | 565 | 565
2016-12-31 20:00 | 558 | 558
2016-12-31 20:30 | 559 | 559
2016-12-31 21:00 | 564 | 564
2016-12-31 21:30 | 535 | 535
2016-12-31 22:00 | 515 | 514
2016-12-31 22:30 | 500 | 500
2016-12-31 23:00 | 489 | 488
2016-12-31 23:30 | 533 | 531
2017-01-01 | 536 | 536
2017-01-01 00:30 | 412 | 412
2017-01-01 01:00 | 450 | 448
2017-01-01 01:30 | 503 | 501
2017-01-01 02:00 | 495 | 493
2017-01-01 02:30 | 479 | 478
2017-01-01 03:00 | 464 | 463
2017-01-01 03:30 | 459 | 458
2017-01-01 04:00 | 455 | 453
2017-01-01 04:30 | 449 | 447
2017-01-01 05:00 | 452 | 450
2017-01-01 05:30 | 454 | 452
2017-01-01 06:00 | 442 | 440
2017-01-01 06:30 | 438 | 435
2017-01-01 07:00 | 428 | 426
2017-01-01 07:30 | 397 | 394
2017-01-01 08:00 | 406 | 402
2017-01-01 08:30 | 415 | 412
2017-01-01 09:00 | 439 | 436
2017-01-01 09:30 | 446 | 444
2017-01-01 10:00 | 457 | 455
2017-01-01 10:30 | 451 | 449
2017-01-01 11:00 | 396 | 394
2017-01-01 11:30 | 374 | 371
2017-01-01 12:00 | 366 | 362
2017-01-01 12:30 | 366 | 362
2017-01-01 13:00 | 386 | 382
2017-01-01 13:30 | 400 | 396
2017-01-01 14:00 | 411 | 408
2017-01-01 14:30 | 417 | 414
2017-01-01 15:00 | 392 | 389
2017-01-01 15:30 | 415 | 412
2017-01-01 16:00 | 338 | 334
2017-01-01 16:30 | 321 | 315
2017-01-01 17:00 | 291 | 283
2017-01-01 17:30 | 292 | 283
2017-01-01 18:00 | 209 | 196
2017-01-01 18:30 | 292 | 278
2017-01-01 19:00 | 316 | 307
2017-01-01 19:30 | 379 | 373
2017-01-01 20:00 | 357 | 353
2017-01-01 20:30 | 365 | 359
2017-01-01 21:00 | 477 | 474
2017-01-01 21:30 | 511 | 509
2017-01-01 22:00 | 486 | 485
2017-01-01 22:30 | 444 | 443
2017-01-01 23:00 | 444 | 441
2017-01-01 23:30 | 487 | 485
2017-01-02 | 573 | 571
2017-01-02 00:30 | 645 | 645
2017-01-02 01:00 | 630 | 630
2017-01-02 01:30 | 618 | 618
2017-01-02 02:00 | 610 | 610
2017-01-02 02:30 | 603 | 603
2017-01-02 03:00 | 596 | 596
2017-01-02 03:30 | 595 | 594
2017-01-02 04:00 | 591 | 591
2017-01-02 04:30 | 588 | 587
2017-01-02 05:00 | 586 | 586
2017-01-02 05:30 | 592 | 591
2017-01-02 06:00 | 587 | 587
2017-01-02 06:30 | 592 | 592
2017-01-02 07:00 | 590 | 589
2017-01-02 07:30 | 563 | 562
2017-01-02 08:00 | 575 | 575
2017-01-02 08:30 | 588 | 588
2017-01-02 09:00 | 549 | 549
2017-01-02 09:30 | 499 | 498
2017-01-02 10:00 | 518 | 517
2017-01-02 10:30 | 521 | 520
2017-01-02 11:00 | 505 | 504
2017-01-02 11:30 | 498 | 497
2017-01-02 12:00 | 491 | 489
2017-01-02 12:30 | 547 | 546
2017-01-02 13:00 | 523 | 523
2017-01-02 13:30 | 521 | 520
2017-01-02 14:00 | 529 | 528
2017-01-02 14:30 | 548 | 547
2017-01-02 15:00 | 558 | 558
2017-01-02 15:30 | 541 | 541
2017-01-02 16:00 | 392 | 391
2017-01-02 16:30 | 386 | 384
2017-01-02 17:00 | 394 | 391
2017-01-02 17:30 | 420 | 419
2017-01-02 18:00 | 440 | 439
2017-01-02 18:30 | 499 | 498
2017-01-02 19:00 | 554 | 554
2017-01-02 19:30 | 568 | 568
2017-01-02 20:00 | 570 | 570
2017-01-02 20:30 | 607 | 607
2017-01-02 21:00 | 591 | 591
2017-01-02 21:30 | 574 | 574
2017-01-02 22:00 | 560 | 560
2017-01-02 22:30 | 572 | 572
2017-01-02 23:00 | 566 | 566
2017-01-02 23:30 | 504 | 503
2017-01-03 | 518 | 517
2017-01-03 00:30 | 514 | 513
2017-01-03 01:00 | 505 | 504
2017-01-03 01:30 | 502 | 501
2017-01-03 02:00 | 560 | 559
2017-01-03 02:30 | 562 | 561
2017-01-03 03:00 | 557 | 557
2017-01-03 03:30 | 554 | 554
2017-01-03 04:00 | 554 | 554
2017-01-03 04:30 | 550 | 549
2017-01-03 05:00 | 550 | 550
2017-01-03 05:30 | 557 | 556
2017-01-03 06:00 | 567 | 567
2017-01-03 06:30 | 531 | 531
2017-01-03 07:00 | 478 | 477
2017-01-03 07:30 | 484 | 483
2017-01-03 08:00 | 463 | 462
2017-01-03 08:30 | 471 | 470
2017-01-03 09:00 | 457 | 456
2017-01-03 09:30 | 491 | 490
2017-01-03 10:00 | 510 | 509
2017-01-03 10:30 | 511 | 511
2017-01-03 11:00 | 515 | 515
2017-01-03 11:30 | 524 | 523
2017-01-03 12:00 | 534 | 534
2017-01-03 12:30 | 487 | 487
2017-01-03 13:00 | 557 | 556
2017-01-03 13:30 | 555 | 555
2017-01-03 14:00 | 566 | 566
2017-01-03 14:30 | 570 | 570
2017-01-03 15:00 | 573 | 573
2017-01-03 15:30 | 574 | 574
2017-01-03 16:00 | 554 | 554
2017-01-03 16:30 | 568 | 568
2017-01-03 17:00 | 578 | 578
2017-01-03 17:30 | 589 | 589
2017-01-03 18:00 | 601 | 601
2017-01-03 18:30 | 636 | 636
2017-01-03 19:00 | 556 | 556
2017-01-03 19:30 | 550 | 550
2017-01-03 20:00 | 575 | 575
2017-01-03 20:30 | 573 | 573
2017-01-03 21:00 | 597 | 597
2017-01-03 21:30 | 672 | 672
2017-01-03 22:00 | 667 | 667
2017-01-03 22:30 | 688 | 688
2017-01-03 23:00 | 671 | 671
2017-01-03 23:30 | 641 | 641
2017-01-04 | 618 | 618
2017-01-04 00:30 | 607 | 607
2017-01-04 01:00 | 595 | 595
2017-01-04 01:30 | 588 | 588
2017-01-04 02:00 | 574 | 574
2017-01-04 02:30 | 566 | 565
2017-01-04 03:00 | 564 | 563
2017-01-04 03:30 | 560 | 559
2017-01-04 04:00 | 558 | 557
2017-01-04 04:30 | 555 | 554
2017-01-04 05:00 | 554 | 554
2017-01-04 05:30 | 561 | 560
2017-01-04 06:00 | 562 | 562
2017-01-04 06:30 | 574 | 574
2017-01-04 07:00 | 596 | 596
2017-01-04 07:30 | 580 | 579
2017-01-04 08:00 | 596 | 595
2017-01-04 08:30 | 614 | 614
2017-01-04 09:00 | 618 | 618
2017-01-04 09:30 | 622 | 622
2017-01-04 10:00 | 629 | 629
2017-01-04 10:30 | 651 | 651
2017-01-04 11:00 | 645 | 645
2017-01-04 11:30 | 634 | 634
2017-01-04 12:00 | 610 | 610
2017-01-04 12:30 | 596 | 596
2017-01-04 13:00 | 606 | 606
2017-01-04 13:30 | 622 | 622
2017-01-04 14:00 | 633 | 633
2017-01-04 14:30 | 642 | 642
2017-01-04 15:00 | 668 | 668
2017-01-04 15:30 | 661 | 661
2017-01-04 16:00 | 678 | 678
2017-01-04 16:30 | 671 | 671
2017-01-04 17:00 | 656 | 656
2017-01-04 17:30 | 669 | 669
2017-01-04 18:00 | 676 | 676
2017-01-04 18:30 | 677 | 677
2017-01-04 19:00 | 664 | 664
2017-01-04 19:30 | 671 | 671
2017-01-04 20:00 | 660 | 660
2017-01-04 20:30 | 646 | 646
2017-01-04 21:00 | 636 | 636
2017-01-04 21:30 | 631 | 631
2017-01-04 22:00 | 618 | 618
2017-01-04 22:30 | 644 | 644
2017-01-04 23:00 | 613 | 613
2017-01-04 23:30 | 537 | 536
2017-01-05 | 559 | 558
2017-01-05 00:30 | 558 | 558
2017-01-05 01:00 | 550 | 549
2017-01-05 01:30 | 533 | 533
2017-01-05 02:00 | 523 | 522
2017-01-05 02:30 | 515 | 514
2017-01-05 03:00 | 509 | 508
2017-01-05 03:30 | 506 | 505
2017-01-05 04:00 | 501 | 500
2017-01-05 04:30 | 500 | 499
2017-01-05 05:00 | 503 | 502
2017-01-05 05:30 | 511 | 510
2017-01-05 06:00 | 508 | 507
2017-01-05 06:30 | 525 | 524
2017-01-05 07:00 | 523 | 522
2017-01-05 07:30 | 518 | 517
2017-01-05 08:00 | 531 | 531
2017-01-05 08:30 | 528 | 527
2017-01-05 09:00 | 537 | 537
2017-01-05 09:30 | 543 | 542
2017-01-05 10:00 | 543 | 543
2017-01-05 10:30 | 541 | 540
2017-01-05 11:00 | 543 | 543
2017-01-05 11:30 | 549 | 549
2017-01-05 12:00 | 568 | 568
2017-01-05 12:30 | 569 | 569
2017-01-05 13:00 | 564 | 564
2017-01-05 13:30 | 559 | 559
2017-01-05 14:00 | 556 | 556
2017-01-05 14:30 | 582 | 582
2017-01-05 15:00 | 585 | 585
2017-01-05 15:30 | 590 | 590
2017-01-05 16:00 | 594 | 594
2017-01-05 16:30 | 572 | 572
2017-01-05 17:00 | 575 | 575
2017-01-05 17:30 | 573 | 573
2017-01-05 18:00 | 598 | 598
2017-01-05 18:30 | 651 | 651
2017-01-05 19:00 | 656 | 656
2017-01-05 19:30 | 658 | 658
2017-01-05 20:00 | 642 | 641
2017-01-05 20:30 | 609 | 609
2017-01-05 21:00 | 585 | 585
2017-01-05 21:30 | 560 | 559
2017-01-05 22:00 | 537 | 537
2017-01-05 22:30 | 456 | 455
2017-01-05 23:00 | 441 | 438
2017-01-05 23:30 | 455 | 453
2017-01-06 | 457 | 455
2017-01-06 00:30 | 443 | 441
2017-01-06 01:00 | 436 | 434
2017-01-06 01:30 | 424 | 421
2017-01-06 02:00 | 415 | 412
2017-01-06 02:30 | 412 | 409
2017-01-06 03:00 | 406 | 403
2017-01-06 03:30 | 400 | 396
2017-01-06 04:00 | 396 | 393
2017-01-06 04:30 | 396 | 392
2017-01-06 05:00 | 393 | 390
2017-01-06 05:30 | 400 | 396
2017-01-06 06:00 | 407 | 403
2017-01-06 06:30 | 427 | 424
2017-01-06 07:00 | 446 | 443
2017-01-06 07:30 | 472 | 470
2017-01-06 08:00 | 495 | 494
2017-01-06 08:30 | 523 | 522
2017-01-06 09:00 | 527 | 526
2017-01-06 09:30 | 514 | 514
2017-01-06 10:00 | 518 | 517
2017-01-06 10:30 | 546 | 545
2017-01-06 11:00 | 556 | 556
2017-01-06 11:30 | 471 | 471
2017-01-06 12:00 | 418 | 417
2017-01-06 12:30 | 408 | 406
2017-01-06 13:00 | 416 | 413
2017-01-06 13:30 | 442 | 439
2017-01-06 14:00 | 449 | 447
2017-01-06 14:30 | 455 | 453
2017-01-06 15:00 | 455 | 453
2017-01-06 15:30 | 415 | 413
2017-01-06 16:00 | 390 | 388
2017-01-06 16:30 | 392 | 388
2017-01-06 17:00 | 396 | 393
2017-01-06 17:30 | 414 | 412
2017-01-06 18:00 | 437 | 435
2017-01-06 18:30 | 440 | 438
2017-01-06 19:00 | 446 | 444
2017-01-06 19:30 | 484 | 482
2017-01-06 20:00 | 476 | 475
2017-01-06 20:30 | 429 | 428
2017-01-06 21:00 | 411 | 408
2017-01-06 21:30 | 380 | 377
2017-01-06 22:00 | 364 | 361
2017-01-06 22:30 | 353 | 348
2017-01-06 23:00 | 337 | 332
2017-01-06 23:30 | 320 | 314
2017-01-07 | 307 | 299
2017-01-07 00:30 | 393 | 387
2017-01-07 01:00 | 411 | 409
2017-01-07 01:30 | 401 | 399
2017-01-07 02:00 | 393 | 390
2017-01-07 02:30 | 387 | 384
2017-01-07 03:00 | 379 | 376
2017-01-07 03:30 | 373 | 369
2017-01-07 04:00 | 369 | 366
2017-01-07 04:30 | 372 | 368
2017-01-07 05:00 | 374 | 371
2017-01-07 05:30 | 378 | 374
2017-01-07 06:00 | 375 | 371
2017-01-07 06:30 | 383 | 379
2017-01-07 07:00 | 396 | 392
2017-01-07 07:30 | 414 | 410
2017-01-07 08:00 | 429 | 426
2017-01-07 08:30 | 451 | 449
2017-01-07 09:00 | 468 | 467
2017-01-07 09:30 | 412 | 411
2017-01-07 10:00 | 341 | 338
2017-01-07 10:30 | 347 | 342
2017-01-07 11:00 | 351 | 346
2017-01-07 11:30 | 367 | 363
2017-01-07 12:00 | 395 | 391
2017-01-07 12:30 | 431 | 428
2017-01-07 13:00 | 432 | 430
2017-01-07 13:30 | 447 | 445
2017-01-07 14:00 | 457 | 455
2017-01-07 14:30 | 460 | 458
2017-01-07 15:00 | 458 | 456
2017-01-07 15:30 | 469 | 468
2017-01-07 16:00 | 481 | 480
2017-01-07 16:30 | 502 | 501
2017-01-07 17:00 | 505 | 505
2017-01-07 17:30 | 501 | 500
2017-01-07 18:00 | 519 | 518
2017-01-07 18:30 | 527 | 526
2017-01-07 19:00 | 524 | 523
2017-01-07 19:30 | 596 | 595
2017-01-07 20:00 | 600 | 600
2017-01-07 20:30 | 572 | 572
2017-01-07 21:00 | 551 | 551
2017-01-07 21:30 | 532 | 532
2017-01-07 22:00 | 517 | 516
2017-01-07 22:30 | 494 | 493
2017-01-07 23:00 | 477 | 476
2017-01-07 23:30 | 448 | 447
2017-01-08 | 432 | 430
2017-01-08 00:30 | 417 | 416
2017-01-08 01:00 | 411 | 409
2017-01-08 01:30 | 394 | 391
2017-01-08 02:00 | 386 | 383
2017-01-08 02:30 | 378 | 375
2017-01-08 03:00 | 375 | 371
2017-01-08 03:30 | 373 | 369
2017-01-08 04:00 | 374 | 370
2017-01-08 04:30 | 366 | 362
2017-01-08 05:00 | 365 | 361
2017-01-08 05:30 | 367 | 363
2017-01-08 06:00 | 367 | 363
2017-01-08 06:30 | 369 | 365
2017-01-08 07:00 | 376 | 372
2017-01-08 07:30 | 390 | 386
2017-01-08 08:00 | 401 | 398
2017-01-08 08:30 | 414 | 411
2017-01-08 09:00 | 428 | 426
2017-01-08 09:30 | 447 | 444
2017-01-08 10:00 | 462 | 460
2017-01-08 10:30 | 464 | 463
2017-01-08 11:00 | 468 | 467
2017-01-08 11:30 | 470 | 468
2017-01-08 12:00 | 478 | 476
2017-01-08 12:30 | 482 | 481
2017-01-08 13:00 | 491 | 490
2017-01-08 13:30 | 502 | 502
2017-01-08 14:00 | 508 | 507
2017-01-08 14:30 | 510 | 510
2017-01-08 15:00 | 518 | 517
2017-01-08 15:30 | 539 | 538
2017-01-08 16:00 | 543 | 543
2017-01-08 16:30 | 535 | 535
2017-01-08 17:00 | 506 | 506
2017-01-08 17:30 | 524 | 523
2017-01-08 18:00 | 521 | 521
2017-01-08 18:30 | 569 | 568
2017-01-08 19:00 | 604 | 603
2017-01-08 19:30 | 611 | 611
2017-01-08 20:00 | 611 | 611
2017-01-08 20:30 | 598 | 598
2017-01-08 21:00 | 576 | 575
2017-01-08 21:30 | 543 | 543
2017-01-08 22:00 | 521 | 520
2017-01-08 22:30 | 493 | 493
2017-01-08 23:00 | 489 | 488
2017-01-08 23:30 | 468 | 467
2017-01-09 | 451 | 450
2017-01-09 00:30 | 437 | 435
2017-01-09 01:00 | 428 | 427
2017-01-09 01:30 | 419 | 418
2017-01-09 02:00 | 411 | 409
2017-01-09 02:30 | 405 | 402
2017-01-09 03:00 | 399 | 397
2017-01-09 03:30 | 401 | 399
2017-01-09 04:00 | 398 | 395
2017-01-09 04:30 | 384 | 381
2017-01-09 05:00 | 385 | 382
2017-01-09 05:30 | 394 | 392
2017-01-09 06:00 | 400 | 398
2017-01-09 06:30 | 440 | 437
2017-01-09 07:00 | 465 | 464
2017-01-09 07:30 | 567 | 566
2017-01-09 08:00 | 595 | 594
2017-01-09 08:30 | 614 | 613
2017-01-09 09:00 | 615 | 615
2017-01-09 09:30 | 524 | 524
2017-01-09 10:00 | 469 | 468
2017-01-09 10:30 | 476 | 475
2017-01-09 11:00 | 486 | 485
2017-01-09 11:30 | 486 | 485
2017-01-09 12:00 | 481 | 480
2017-01-09 12:30 | 477 | 477
2017-01-09 13:00 | 490 | 489
2017-01-09 13:30 | 502 | 501
2017-01-09 14:00 | 503 | 502
2017-01-09 14:30 | 502 | 502
2017-01-09 15:00 | 512 | 511
2017-01-09 15:30 | 525 | 525
2017-01-09 16:00 | 528 | 528
2017-01-09 16:30 | 533 | 533
2017-01-09 17:00 | 540 | 540
2017-01-09 17:30 | 549 | 549
2017-01-09 18:00 | 551 | 551
2017-01-09 18:30 | 554 | 554
2017-01-09 19:00 | 565 | 565
2017-01-09 19:30 | 572 | 572
2017-01-09 20:00 | 554 | 554
2017-01-09 20:30 | 477 | 477
2017-01-09 21:00 | 462 | 462
2017-01-09 21:30 | 433 | 433
2017-01-09 22:00 | 411 | 410
2017-01-09 22:30 | 379 | 377
2017-01-09 23:00 | 353 | 351
2017-01-09 23:30 | 387 | 384
2017-01-10 | 447 | 445
2017-01-10 00:30 | 435 | 434
2017-01-10 01:00 | 426 | 424
2017-01-10 01:30 | 420 | 419
2017-01-10 02:00 | 403 | 401
2017-01-10 02:30 | 396 | 394
2017-01-10 03:00 | 393 | 391
2017-01-10 03:30 | 392 | 389
2017-01-10 04:00 | 388 | 386
2017-01-10 04:30 | 459 | 457
2017-01-10 05:00 | 470 | 468
2017-01-10 05:30 | 481 | 480
2017-01-10 06:00 | 487 | 486
2017-01-10 06:30 | 473 | 472
2017-01-10 07:00 | 396 | 395
2017-01-10 07:30 | 427 | 424
2017-01-10 08:00 | 456 | 453
2017-01-10 08:30 | 486 | 484
2017-01-10 09:00 | 513 | 512
2017-01-10 09:30 | 507 | 506
2017-01-10 10:00 | 502 | 501
2017-01-10 10:30 | 441 | 440
2017-01-10 11:00 | 415 | 413
2017-01-10 11:30 | 417 | 414
2017-01-10 12:00 | 420 | 418
2017-01-10 12:30 | 413 | 411
2017-01-10 13:00 | 424 | 422
2017-01-10 13:30 | 409 | 407
2017-01-10 14:00 | 438 | 435
2017-01-10 14:30 | 409 | 407
2017-01-10 15:00 | 412 | 410
2017-01-10 15:30 | 407 | 405
2017-01-10 16:00 | 359 | 356
2017-01-10 16:30 | 228 | 223
2017-01-10 17:00 | 259 | 248
2017-01-10 17:30 | 277 | 268
2017-01-10 18:00 | 276 | 268
2017-01-10 18:30 | 282 | 274
2017-01-10 19:00 | 292 | 285
2017-01-10 19:30 | 305 | 299
2017-01-10 20:00 | 293 | 288
2017-01-10 20:30 | 446 | 442
2017-01-10 21:00 | 475 | 474
2017-01-10 21:30 | 452 | 451
2017-01-10 22:00 | 423 | 422
2017-01-10 22:30 | 376 | 374
2017-01-10 23:00 | 363 | 361
2017-01-10 23:30 | 344 | 341
2017-01-11 | 322 | 318
2017-01-11 00:30 | 309 | 304
2017-01-11 01:00 | 304 | 298
2017-01-11 01:30 | 298 | 292
2017-01-11 02:00 | 293 | 286
2017-01-11 02:30 | 291 | 283
2017-01-11 03:00 | 281 | 273
2017-01-11 03:30 | 278 | 268
2017-01-11 04:00 | 278 | 267
2017-01-11 04:30 | 278 | 266
2017-01-11 05:00 | 277 | 266
2017-01-11 05:30 | 283 | 272
2017-01-11 06:00 | 286 | 276
2017-01-11 06:30 | 309 | 299
2017-01-11 07:00 | 293 | 284
2017-01-11 07:30 | 345 | 337
2017-01-11 08:00 | 365 | 359
2017-01-11 08:30 | 317 | 311
2017-01-11 09:00 | 325 | 318
2017-01-11 09:30 | 328 | 321
2017-01-11 10:00 | 328 | 321
2017-01-11 10:30 | 336 | 330
2017-01-11 11:00 | 380 | 374
2017-01-11 11:30 | 364 | 359
2017-01-11 12:00 | 377 | 372
2017-01-11 12:30 | 359 | 354
2017-01-11 13:00 | 352 | 346
2017-01-11 13:30 | 296 | 289
2017-01-11 14:00 | 225 | 213
2017-01-11 14:30 | 146 | 118
2017-01-11 15:00 | 109 | 42
2017-01-11 15:30 | 110 | 15
2017-01-11 16:00 | 114 | 9
2017-01-11 16:30 | 157 | 108
2017-01-11 17:00 | 130 | 81
2017-01-11 17:30 | 106 | 20
2017-01-11 18:00 | 117 | 20
2017-01-11 18:30 | 160 | 112
2017-01-11 19:00 | 107 | 35
2017-01-11 19:30 | 116 | 40
2017-01-11 20:00 | 192 | 159
2017-01-11 20:30 | 233 | 214
2017-01-11 21:00 | 310 | 299
2017-01-11 21:30 | 358 | 351
2017-01-11 22:00 | 358 | 352
2017-01-11 22:30 | 210 | 200
2017-01-11 23:00 | 158 | 131
2017-01-11 23:30 | 264 | 245
2017-01-12 | 334 | 325
2017-01-12 00:30 | 328 | 321
2017-01-12 01:00 | 321 | 313
2017-01-12 01:30 | 313 | 305
2017-01-12 02:00 | 310 | 302
2017-01-12 02:30 | 299 | 290
2017-01-12 03:00 | 298 | 289
2017-01-12 03:30 | 295 | 286
2017-01-12 04:00 | 296 | 286
2017-01-12 04:30 | 294 | 284
2017-01-12 05:00 | 297 | 287
2017-01-12 05:30 | 305 | 295
2017-01-12 06:00 | 310 | 300
2017-01-12 06:30 | 336 | 328
2017-01-12 07:00 | 353 | 346
2017-01-12 07:30 | 388 | 383
2017-01-12 08:00 | 410 | 406
2017-01-12 08:30 | 424 | 421
2017-01-12 09:00 | 409 | 406
2017-01-12 09:30 | 439 | 436
2017-01-12 10:00 | 451 | 449
2017-01-12 10:30 | 434 | 432
2017-01-12 11:00 | 428 | 426
2017-01-12 11:30 | 430 | 428
2017-01-12 12:00 | 395 | 393
2017-01-12 12:30 | 330 | 327
2017-01-12 13:00 | 267 | 261
2017-01-12 13:30 | 190 | 178
2017-01-12 14:00 | 115 | 80
2017-01-12 14:30 | 91 | 23
2017-01-12 15:00 | 91 | 19
2017-01-12 15:30 | 89 | 8
2017-01-12 16:00 | 92 | 21
2017-01-12 16:30 | 97 | 32
2017-01-12 17:00 | 98 | 30
2017-01-12 17:30 | 110 | 44
2017-01-12 18:00 | 112 | 36
2017-01-12 18:30 | 107 | 17
2017-01-12 19:00 | 132 | 88
2017-01-12 19:30 | 122 | 81
2017-01-12 20:00 | 119 | 78
2017-01-12 20:30 | 151 | 122
2017-01-12 21:00 | 241 | 225
2017-01-12 21:30 | 279 | 271
2017-01-12 22:00 | 269 | 262
2017-01-12 22:30 | 184 | 172
2017-01-12 23:00 | 192 | 175
2017-01-12 23:30 | 263 | 251
2017-01-13 | 324 | 317
2017-01-13 00:30 | 327 | 322
2017-01-13 01:00 | 326 | 321
2017-01-13 01:30 | 320 | 314
2017-01-13 02:00 | 312 | 306
2017-01-13 02:30 | 307 | 301
2017-01-13 03:00 | 302 | 295
2017-01-13 03:30 | 296 | 289
2017-01-13 04:00 | 293 | 285
2017-01-13 04:30 | 295 | 288
2017-01-13 05:00 | 300 | 292
2017-01-13 05:30 | 311 | 304
2017-01-13 06:00 | 319 | 312
2017-01-13 06:30 | 340 | 334
2017-01-13 07:00 | 238 | 230
2017-01-13 07:30 | 333 | 323
2017-01-13 08:00 | 403 | 398
2017-01-13 08:30 | 426 | 424
2017-01-13 09:00 | 405 | 403
2017-01-13 09:30 | 399 | 397
2017-01-13 10:00 | 403 | 400
2017-01-13 10:30 | 386 | 383
2017-01-13 11:00 | 341 | 337
2017-01-13 11:30 | 332 | 327
2017-01-13 12:00 | 213 | 204
2017-01-13 12:30 | 208 | 192
2017-01-13 13:00 | 229 | 215
2017-01-13 13:30 | 172 | 157
2017-01-13 14:00 | 221 | 206
2017-01-13 14:30 | 190 | 176
2017-01-13 15:00 | 107 | 73
2017-01-13 15:30 | 150 | 120
2017-01-13 16:00 | 107 | 72
2017-01-13 16:30 | 89 | 21
2017-01-13 17:00 | 95 | 18
2017-01-13 17:30 | 98 | 22
2017-01-13 18:00 | 101 | 35
2017-01-13 18:30 | 97 | 25
2017-01-13 19:00 | 98 | 28
2017-01-13 19:30 | 100 | 9
2017-01-13 20:00 | 104 | 25
2017-01-13 20:30 | 119 | 67
2017-01-13 21:00 | 249 | 231
2017-01-13 21:30 | 355 | 348
2017-01-13 22:00 | 363 | 360
2017-01-13 22:30 | 195 | 189
2017-01-13 23:00 | 102 | 64
2017-01-13 23:30 | 216 | 193
2017-01-14 | 297 | 286
2017-01-14 00:30 | 273 | 265
2017-01-14 01:00 | 349 | 342
2017-01-14 01:30 | 443 | 439
2017-01-14 02:00 | 442 | 440
2017-01-14 02:30 | 439 | 437
2017-01-14 03:00 | 433 | 430
2017-01-14 03:30 | 427 | 425
2017-01-14 04:00 | 424 | 422
2017-01-14 04:30 | 419 | 417
2017-01-14 05:00 | 418 | 415
2017-01-14 05:30 | 423 | 420
2017-01-14 06:00 | 436 | 433
2017-01-14 06:30 | 431 | 428
2017-01-14 07:00 | 380 | 378
2017-01-14 07:30 | 389 | 386
2017-01-14 08:00 | 422 | 419
2017-01-14 08:30 | 451 | 449
2017-01-14 09:00 | 497 | 496
2017-01-14 09:30 | 506 | 505
2017-01-14 10:00 | 448 | 448
2017-01-14 10:30 | 410 | 408
2017-01-14 11:00 | 412 | 410
2017-01-14 11:30 | 380 | 377
2017-01-14 12:00 | 382 | 380
2017-01-14 12:30 | 357 | 354
2017-01-14 13:00 | 389 | 385
2017-01-14 13:30 | 401 | 399
2017-01-14 14:00 | 312 | 309
2017-01-14 14:30 | 291 | 286
2017-01-14 15:00 | 239 | 231
2017-01-14 15:30 | 139 | 119
2017-01-14 16:00 | 147 | 119
2017-01-14 16:30 | 135 | 103
2017-01-14 17:00 | 156 | 128
2017-01-14 17:30 | 97 | 41
2017-01-14 18:00 | 112 | 55
2017-01-14 18:30 | 116 | 66
2017-01-14 19:00 | 112 | 63
2017-01-14 19:30 | 150 | 118
2017-01-14 20:00 | 180 | 157
2017-01-14 20:30 | 196 | 178
2017-01-14 21:00 | 302 | 292
2017-01-14 21:30 | 356 | 350
2017-01-14 22:00 | 316 | 312
2017-01-14 22:30 | 225 | 217
2017-01-14 23:00 | 112 | 87
2017-01-14 23:30 | 218 | 198
2017-01-15 | 289 | 279
2017-01-15 00:30 | 403 | 399
2017-01-15 01:00 | 455 | 453
2017-01-15 01:30 | 449 | 448
2017-01-15 02:00 | 440 | 439
2017-01-15 02:30 | 438 | 436
2017-01-15 03:00 | 434 | 433
2017-01-15 03:30 | 452 | 450
2017-01-15 04:00 | 432 | 431
2017-01-15 04:30 | 432 | 430
2017-01-15 05:00 | 433 | 432
2017-01-15 05:30 | 439 | 438
2017-01-15 06:00 | 453 | 452
2017-01-15 06:30 | 439 | 438
2017-01-15 07:00 | 451 | 450
2017-01-15 07:30 | 452 | 451
2017-01-15 08:00 | 461 | 460
2017-01-15 08:30 | 478 | 476
2017-01-15 09:00 | 494 | 493
2017-01-15 09:30 | 520 | 520
2017-01-15 10:00 | 527 | 526
2017-01-15 10:30 | 475 | 475
2017-01-15 11:00 | 361 | 360
2017-01-15 11:30 | 358 | 355
2017-01-15 12:00 | 370 | 367
2017-01-15 12:30 | 348 | 345
2017-01-15 13:00 | 376 | 372
2017-01-15 13:30 | 306 | 303
2017-01-15 14:00 | 286 | 280
2017-01-15 14:30 | 255 | 247
2017-01-15 15:00 | 180 | 167
2017-01-15 15:30 | 189 | 170
2017-01-15 16:00 | 188 | 170
2017-01-15 16:30 | 192 | 174
2017-01-15 17:00 | 184 | 166
2017-01-15 17:30 | 194 | 174
2017-01-15 18:00 | 201 | 183
2017-01-15 18:30 | 202 | 186
2017-01-15 19:00 | 169 | 150
2017-01-15 19:30 | 198 | 179
2017-01-15 20:00 | 241 | 228
2017-01-15 20:30 | 362 | 356
2017-01-15 21:00 | 438 | 436
2017-01-15 21:30 | 484 | 483
2017-01-15 22:00 | 448 | 448
2017-01-15 22:30 | 353 | 352
2017-01-15 23:00 | 378 | 375
2017-01-15 23:30 | 370 | 367
2017-01-16 | 370 | 367
2017-01-16 00:30 | 389 | 387
2017-01-16 01:00 | 409 | 407
2017-01-16 01:30 | 402 | 400
2017-01-16 02:00 | 390 | 388
2017-01-16 02:30 | 388 | 386
2017-01-16 03:00 | 385 | 383
2017-01-16 03:30 | 380 | 378
2017-01-16 04:00 | 373 | 370
2017-01-16 04:30 | 379 | 375
2017-01-16 05:00 | 382 | 379
2017-01-16 05:30 | 392 | 389
2017-01-16 06:00 | 401 | 399
2017-01-16 06:30 | 389 | 387
2017-01-16 07:00 | 361 | 358
2017-01-16 07:30 | 414 | 412
2017-01-16 08:00 | 450 | 448
2017-01-16 08:30 | 503 | 503
2017-01-16 09:00 | 512 | 512
2017-01-16 09:30 | 508 | 508
2017-01-16 10:00 | 508 | 508
2017-01-16 10:30 | 514 | 514
2017-01-16 11:00 | 529 | 528
2017-01-16 11:30 | 538 | 538
2017-01-16 12:00 | 550 | 550
2017-01-16 12:30 | 551 | 551
2017-01-16 13:00 | 559 | 559
2017-01-16 13:30 | 560 | 560
2017-01-16 14:00 | 506 | 506
2017-01-16 14:30 | 464 | 463
2017-01-16 15:00 | 362 | 360
2017-01-16 15:30 | 318 | 314
2017-01-16 16:00 | 393 | 389
2017-01-16 16:30 | 381 | 378
2017-01-16 17:00 | 379 | 377
2017-01-16 17:30 | 470 | 468
2017-01-16 18:00 | 515 | 515
2017-01-16 18:30 | 523 | 522
2017-01-16 19:00 | 497 | 496
2017-01-16 19:30 | 554 | 553
2017-01-16 20:00 | 638 | 638
2017-01-16 20:30 | 639 | 639
2017-01-16 21:00 | 602 | 602
2017-01-16 21:30 | 571 | 571
2017-01-16 22:00 | 531 | 531
2017-01-16 22:30 | 474 | 474
2017-01-16 23:00 | 454 | 453
2017-01-16 23:30 | 457 | 455
2017-01-17 | 441 | 439
2017-01-17 00:30 | 446 | 444
2017-01-17 01:00 | 452 | 450
2017-01-17 01:30 | 456 | 454
2017-01-17 02:00 | 433 | 431
2017-01-17 02:30 | 427 | 425
2017-01-17 03:00 | 417 | 415
2017-01-17 03:30 | 420 | 417
2017-01-17 04:00 | 418 | 416
2017-01-17 04:30 | 417 | 415
2017-01-17 05:00 | 422 | 420
2017-01-17 05:30 | 426 | 423
2017-01-17 06:00 | 418 | 416
2017-01-17 06:30 | 394 | 391
2017-01-17 07:00 | 430 | 428
2017-01-17 07:30 | 473 | 472
2017-01-17 08:00 | 501 | 500
2017-01-17 08:30 | 514 | 514
2017-01-17 09:00 | 511 | 511
2017-01-17 09:30 | 501 | 501
2017-01-17 10:00 | 512 | 512
2017-01-17 10:30 | 526 | 526
2017-01-17 11:00 | 522 | 521
2017-01-17 11:30 | 531 | 531
2017-01-17 12:00 | 540 | 540
2017-01-17 12:30 | 535 | 535
2017-01-17 13:00 | 537 | 536
2017-01-17 13:30 | 548 | 548
2017-01-17 14:00 | 565 | 565
2017-01-17 14:30 | 507 | 506
2017-01-17 15:00 | 413 | 412
2017-01-17 15:30 | 336 | 334
2017-01-17 16:00 | 345 | 342
2017-01-17 16:30 | 262 | 258
2017-01-17 17:00 | 182 | 172
2017-01-17 17:30 | 187 | 170
2017-01-17 18:00 | 185 | 168
2017-01-17 18:30 | 224 | 209
2017-01-17 19:00 | 350 | 342
2017-01-17 19:30 | 424 | 422
2017-01-17 20:00 | 306 | 305
2017-01-17 20:30 | 362 | 358
2017-01-17 21:00 | 429 | 427
2017-01-17 21:30 | 415 | 413
2017-01-17 22:00 | 404 | 402
2017-01-17 22:30 | 332 | 330
2017-01-17 23:00 | 368 | 366
2017-01-17 23:30 | 378 | 376
2017-01-18 | 361 | 359
2017-01-18 00:30 | 438 | 436
2017-01-18 01:00 | 449 | 447
2017-01-18 01:30 | 440 | 438
2017-01-18 02:00 | 414 | 412
2017-01-18 02:30 | 408 | 405
2017-01-18 03:00 | 405 | 402
2017-01-18 03:30 | 405 | 402
2017-01-18 04:00 | 396 | 393
2017-01-18 04:30 | 398 | 395
2017-01-18 05:00 | 399 | 396
2017-01-18 05:30 | 406 | 403
2017-01-18 06:00 | 412 | 409
2017-01-18 06:30 | 436 | 433
2017-01-18 07:00 | 390 | 388
2017-01-18 07:30 | 432 | 429
2017-01-18 08:00 | 495 | 494
2017-01-18 08:30 | 507 | 506
2017-01-18 09:00 | 457 | 456
2017-01-18 09:30 | 431 | 430
2017-01-18 10:00 | 427 | 426
2017-01-18 10:30 | 429 | 427
2017-01-18 11:00 | 429 | 427
2017-01-18 11:30 | 443 | 442
2017-01-18 12:00 | 443 | 442
2017-01-18 12:30 | 445 | 444
2017-01-18 13:00 | 449 | 448
2017-01-18 13:30 | 474 | 473
2017-01-18 14:00 | 407 | 407
2017-01-18 14:30 | 385 | 383
2017-01-18 15:00 | 240 | 236
2017-01-18 15:30 | 143 | 124
2017-01-18 16:00 | 120 | 77
2017-01-18 16:30 | 95 | 14
2017-01-18 17:00 | 106 | 34
2017-01-18 17:30 | 128 | 70
2017-01-18 18:00 | 128 | 57
2017-01-18 18:30 | 110 | 16
2017-01-18 19:00 | 126 | 68
2017-01-18 19:30 | 126 | 82
2017-01-18 20:00 | 134 | 94
2017-01-18 20:30 | 241 | 221
2017-01-18 21:00 | 375 | 367
2017-01-18 21:30 | 382 | 379
2017-01-18 22:00 | 332 | 328
2017-01-18 22:30 | 236 | 228
2017-01-18 23:00 | 198 | 182
2017-01-18 23:30 | 283 | 269
2017-01-19 | 302 | 293
2017-01-19 00:30 | 357 | 349
2017-01-19 01:00 | 426 | 421
2017-01-19 01:30 | 415 | 412
2017-01-19 02:00 | 406 | 403
2017-01-19 02:30 | 408 | 404
2017-01-19 03:00 | 402 | 397
2017-01-19 03:30 | 398 | 394
2017-01-19 04:00 | 399 | 394
2017-01-19 04:30 | 401 | 397
2017-01-19 05:00 | 406 | 402
2017-01-19 05:30 | 417 | 413
2017-01-19 06:00 | 433 | 429
2017-01-19 06:30 | 458 | 455
2017-01-19 07:00 | 396 | 394
2017-01-19 07:30 | 496 | 493
2017-01-19 08:00 | 529 | 528
2017-01-19 08:30 | 533 | 533
2017-01-19 09:00 | 507 | 506
2017-01-19 09:30 | 455 | 454
2017-01-19 10:00 | 436 | 435
2017-01-19 10:30 | 442 | 441
2017-01-19 11:00 | 434 | 433
2017-01-19 11:30 | 386 | 384
2017-01-19 12:00 | 437 | 434
2017-01-19 12:30 | 457 | 455
2017-01-19 13:00 | 459 | 458
2017-01-19 13:30 | 454 | 453
2017-01-19 14:00 | 442 | 440
2017-01-19 14:30 | 452 | 450
2017-01-19 15:00 | 459 | 458
2017-01-19 15:30 | 455 | 454
2017-01-19 16:00 | 380 | 379
2017-01-19 16:30 | 381 | 378
2017-01-19 17:00 | 314 | 310
2017-01-19 17:30 | 371 | 366
2017-01-19 18:00 | 502 | 500
2017-01-19 18:30 | 502 | 502
2017-01-19 19:00 | 503 | 503
2017-01-19 19:30 | 515 | 514
2017-01-19 20:00 | 509 | 509
2017-01-19 20:30 | 490 | 490
2017-01-19 21:00 | 495 | 495
2017-01-19 21:30 | 469 | 468
2017-01-19 22:00 | 438 | 436
2017-01-19 22:30 | 362 | 360
2017-01-19 23:00 | 328 | 324
2017-01-19 23:30 | 328 | 323
2017-01-20 | 321 | 315
2017-01-20 00:30 | 413 | 408
2017-01-20 01:00 | 503 | 501
2017-01-20 01:30 | 485 | 484
2017-01-20 02:00 | 456 | 455
2017-01-20 02:30 | 441 | 439
2017-01-20 03:00 | 436 | 434
2017-01-20 03:30 | 430 | 428
2017-01-20 04:00 | 428 | 425
2017-01-20 04:30 | 433 | 430
2017-01-20 05:00 | 430 | 427
2017-01-20 05:30 | 444 | 441
2017-01-20 06:00 | 452 | 450
2017-01-20 06:30 | 474 | 472
2017-01-20 07:00 | 444 | 442
2017-01-20 07:30 | 482 | 480
2017-01-20 08:00 | 550 | 549
2017-01-20 08:30 | 584 | 584
2017-01-20 09:00 | 590 | 590
2017-01-20 09:30 | 579 | 579
2017-01-20 10:00 | 541 | 541
2017-01-20 10:30 | 541 | 540
2017-01-20 11:00 | 492 | 492
2017-01-20 11:30 | 565 | 565
2017-01-20 12:00 | 575 | 574
2017-01-20 12:30 | 540 | 540
2017-01-20 13:00 | 543 | 543
2017-01-20 13:30 | 512 | 511
2017-01-20 14:00 | 445 | 445
2017-01-20 14:30 | 363 | 361
2017-01-20 15:00 | 347 | 343
2017-01-20 15:30 | 253 | 247
2017-01-20 16:00 | 103 | 74
2017-01-20 16:30 | 162 | 134
2017-01-20 17:00 | 94 | 39
2017-01-20 17:30 | 98 | 3
2017-01-20 18:00 | 124 | 66
2017-01-20 18:30 | 141 | 105
2017-01-20 19:00 | 132 | 98
2017-01-20 19:30 | 142 | 101
2017-01-20 20:00 | 152 | 114
2017-01-20 20:30 | 141 | 102
2017-01-20 21:00 | 226 | 204
2017-01-20 21:30 | 352 | 342
2017-01-20 22:00 | 361 | 357
2017-01-20 22:30 | 165 | 154
2017-01-20 23:00 | 138 | 102
2017-01-20 23:30 | 155 | 116
2017-01-21 | 262 | 242
2017-01-21 00:30 | 300 | 288
2017-01-21 01:00 | 328 | 320
2017-01-21 01:30 | 349 | 341
2017-01-21 02:00 | 325 | 317
2017-01-21 02:30 | 318 | 310
2017-01-21 03:00 | 314 | 305
2017-01-21 03:30 | 310 | 301
2017-01-21 04:00 | 308 | 299
2017-01-21 04:30 | 317 | 307
2017-01-21 05:00 | 330 | 322
2017-01-21 05:30 | 327 | 319
2017-01-21 06:00 | 329 | 321
2017-01-21 06:30 | 323 | 315
2017-01-21 07:00 | 350 | 343
2017-01-21 07:30 | 357 | 351
2017-01-21 08:00 | 379 | 373
2017-01-21 08:30 | 413 | 409
2017-01-21 09:00 | 420 | 417
2017-01-21 09:30 | 397 | 394
2017-01-21 10:00 | 406 | 403
2017-01-21 10:30 | 405 | 402
2017-01-21 11:00 | 331 | 327
2017-01-21 11:30 | 411 | 406
2017-01-21 12:00 | 444 | 441
2017-01-21 12:30 | 467 | 465
2017-01-21 13:00 | 499 | 498
2017-01-21 13:30 | 512 | 511
2017-01-21 14:00 | 430 | 428
2017-01-21 14:30 | 467 | 465
2017-01-21 15:00 | 533 | 532
2017-01-21 15:30 | 547 | 546
2017-01-21 16:00 | 573 | 572
2017-01-21 16:30 | 582 | 582
2017-01-21 17:00 | 601 | 601
2017-01-21 17:30 | 615 | 615
2017-01-21 18:00 | 609 | 609
2017-01-21 18:30 | 611 | 611
2017-01-21 19:00 | 643 | 643
2017-01-21 19:30 | 709 | 709
2017-01-21 20:00 | 787 | 786
2017-01-21 20:30 | 773 | 772
2017-01-21 21:00 | 749 | 748
2017-01-21 21:30 | 723 | 722
2017-01-21 22:00 | 699 | 698
2017-01-21 22:30 | 649 | 649
2017-01-21 23:00 | 616 | 616
2017-01-21 23:30 | 592 | 592
2017-01-22 | 579 | 579
2017-01-22 00:30 | 588 | 588
2017-01-22 01:00 | 582 | 581
2017-01-22 01:30 | 558 | 558
2017-01-22 02:00 | 532 | 532
2017-01-22 02:30 | 521 | 521
2017-01-22 03:00 | 507 | 506
2017-01-22 03:30 | 473 | 472
2017-01-22 04:00 | 445 | 444
2017-01-22 04:30 | 437 | 436
2017-01-22 05:00 | 444 | 442
2017-01-22 05:30 | 441 | 440
2017-01-22 06:00 | 449 | 448
2017-01-22 06:30 | 440 | 439
2017-01-22 07:00 | 460 | 458
2017-01-22 07:30 | 461 | 460
2017-01-22 08:00 | 469 | 468
2017-01-22 08:30 | 491 | 490
2017-01-22 09:00 | 497 | 497
2017-01-22 09:30 | 515 | 515
2017-01-22 10:00 | 533 | 532
2017-01-22 10:30 | 541 | 540
2017-01-22 11:00 | 551 | 551
2017-01-22 11:30 | 559 | 558
2017-01-22 12:00 | 571 | 571
2017-01-22 12:30 | 580 | 580
2017-01-22 13:00 | 625 | 625
2017-01-22 13:30 | 642 | 642
2017-01-22 14:00 | 654 | 654
2017-01-22 14:30 | 665 | 665
2017-01-22 15:00 | 672 | 672
2017-01-22 15:30 | 697 | 697
2017-01-22 16:00 | 698 | 698
2017-01-22 16:30 | 707 | 707
2017-01-22 17:00 | 715 | 715
2017-01-22 17:30 | 707 | 707
2017-01-22 18:00 | 621 | 620
2017-01-22 18:30 | 631 | 631
2017-01-22 19:00 | 604 | 604
2017-01-22 19:30 | 560 | 560
2017-01-22 20:00 | 565 | 564
2017-01-22 20:30 | 601 | 600
2017-01-22 21:00 | 604 | 604
2017-01-22 21:30 | 596 | 595
2017-01-22 22:00 | 577 | 577
2017-01-22 22:30 | 508 | 507
2017-01-22 23:00 | 476 | 475
2017-01-22 23:30 | 470 | 469
2017-01-23 | 468 | 467
2017-01-23 00:30 | 485 | 484
2017-01-23 01:00 | 480 | 478
2017-01-23 01:30 | 469 | 467
2017-01-23 02:00 | 477 | 475
2017-01-23 02:30 | 506 | 504
2017-01-23 03:00 | 497 | 496
2017-01-23 03:30 | 476 | 475
2017-01-23 04:00 | 451 | 450
2017-01-23 04:30 | 448 | 446
2017-01-23 05:00 | 449 | 447
2017-01-23 05:30 | 459 | 458
2017-01-23 06:00 | 471 | 470
2017-01-23 06:30 | 499 | 498
2017-01-23 07:00 | 474 | 473
2017-01-23 07:30 | 566 | 565
2017-01-23 08:00 | 597 | 597
2017-01-23 08:30 | 609 | 608
2017-01-23 09:00 | 617 | 617
2017-01-23 09:30 | 630 | 630
2017-01-23 10:00 | 637 | 637
2017-01-23 10:30 | 644 | 644
2017-01-23 11:00 | 654 | 654
2017-01-23 11:30 | 665 | 665
2017-01-23 12:00 | 685 | 685
2017-01-23 12:30 | 685 | 685
2017-01-23 13:00 | 673 | 673
2017-01-23 13:30 | 677 | 677
2017-01-23 14:00 | 689 | 688
2017-01-23 14:30 | 696 | 696
2017-01-23 15:00 | 695 | 695
2017-01-23 15:30 | 707 | 707
2017-01-23 16:00 | 726 | 726
2017-01-23 16:30 | 659 | 659
2017-01-23 17:00 | 626 | 626
2017-01-23 17:30 | 656 | 656
2017-01-23 18:00 | 683 | 683
2017-01-23 18:30 | 701 | 701
2017-01-23 19:00 | 684 | 684
2017-01-23 19:30 | 726 | 726
2017-01-23 20:00 | 718 | 718
2017-01-23 20:30 | 745 | 745
2017-01-23 21:00 | 740 | 740
2017-01-23 21:30 | 701 | 701
2017-01-23 22:00 | 657 | 657
2017-01-23 22:30 | 566 | 566
2017-01-23 23:00 | 535 | 534
2017-01-23 23:30 | 524 | 523
2017-01-24 | 512 | 511
2017-01-24 00:30 | 519 | 518
2017-01-24 01:00 | 521 | 520
2017-01-24 01:30 | 501 | 500
2017-01-24 02:00 | 476 | 475
2017-01-24 02:30 | 468 | 466
2017-01-24 03:00 | 459 | 457
2017-01-24 03:30 | 456 | 454
2017-01-24 04:00 | 451 | 448
2017-01-24 04:30 | 454 | 452
2017-01-24 05:00 | 461 | 459
2017-01-24 05:30 | 469 | 466
2017-01-24 06:00 | 462 | 460
2017-01-24 06:30 | 465 | 463
2017-01-24 07:00 | 480 | 479
2017-01-24 07:30 | 612 | 611
2017-01-24 08:00 | 630 | 630
2017-01-24 08:30 | 627 | 627
2017-01-24 09:00 | 592 | 592
2017-01-24 09:30 | 600 | 600
2017-01-24 10:00 | 596 | 596
2017-01-24 10:30 | 588 | 588
2017-01-24 11:00 | 596 | 596
2017-01-24 11:30 | 607 | 607
2017-01-24 12:00 | 616 | 616
2017-01-24 12:30 | 575 | 575
2017-01-24 13:00 | 545 | 545
2017-01-24 13:30 | 452 | 452
2017-01-24 14:00 | 443 | 442
2017-01-24 14:30 | 408 | 407
2017-01-24 15:00 | 434 | 432
2017-01-24 15:30 | 445 | 444
2017-01-24 16:00 | 432 | 431
2017-01-24 16:30 | 349 | 348
2017-01-24 17:00 | 205 | 199
2017-01-24 17:30 | 257 | 246
2017-01-24 18:00 | 309 | 301
2017-01-24 18:30 | 352 | 348
2017-01-24 19:00 | 349 | 345
2017-01-24 19:30 | 361 | 358
2017-01-24 20:00 | 371 | 368
2017-01-24 20:30 | 419 | 416
2017-01-24 21:00 | 553 | 551
2017-01-24 21:30 | 554 | 553
2017-01-24 22:00 | 513 | 513
2017-01-24 22:30 | 414 | 413
2017-01-24 23:00 | 418 | 416
2017-01-24 23:30 | 419 | 416
2017-01-25 | 401 | 399
2017-01-25 00:30 | 428 | 425
2017-01-25 01:00 | 434 | 432
2017-01-25 01:30 | 413 | 412
2017-01-25 02:00 | 386 | 383
2017-01-25 02:30 | 377 | 375
2017-01-25 03:00 | 371 | 368
2017-01-25 03:30 | 372 | 368
2017-01-25 04:00 | 370 | 366
2017-01-25 04:30 | 367 | 364
2017-01-25 05:00 | 372 | 369
2017-01-25 05:30 | 379 | 376
2017-01-25 06:00 | 394 | 391
2017-01-25 06:30 | 384 | 381
2017-01-25 07:00 | 393 | 391
2017-01-25 07:30 | 446 | 444
2017-01-25 08:00 | 520 | 519
2017-01-25 08:30 | 524 | 524
2017-01-25 09:00 | 533 | 532
2017-01-25 09:30 | 543 | 543
2017-01-25 10:00 | 549 | 548
2017-01-25 10:30 | 553 | 552
2017-01-25 11:00 | 458 | 457
2017-01-25 11:30 | 444 | 441
2017-01-25 12:00 | 456 | 452
2017-01-25 12:30 | 462 | 460
2017-01-25 13:00 | 474 | 472
2017-01-25 13:30 | 481 | 479
2017-01-25 14:00 | 472 | 470
2017-01-25 14:30 | 505 | 503
2017-01-25 15:00 | 493 | 492
2017-01-25 15:30 | 486 | 485
2017-01-25 16:00 | 462 | 460
2017-01-25 16:30 | 364 | 362
2017-01-25 17:00 | 260 | 252
2017-01-25 17:30 | 224 | 210
2017-01-25 18:00 | 312 | 300
2017-01-25 18:30 | 405 | 399
2017-01-25 19:00 | 444 | 441
2017-01-25 19:30 | 424 | 422
2017-01-25 20:00 | 405 | 402
2017-01-25 20:30 | 404 | 402
2017-01-25 21:00 | 482 | 479
2017-01-25 21:30 | 472 | 470
2017-01-25 22:00 | 423 | 421
2017-01-25 22:30 | 374 | 371
2017-01-25 23:00 | 325 | 319
2017-01-25 23:30 | 403 | 396
2017-01-26 | 434 | 430
2017-01-26 00:30 | 472 | 470
2017-01-26 01:00 | 538 | 537
2017-01-26 01:30 | 527 | 527
2017-01-26 02:00 | 518 | 517
2017-01-26 02:30 | 516 | 514
2017-01-26 03:00 | 519 | 517
2017-01-26 03:30 | 504 | 503
2017-01-26 04:00 | 495 | 493
2017-01-26 04:30 | 491 | 489
2017-01-26 05:00 | 492 | 490
2017-01-26 05:30 | 490 | 488
2017-01-26 06:00 | 493 | 491
2017-01-26 06:30 | 501 | 500
2017-01-26 07:00 | 510 | 509
2017-01-26 07:30 | 531 | 529
2017-01-26 08:00 | 544 | 543
2017-01-26 08:30 | 562 | 561
2017-01-26 09:00 | 569 | 569
2017-01-26 09:30 | 575 | 575
2017-01-26 10:00 | 575 | 575
2017-01-26 10:30 | 575 | 575
2017-01-26 11:00 | 565 | 565
2017-01-26 11:30 | 556 | 556
2017-01-26 12:00 | 550 | 549
2017-01-26 12:30 | 548 | 547
2017-01-26 13:00 | 558 | 557
2017-01-26 13:30 | 566 | 565
2017-01-26 14:00 | 567 | 567
2017-01-26 14:30 | 576 | 576
2017-01-26 15:00 | 589 | 588
2017-01-26 15:30 | 551 | 551
2017-01-26 16:00 | 601 | 601
2017-01-26 16:30 | 534 | 534
2017-01-26 17:00 | 418 | 417
2017-01-26 17:30 | 445 | 443
2017-01-26 18:00 | 452 | 450
2017-01-26 18:30 | 497 | 496
2017-01-26 19:00 | 462 | 461
2017-01-26 19:30 | 508 | 506
2017-01-26 20:00 | 505 | 504
2017-01-26 20:30 | 512 | 511
2017-01-26 21:00 | 520 | 518
2017-01-26 21:30 | 502 | 500
2017-01-26 22:00 | 541 | 540
2017-01-26 22:30 | 433 | 432
2017-01-26 23:00 | 459 | 456
2017-01-26 23:30 | 463 | 460
2017-01-27 | 527 | 525
2017-01-27 00:30 | 500 | 499
2017-01-27 01:00 | 437 | 435
2017-01-27 01:30 | 492 | 489
2017-01-27 02:00 | 494 | 492
2017-01-27 02:30 | 493 | 491
2017-01-27 03:00 | 491 | 490
2017-01-27 03:30 | 486 | 485
2017-01-27 04:00 | 485 | 483
2017-01-27 04:30 | 483 | 481
2017-01-27 05:00 | 486 | 484
2017-01-27 05:30 | 494 | 493
2017-01-27 06:00 | 488 | 486
2017-01-27 06:30 | 473 | 471
2017-01-27 07:00 | 460 | 458
2017-01-27 07:30 | 503 | 501
2017-01-27 08:00 | 565 | 564
2017-01-27 08:30 | 570 | 569
2017-01-27 09:00 | 594 | 594
2017-01-27 09:30 | 580 | 580
2017-01-27 10:00 | 616 | 616
2017-01-27 10:30 | 607 | 607
2017-01-27 11:00 | 476 | 476
2017-01-27 11:30 | 470 | 470
2017-01-27 12:00 | 555 | 554
2017-01-27 12:30 | 572 | 572
2017-01-27 13:00 | 577 | 577
2017-01-27 13:30 | 584 | 584
2017-01-27 14:00 | 588 | 588
2017-01-27 14:30 | 600 | 600
2017-01-27 15:00 | 593 | 593
2017-01-27 15:30 | 552 | 552
2017-01-27 16:00 | 558 | 558
2017-01-27 16:30 | 529 | 529
2017-01-27 17:00 | 507 | 507
2017-01-27 17:30 | 598 | 598
2017-01-27 18:00 | 613 | 613
2017-01-27 18:30 | 647 | 647
2017-01-27 19:00 | 699 | 699
2017-01-27 19:30 | 723 | 723
2017-01-27 20:00 | 744 | 744
2017-01-27 20:30 | 749 | 749
2017-01-27 21:00 | 736 | 736
2017-01-27 21:30 | 704 | 704
2017-01-27 22:00 | 638 | 638
2017-01-27 22:30 | 530 | 530
2017-01-27 23:00 | 482 | 481
2017-01-27 23:30 | 520 | 519
2017-01-28 | 536 | 536
2017-01-28 00:30 | 555 | 554
2017-01-28 01:00 | 558 | 557
2017-01-28 01:30 | 545 | 544
2017-01-28 02:00 | 520 | 520
2017-01-28 02:30 | 500 | 499
2017-01-28 03:00 | 496 | 495
2017-01-28 03:30 | 496 | 495
2017-01-28 04:00 | 494 | 492
2017-01-28 04:30 | 493 | 492
2017-01-28 05:00 | 490 | 489
2017-01-28 05:30 | 489 | 487
2017-01-28 06:00 | 444 | 443
2017-01-28 06:30 | 423 | 421
2017-01-28 07:00 | 428 | 425
2017-01-28 07:30 | 491 | 488
2017-01-28 08:00 | 513 | 512
2017-01-28 08:30 | 534 | 533
2017-01-28 09:00 | 556 | 556
2017-01-28 09:30 | 572 | 572
2017-01-28 10:00 | 571 | 570
2017-01-28 10:30 | 571 | 571
2017-01-28 11:00 | 579 | 579
2017-01-28 11:30 | 588 | 588
2017-01-28 12:00 | 599 | 598
2017-01-28 12:30 | 606 | 606
2017-01-28 13:00 | 621 | 621
2017-01-28 13:30 | 627 | 627
2017-01-28 14:00 | 630 | 630
2017-01-28 14:30 | 608 | 608
2017-01-28 15:00 | 614 | 614
2017-01-28 15:30 | 634 | 634
2017-01-28 16:00 | 609 | 609
2017-01-28 16:30 | 621 | 621
2017-01-28 17:00 | 552 | 552
2017-01-28 17:30 | 569 | 569
2017-01-28 18:00 | 554 | 554
2017-01-28 18:30 | 569 | 569
2017-01-28 19:00 | 576 | 576
2017-01-28 19:30 | 656 | 656
2017-01-28 20:00 | 729 | 729
2017-01-28 20:30 | 712 | 712
2017-01-28 21:00 | 713 | 713
2017-01-28 21:30 | 707 | 707
2017-01-28 22:00 | 676 | 676
2017-01-28 22:30 | 593 | 593
2017-01-28 23:00 | 539 | 539
2017-01-28 23:30 | 562 | 561
2017-01-29 | 575 | 574
2017-01-29 00:30 | 559 | 558
2017-01-29 01:00 | 547 | 547
2017-01-29 01:30 | 535 | 534
2017-01-29 02:00 | 526 | 525
2017-01-29 02:30 | 518 | 517
2017-01-29 03:00 | 507 | 506
2017-01-29 03:30 | 502 | 500
2017-01-29 04:00 | 502 | 501
2017-01-29 04:30 | 495 | 494
2017-01-29 05:00 | 495 | 493
2017-01-29 05:30 | 491 | 490
2017-01-29 06:00 | 483 | 482
2017-01-29 06:30 | 481 | 480
2017-01-29 07:00 | 492 | 491
2017-01-29 07:30 | 512 | 511
2017-01-29 08:00 | 521 | 521
2017-01-29 08:30 | 540 | 539
2017-01-29 09:00 | 557 | 556
2017-01-29 09:30 | 570 | 570
2017-01-29 10:00 | 561 | 561
2017-01-29 10:30 | 558 | 558
2017-01-29 11:00 | 541 | 541
2017-01-29 11:30 | 477 | 477
2017-01-29 12:00 | 483 | 482
2017-01-29 12:30 | 504 | 503
2017-01-29 13:00 | 522 | 522
2017-01-29 13:30 | 525 | 525
2017-01-29 14:00 | 536 | 535
2017-01-29 14:30 | 530 | 530
2017-01-29 15:00 | 527 | 527
2017-01-29 15:30 | 567 | 567
2017-01-29 16:00 | 515 | 515
2017-01-29 16:30 | 378 | 378
2017-01-29 17:00 | 360 | 357
2017-01-29 17:30 | 354 | 350
2017-01-29 18:00 | 413 | 411
2017-01-29 18:30 | 457 | 456
2017-01-29 19:00 | 367 | 366
2017-01-29 19:30 | 309 | 306
2017-01-29 20:00 | 316 | 312
2017-01-29 20:30 | 375 | 372
2017-01-29 21:00 | 415 | 413
2017-01-29 21:30 | 595 | 594
2017-01-29 22:00 | 629 | 629
2017-01-29 22:30 | 553 | 553
2017-01-29 23:00 | 491 | 491
2017-01-29 23:30 | 517 | 517
2017-01-30 | 527 | 527
2017-01-30 00:30 | 531 | 531
2017-01-30 01:00 | 512 | 512
2017-01-30 01:30 | 498 | 498
2017-01-30 02:00 | 490 | 489
2017-01-30 02:30 | 488 | 487
2017-01-30 03:00 | 486 | 485
2017-01-30 03:30 | 479 | 479
2017-01-30 04:00 | 478 | 477
2017-01-30 04:30 | 477 | 477
2017-01-30 05:00 | 479 | 479
2017-01-30 05:30 | 494 | 493
2017-01-30 06:00 | 493 | 492
2017-01-30 06:30 | 424 | 423
2017-01-30 07:00 | 395 | 394
2017-01-30 07:30 | 477 | 475
2017-01-30 08:00 | 538 | 537
2017-01-30 08:30 | 556 | 556
2017-01-30 09:00 | 536 | 536
2017-01-30 09:30 | 549 | 549
2017-01-30 10:00 | 553 | 553
2017-01-30 10:30 | 564 | 564
2017-01-30 11:00 | 566 | 566
2017-01-30 11:30 | 556 | 555
2017-01-30 12:00 | 551 | 551
2017-01-30 12:30 | 556 | 556
2017-01-30 13:00 | 564 | 564
2017-01-30 13:30 | 514 | 514
2017-01-30 14:00 | 470 | 470
2017-01-30 14:30 | 329 | 328
2017-01-30 15:00 | 262 | 257
2017-01-30 15:30 | 163 | 150
2017-01-30 16:00 | 172 | 151
2017-01-30 16:30 | 193 | 176
2017-01-30 17:00 | 255 | 245
2017-01-30 17:30 | 291 | 284
2017-01-30 18:00 | 253 | 247
2017-01-30 18:30 | 231 | 222
2017-01-30 19:00 | 194 | 182
2017-01-30 19:30 | 204 | 190
2017-01-30 20:00 | 321 | 312
2017-01-30 20:30 | 336 | 333
2017-01-30 21:00 | 430 | 428
2017-01-30 21:30 | 472 | 472
2017-01-30 22:00 | 434 | 434
2017-01-30 22:30 | 309 | 308
2017-01-30 23:00 | 293 | 289
2017-01-30 23:30 | 385 | 381
2017-01-31 | 396 | 394
2017-01-31 00:30 | 395 | 393
2017-01-31 01:00 | 383 | 382
2017-01-31 01:30 | 370 | 367
2017-01-31 02:00 | 360 | 358
2017-01-31 02:30 | 360 | 357
2017-01-31 03:00 | 360 | 357
2017-01-31 03:30 | 361 | 358
2017-01-31 04:00 | 359 | 356
2017-01-31 04:30 | 360 | 357
2017-01-31 05:00 | 364 | 361
2017-01-31 05:30 | 373 | 370
2017-01-31 06:00 | 389 | 387
2017-01-31 06:30 | 370 | 368
2017-01-31 07:00 | 372 | 370
2017-01-31 07:30 | 449 | 447
2017-01-31 08:00 | 436 | 435
2017-01-31 08:30 | 460 | 459
2017-01-31 09:00 | 462 | 462
2017-01-31 09:30 | 456 | 456
2017-01-31 10:00 | 504 | 504
2017-01-31 10:30 | 511 | 510
2017-01-31 11:00 | 414 | 414
2017-01-31 11:30 | 446 | 445
2017-01-31 12:00 | 472 | 471
2017-01-31 12:30 | 497 | 496
2017-01-31 13:00 | 451 | 451
2017-01-31 13:30 | 435 | 435
2017-01-31 14:00 | 413 | 412
2017-01-31 14:30 | 358 | 357
2017-01-31 15:00 | 345 | 343
2017-01-31 15:30 | 195 | 190
2017-01-31 16:00 | 151 | 132
2017-01-31 16:30 | 167 | 146
2017-01-31 17:00 | 80 | 25
2017-01-31 17:30 | 93 | 17
2017-01-31 18:00 | 103 | 42
2017-01-31 18:30 | 89 | 12
2017-01-31 19:00 | 96 | 26
2017-01-31 19:30 | 103 | 40
2017-01-31 20:00 | 106 | 39
2017-01-31 20:30 | 141 | 108
2017-01-31 21:00 | 287 | 276
2017-01-31 21:30 | 415 | 412
2017-01-31 22:00 | 434 | 433
2017-01-31 22:30 | 316 | 315
2017-01-31 23:00 | 359 | 356
2017-01-31 23:30 | 303 | 300
2017-02-01 | 326 | 322
2017-02-01 00:30 | 362 | 359
2017-02-01 01:00 | 389 | 387
2017-02-01 01:30 | 420 | 419
2017-02-01 02:00 | 428 | 427
2017-02-01 02:30 | 414 | 413
2017-02-01 03:00 | 440 | 439
2017-02-01 03:30 | 451 | 449
2017-02-01 04:00 | 454 | 453
2017-02-01 04:30 | 455 | 454
2017-02-01 05:00 | 460 | 459
2017-02-01 05:30 | 476 | 475
2017-02-01 06:00 | 462 | 461
2017-02-01 06:30 | 462 | 461
2017-02-01 07:00 | 507 | 507
2017-02-01 07:30 | 554 | 554
2017-02-01 08:00 | 563 | 563
2017-02-01 08:30 | 598 | 598
2017-02-01 09:00 | 626 | 626
2017-02-01 09:30 | 644 | 644
2017-02-01 10:00 | 587 | 587
2017-02-01 10:30 | 560 | 560
2017-02-01 11:00 | 522 | 521
2017-02-01 11:30 | 480 | 480
2017-02-01 12:00 | 397 | 396
2017-02-01 12:30 | 410 | 408
2017-02-01 13:00 | 427 | 425
2017-02-01 13:30 | 400 | 398
2017-02-01 14:00 | 365 | 363
2017-02-01 14:30 | 307 | 304
2017-02-01 15:00 | 248 | 243
2017-02-01 15:30 | 177 | 166
2017-02-01 16:00 | 164 | 150
2017-02-01 16:30 | 74 | 37
2017-02-01 17:00 | 93 | 47
2017-02-01 17:30 | 90 | 2
2017-02-01 18:00 | 100 | 52
2017-02-01 18:30 | 105 | 69
2017-02-01 19:00 | 99 | 59
2017-02-01 19:30 | 174 | 156
2017-02-01 20:00 | 251 | 241
2017-02-01 20:30 | 258 | 253
2017-02-01 21:00 | 342 | 338
2017-02-01 21:30 | 364 | 362
2017-02-01 22:00 | 330 | 328
2017-02-01 22:30 | 220 | 216
2017-02-01 23:00 | 196 | 188
2017-02-01 23:30 | 222 | 212
2017-02-02 | 226 | 217
2017-02-02 00:30 | 330 | 324
2017-02-02 01:00 | 422 | 420
2017-02-02 01:30 | 425 | 424
2017-02-02 02:00 | 420 | 419
2017-02-02 02:30 | 422 | 421
2017-02-02 03:00 | 417 | 416
2017-02-02 03:30 | 420 | 419
2017-02-02 04:00 | 421 | 420
2017-02-02 04:30 | 407 | 406
2017-02-02 05:00 | 416 | 414
2017-02-02 05:30 | 426 | 425
2017-02-02 06:00 | 424 | 423
2017-02-02 06:30 | 415 | 414
2017-02-02 07:00 | 405 | 404
2017-02-02 07:30 | 470 | 469
2017-02-02 08:00 | 529 | 529
2017-02-02 08:30 | 544 | 544
2017-02-02 09:00 | 532 | 532
2017-02-02 09:30 | 541 | 541
2017-02-02 10:00 | 501 | 501
2017-02-02 10:30 | 508 | 508
2017-02-02 11:00 | 515 | 515
2017-02-02 11:30 | 488 | 488
2017-02-02 12:00 | 436 | 436
2017-02-02 12:30 | 454 | 453
2017-02-02 13:00 | 387 | 387
2017-02-02 13:30 | 234 | 231
2017-02-02 14:00 | 299 | 288
2017-02-02 14:30 | 272 | 265
2017-02-02 15:00 | 243 | 234
2017-02-02 15:30 | 170 | 154
2017-02-02 16:00 | 127 | 93
2017-02-02 16:30 | 99 | 31
2017-02-02 17:00 | 107 | 35
2017-02-02 17:30 | 104 | 22
2017-02-02 18:00 | 117 | 45
2017-02-02 18:30 | 134 | 86
2017-02-02 19:00 | 106 | 42
2017-02-02 19:30 | 101 | 12
2017-02-02 20:00 | 138 | 88
2017-02-02 20:30 | 249 | 228
2017-02-02 21:00 | 381 | 373
2017-02-02 21:30 | 440 | 437
2017-02-02 22:00 | 407 | 405
2017-02-02 22:30 | 231 | 226
2017-02-02 23:00 | 212 | 195
2017-02-02 23:30 | 225 | 208
2017-02-03 | 253 | 240
2017-02-03 00:30 | 358 | 350
2017-02-03 01:00 | 425 | 421
2017-02-03 01:30 | 413 | 410
2017-02-03 02:00 | 408 | 405
2017-02-03 02:30 | 405 | 402
2017-02-03 03:00 | 404 | 400
2017-02-03 03:30 | 403 | 400
2017-02-03 04:00 | 401 | 398
2017-02-03 04:30 | 407 | 403
2017-02-03 05:00 | 416 | 413
2017-02-03 05:30 | 423 | 420
2017-02-03 06:00 | 415 | 412
2017-02-03 06:30 | 413 | 410
2017-02-03 07:00 | 402 | 400
2017-02-03 07:30 | 475 | 473
2017-02-03 08:00 | 531 | 530
2017-02-03 08:30 | 548 | 547
2017-02-03 09:00 | 561 | 560
2017-02-03 09:30 | 524 | 524
2017-02-03 10:00 | 496 | 495
2017-02-03 10:30 | 500 | 499
2017-02-03 11:00 | 482 | 481
2017-02-03 11:30 | 404 | 402
2017-02-03 12:00 | 371 | 368
2017-02-03 12:30 | 389 | 386
2017-02-03 13:00 | 399 | 397
2017-02-03 13:30 | 409 | 408
2017-02-03 14:00 | 397 | 396
2017-02-03 14:30 | 363 | 361
2017-02-03 15:00 | 366 | 365
2017-02-03 15:30 | 376 | 374
2017-02-03 16:00 | 382 | 381
2017-02-03 16:30 | 334 | 332
2017-02-03 17:00 | 256 | 253
2017-02-03 17:30 | 338 | 334
2017-02-03 18:00 | 360 | 358
2017-02-03 18:30 | 385 | 384
2017-02-03 19:00 | 392 | 391
2017-02-03 19:30 | 412 | 411
2017-02-03 20:00 | 414 | 413
2017-02-03 20:30 | 388 | 387
2017-02-03 21:00 | 452 | 451
2017-02-03 21:30 | 477 | 476
2017-02-03 22:00 | 419 | 419
2017-02-03 22:30 | 330 | 329
2017-02-03 23:00 | 333 | 330
2017-02-03 23:30 | 438 | 436
2017-02-04 | 466 | 465
2017-02-04 00:30 | 457 | 457
2017-02-04 01:00 | 439 | 439
2017-02-04 01:30 | 426 | 425
2017-02-04 02:00 | 412 | 411
2017-02-04 02:30 | 405 | 404
2017-02-04 03:00 | 405 | 403
2017-02-04 03:30 | 401 | 400
2017-02-04 04:00 | 398 | 397
2017-02-04 04:30 | 396 | 394
2017-02-04 05:00 | 393 | 391
2017-02-04 05:30 | 396 | 395
2017-02-04 06:00 | 377 | 375
2017-02-04 06:30 | 360 | 358
2017-02-04 07:00 | 369 | 367
2017-02-04 07:30 | 424 | 422
2017-02-04 08:00 | 459 | 458
2017-02-04 08:30 | 476 | 476
2017-02-04 09:00 | 483 | 482
2017-02-04 09:30 | 491 | 491
2017-02-04 10:00 | 501 | 501
2017-02-04 10:30 | 516 | 516
2017-02-04 11:00 | 516 | 516
2017-02-04 11:30 | 509 | 509
2017-02-04 12:00 | 512 | 512
2017-02-04 12:30 | 502 | 502
2017-02-04 13:00 | 531 | 531
2017-02-04 13:30 | 494 | 494
2017-02-04 14:00 | 446 | 446
2017-02-04 14:30 | 446 | 445
2017-02-04 15:00 | 375 | 374
2017-02-04 15:30 | 378 | 376
2017-02-04 16:00 | 352 | 351
2017-02-04 16:30 | 280 | 278
2017-02-04 17:00 | 276 | 272
2017-02-04 17:30 | 318 | 314
2017-02-04 18:00 | 317 | 315
2017-02-04 18:30 | 362 | 360
2017-02-04 19:00 | 305 | 303
2017-02-04 19:30 | 366 | 364
2017-02-04 20:00 | 393 | 392
2017-02-04 20:30 | 425 | 424
2017-02-04 21:00 | 513 | 513
2017-02-04 21:30 | 547 | 547
2017-02-04 22:00 | 499 | 499
2017-02-04 22:30 | 366 | 366
2017-02-04 23:00 | 320 | 317
2017-02-04 23:30 | 356 | 354
2017-02-05 | 415 | 413
2017-02-05 00:30 | 447 | 446
2017-02-05 01:00 | 439 | 438
2017-02-05 01:30 | 425 | 424
2017-02-05 02:00 | 414 | 413
2017-02-05 02:30 | 409 | 408
2017-02-05 03:00 | 411 | 409
2017-02-05 03:30 | 408 | 406
2017-02-05 04:00 | 403 | 402
2017-02-05 04:30 | 406 | 404
2017-02-05 05:00 | 404 | 402
2017-02-05 05:30 | 403 | 401
2017-02-05 06:00 | 380 | 378
2017-02-05 06:30 | 363 | 360
2017-02-05 07:00 | 368 | 365
2017-02-05 07:30 | 424 | 422
2017-02-05 08:00 | 450 | 449
2017-02-05 08:30 | 469 | 468
2017-02-05 09:00 | 493 | 493
2017-02-05 09:30 | 512 | 512
2017-02-05 10:00 | 497 | 497
2017-02-05 10:30 | 498 | 497
2017-02-05 11:00 | 485 | 485
2017-02-05 11:30 | 493 | 493
2017-02-05 12:00 | 493 | 493
2017-02-05 12:30 | 495 | 495
2017-02-05 13:00 | 440 | 440
2017-02-05 13:30 | 405 | 404
2017-02-05 14:00 | 269 | 268
2017-02-05 14:30 | 247 | 241
2017-02-05 15:00 | 257 | 251
2017-02-05 15:30 | 276 | 270
2017-02-05 16:00 | 224 | 218
2017-02-05 16:30 | 212 | 202
2017-02-05 17:00 | 227 | 218
2017-02-05 17:30 | 217 | 209
2017-02-05 18:00 | 202 | 192
2017-02-05 18:30 | 200 | 189
2017-02-05 19:00 | 173 | 160
2017-02-05 19:30 | 173 | 157
2017-02-05 20:00 | 183 | 169
2017-02-05 20:30 | 237 | 227
2017-02-05 21:00 | 326 | 321
2017-02-05 21:30 | 472 | 470
2017-02-05 22:00 | 533 | 532
2017-02-05 22:30 | 447 | 447
2017-02-05 23:00 | 410 | 409
2017-02-05 23:30 | 402 | 401
2017-02-06 | 412 | 410
2017-02-06 00:30 | 421 | 419
2017-02-06 01:00 | 415 | 414
2017-02-06 01:30 | 403 | 402
2017-02-06 02:00 | 397 | 395
2017-02-06 02:30 | 401 | 399
2017-02-06 03:00 | 396 | 395
2017-02-06 03:30 | 392 | 390
2017-02-06 04:00 | 390 | 387
2017-02-06 04:30 | 394 | 392
2017-02-06 05:00 | 397 | 395
2017-02-06 05:30 | 410 | 408
2017-02-06 06:00 | 389 | 387
2017-02-06 06:30 | 384 | 382
2017-02-06 07:00 | 397 | 395
2017-02-06 07:30 | 455 | 454
2017-02-06 08:00 | 452 | 451
2017-02-06 08:30 | 459 | 458
2017-02-06 09:00 | 479 | 479
2017-02-06 09:30 | 464 | 464
2017-02-06 10:00 | 409 | 408
2017-02-06 10:30 | 396 | 395
2017-02-06 11:00 | 396 | 395
2017-02-06 11:30 | 404 | 403
2017-02-06 12:00 | 420 | 419
2017-02-06 12:30 | 420 | 420
2017-02-06 13:00 | 376 | 375
2017-02-06 13:30 | 250 | 248
2017-02-06 14:00 | 136 | 124
2017-02-06 14:30 | 99 | 63
2017-02-06 15:00 | 90 | 27
2017-02-06 15:30 | 102 | 38
2017-02-06 16:00 | 100 | 33
2017-02-06 16:30 | 106 | 51
2017-02-06 17:00 | 106 | 48
2017-02-06 17:30 | 96 | 9
2017-02-06 18:00 | 94 | 19
2017-02-06 18:30 | 157 | 129
2017-02-06 19:00 | 152 | 132
2017-02-06 19:30 | 145 | 125
2017-02-06 20:00 | 216 | 203
2017-02-06 20:30 | 319 | 313
2017-02-06 21:00 | 342 | 339
2017-02-06 21:30 | 378 | 376
2017-02-06 22:00 | 404 | 402
2017-02-06 22:30 | 233 | 231
2017-02-06 23:00 | 215 | 208
2017-02-06 23:30 | 298 | 291
2017-02-07 | 350 | 346
2017-02-07 00:30 | 377 | 375
2017-02-07 01:00 | 471 | 469
2017-02-07 01:30 | 461 | 460
2017-02-07 02:00 | 445 | 445
2017-02-07 02:30 | 433 | 432
2017-02-07 03:00 | 423 | 422
2017-02-07 03:30 | 417 | 416
2017-02-07 04:00 | 407 | 406
2017-02-07 04:30 | 414 | 413
2017-02-07 05:00 | 420 | 419
2017-02-07 05:30 | 428 | 427
2017-02-07 06:00 | 437 | 436
2017-02-07 06:30 | 424 | 423
2017-02-07 07:00 | 447 | 446
2017-02-07 07:30 | 486 | 485
2017-02-07 08:00 | 540 | 540
2017-02-07 08:30 | 548 | 548
2017-02-07 09:00 | 561 | 561
2017-02-07 09:30 | 529 | 529
2017-02-07 10:00 | 480 | 480
2017-02-07 10:30 | 485 | 484
2017-02-07 11:00 | 491 | 491
2017-02-07 11:30 | 455 | 455
2017-02-07 12:00 | 423 | 422
2017-02-07 12:30 | 432 | 431
2017-02-07 13:00 | 396 | 395
2017-02-07 13:30 | 335 | 333
2017-02-07 14:00 | 324 | 322
2017-02-07 14:30 | 162 | 156
2017-02-07 15:00 | 201 | 187
2017-02-07 15:30 | 193 | 180
2017-02-07 16:00 | 187 | 174
2017-02-07 16:30 | 116 | 91
2017-02-07 17:00 | 84 | 12
2017-02-07 17:30 | 90 | 2
2017-02-07 18:00 | 124 | 80
2017-02-07 18:30 | 268 | 253
2017-02-07 19:00 | 309 | 303
2017-02-07 19:30 | 315 | 311
2017-02-07 20:00 | 345 | 342
2017-02-07 20:30 | 424 | 422
2017-02-07 21:00 | 454 | 453
2017-02-07 21:30 | 428 | 427
2017-02-07 22:00 | 386 | 385
2017-02-07 22:30 | 298 | 296
2017-02-07 23:00 | 270 | 265
2017-02-07 23:30 | 338 | 333
2017-02-08 | 339 | 335
2017-02-08 00:30 | 378 | 375
2017-02-08 01:00 | 436 | 434
2017-02-08 01:30 | 424 | 423
2017-02-08 02:00 | 416 | 415
2017-02-08 02:30 | 411 | 409
2017-02-08 03:00 | 407 | 405
2017-02-08 03:30 | 411 | 409
2017-02-08 04:00 | 405 | 403
2017-02-08 04:30 | 412 | 411
2017-02-08 05:00 | 415 | 413
2017-02-08 05:30 | 431 | 430
2017-02-08 06:00 | 419 | 417
2017-02-08 06:30 | 383 | 382
2017-02-08 07:00 | 416 | 414
2017-02-08 07:30 | 514 | 513
2017-02-08 08:00 | 552 | 551
2017-02-08 08:30 | 547 | 547
2017-02-08 09:00 | 554 | 554
2017-02-08 09:30 | 514 | 514
2017-02-08 10:00 | 480 | 479
2017-02-08 10:30 | 506 | 505
2017-02-08 11:00 | 512 | 512
2017-02-08 11:30 | 468 | 468
2017-02-08 12:00 | 474 | 473
2017-02-08 12:30 | 485 | 484
2017-02-08 13:00 | 480 | 480
2017-02-08 13:30 | 463 | 463
2017-02-08 14:00 | 442 | 442
2017-02-08 14:30 | 437 | 437
2017-02-08 15:00 | 360 | 359
2017-02-08 15:30 | 320 | 318
2017-02-08 16:00 | 278 | 274
2017-02-08 16:30 | 286 | 281
2017-02-08 17:00 | 277 | 272
2017-02-08 17:30 | 291 | 285
2017-02-08 18:00 | 319 | 315
2017-02-08 18:30 | 388 | 385
2017-02-08 19:00 | 431 | 430
2017-02-08 19:30 | 460 | 459
2017-02-08 20:00 | 480 | 479
2017-02-08 20:30 | 473 | 473
2017-02-08 21:00 | 514 | 513
2017-02-08 21:30 | 498 | 498
2017-02-08 22:00 | 456 | 456
2017-02-08 22:30 | 341 | 340
2017-02-08 23:00 | 319 | 316
2017-02-08 23:30 | 337 | 333
2017-02-09 | 342 | 338
2017-02-09 00:30 | 396 | 392
2017-02-09 01:00 | 457 | 455
2017-02-09 01:30 | 442 | 441
2017-02-09 02:00 | 440 | 439
2017-02-09 02:30 | 429 | 427
2017-02-09 03:00 | 421 | 420
2017-02-09 03:30 | 422 | 421
2017-02-09 04:00 | 421 | 420
2017-02-09 04:30 | 418 | 416
2017-02-09 05:00 | 418 | 416
2017-02-09 05:30 | 435 | 433
2017-02-09 06:00 | 438 | 436
2017-02-09 06:30 | 395 | 394
2017-02-09 07:00 | 419 | 417
2017-02-09 07:30 | 507 | 506
2017-02-09 08:00 | 558 | 557
2017-02-09 08:30 | 557 | 557
2017-02-09 09:00 | 536 | 536
2017-02-09 09:30 | 477 | 477
2017-02-09 10:00 | 460 | 459
2017-02-09 10:30 | 461 | 459
2017-02-09 11:00 | 466 | 465
2017-02-09 11:30 | 406 | 405
2017-02-09 12:00 | 377 | 375
2017-02-09 12:30 | 383 | 381
2017-02-09 13:00 | 385 | 384
2017-02-09 13:30 | 391 | 390
2017-02-09 14:00 | 392 | 391
2017-02-09 14:30 | 340 | 339
2017-02-09 15:00 | 330 | 328
2017-02-09 15:30 | 319 | 316
2017-02-09 16:00 | 195 | 190
2017-02-09 16:30 | 174 | 162
2017-02-09 17:00 | 198 | 186
2017-02-09 17:30 | 288 | 281
2017-02-09 18:00 | 255 | 250
2017-02-09 18:30 | 226 | 221
2017-02-09 19:00 | 373 | 369
2017-02-09 19:30 | 303 | 301
2017-02-09 20:00 | 361 | 358
2017-02-09 20:30 | 361 | 359
2017-02-09 21:00 | 396 | 395
2017-02-09 21:30 | 491 | 490
2017-02-09 22:00 | 466 | 465
2017-02-09 22:30 | 296 | 295
2017-02-09 23:00 | 265 | 261
2017-02-09 23:30 | 319 | 315
2017-02-10 | 360 | 358
2017-02-10 00:30 | 406 | 405
2017-02-10 01:00 | 470 | 469
2017-02-10 01:30 | 459 | 458
2017-02-10 02:00 | 451 | 451
2017-02-10 02:30 | 444 | 444
2017-02-10 03:00 | 444 | 444
2017-02-10 03:30 | 442 | 442
2017-02-10 04:00 | 441 | 440
2017-02-10 04:30 | 437 | 437
2017-02-10 05:00 | 440 | 440
2017-02-10 05:30 | 452 | 451
2017-02-10 06:00 | 462 | 461
2017-02-10 06:30 | 401 | 401
2017-02-10 07:00 | 431 | 430
2017-02-10 07:30 | 531 | 531
2017-02-10 08:00 | 577 | 577
2017-02-10 08:30 | 519 | 519
2017-02-10 09:00 | 473 | 473
2017-02-10 09:30 | 471 | 471
2017-02-10 10:00 | 476 | 475
2017-02-10 10:30 | 422 | 421
2017-02-10 11:00 | 375 | 374
2017-02-10 11:30 | 374 | 373
2017-02-10 12:00 | 384 | 383
2017-02-10 12:30 | 386 | 384
2017-02-10 13:00 | 390 | 389
2017-02-10 13:30 | 333 | 332
2017-02-10 14:00 | 291 | 288
2017-02-10 14:30 | 145 | 136
2017-02-10 15:00 | 75 | 7
2017-02-10 15:30 | 100 | 42
2017-02-10 16:00 | 103 | 28
2017-02-10 16:30 | 98 | 11
2017-02-10 17:00 | 96 | 11
2017-02-10 17:30 | 119 | 72
2017-02-10 18:00 | 99 | 50
2017-02-10 18:30 | 145 | 117
2017-02-10 19:00 | 127 | 101
2017-02-10 19:30 | 148 | 127
2017-02-10 20:00 | 193 | 178
2017-02-10 20:30 | 248 | 240
2017-02-10 21:00 | 296 | 291
2017-02-10 21:30 | 265 | 261
2017-02-10 22:00 | 279 | 275
2017-02-10 22:30 | 199 | 193
2017-02-10 23:00 | 182 | 170
2017-02-10 23:30 | 246 | 236
2017-02-11 | 286 | 281
2017-02-11 00:30 | 364 | 361
2017-02-11 01:00 | 423 | 422
2017-02-11 01:30 | 417 | 416
2017-02-11 02:00 | 420 | 419
2017-02-11 02:30 | 419 | 419
2017-02-11 03:00 | 418 | 418
2017-02-11 03:30 | 417 | 416
2017-02-11 04:00 | 410 | 409
2017-02-11 04:30 | 410 | 409
2017-02-11 05:00 | 410 | 409
2017-02-11 05:30 | 416 | 415
2017-02-11 06:00 | 422 | 422
2017-02-11 06:30 | 383 | 382
2017-02-11 07:00 | 408 | 407
2017-02-11 07:30 | 457 | 457
2017-02-11 08:00 | 491 | 491
2017-02-11 08:30 | 490 | 490
2017-02-11 09:00 | 475 | 475
2017-02-11 09:30 | 480 | 479
2017-02-11 10:00 | 436 | 436
2017-02-11 10:30 | 374 | 373
2017-02-11 11:00 | 364 | 362
2017-02-11 11:30 | 365 | 362
2017-02-11 12:00 | 312 | 309
2017-02-11 12:30 | 269 | 265
2017-02-11 13:00 | 276 | 271
2017-02-11 13:30 | 291 | 287
2017-02-11 14:00 | 208 | 203
2017-02-11 14:30 | 168 | 158
2017-02-11 15:00 | 182 | 170
2017-02-11 15:30 | 87 | 58
2017-02-11 16:00 | 91 | 44
2017-02-11 16:30 | 99 | 33
2017-02-11 17:00 | 97 | 21
2017-02-11 17:30 | 97 | 23
2017-02-11 18:00 | 91 | 2
2017-02-11 18:30 | 98 | 28
2017-02-11 19:00 | 148 | 117
2017-02-11 19:30 | 171 | 150
2017-02-11 20:00 | 176 | 158
2017-02-11 20:30 | 306 | 297
2017-02-11 21:00 | 337 | 333
2017-02-11 21:30 | 351 | 348
2017-02-11 22:00 | 329 | 326
2017-02-11 22:30 | 290 | 287
2017-02-11 23:00 | 289 | 285
2017-02-11 23:30 | 306 | 302
2017-02-12 | 332 | 328
2017-02-12 00:30 | 373 | 371
2017-02-12 01:00 | 353 | 351
2017-02-12 01:30 | 339 | 337
2017-02-12 02:00 | 334 | 331
2017-02-12 02:30 | 325 | 322
2017-02-12 03:00 | 320 | 316
2017-02-12 03:30 | 320 | 317
2017-02-12 04:00 | 319 | 316
2017-02-12 04:30 | 314 | 310
2017-02-12 05:00 | 312 | 308
2017-02-12 05:30 | 314 | 310
2017-02-12 06:00 | 313 | 309
2017-02-12 06:30 | 317 | 313
2017-02-12 07:00 | 312 | 308
2017-02-12 07:30 | 334 | 330
2017-02-12 08:00 | 367 | 364
2017-02-12 08:30 | 394 | 391
2017-02-12 09:00 | 405 | 404
2017-02-12 09:30 | 382 | 381
2017-02-12 10:00 | 359 | 357
2017-02-12 10:30 | 382 | 379
2017-02-12 11:00 | 334 | 332
2017-02-12 11:30 | 289 | 286
2017-02-12 12:00 | 185 | 178
2017-02-12 12:30 | 112 | 87
2017-02-12 13:00 | 114 | 76
2017-02-12 13:30 | 94 | 38
2017-02-12 14:00 | 116 | 49
2017-02-12 14:30 | 119 | 55
2017-02-12 15:00 | 121 | 58
2017-02-12 15:30 | 114 | 43
2017-02-12 16:00 | 109 | 31
2017-02-12 16:30 | 105 | 16
2017-02-12 17:00 | 103 | 3
2017-02-12 17:30 | 104 | 16
2017-02-12 18:00 | 102 | 21
2017-02-12 18:30 | 101 | 14
2017-02-12 19:00 | 106 | 16
2017-02-12 19:30 | 105 | 8
2017-02-12 20:00 | 104 | 23
2017-02-12 20:30 | 129 | 81
2017-02-12 21:00 | 170 | 143
2017-02-12 21:30 | 280 | 267
2017-02-12 22:00 | 416 | 411
2017-02-12 22:30 | 229 | 226
2017-02-12 23:00 | 246 | 236
2017-02-12 23:30 | 356 | 349
2017-02-13 | 374 | 371
2017-02-13 00:30 | 368 | 365
2017-02-13 01:00 | 356 | 353
2017-02-13 01:30 | 347 | 343
2017-02-13 02:00 | 343 | 339
2017-02-13 02:30 | 337 | 332
2017-02-13 03:00 | 334 | 330
2017-02-13 03:30 | 333 | 329
2017-02-13 04:00 | 336 | 332
2017-02-13 04:30 | 332 | 327
2017-02-13 05:00 | 357 | 352
2017-02-13 05:30 | 375 | 372
2017-02-13 06:00 | 352 | 349
2017-02-13 06:30 | 359 | 356
2017-02-13 07:00 | 335 | 331
2017-02-13 07:30 | 370 | 366
2017-02-13 08:00 | 429 | 427
2017-02-13 08:30 | 389 | 388
2017-02-13 09:00 | 381 | 378
2017-02-13 09:30 | 376 | 374
2017-02-13 10:00 | 304 | 301
2017-02-13 10:30 | 272 | 266
2017-02-13 11:00 | 247 | 239
2017-02-13 11:30 | 224 | 215
2017-02-13 12:00 | 203 | 191
2017-02-13 12:30 | 172 | 156
2017-02-13 13:00 | 150 | 126
2017-02-13 13:30 | 168 | 143
2017-02-13 14:00 | 168 | 145
2017-02-13 14:30 | 181 | 161
2017-02-13 15:00 | 192 | 174
2017-02-13 15:30 | 208 | 192
2017-02-13 16:00 | 223 | 210
2017-02-13 16:30 | 222 | 212
2017-02-13 17:00 | 239 | 230
2017-02-13 17:30 | 270 | 262
2017-02-13 18:00 | 272 | 266
2017-02-13 18:30 | 288 | 282
2017-02-13 19:00 | 475 | 471
2017-02-13 19:30 | 538 | 538
2017-02-13 20:00 | 552 | 552
2017-02-13 20:30 | 542 | 542
2017-02-13 21:00 | 534 | 534
2017-02-13 21:30 | 575 | 575
2017-02-13 22:00 | 590 | 590
2017-02-13 22:30 | 462 | 462
2017-02-13 23:00 | 427 | 426
2017-02-13 23:30 | 432 | 430
2017-02-14 | 429 | 427
2017-02-14 00:30 | 509 | 507
2017-02-14 01:00 | 577 | 576
2017-02-14 01:30 | 566 | 566
2017-02-14 02:00 | 558 | 558
2017-02-14 02:30 | 545 | 544
2017-02-14 03:00 | 541 | 541
2017-02-14 03:30 | 535 | 534
2017-02-14 04:00 | 530 | 530
2017-02-14 04:30 | 522 | 522
2017-02-14 05:00 | 524 | 524
2017-02-14 05:30 | 538 | 537
2017-02-14 06:00 | 530 | 530
2017-02-14 06:30 | 516 | 516
2017-02-14 07:00 | 546 | 546
2017-02-14 07:30 | 603 | 603
2017-02-14 08:00 | 641 | 641
2017-02-14 08:30 | 662 | 662
2017-02-14 09:00 | 663 | 663
2017-02-14 09:30 | 681 | 681
2017-02-14 10:00 | 688 | 688
2017-02-14 10:30 | 694 | 694
2017-02-14 11:00 | 707 | 707
2017-02-14 11:30 | 725 | 725
2017-02-14 12:00 | 745 | 744
2017-02-14 12:30 | 758 | 756
2017-02-14 13:00 | 773 | 771
2017-02-14 13:30 | 768 | 766
2017-02-14 14:00 | 771 | 768
2017-02-14 14:30 | 773 | 770
2017-02-14 15:00 | 790 | 787
2017-02-14 15:30 | 815 | 813
2017-02-14 16:00 | 822 | 818
2017-02-14 16:30 | 772 | 769
2017-02-14 17:00 | 769 | 766
2017-02-14 17:30 | 762 | 759
2017-02-14 18:00 | 777 | 774
2017-02-14 18:30 | 814 | 812
2017-02-14 19:00 | 839 | 837
2017-02-14 19:30 | 877 | 874
2017-02-14 20:00 | 860 | 857
2017-02-14 20:30 | 831 | 827
2017-02-14 21:00 | 798 | 795
2017-02-14 21:30 | 778 | 776
2017-02-14 22:00 | 750 | 749
2017-02-14 22:30 | 714 | 713
2017-02-14 23:00 | 683 | 682
2017-02-14 23:30 | 666 | 665
2017-02-15 | 634 | 634
2017-02-15 00:30 | 609 | 609
2017-02-15 01:00 | 586 | 586
2017-02-15 01:30 | 573 | 572
2017-02-15 02:00 | 565 | 564
2017-02-15 02:30 | 562 | 561
2017-02-15 03:00 | 556 | 555
2017-02-15 03:30 | 556 | 554
2017-02-15 04:00 | 550 | 549
2017-02-15 04:30 | 549 | 547
2017-02-15 05:00 | 510 | 508
2017-02-15 05:30 | 511 | 509
2017-02-15 06:00 | 526 | 524
2017-02-15 06:30 | 528 | 526
2017-02-15 07:00 | 551 | 550
2017-02-15 07:30 | 606 | 605
2017-02-15 08:00 | 649 | 649
2017-02-15 08:30 | 654 | 654
2017-02-15 09:00 | 656 | 656
2017-02-15 09:30 | 668 | 668
2017-02-15 10:00 | 674 | 674
2017-02-15 10:30 | 677 | 677
2017-02-15 11:00 | 683 | 683
2017-02-15 11:30 | 697 | 697
2017-02-15 12:00 | 715 | 714
2017-02-15 12:30 | 723 | 723
2017-02-15 13:00 | 722 | 722
2017-02-15 13:30 | 721 | 720
2017-02-15 14:00 | 711 | 711
2017-02-15 14:30 | 699 | 699
2017-02-15 15:00 | 690 | 690
2017-02-15 15:30 | 690 | 690
2017-02-15 16:00 | 691 | 691
2017-02-15 16:30 | 697 | 697
2017-02-15 17:00 | 700 | 700
2017-02-15 17:30 | 702 | 702
2017-02-15 18:00 | 710 | 710
2017-02-15 18:30 | 719 | 719
2017-02-15 19:00 | 722 | 722
2017-02-15 19:30 | 731 | 731
2017-02-15 20:00 | 721 | 720
2017-02-15 20:30 | 697 | 697
2017-02-15 21:00 | 667 | 667
2017-02-15 21:30 | 642 | 642
2017-02-15 22:00 | 632 | 632
2017-02-15 22:30 | 623 | 622
2017-02-15 23:00 | 600 | 599
2017-02-15 23:30 | 569 | 569
2017-02-16 | 548 | 547
2017-02-16 00:30 | 531 | 530
2017-02-16 01:00 | 519 | 518
2017-02-16 01:30 | 510 | 508
2017-02-16 02:00 | 503 | 502
2017-02-16 02:30 | 498 | 497
2017-02-16 03:00 | 496 | 495
2017-02-16 03:30 | 495 | 494
2017-02-16 04:00 | 496 | 494
2017-02-16 04:30 | 506 | 505
2017-02-16 05:00 | 513 | 512
2017-02-16 05:30 | 527 | 526
2017-02-16 06:00 | 543 | 542
2017-02-16 06:30 | 566 | 565
2017-02-16 07:00 | 585 | 584
2017-02-16 07:30 | 584 | 583
2017-02-16 08:00 | 558 | 558
2017-02-16 08:30 | 568 | 568
2017-02-16 09:00 | 576 | 576
2017-02-16 09:30 | 581 | 581
2017-02-16 10:00 | 577 | 577
2017-02-16 10:30 | 579 | 579
2017-02-16 11:00 | 573 | 573
2017-02-16 11:30 | 518 | 518
2017-02-16 12:00 | 492 | 491
2017-02-16 12:30 | 510 | 509
2017-02-16 13:00 | 512 | 511
2017-02-16 13:30 | 422 | 421
2017-02-16 14:00 | 290 | 286
2017-02-16 14:30 | 182 | 170
2017-02-16 15:00 | 178 | 156
2017-02-16 15:30 | 185 | 160
2017-02-16 16:00 | 194 | 169
2017-02-16 16:30 | 187 | 163
2017-02-16 17:00 | 191 | 166
2017-02-16 17:30 | 205 | 182
2017-02-16 18:00 | 214 | 193
2017-02-16 18:30 | 220 | 200
2017-02-16 19:00 | 226 | 208
2017-02-16 19:30 | 223 | 205
2017-02-16 20:00 | 211 | 191
2017-02-16 20:30 | 252 | 235
2017-02-16 21:00 | 243 | 228
2017-02-16 21:30 | 217 | 200
2017-02-16 22:00 | 221 | 202
2017-02-16 22:30 | 194 | 172
2017-02-16 23:00 | 212 | 188
2017-02-16 23:30 | 266 | 249
2017-02-17 | 306 | 293
2017-02-17 00:30 | 414 | 406
2017-02-17 01:00 | 480 | 477
2017-02-17 01:30 | 472 | 470
2017-02-17 02:00 | 463 | 460
2017-02-17 02:30 | 459 | 456
2017-02-17 03:00 | 458 | 455
2017-02-17 03:30 | 458 | 455
2017-02-17 04:00 | 454 | 451
2017-02-17 04:30 | 460 | 457
2017-02-17 05:00 | 463 | 460
2017-02-17 05:30 | 476 | 473
2017-02-17 06:00 | 482 | 480
2017-02-17 06:30 | 494 | 492
2017-02-17 07:00 | 519 | 517
2017-02-17 07:30 | 539 | 538
2017-02-17 08:00 | 559 | 558
2017-02-17 08:30 | 543 | 543
2017-02-17 09:00 | 518 | 517
2017-02-17 09:30 | 517 | 516
2017-02-17 10:00 | 535 | 534
2017-02-17 10:30 | 480 | 479
2017-02-17 11:00 | 434 | 432
2017-02-17 11:30 | 450 | 447
2017-02-17 12:00 | 459 | 456
2017-02-17 12:30 | 466 | 463
2017-02-17 13:00 | 473 | 471
2017-02-17 13:30 | 489 | 486
2017-02-17 14:00 | 488 | 486
2017-02-17 14:30 | 456 | 454
2017-02-17 15:00 | 425 | 422
2017-02-17 15:30 | 393 | 390
2017-02-17 16:00 | 261 | 254
2017-02-17 16:30 | 264 | 250
2017-02-17 17:00 | 258 | 245
2017-02-17 17:30 | 263 | 252
2017-02-17 18:00 | 260 | 249
2017-02-17 18:30 | 260 | 248
2017-02-17 19:00 | 263 | 250
2017-02-17 19:30 | 267 | 255
2017-02-17 20:00 | 254 | 243
2017-02-17 20:30 | 242 | 229
2017-02-17 21:00 | 313 | 302
2017-02-17 21:30 | 325 | 317
2017-02-17 22:00 | 339 | 332
2017-02-17 22:30 | 346 | 340
2017-02-17 23:00 | 330 | 324
2017-02-17 23:30 | 395 | 390
2017-02-18 | 394 | 390
2017-02-18 00:30 | 376 | 371
2017-02-18 01:00 | 362 | 357
2017-02-18 01:30 | 354 | 348
2017-02-18 02:00 | 349 | 343
2017-02-18 02:30 | 343 | 337
2017-02-18 03:00 | 335 | 328
2017-02-18 03:30 | 331 | 323
2017-02-18 04:00 | 335 | 328
2017-02-18 04:30 | 337 | 330
2017-02-18 05:00 | 339 | 333
2017-02-18 05:30 | 342 | 336
2017-02-18 06:00 | 347 | 341
2017-02-18 06:30 | 346 | 340
2017-02-18 07:00 | 346 | 339
2017-02-18 07:30 | 349 | 343
2017-02-18 08:00 | 363 | 357
2017-02-18 08:30 | 386 | 380
2017-02-18 09:00 | 398 | 394
2017-02-18 09:30 | 413 | 410
2017-02-18 10:00 | 417 | 414
2017-02-18 10:30 | 418 | 415
2017-02-18 11:00 | 413 | 410
2017-02-18 11:30 | 416 | 412
2017-02-18 12:00 | 419 | 416
2017-02-18 12:30 | 369 | 365
2017-02-18 13:00 | 294 | 288
2017-02-18 13:30 | 175 | 160
2017-02-18 14:00 | 230 | 209
2017-02-18 14:30 | 243 | 227
2017-02-18 15:00 | 183 | 163
2017-02-18 15:30 | 271 | 254
2017-02-18 16:00 | 262 | 251
2017-02-18 16:30 | 228 | 215
2017-02-18 17:00 | 215 | 199
2017-02-18 17:30 | 311 | 299
2017-02-18 18:00 | 313 | 306
2017-02-18 18:30 | 356 | 350
2017-02-18 19:00 | 267 | 261
2017-02-18 19:30 | 243 | 232
2017-02-18 20:00 | 264 | 252
2017-02-18 20:30 | 369 | 362
2017-02-18 21:00 | 427 | 423
2017-02-18 21:30 | 458 | 455
2017-02-18 22:00 | 467 | 465
2017-02-18 22:30 | 399 | 397
2017-02-18 23:00 | 375 | 371
2017-02-18 23:30 | 412 | 408
2017-02-19 | 464 | 462
2017-02-19 00:30 | 525 | 523
2017-02-19 01:00 | 514 | 514
2017-02-19 01:30 | 505 | 504
2017-02-19 02:00 | 487 | 486
2017-02-19 02:30 | 484 | 482
2017-02-19 03:00 | 477 | 475
2017-02-19 03:30 | 470 | 469
2017-02-19 04:00 | 466 | 465
2017-02-19 04:30 | 464 | 462
2017-02-19 05:00 | 464 | 462
2017-02-19 05:30 | 466 | 464
2017-02-19 06:00 | 467 | 465
2017-02-19 06:30 | 466 | 464
2017-02-19 07:00 | 459 | 456
2017-02-19 07:30 | 459 | 457
2017-02-19 08:00 | 469 | 467
2017-02-19 08:30 | 491 | 489
2017-02-19 09:00 | 501 | 499
2017-02-19 09:30 | 517 | 516
2017-02-19 10:00 | 520 | 519
2017-02-19 10:30 | 526 | 525
2017-02-19 11:00 | 530 | 530
2017-02-19 11:30 | 545 | 545
2017-02-19 12:00 | 557 | 557
2017-02-19 12:30 | 575 | 575
2017-02-19 13:00 | 589 | 588
2017-02-19 13:30 | 601 | 601
2017-02-19 14:00 | 614 | 614
2017-02-19 14:30 | 590 | 590
2017-02-19 15:00 | 587 | 587
2017-02-19 15:30 | 608 | 608
2017-02-19 16:00 | 541 | 541
2017-02-19 16:30 | 526 | 526
2017-02-19 17:00 | 492 | 492
2017-02-19 17:30 | 478 | 478
2017-02-19 18:00 | 468 | 467
2017-02-19 18:30 | 525 | 525
2017-02-19 19:00 | 554 | 553
2017-02-19 19:30 | 556 | 556
2017-02-19 20:00 | 576 | 576
2017-02-19 20:30 | 569 | 569
2017-02-19 21:00 | 545 | 545
2017-02-19 21:30 | 541 | 541
2017-02-19 22:00 | 609 | 608
2017-02-19 22:30 | 592 | 592
2017-02-19 23:00 | 569 | 568
2017-02-19 23:30 | 547 | 547
2017-02-20 | 525 | 524
2017-02-20 00:30 | 504 | 504
2017-02-20 01:00 | 496 | 495
2017-02-20 01:30 | 488 | 487
2017-02-20 02:00 | 483 | 482
2017-02-20 02:30 | 481 | 480
2017-02-20 03:00 | 476 | 475
2017-02-20 03:30 | 473 | 472
2017-02-20 04:00 | 467 | 466
2017-02-20 04:30 | 472 | 471
2017-02-20 05:00 | 475 | 474
2017-02-20 05:30 | 485 | 484
2017-02-20 06:00 | 501 | 501
2017-02-20 06:30 | 536 | 535
2017-02-20 07:00 | 562 | 561
2017-02-20 07:30 | 568 | 568
2017-02-20 08:00 | 586 | 586
2017-02-20 08:30 | 601 | 601
2017-02-20 09:00 | 607 | 607
2017-02-20 09:30 | 608 | 608
2017-02-20 10:00 | 616 | 616
2017-02-20 10:30 | 612 | 612
2017-02-20 11:00 | 627 | 627
2017-02-20 11:30 | 637 | 637
2017-02-20 12:00 | 656 | 656
2017-02-20 12:30 | 660 | 660
2017-02-20 13:00 | 661 | 661
2017-02-20 13:30 | 620 | 620
2017-02-20 14:00 | 601 | 601
2017-02-20 14:30 | 595 | 595
2017-02-20 15:00 | 426 | 426
2017-02-20 15:30 | 391 | 389
2017-02-20 16:00 | 409 | 406
2017-02-20 16:30 | 372 | 370
2017-02-20 17:00 | 359 | 357
2017-02-20 17:30 | 363 | 361
2017-02-20 18:00 | 365 | 363
2017-02-20 18:30 | 362 | 360
2017-02-20 19:00 | 373 | 371
2017-02-20 19:30 | 387 | 385
2017-02-20 20:00 | 370 | 368
2017-02-20 20:30 | 342 | 339
2017-02-20 21:00 | 549 | 548
2017-02-20 21:30 | 611 | 611
2017-02-20 22:00 | 585 | 585
2017-02-20 22:30 | 630 | 630
2017-02-20 23:00 | 611 | 610
2017-02-20 23:30 | 574 | 574
2017-02-21 | 555 | 555
2017-02-21 00:30 | 536 | 536
2017-02-21 01:00 | 523 | 523
2017-02-21 01:30 | 510 | 509
2017-02-21 02:00 | 505 | 505
2017-02-21 02:30 | 500 | 500
2017-02-21 03:00 | 494 | 494
2017-02-21 03:30 | 492 | 492
2017-02-21 04:00 | 489 | 488
2017-02-21 04:30 | 488 | 487
2017-02-21 05:00 | 496 | 496
2017-02-21 05:30 | 507 | 506
2017-02-21 06:00 | 525 | 524
2017-02-21 06:30 | 470 | 470
2017-02-21 07:00 | 466 | 466
2017-02-21 07:30 | 524 | 523
2017-02-21 08:00 | 594 | 594
2017-02-21 08:30 | 539 | 539
2017-02-21 09:00 | 508 | 508
2017-02-21 09:30 | 499 | 498
2017-02-21 10:00 | 487 | 487
2017-02-21 10:30 | 488 | 487
2017-02-21 11:00 | 507 | 507
2017-02-21 11:30 | 505 | 505
2017-02-21 12:00 | 508 | 508
2017-02-21 12:30 | 515 | 515
2017-02-21 13:00 | 519 | 519
2017-02-21 13:30 | 536 | 536
2017-02-21 14:00 | 549 | 548
2017-02-21 14:30 | 552 | 552
2017-02-21 15:00 | 553 | 553
2017-02-21 15:30 | 564 | 564
2017-02-21 16:00 | 577 | 577
2017-02-21 16:30 | 559 | 559
2017-02-21 17:00 | 464 | 464
2017-02-21 17:30 | 462 | 462
2017-02-21 18:00 | 461 | 460
2017-02-21 18:30 | 472 | 471
2017-02-21 19:00 | 489 | 488
2017-02-21 19:30 | 517 | 517
2017-02-21 20:00 | 619 | 619
2017-02-21 20:30 | 649 | 649
2017-02-21 21:00 | 663 | 663
2017-02-21 21:30 | 650 | 650
2017-02-21 22:00 | 655 | 655
2017-02-21 22:30 | 636 | 636
2017-02-21 23:00 | 606 | 606
2017-02-21 23:30 | 575 | 575
2017-02-22 | 556 | 556
2017-02-22 00:30 | 540 | 540
2017-02-22 01:00 | 515 | 514
2017-02-22 01:30 | 507 | 507
2017-02-22 02:00 | 495 | 495
2017-02-22 02:30 | 491 | 490
2017-02-22 03:00 | 489 | 488
2017-02-22 03:30 | 480 | 479
2017-02-22 04:00 | 474 | 473
2017-02-22 04:30 | 475 | 474
2017-02-22 05:00 | 482 | 481
2017-02-22 05:30 | 496 | 495
2017-02-22 06:00 | 517 | 516
2017-02-22 06:30 | 552 | 551
2017-02-22 07:00 | 579 | 579
2017-02-22 07:30 | 624 | 623
2017-02-22 08:00 | 633 | 633
2017-02-22 08:30 | 582 | 582
2017-02-22 09:00 | 551 | 551
2017-02-22 09:30 | 540 | 540
2017-02-22 10:00 | 543 | 542
2017-02-22 10:30 | 550 | 550
2017-02-22 11:00 | 559 | 559
2017-02-22 11:30 | 566 | 565
2017-02-22 12:00 | 569 | 569
2017-02-22 12:30 | 513 | 513
2017-02-22 13:00 | 526 | 526
2017-02-22 13:30 | 524 | 524
2017-02-22 14:00 | 530 | 530
2017-02-22 14:30 | 521 | 521
2017-02-22 15:00 | 456 | 456
2017-02-22 15:30 | 450 | 450
2017-02-22 16:00 | 357 | 357
2017-02-22 16:30 | 397 | 395
2017-02-22 17:00 | 401 | 400
2017-02-22 17:30 | 409 | 408
2017-02-22 18:00 | 481 | 480
2017-02-22 18:30 | 495 | 494
2017-02-22 19:00 | 492 | 491
2017-02-22 19:30 | 477 | 476
2017-02-22 20:00 | 517 | 516
2017-02-22 20:30 | 608 | 608
2017-02-22 21:00 | 589 | 589
2017-02-22 21:30 | 562 | 562
2017-02-22 22:00 | 527 | 527
2017-02-22 22:30 | 505 | 505
2017-02-22 23:00 | 467 | 466
2017-02-22 23:30 | 439 | 438
2017-02-23 | 422 | 420
2017-02-23 00:30 | 406 | 404
2017-02-23 01:00 | 393 | 390
2017-02-23 01:30 | 386 | 383
2017-02-23 02:00 | 380 | 377
2017-02-23 02:30 | 369 | 366
2017-02-23 03:00 | 364 | 360
2017-02-23 03:30 | 366 | 362
2017-02-23 04:00 | 357 | 353
2017-02-23 04:30 | 358 | 354
2017-02-23 05:00 | 355 | 351
2017-02-23 05:30 | 327 | 323
2017-02-23 06:00 | 348 | 343
2017-02-23 06:30 | 378 | 374
2017-02-23 07:00 | 275 | 270
2017-02-23 07:30 | 351 | 344
2017-02-23 08:00 | 414 | 410
2017-02-23 08:30 | 433 | 431
2017-02-23 09:00 | 430 | 428
2017-02-23 09:30 | 437 | 436
2017-02-23 10:00 | 430 | 429
2017-02-23 10:30 | 335 | 333
2017-02-23 11:00 | 339 | 335
2017-02-23 11:30 | 404 | 401
2017-02-23 12:00 | 384 | 382
2017-02-23 12:30 | 396 | 394
2017-02-23 13:00 | 278 | 276
2017-02-23 13:30 | 229 | 221
2017-02-23 14:00 | 252 | 242
2017-02-23 14:30 | 239 | 230
2017-02-23 15:00 | 184 | 173
2017-02-23 15:30 | 190 | 175
2017-02-23 16:00 | 181 | 165
2017-02-23 16:30 | 146 | 124
2017-02-23 17:00 | 95 | 49
2017-02-23 17:30 | 125 | 83
2017-02-23 18:00 | 235 | 216
2017-02-23 18:30 | 309 | 301
2017-02-23 19:00 | 219 | 211
2017-02-23 19:30 | 205 | 193
2017-02-23 20:00 | 304 | 295
2017-02-23 20:30 | 498 | 495
2017-02-23 21:00 | 564 | 564
2017-02-23 21:30 | 506 | 506
2017-02-23 22:00 | 481 | 481
2017-02-23 22:30 | 484 | 483
2017-02-23 23:00 | 475 | 474
2017-02-23 23:30 | 456 | 455
2017-02-24 | 436 | 435
2017-02-24 00:30 | 421 | 419
2017-02-24 01:00 | 407 | 405
2017-02-24 01:30 | 393 | 391
2017-02-24 02:00 | 384 | 381
2017-02-24 02:30 | 381 | 378
2017-02-24 03:00 | 374 | 370
2017-02-24 03:30 | 372 | 368
2017-02-24 04:00 | 375 | 371
2017-02-24 04:30 | 371 | 368
2017-02-24 05:00 | 369 | 366
2017-02-24 05:30 | 386 | 382
2017-02-24 06:00 | 396 | 394
2017-02-24 06:30 | 360 | 358
2017-02-24 07:00 | 356 | 352
2017-02-24 07:30 | 383 | 379
2017-02-24 08:00 | 477 | 475
2017-02-24 08:30 | 472 | 471
2017-02-24 09:00 | 479 | 478
2017-02-24 09:30 | 479 | 478
2017-02-24 10:00 | 480 | 479
2017-02-24 10:30 | 401 | 401
2017-02-24 11:00 | 404 | 402
2017-02-24 11:30 | 438 | 436
2017-02-24 12:00 | 371 | 370
2017-02-24 12:30 | 337 | 335
2017-02-24 13:00 | 328 | 324
2017-02-24 13:30 | 325 | 320
2017-02-24 14:00 | 267 | 261
2017-02-24 14:30 | 265 | 257
2017-02-24 15:00 | 249 | 241
2017-02-24 15:30 | 217 | 206
2017-02-24 16:00 | 226 | 214
2017-02-24 16:30 | 129 | 109
2017-02-24 17:00 | 137 | 104
2017-02-24 17:30 | 139 | 106
2017-02-24 18:00 | 140 | 108
2017-02-24 18:30 | 192 | 170
2017-02-24 19:00 | 137 | 110
2017-02-24 19:30 | 152 | 123
2017-02-24 20:00 | 165 | 142
2017-02-24 20:30 | 229 | 214
2017-02-24 21:00 | 400 | 394
2017-02-24 21:30 | 414 | 412
2017-02-24 22:00 | 450 | 449
2017-02-24 22:30 | 489 | 489
2017-02-24 23:00 | 476 | 476
2017-02-24 23:30 | 516 | 515
2017-02-25 | 579 | 579
2017-02-25 00:30 | 566 | 566
2017-02-25 01:00 | 550 | 550
2017-02-25 01:30 | 540 | 540
2017-02-25 02:00 | 529 | 529
2017-02-25 02:30 | 521 | 520
2017-02-25 03:00 | 513 | 513
2017-02-25 03:30 | 504 | 503
2017-02-25 04:00 | 505 | 504
2017-02-25 04:30 | 499 | 498
2017-02-25 05:00 | 488 | 488
2017-02-25 05:30 | 500 | 499
2017-02-25 06:00 | 512 | 511
2017-02-25 06:30 | 520 | 519
2017-02-25 07:00 | 529 | 529
2017-02-25 07:30 | 549 | 549
2017-02-25 08:00 | 560 | 560
2017-02-25 08:30 | 558 | 558
2017-02-25 09:00 | 575 | 574
2017-02-25 09:30 | 582 | 582
2017-02-25 10:00 | 580 | 580
2017-02-25 10:30 | 574 | 574
2017-02-25 11:00 | 572 | 572
2017-02-25 11:30 | 585 | 585
2017-02-25 12:00 | 602 | 602
2017-02-25 12:30 | 608 | 608
2017-02-25 13:00 | 602 | 602
2017-02-25 13:30 | 586 | 586
2017-02-25 14:00 | 595 | 595
2017-02-25 14:30 | 594 | 594
2017-02-25 15:00 | 595 | 595
2017-02-25 15:30 | 603 | 603
2017-02-25 16:00 | 610 | 610
2017-02-25 16:30 | 612 | 611
2017-02-25 17:00 | 628 | 628
2017-02-25 17:30 | 624 | 624
2017-02-25 18:00 | 556 | 556
2017-02-25 18:30 | 512 | 512
2017-02-25 19:00 | 508 | 508
2017-02-25 19:30 | 515 | 515
2017-02-25 20:00 | 504 | 504
2017-02-25 20:30 | 486 | 486
2017-02-25 21:00 | 468 | 468
2017-02-25 21:30 | 451 | 451
2017-02-25 22:00 | 456 | 455
2017-02-25 22:30 | 458 | 457
2017-02-25 23:00 | 531 | 530
2017-02-25 23:30 | 535 | 534
2017-02-26 | 515 | 515
2017-02-26 00:30 | 501 | 500
2017-02-26 01:00 | 481 | 480
2017-02-26 01:30 | 473 | 472
2017-02-26 02:00 | 467 | 466
2017-02-26 02:30 | 461 | 460
2017-02-26 03:00 | 461 | 460
2017-02-26 03:30 | 461 | 460
2017-02-26 04:00 | 457 | 456
2017-02-26 04:30 | 460 | 459
2017-02-26 05:00 | 459 | 458
2017-02-26 05:30 | 462 | 461
2017-02-26 06:00 | 459 | 458
2017-02-26 06:30 | 460 | 459
2017-02-26 07:00 | 465 | 464
2017-02-26 07:30 | 482 | 480
2017-02-26 08:00 | 502 | 501
2017-02-26 08:30 | 510 | 509
2017-02-26 09:00 | 521 | 520
2017-02-26 09:30 | 528 | 528
2017-02-26 10:00 | 520 | 520
2017-02-26 10:30 | 514 | 514
2017-02-26 11:00 | 515 | 515
2017-02-26 11:30 | 525 | 524
2017-02-26 12:00 | 538 | 537
2017-02-26 12:30 | 546 | 546
2017-02-26 13:00 | 555 | 554
2017-02-26 13:30 | 557 | 557
2017-02-26 14:00 | 544 | 544
2017-02-26 14:30 | 541 | 541
2017-02-26 15:00 | 558 | 558
2017-02-26 15:30 | 572 | 572
2017-02-26 16:00 | 586 | 586
2017-02-26 16:30 | 596 | 596
2017-02-26 17:00 | 615 | 615
2017-02-26 17:30 | 628 | 628
2017-02-26 18:00 | 646 | 645
2017-02-26 18:30 | 654 | 654
2017-02-26 19:00 | 666 | 666
2017-02-26 19:30 | 681 | 681
2017-02-26 20:00 | 671 | 671
2017-02-26 20:30 | 652 | 652
2017-02-26 21:00 | 628 | 628
2017-02-26 21:30 | 605 | 605
2017-02-26 22:00 | 576 | 576
2017-02-26 22:30 | 568 | 568
2017-02-26 23:00 | 571 | 571
2017-02-26 23:30 | 553 | 553
2017-02-27 | 531 | 531
2017-02-27 00:30 | 518 | 517
2017-02-27 01:00 | 503 | 502
2017-02-27 01:30 | 497 | 496
2017-02-27 02:00 | 490 | 489
2017-02-27 02:30 | 482 | 481
2017-02-27 03:00 | 476 | 475
2017-02-27 03:30 | 474 | 473
2017-02-27 04:00 | 474 | 473
2017-02-27 04:30 | 475 | 474
2017-02-27 05:00 | 475 | 475
2017-02-27 05:30 | 492 | 491
2017-02-27 06:00 | 514 | 513
2017-02-27 06:30 | 544 | 544
2017-02-27 07:00 | 571 | 571
2017-02-27 07:30 | 586 | 586
2017-02-27 08:00 | 600 | 600
2017-02-27 08:30 | 608 | 608
2017-02-27 09:00 | 611 | 611
2017-02-27 09:30 | 610 | 610
2017-02-27 10:00 | 611 | 611
2017-02-27 10:30 | 615 | 615
2017-02-27 11:00 | 607 | 607
2017-02-27 11:30 | 598 | 597
2017-02-27 12:00 | 601 | 601
2017-02-27 12:30 | 620 | 620
2017-02-27 13:00 | 629 | 629
2017-02-27 13:30 | 635 | 635
2017-02-27 14:00 | 626 | 626
2017-02-27 14:30 | 635 | 635
2017-02-27 15:00 | 633 | 632
2017-02-27 15:30 | 641 | 640
2017-02-27 16:00 | 658 | 658
2017-02-27 16:30 | 666 | 666
2017-02-27 17:00 | 681 | 680
2017-02-27 17:30 | 685 | 684
2017-02-27 18:00 | 683 | 683
2017-02-27 18:30 | 688 | 688
2017-02-27 19:00 | 701 | 701
2017-02-27 19:30 | 708 | 707
2017-02-27 20:00 | 689 | 689
2017-02-27 20:30 | 666 | 666
2017-02-27 21:00 | 659 | 659
2017-02-27 21:30 | 654 | 654
2017-02-27 22:00 | 633 | 633
2017-02-27 22:30 | 597 | 597
2017-02-27 23:00 | 573 | 573
2017-02-27 23:30 | 547 | 546
2017-02-28 | 526 | 525
2017-02-28 00:30 | 509 | 508
2017-02-28 01:00 | 495 | 494
2017-02-28 01:30 | 484 | 483
2017-02-28 02:00 | 476 | 474
2017-02-28 02:30 | 472 | 471
2017-02-28 03:00 | 469 | 468
2017-02-28 03:30 | 465 | 464
2017-02-28 04:00 | 466 | 465
2017-02-28 04:30 | 459 | 458
2017-02-28 05:00 | 462 | 461
2017-02-28 05:30 | 476 | 475
2017-02-28 06:00 | 494 | 493
2017-02-28 06:30 | 522 | 521
2017-02-28 07:00 | 547 | 547
2017-02-28 07:30 | 591 | 590
2017-02-28 08:00 | 608 | 608
2017-02-28 08:30 | 609 | 609
2017-02-28 09:00 | 621 | 621
2017-02-28 09:30 | 625 | 625
2017-02-28 10:00 | 601 | 601
2017-02-28 10:30 | 597 | 597
2017-02-28 11:00 | 601 | 601
2017-02-28 11:30 | 607 | 606
2017-02-28 12:00 | 625 | 625
2017-02-28 12:30 | 637 | 637
2017-02-28 13:00 | 634 | 634
2017-02-28 13:30 | 632 | 632
2017-02-28 14:00 | 631 | 631
2017-02-28 14:30 | 624 | 624
2017-02-28 15:00 | 621 | 621
2017-02-28 15:30 | 627 | 627
2017-02-28 16:00 | 647 | 647
2017-02-28 16:30 | 656 | 656
2017-02-28 17:00 | 666 | 666
2017-02-28 17:30 | 671 | 671
2017-02-28 18:00 | 673 | 673
2017-02-28 18:30 | 678 | 678
2017-02-28 19:00 | 684 | 684
2017-02-28 19:30 | 728 | 727
2017-02-28 20:00 | 748 | 748
2017-02-28 20:30 | 725 | 723
2017-02-28 21:00 | 698 | 697
2017-02-28 21:30 | 672 | 672
2017-02-28 22:00 | 642 | 642
2017-02-28 22:30 | 602 | 602
2017-02-28 23:00 | 577 | 577
2017-02-28 23:30 | 551 | 551
2017-03-01 | 530 | 529
2017-03-01 00:30 | 513 | 513
2017-03-01 01:00 | 502 | 501
2017-03-01 01:30 | 493 | 492
2017-03-01 02:00 | 481 | 480
2017-03-01 02:30 | 483 | 481
2017-03-01 03:00 | 478 | 476
2017-03-01 03:30 | 472 | 471
2017-03-01 04:00 | 470 | 468
2017-03-01 04:30 | 471 | 469
2017-03-01 05:00 | 473 | 471
2017-03-01 05:30 | 485 | 483
2017-03-01 06:00 | 493 | 491
2017-03-01 06:30 | 521 | 519
2017-03-01 07:00 | 553 | 552
2017-03-01 07:30 | 592 | 591
2017-03-01 08:00 | 615 | 615
2017-03-01 08:30 | 630 | 630
2017-03-01 09:00 | 625 | 625
2017-03-01 09:30 | 595 | 595
2017-03-01 10:00 | 536 | 536
2017-03-01 10:30 | 541 | 541
2017-03-01 11:00 | 549 | 548
2017-03-01 11:30 | 540 | 540
2017-03-01 12:00 | 562 | 562
2017-03-01 12:30 | 567 | 567
2017-03-01 13:00 | 570 | 570
2017-03-01 13:30 | 489 | 489
2017-03-01 14:00 | 416 | 416
2017-03-01 14:30 | 409 | 407
2017-03-01 15:00 | 416 | 414
2017-03-01 15:30 | 424 | 422
2017-03-01 16:00 | 438 | 436
2017-03-01 16:30 | 438 | 436
2017-03-01 17:00 | 450 | 449
2017-03-01 17:30 | 465 | 463
2017-03-01 18:00 | 468 | 467
2017-03-01 18:30 | 487 | 486
2017-03-01 19:00 | 490 | 490
2017-03-01 19:30 | 549 | 549
2017-03-01 20:00 | 548 | 548
2017-03-01 20:30 | 602 | 602
2017-03-01 21:00 | 586 | 586
2017-03-01 21:30 | 556 | 556
2017-03-01 22:00 | 519 | 519
2017-03-01 22:30 | 486 | 485
2017-03-01 23:00 | 457 | 456
2017-03-01 23:30 | 435 | 433
2017-03-02 | 409 | 407
2017-03-02 00:30 | 399 | 397
2017-03-02 01:00 | 382 | 380
2017-03-02 01:30 | 363 | 360
2017-03-02 02:00 | 361 | 358
2017-03-02 02:30 | 355 | 352
2017-03-02 03:00 | 349 | 345
2017-03-02 03:30 | 342 | 338
2017-03-02 04:00 | 344 | 339
2017-03-02 04:30 | 349 | 345
2017-03-02 05:00 | 353 | 348
2017-03-02 05:30 | 363 | 359
2017-03-02 06:00 | 374 | 371
2017-03-02 06:30 | 399 | 396
2017-03-02 07:00 | 426 | 424
2017-03-02 07:30 | 463 | 461
2017-03-02 08:00 | 479 | 478
2017-03-02 08:30 | 494 | 493
2017-03-02 09:00 | 504 | 503
2017-03-02 09:30 | 511 | 510
2017-03-02 10:00 | 487 | 486
2017-03-02 10:30 | 472 | 471
2017-03-02 11:00 | 465 | 464
2017-03-02 11:30 | 466 | 465
2017-03-02 12:00 | 475 | 474
2017-03-02 12:30 | 483 | 483
2017-03-02 13:00 | 500 | 499
2017-03-02 13:30 | 422 | 421
2017-03-02 14:00 | 409 | 407
2017-03-02 14:30 | 416 | 414
2017-03-02 15:00 | 419 | 417
2017-03-02 15:30 | 426 | 425
2017-03-02 16:00 | 438 | 436
2017-03-02 16:30 | 440 | 439
2017-03-02 17:00 | 432 | 431
2017-03-02 17:30 | 431 | 430
2017-03-02 18:00 | 442 | 441
2017-03-02 18:30 | 467 | 466
2017-03-02 19:00 | 488 | 487
2017-03-02 19:30 | 516 | 516
2017-03-02 20:00 | 549 | 549
2017-03-02 20:30 | 608 | 608
2017-03-02 21:00 | 581 | 581
2017-03-02 21:30 | 550 | 550
2017-03-02 22:00 | 516 | 516
2017-03-02 22:30 | 485 | 485
2017-03-02 23:00 | 455 | 455
2017-03-02 23:30 | 429 | 428
2017-03-03 | 408 | 407
2017-03-03 00:30 | 397 | 396
2017-03-03 01:00 | 384 | 383
2017-03-03 01:30 | 371 | 370
2017-03-03 02:00 | 368 | 366
2017-03-03 02:30 | 355 | 353
2017-03-03 03:00 | 350 | 348
2017-03-03 03:30 | 345 | 342
2017-03-03 04:00 | 350 | 347
2017-03-03 04:30 | 354 | 351
2017-03-03 05:00 | 356 | 353
2017-03-03 05:30 | 370 | 368
2017-03-03 06:00 | 383 | 381
2017-03-03 06:30 | 373 | 371
2017-03-03 07:00 | 345 | 343
2017-03-03 07:30 | 394 | 392
2017-03-03 08:00 | 452 | 451
2017-03-03 08:30 | 419 | 419
2017-03-03 09:00 | 427 | 426
2017-03-03 09:30 | 432 | 432
2017-03-03 10:00 | 434 | 433
2017-03-03 10:30 | 444 | 443
2017-03-03 11:00 | 435 | 435
2017-03-03 11:30 | 440 | 440
2017-03-03 12:00 | 459 | 458
2017-03-03 12:30 | 428 | 428
2017-03-03 13:00 | 397 | 397
2017-03-03 13:30 | 397 | 396
2017-03-03 14:00 | 403 | 402
2017-03-03 14:30 | 384 | 384
2017-03-03 15:00 | 374 | 373
2017-03-03 15:30 | 369 | 368
2017-03-03 16:00 | 380 | 378
2017-03-03 16:30 | 394 | 393
2017-03-03 17:00 | 393 | 393
2017-03-03 17:30 | 382 | 381
2017-03-03 18:00 | 376 | 375
2017-03-03 18:30 | 425 | 424
2017-03-03 19:00 | 383 | 382
2017-03-03 19:30 | 425 | 424
2017-03-03 20:00 | 472 | 471
2017-03-03 20:30 | 491 | 491
2017-03-03 21:00 | 490 | 490
2017-03-03 21:30 | 477 | 477
2017-03-03 22:00 | 457 | 457
2017-03-03 22:30 | 432 | 432
2017-03-03 23:00 | 416 | 415
2017-03-03 23:30 | 397 | 396
2017-03-04 | 381 | 380
2017-03-04 00:30 | 371 | 369
2017-03-04 01:00 | 359 | 357
2017-03-04 01:30 | 348 | 345
2017-03-04 02:00 | 338 | 335
2017-03-04 02:30 | 337 | 334
2017-03-04 03:00 | 340 | 337
2017-03-04 03:30 | 336 | 333
2017-03-04 04:00 | 335 | 332
2017-03-04 04:30 | 336 | 333
2017-03-04 05:00 | 338 | 335
2017-03-04 05:30 | 341 | 338
2017-03-04 06:00 | 348 | 345
2017-03-04 06:30 | 360 | 357
2017-03-04 07:00 | 370 | 367
2017-03-04 07:30 | 389 | 387
2017-03-04 08:00 | 388 | 386
2017-03-04 08:30 | 345 | 343
2017-03-04 09:00 | 353 | 350
2017-03-04 09:30 | 358 | 356
2017-03-04 10:00 | 335 | 332
2017-03-04 10:30 | 331 | 328
2017-03-04 11:00 | 320 | 316
2017-03-04 11:30 | 314 | 310
2017-03-04 12:00 | 323 | 319
2017-03-04 12:30 | 344 | 341
2017-03-04 13:00 | 354 | 351
2017-03-04 13:30 | 360 | 358
2017-03-04 14:00 | 364 | 362
2017-03-04 14:30 | 361 | 360
2017-03-04 15:00 | 359 | 357
2017-03-04 15:30 | 348 | 347
2017-03-04 16:00 | 368 | 366
2017-03-04 16:30 | 360 | 359
2017-03-04 17:00 | 365 | 363
2017-03-04 17:30 | 372 | 370
2017-03-04 18:00 | 374 | 373
2017-03-04 18:30 | 385 | 384
2017-03-04 19:00 | 389 | 388
2017-03-04 19:30 | 415 | 414
2017-03-04 20:00 | 457 | 456
2017-03-04 20:30 | 439 | 439
2017-03-04 21:00 | 476 | 476
2017-03-04 21:30 | 478 | 478
2017-03-04 22:00 | 460 | 460
2017-03-04 22:30 | 427 | 427
2017-03-04 23:00 | 368 | 367
2017-03-04 23:30 | 398 | 396
2017-03-05 | 381 | 380
2017-03-05 00:30 | 372 | 371
2017-03-05 01:00 | 351 | 350
2017-03-05 01:30 | 341 | 338
2017-03-05 02:00 | 336 | 333
2017-03-05 02:30 | 337 | 334
2017-03-05 03:00 | 299 | 296
2017-03-05 03:30 | 271 | 266
2017-03-05 04:00 | 270 | 264
2017-03-05 04:30 | 266 | 259
2017-03-05 05:00 | 266 | 260
2017-03-05 05:30 | 268 | 262
2017-03-05 06:00 | 269 | 263
2017-03-05 06:30 | 274 | 267
2017-03-05 07:00 | 279 | 273
2017-03-05 07:30 | 299 | 294
2017-03-05 08:00 | 312 | 307
2017-03-05 08:30 | 336 | 333
2017-03-05 09:00 | 351 | 348
2017-03-05 09:30 | 353 | 351
2017-03-05 10:00 | 361 | 359
2017-03-05 10:30 | 373 | 371
2017-03-05 11:00 | 375 | 374
2017-03-05 11:30 | 381 | 380
2017-03-05 12:00 | 394 | 393
2017-03-05 12:30 | 395 | 394
2017-03-05 13:00 | 405 | 404
2017-03-05 13:30 | 419 | 418
2017-03-05 14:00 | 431 | 431
2017-03-05 14:30 | 427 | 427
2017-03-05 15:00 | 380 | 380
2017-03-05 15:30 | 413 | 412
2017-03-05 16:00 | 378 | 377
2017-03-05 16:30 | 337 | 336
2017-03-05 17:00 | 343 | 341
2017-03-05 17:30 | 254 | 252
2017-03-05 18:00 | 244 | 239
2017-03-05 18:30 | 246 | 240
2017-03-05 19:00 | 233 | 227
2017-03-05 19:30 | 309 | 304
2017-03-05 20:00 | 440 | 438
2017-03-05 20:30 | 506 | 506
2017-03-05 21:00 | 557 | 557
2017-03-05 21:30 | 528 | 528
2017-03-05 22:00 | 501 | 501
2017-03-05 22:30 | 468 | 467
2017-03-05 23:00 | 445 | 445
2017-03-05 23:30 | 420 | 420
2017-03-06 | 403 | 402
2017-03-06 00:30 | 393 | 392
2017-03-06 01:00 | 379 | 377
2017-03-06 01:30 | 375 | 373
2017-03-06 02:00 | 367 | 365
2017-03-06 02:30 | 366 | 363
2017-03-06 03:00 | 367 | 364
2017-03-06 03:30 | 360 | 358
2017-03-06 04:00 | 357 | 354
2017-03-06 04:30 | 361 | 359
2017-03-06 05:00 | 367 | 364
2017-03-06 05:30 | 370 | 368
2017-03-06 06:00 | 383 | 381
2017-03-06 06:30 | 393 | 391
2017-03-06 07:00 | 361 | 360
2017-03-06 07:30 | 438 | 436
2017-03-06 08:00 | 483 | 483
2017-03-06 08:30 | 496 | 496
2017-03-06 09:00 | 430 | 430
2017-03-06 09:30 | 434 | 433
2017-03-06 10:00 | 477 | 477
2017-03-06 10:30 | 514 | 514
2017-03-06 11:00 | 459 | 459
2017-03-06 11:30 | 444 | 444
2017-03-06 12:00 | 469 | 469
2017-03-06 12:30 | 473 | 473
2017-03-06 13:00 | 477 | 477
2017-03-06 13:30 | 481 | 481
2017-03-06 14:00 | 481 | 481
2017-03-06 14:30 | 488 | 488
2017-03-06 15:00 | 483 | 483
2017-03-06 15:30 | 486 | 486
2017-03-06 16:00 | 514 | 514
2017-03-06 16:30 | 527 | 527
2017-03-06 17:00 | 525 | 525
2017-03-06 17:30 | 518 | 518
2017-03-06 18:00 | 532 | 532
2017-03-06 18:30 | 540 | 540
2017-03-06 19:00 | 563 | 563
2017-03-06 19:30 | 593 | 592
2017-03-06 20:00 | 606 | 606
2017-03-06 20:30 | 640 | 639
2017-03-06 21:00 | 641 | 641
2017-03-06 21:30 | 610 | 609
2017-03-06 22:00 | 573 | 573
2017-03-06 22:30 | 530 | 530
2017-03-06 23:00 | 499 | 499
2017-03-06 23:30 | 470 | 470
2017-03-07 | 456 | 456
2017-03-07 00:30 | 449 | 449
2017-03-07 01:00 | 427 | 427
2017-03-07 01:30 | 420 | 419
2017-03-07 02:00 | 410 | 410
2017-03-07 02:30 | 403 | 402
2017-03-07 03:00 | 399 | 398
2017-03-07 03:30 | 394 | 393
2017-03-07 04:00 | 392 | 391
2017-03-07 04:30 | 395 | 394
2017-03-07 05:00 | 400 | 399
2017-03-07 05:30 | 406 | 406
2017-03-07 06:00 | 423 | 422
2017-03-07 06:30 | 390 | 390
2017-03-07 07:00 | 394 | 393
2017-03-07 07:30 | 429 | 428
2017-03-07 08:00 | 449 | 449
2017-03-07 08:30 | 470 | 469
2017-03-07 09:00 | 478 | 478
2017-03-07 09:30 | 482 | 482
2017-03-07 10:00 | 459 | 459
2017-03-07 10:30 | 459 | 458
2017-03-07 11:00 | 462 | 461
2017-03-07 11:30 | 468 | 467
2017-03-07 12:00 | 472 | 471
2017-03-07 12:30 | 486 | 485
2017-03-07 13:00 | 494 | 494
2017-03-07 13:30 | 507 | 506
2017-03-07 14:00 | 500 | 500
2017-03-07 14:30 | 492 | 492
2017-03-07 15:00 | 500 | 500
2017-03-07 15:30 | 509 | 508
2017-03-07 16:00 | 529 | 529
2017-03-07 16:30 | 543 | 543
2017-03-07 17:00 | 551 | 551
2017-03-07 17:30 | 556 | 556
2017-03-07 18:00 | 555 | 555
2017-03-07 18:30 | 582 | 582
2017-03-07 19:00 | 636 | 636
2017-03-07 19:30 | 644 | 644
2017-03-07 20:00 | 631 | 631
2017-03-07 20:30 | 618 | 618
2017-03-07 21:00 | 593 | 593
2017-03-07 21:30 | 552 | 552
2017-03-07 22:00 | 561 | 560
2017-03-07 22:30 | 480 | 479
2017-03-07 23:00 | 429 | 427
2017-03-07 23:30 | 405 | 402
2017-03-08 | 419 | 415
2017-03-08 00:30 | 446 | 442
2017-03-08 01:00 | 430 | 427
2017-03-08 01:30 | 415 | 412
2017-03-08 02:00 | 408 | 405
2017-03-08 02:30 | 395 | 392
2017-03-08 03:00 | 390 | 386
2017-03-08 03:30 | 391 | 388
2017-03-08 04:00 | 388 | 384
2017-03-08 04:30 | 390 | 386
2017-03-08 05:00 | 370 | 366
2017-03-08 05:30 | 355 | 351
2017-03-08 06:00 | 346 | 341
2017-03-08 06:30 | 281 | 275
2017-03-08 07:00 | 303 | 295
2017-03-08 07:30 | 348 | 342
2017-03-08 08:00 | 369 | 365
2017-03-08 08:30 | 394 | 390
2017-03-08 09:00 | 400 | 396
2017-03-08 09:30 | 402 | 399
2017-03-08 10:00 | 403 | 400
2017-03-08 10:30 | 409 | 407
2017-03-08 11:00 | 407 | 405
2017-03-08 11:30 | 403 | 401
2017-03-08 12:00 | 391 | 389
2017-03-08 12:30 | 394 | 392
2017-03-08 13:00 | 403 | 401
2017-03-08 13:30 | 418 | 417
2017-03-08 14:00 | 419 | 417
2017-03-08 14:30 | 427 | 425
2017-03-08 15:00 | 437 | 435
2017-03-08 15:30 | 422 | 421
2017-03-08 16:00 | 420 | 419
2017-03-08 16:30 | 433 | 432
2017-03-08 17:00 | 430 | 428
2017-03-08 17:30 | 425 | 423
2017-03-08 18:00 | 427 | 425
2017-03-08 18:30 | 435 | 434
2017-03-08 19:00 | 511 | 509
2017-03-08 19:30 | 561 | 560
2017-03-08 20:00 | 559 | 559
2017-03-08 20:30 | 536 | 536
2017-03-08 21:00 | 516 | 515
2017-03-08 21:30 | 486 | 485
2017-03-08 22:00 | 479 | 478
2017-03-08 22:30 | 431 | 429
2017-03-08 23:00 | 386 | 384
2017-03-08 23:30 | 424 | 421
2017-03-09 | 475 | 473
2017-03-09 00:30 | 540 | 538
2017-03-09 01:00 | 521 | 520
2017-03-09 01:30 | 513 | 512
2017-03-09 02:00 | 503 | 502
2017-03-09 02:30 | 497 | 496
2017-03-09 03:00 | 488 | 487
2017-03-09 03:30 | 484 | 483
2017-03-09 04:00 | 479 | 478
2017-03-09 04:30 | 479 | 478
2017-03-09 05:00 | 486 | 485
2017-03-09 05:30 | 494 | 493
2017-03-09 06:00 | 510 | 509
2017-03-09 06:30 | 546 | 545
2017-03-09 07:00 | 573 | 572
2017-03-09 07:30 | 615 | 615
2017-03-09 08:00 | 624 | 624
2017-03-09 08:30 | 648 | 648
2017-03-09 09:00 | 657 | 657
2017-03-09 09:30 | 666 | 666
2017-03-09 10:00 | 662 | 662
2017-03-09 10:30 | 667 | 667
2017-03-09 11:00 | 664 | 664
2017-03-09 11:30 | 577 | 577
2017-03-09 12:00 | 533 | 532
2017-03-09 12:30 | 525 | 524
2017-03-09 13:00 | 520 | 520
2017-03-09 13:30 | 530 | 530
2017-03-09 14:00 | 531 | 531
2017-03-09 14:30 | 526 | 525
2017-03-09 15:00 | 516 | 515
2017-03-09 15:30 | 515 | 515
2017-03-09 16:00 | 507 | 507
2017-03-09 16:30 | 479 | 479
2017-03-09 17:00 | 478 | 478
2017-03-09 17:30 | 474 | 474
2017-03-09 18:00 | 481 | 480
2017-03-09 18:30 | 487 | 486
2017-03-09 19:00 | 508 | 508
2017-03-09 19:30 | 532 | 531
2017-03-09 20:00 | 543 | 543
2017-03-09 20:30 | 524 | 524
2017-03-09 21:00 | 504 | 504
2017-03-09 21:30 | 474 | 473
2017-03-09 22:00 | 493 | 492
2017-03-09 22:30 | 418 | 417
2017-03-09 23:00 | 384 | 382
2017-03-09 23:30 | 363 | 360
2017-03-10 | 347 | 343
2017-03-10 00:30 | 448 | 445
2017-03-10 01:00 | 459 | 457
2017-03-10 01:30 | 451 | 450
2017-03-10 02:00 | 440 | 438
2017-03-10 02:30 | 434 | 432
2017-03-10 03:00 | 429 | 426
2017-03-10 03:30 | 424 | 422
2017-03-10 04:00 | 424 | 421
2017-03-10 04:30 | 424 | 421
2017-03-10 05:00 | 428 | 425
2017-03-10 05:30 | 441 | 439
2017-03-10 06:00 | 463 | 461
2017-03-10 06:30 | 490 | 489
2017-03-10 07:00 | 516 | 515
2017-03-10 07:30 | 488 | 488
2017-03-10 08:00 | 441 | 441
2017-03-10 08:30 | 423 | 423
2017-03-10 09:00 | 423 | 422
2017-03-10 09:30 | 423 | 422
2017-03-10 10:00 | 426 | 425
2017-03-10 10:30 | 431 | 430
2017-03-10 11:00 | 434 | 433
2017-03-10 11:30 | 429 | 428
2017-03-10 12:00 | 437 | 436
2017-03-10 12:30 | 446 | 445
2017-03-10 13:00 | 453 | 452
2017-03-10 13:30 | 456 | 455
2017-03-10 14:00 | 456 | 455
2017-03-10 14:30 | 453 | 453
2017-03-10 15:00 | 457 | 456
2017-03-10 15:30 | 461 | 461
2017-03-10 16:00 | 473 | 472
2017-03-10 16:30 | 470 | 470
2017-03-10 17:00 | 478 | 478
2017-03-10 17:30 | 472 | 471
2017-03-10 18:00 | 467 | 467
2017-03-10 18:30 | 468 | 468
2017-03-10 19:00 | 482 | 482
2017-03-10 19:30 | 494 | 494
2017-03-10 20:00 | 476 | 476
2017-03-10 20:30 | 452 | 452
2017-03-10 21:00 | 431 | 430
2017-03-10 21:30 | 410 | 409
2017-03-10 22:00 | 453 | 452
2017-03-10 22:30 | 424 | 423
2017-03-10 23:00 | 395 | 394
2017-03-10 23:30 | 378 | 376
2017-03-11 | 350 | 347
2017-03-11 00:30 | 451 | 448
2017-03-11 01:00 | 467 | 466
2017-03-11 01:30 | 456 | 455
2017-03-11 02:00 | 445 | 444
2017-03-11 02:30 | 438 | 437
2017-03-11 03:00 | 435 | 433
2017-03-11 03:30 | 430 | 429
2017-03-11 04:00 | 427 | 426
2017-03-11 04:30 | 428 | 426
2017-03-11 05:00 | 425 | 423
2017-03-11 05:30 | 428 | 427
2017-03-11 06:00 | 431 | 430
2017-03-11 06:30 | 434 | 432
2017-03-11 07:00 | 444 | 443
2017-03-11 07:30 | 466 | 465
2017-03-11 08:00 | 488 | 487
2017-03-11 08:30 | 507 | 506
2017-03-11 09:00 | 517 | 516
2017-03-11 09:30 | 453 | 452
2017-03-11 10:00 | 364 | 363
2017-03-11 10:30 | 352 | 349
2017-03-11 11:00 | 346 | 343
2017-03-11 11:30 | 349 | 346
2017-03-11 12:00 | 350 | 347
2017-03-11 12:30 | 355 | 352
2017-03-11 13:00 | 361 | 359
2017-03-11 13:30 | 370 | 368
2017-03-11 14:00 | 377 | 375
2017-03-11 14:30 | 366 | 364
2017-03-11 15:00 | 367 | 365
2017-03-11 15:30 | 379 | 378
2017-03-11 16:00 | 392 | 390
2017-03-11 16:30 | 407 | 405
2017-03-11 17:00 | 420 | 419
2017-03-11 17:30 | 430 | 429
2017-03-11 18:00 | 458 | 457
2017-03-11 18:30 | 487 | 487
2017-03-11 19:00 | 509 | 508
2017-03-11 19:30 | 636 | 635
2017-03-11 20:00 | 650 | 650
2017-03-11 20:30 | 629 | 629
2017-03-11 21:00 | 607 | 607
2017-03-11 21:30 | 589 | 589
2017-03-11 22:00 | 568 | 568
2017-03-11 22:30 | 545 | 545
2017-03-11 23:00 | 523 | 523
2017-03-11 23:30 | 501 | 500
2017-03-12 | 485 | 484
2017-03-12 00:30 | 474 | 473
2017-03-12 01:00 | 455 | 454
2017-03-12 01:30 | 443 | 442
2017-03-12 02:00 | 435 | 434
2017-03-12 02:30 | 427 | 425
2017-03-12 03:00 | 421 | 419
2017-03-12 03:30 | 416 | 414
2017-03-12 04:00 | 415 | 413
2017-03-12 04:30 | 418 | 416
2017-03-12 05:00 | 420 | 418
2017-03-12 05:30 | 419 | 417
2017-03-12 06:00 | 419 | 417
2017-03-12 06:30 | 421 | 419
2017-03-12 07:00 | 427 | 425
2017-03-12 07:30 | 440 | 438
2017-03-12 08:00 | 452 | 450
2017-03-12 08:30 | 468 | 466
2017-03-12 09:00 | 474 | 473
2017-03-12 09:30 | 494 | 493
2017-03-12 10:00 | 503 | 502
2017-03-12 10:30 | 512 | 511
2017-03-12 11:00 | 516 | 515
2017-03-12 11:30 | 516 | 515
2017-03-12 12:00 | 521 | 520
2017-03-12 12:30 | 510 | 510
2017-03-12 13:00 | 510 | 509
2017-03-12 13:30 | 517 | 516
2017-03-12 14:00 | 516 | 515
2017-03-12 14:30 | 519 | 519
2017-03-12 15:00 | 533 | 533
2017-03-12 15:30 | 542 | 541
2017-03-12 16:00 | 566 | 566
2017-03-12 16:30 | 567 | 567
2017-03-12 17:00 | 592 | 592
2017-03-12 17:30 | 604 | 604
2017-03-12 18:00 | 617 | 617
2017-03-12 18:30 | 635 | 635
2017-03-12 19:00 | 649 | 649
2017-03-12 19:30 | 679 | 679
2017-03-12 20:00 | 688 | 688
2017-03-12 20:30 | 669 | 669
2017-03-12 21:00 | 651 | 651
2017-03-12 21:30 | 624 | 624
2017-03-12 22:00 | 591 | 591
2017-03-12 22:30 | 562 | 562
2017-03-12 23:00 | 553 | 552
2017-03-12 23:30 | 528 | 527
2017-03-13 | 506 | 505
2017-03-13 00:30 | 493 | 492
2017-03-13 01:00 | 485 | 484
2017-03-13 01:30 | 468 | 467
2017-03-13 02:00 | 467 | 466
2017-03-13 02:30 | 480 | 479
2017-03-13 03:00 | 462 | 460
2017-03-13 03:30 | 449 | 447
2017-03-13 04:00 | 451 | 450
2017-03-13 04:30 | 439 | 438
2017-03-13 05:00 | 400 | 398
2017-03-13 05:30 | 411 | 408
2017-03-13 06:00 | 427 | 424
2017-03-13 06:30 | 455 | 453
2017-03-13 07:00 | 489 | 487
2017-03-13 07:30 | 524 | 523
2017-03-13 08:00 | 539 | 539
2017-03-13 08:30 | 548 | 548
2017-03-13 09:00 | 551 | 551
2017-03-13 09:30 | 473 | 473
2017-03-13 10:00 | 477 | 476
2017-03-13 10:30 | 481 | 481
2017-03-13 11:00 | 487 | 487
2017-03-13 11:30 | 488 | 487
2017-03-13 12:00 | 507 | 507
2017-03-13 12:30 | 541 | 541
2017-03-13 13:00 | 553 | 553
2017-03-13 13:30 | 537 | 536
2017-03-13 14:00 | 534 | 534
2017-03-13 14:30 | 549 | 549
2017-03-13 15:00 | 564 | 564
2017-03-13 15:30 | 570 | 570
2017-03-13 16:00 | 570 | 570
2017-03-13 16:30 | 558 | 558
2017-03-13 17:00 | 562 | 562
2017-03-13 17:30 | 557 | 557
2017-03-13 18:00 | 565 | 565
2017-03-13 18:30 | 596 | 596
2017-03-13 19:00 | 641 | 641
2017-03-13 19:30 | 656 | 656
2017-03-13 20:00 | 643 | 643
2017-03-13 20:30 | 616 | 616
2017-03-13 21:00 | 595 | 595
2017-03-13 21:30 | 564 | 564
2017-03-13 22:00 | 534 | 534
2017-03-13 22:30 | 495 | 494
2017-03-13 23:00 | 463 | 462
2017-03-13 23:30 | 434 | 433
2017-03-14 | 411 | 409
2017-03-14 00:30 | 407 | 404
2017-03-14 01:00 | 396 | 394
2017-03-14 01:30 | 390 | 387
2017-03-14 02:00 | 375 | 372
2017-03-14 02:30 | 389 | 386
2017-03-14 03:00 | 429 | 427
2017-03-14 03:30 | 417 | 415
2017-03-14 04:00 | 397 | 396
2017-03-14 04:30 | 373 | 371
2017-03-14 05:00 | 376 | 373
2017-03-14 05:30 | 384 | 381
2017-03-14 06:00 | 391 | 389
2017-03-14 06:30 | 405 | 403
2017-03-14 07:00 | 427 | 425
2017-03-14 07:30 | 466 | 464
2017-03-14 08:00 | 488 | 487
2017-03-14 08:30 | 501 | 500
2017-03-14 09:00 | 526 | 525
2017-03-14 09:30 | 538 | 537
2017-03-14 10:00 | 528 | 528
2017-03-14 10:30 | 531 | 531
2017-03-14 11:00 | 536 | 535
2017-03-14 11:30 | 536 | 536
2017-03-14 12:00 | 548 | 548
2017-03-14 12:30 | 558 | 557
2017-03-14 13:00 | 565 | 565
2017-03-14 13:30 | 547 | 547
2017-03-14 14:00 | 551 | 551
2017-03-14 14:30 | 551 | 551
2017-03-14 15:00 | 584 | 584
2017-03-14 15:30 | 601 | 601
2017-03-14 16:00 | 609 | 609
2017-03-14 16:30 | 614 | 614
2017-03-14 17:00 | 607 | 607
2017-03-14 17:30 | 578 | 578
2017-03-14 18:00 | 575 | 575
2017-03-14 18:30 | 583 | 583
2017-03-14 19:00 | 621 | 621
2017-03-14 19:30 | 656 | 656
2017-03-14 20:00 | 653 | 653
2017-03-14 20:30 | 633 | 633
2017-03-14 21:00 | 609 | 609
2017-03-14 21:30 | 581 | 581
2017-03-14 22:00 | 547 | 547
2017-03-14 22:30 | 504 | 503
2017-03-14 23:00 | 475 | 474
2017-03-14 23:30 | 445 | 444
2017-03-15 | 422 | 420
2017-03-15 00:30 | 515 | 513
2017-03-15 01:00 | 532 | 532
2017-03-15 01:30 | 520 | 519
2017-03-15 02:00 | 510 | 509
2017-03-15 02:30 | 509 | 508
2017-03-15 03:00 | 503 | 502
2017-03-15 03:30 | 510 | 509
2017-03-15 04:00 | 515 | 514
2017-03-15 04:30 | 519 | 518
2017-03-15 05:00 | 524 | 523
2017-03-15 05:30 | 535 | 534
2017-03-15 06:00 | 533 | 532
2017-03-15 06:30 | 552 | 551
2017-03-15 07:00 | 493 | 492
2017-03-15 07:30 | 478 | 477
2017-03-15 08:00 | 498 | 497
2017-03-15 08:30 | 508 | 507
2017-03-15 09:00 | 512 | 512
2017-03-15 09:30 | 510 | 509
2017-03-15 10:00 | 520 | 519
2017-03-15 10:30 | 526 | 525
2017-03-15 11:00 | 526 | 525
2017-03-15 11:30 | 511 | 511
2017-03-15 12:00 | 520 | 519
2017-03-15 12:30 | 528 | 528
2017-03-15 13:00 | 533 | 532
2017-03-15 13:30 | 542 | 542
2017-03-15 14:00 | 549 | 549
2017-03-15 14:30 | 567 | 567
2017-03-15 15:00 | 558 | 558
2017-03-15 15:30 | 568 | 568
2017-03-15 16:00 | 589 | 589
2017-03-15 16:30 | 559 | 559
2017-03-15 17:00 | 536 | 536
2017-03-15 17:30 | 538 | 538
2017-03-15 18:00 | 546 | 546
2017-03-15 18:30 | 578 | 578
2017-03-15 19:00 | 597 | 597
2017-03-15 19:30 | 607 | 607
2017-03-15 20:00 | 589 | 589
2017-03-15 20:30 | 537 | 537
2017-03-15 21:00 | 506 | 506
2017-03-15 21:30 | 475 | 474
2017-03-15 22:00 | 431 | 430
2017-03-15 22:30 | 397 | 394
2017-03-15 23:00 | 371 | 367
2017-03-15 23:30 | 347 | 343
2017-03-16 | 325 | 319
2017-03-16 00:30 | 420 | 414
2017-03-16 01:00 | 429 | 426
2017-03-16 01:30 | 420 | 417
2017-03-16 02:00 | 429 | 426
2017-03-16 02:30 | 441 | 438
2017-03-16 03:00 | 438 | 435
2017-03-16 03:30 | 436 | 433
2017-03-16 04:00 | 433 | 430
2017-03-16 04:30 | 433 | 430
2017-03-16 05:00 | 434 | 431
2017-03-16 05:30 | 468 | 465
2017-03-16 06:00 | 491 | 489
2017-03-16 06:30 | 528 | 527
2017-03-16 07:00 | 499 | 498
2017-03-16 07:30 | 450 | 449
2017-03-16 08:00 | 461 | 459
2017-03-16 08:30 | 479 | 477
2017-03-16 09:00 | 493 | 491
2017-03-16 09:30 | 497 | 496
2017-03-16 10:00 | 505 | 504
2017-03-16 10:30 | 510 | 509
2017-03-16 11:00 | 530 | 529
2017-03-16 11:30 | 553 | 552
2017-03-16 12:00 | 560 | 559
2017-03-16 12:30 | 562 | 561
2017-03-16 13:00 | 550 | 550
2017-03-16 13:30 | 535 | 534
2017-03-16 14:00 | 541 | 541
2017-03-16 14:30 | 551 | 551
2017-03-16 15:00 | 563 | 563
2017-03-16 15:30 | 507 | 507
2017-03-16 16:00 | 545 | 544
2017-03-16 16:30 | 546 | 546
2017-03-16 17:00 | 514 | 514
2017-03-16 17:30 | 514 | 514
2017-03-16 18:00 | 510 | 509
2017-03-16 18:30 | 529 | 529
2017-03-16 19:00 | 562 | 561
2017-03-16 19:30 | 619 | 619
2017-03-16 20:00 | 646 | 646
2017-03-16 20:30 | 631 | 631
2017-03-16 21:00 | 609 | 609
2017-03-16 21:30 | 567 | 567
2017-03-16 22:00 | 535 | 535
2017-03-16 22:30 | 507 | 506
2017-03-16 23:00 | 474 | 473
2017-03-16 23:30 | 447 | 445
2017-03-17 | 425 | 423
2017-03-17 00:30 | 514 | 512
2017-03-17 01:00 | 533 | 532
2017-03-17 01:30 | 524 | 523
2017-03-17 02:00 | 517 | 517
2017-03-17 02:30 | 508 | 507
2017-03-17 03:00 | 500 | 499
2017-03-17 03:30 | 499 | 498
2017-03-17 04:00 | 495 | 494
2017-03-17 04:30 | 493 | 492
2017-03-17 05:00 | 496 | 495
2017-03-17 05:30 | 510 | 509
2017-03-17 06:00 | 443 | 442
2017-03-17 06:30 | 407 | 405
2017-03-17 07:00 | 429 | 427
2017-03-17 07:30 | 471 | 469
2017-03-17 08:00 | 491 | 490
2017-03-17 08:30 | 510 | 509
2017-03-17 09:00 | 521 | 520
2017-03-17 09:30 | 532 | 532
2017-03-17 10:00 | 538 | 538
2017-03-17 10:30 | 543 | 543
2017-03-17 11:00 | 544 | 544
2017-03-17 11:30 | 549 | 548
2017-03-17 12:00 | 556 | 556
2017-03-17 12:30 | 543 | 543
2017-03-17 13:00 | 543 | 543
2017-03-17 13:30 | 552 | 551
2017-03-17 14:00 | 561 | 561
2017-03-17 14:30 | 576 | 576
2017-03-17 15:00 | 588 | 588
2017-03-17 15:30 | 601 | 601
2017-03-17 16:00 | 621 | 621
2017-03-17 16:30 | 635 | 635
2017-03-17 17:00 | 647 | 647
2017-03-17 17:30 | 641 | 641
2017-03-17 18:00 | 629 | 629
2017-03-17 18:30 | 624 | 624
2017-03-17 19:00 | 638 | 638
2017-03-17 19:30 | 669 | 669
2017-03-17 20:00 | 662 | 662
2017-03-17 20:30 | 643 | 643
2017-03-17 21:00 | 621 | 621
2017-03-17 21:30 | 598 | 598
2017-03-17 22:00 | 574 | 574
2017-03-17 22:30 | 544 | 544
2017-03-17 23:00 | 528 | 528
2017-03-17 23:30 | 502 | 501
2017-03-18 | 477 | 476
2017-03-18 00:30 | 568 | 566
2017-03-18 01:00 | 586 | 586
2017-03-18 01:30 | 577 | 577
2017-03-18 02:00 | 563 | 563
2017-03-18 02:30 | 558 | 558
2017-03-18 03:00 | 552 | 551
2017-03-18 03:30 | 543 | 543
2017-03-18 04:00 | 538 | 537
2017-03-18 04:30 | 532 | 532
2017-03-18 05:00 | 529 | 528
2017-03-18 05:30 | 524 | 523
2017-03-18 06:00 | 529 | 528
2017-03-18 06:30 | 538 | 537
2017-03-18 07:00 | 552 | 551
2017-03-18 07:30 | 576 | 576
2017-03-18 08:00 | 599 | 598
2017-03-18 08:30 | 615 | 615
2017-03-18 09:00 | 624 | 624
2017-03-18 09:30 | 539 | 539
2017-03-18 10:00 | 499 | 499
2017-03-18 10:30 | 512 | 511
2017-03-18 11:00 | 518 | 518
2017-03-18 11:30 | 535 | 535
2017-03-18 12:00 | 544 | 544
2017-03-18 12:30 | 538 | 537
2017-03-18 13:00 | 526 | 526
2017-03-18 13:30 | 497 | 496
2017-03-18 14:00 | 482 | 482
2017-03-18 14:30 | 488 | 487
2017-03-18 15:00 | 504 | 504
2017-03-18 15:30 | 529 | 529
2017-03-18 16:00 | 550 | 549
2017-03-18 16:30 | 541 | 541
2017-03-18 17:00 | 525 | 525
2017-03-18 17:30 | 542 | 542
2017-03-18 18:00 | 545 | 545
2017-03-18 18:30 | 555 | 554
2017-03-18 19:00 | 568 | 567
2017-03-18 19:30 | 570 | 570
2017-03-18 20:00 | 555 | 555
2017-03-18 20:30 | 555 | 555
2017-03-18 21:00 | 570 | 570
2017-03-18 21:30 | 553 | 553
2017-03-18 22:00 | 534 | 533
2017-03-18 22:30 | 615 | 614
2017-03-18 23:00 | 621 | 621
2017-03-18 23:30 | 600 | 600
2017-03-19 | 581 | 580
2017-03-19 00:30 | 566 | 566
2017-03-19 01:00 | 553 | 552
2017-03-19 01:30 | 537 | 536
2017-03-19 02:00 | 524 | 523
2017-03-19 02:30 | 521 | 519
2017-03-19 03:00 | 509 | 507
2017-03-19 03:30 | 501 | 499
2017-03-19 04:00 | 496 | 495
2017-03-19 04:30 | 490 | 488
2017-03-19 05:00 | 484 | 483
2017-03-19 05:30 | 489 | 487
2017-03-19 06:00 | 493 | 491
2017-03-19 06:30 | 492 | 491
2017-03-19 07:00 | 498 | 497
2017-03-19 07:30 | 514 | 512
2017-03-19 08:00 | 522 | 521
2017-03-19 08:30 | 543 | 542
2017-03-19 09:00 | 552 | 551
2017-03-19 09:30 | 551 | 551
2017-03-19 10:00 | 511 | 510
2017-03-19 10:30 | 546 | 545
2017-03-19 11:00 | 582 | 582
2017-03-19 11:30 | 589 | 588
2017-03-19 12:00 | 591 | 591
2017-03-19 12:30 | 608 | 608
2017-03-19 13:00 | 622 | 622
2017-03-19 13:30 | 617 | 617
2017-03-19 14:00 | 609 | 609
2017-03-19 14:30 | 619 | 619
2017-03-19 15:00 | 622 | 622
2017-03-19 15:30 | 587 | 587
2017-03-19 16:00 | 567 | 566
2017-03-19 16:30 | 613 | 612
2017-03-19 17:00 | 544 | 544
2017-03-19 17:30 | 540 | 540
2017-03-19 18:00 | 572 | 572
2017-03-19 18:30 | 587 | 587
2017-03-19 19:00 | 596 | 596
2017-03-19 19:30 | 637 | 637
2017-03-19 20:00 | 634 | 634
2017-03-19 20:30 | 618 | 618
2017-03-19 21:00 | 639 | 639
2017-03-19 21:30 | 626 | 626
2017-03-19 22:00 | 603 | 603
2017-03-19 22:30 | 578 | 578
2017-03-19 23:00 | 550 | 550
2017-03-19 23:30 | 531 | 530
2017-03-20 | 516 | 515
2017-03-20 00:30 | 503 | 501
2017-03-20 01:00 | 492 | 491
2017-03-20 01:30 | 482 | 480
2017-03-20 02:00 | 477 | 475
2017-03-20 02:30 | 471 | 468
2017-03-20 03:00 | 459 | 456
2017-03-20 03:30 | 458 | 455
2017-03-20 04:00 | 453 | 450
2017-03-20 04:30 | 452 | 450
2017-03-20 05:00 | 462 | 459
2017-03-20 05:30 | 480 | 478
2017-03-20 06:00 | 418 | 416
2017-03-20 06:30 | 374 | 370
2017-03-20 07:00 | 345 | 339
2017-03-20 07:30 | 412 | 406
2017-03-20 08:00 | 448 | 444
2017-03-20 08:30 | 406 | 403
2017-03-20 09:00 | 388 | 384
2017-03-20 09:30 | 398 | 394
2017-03-20 10:00 | 406 | 401
2017-03-20 10:30 | 399 | 395
2017-03-20 11:00 | 405 | 401
2017-03-20 11:30 | 411 | 407
2017-03-20 12:00 | 426 | 422
2017-03-20 12:30 | 435 | 432
2017-03-20 13:00 | 438 | 435
2017-03-20 13:30 | 431 | 428
2017-03-20 14:00 | 420 | 417
2017-03-20 14:30 | 435 | 431
2017-03-20 15:00 | 425 | 422
2017-03-20 15:30 | 409 | 405
2017-03-20 16:00 | 419 | 414
2017-03-20 16:30 | 435 | 431
2017-03-20 17:00 | 433 | 430
2017-03-20 17:30 | 442 | 438
2017-03-20 18:00 | 447 | 444
2017-03-20 18:30 | 468 | 465
2017-03-20 19:00 | 470 | 468
2017-03-20 19:30 | 488 | 486
2017-03-20 20:00 | 483 | 481
2017-03-20 20:30 | 459 | 457
2017-03-20 21:00 | 434 | 431
2017-03-20 21:30 | 410 | 406
2017-03-20 22:00 | 391 | 386
2017-03-20 22:30 | 359 | 352
2017-03-20 23:00 | 332 | 325
2017-03-20 23:30 | 316 | 307
2017-03-21 | 299 | 290
2017-03-21 00:30 | 404 | 396
2017-03-21 01:00 | 415 | 411
2017-03-21 01:30 | 405 | 401
2017-03-21 02:00 | 397 | 393
2017-03-21 02:30 | 393 | 389
2017-03-21 03:00 | 393 | 389
2017-03-21 03:30 | 387 | 383
2017-03-21 04:00 | 386 | 381
2017-03-21 04:30 | 409 | 405
2017-03-21 05:00 | 413 | 409
2017-03-21 05:30 | 442 | 438
2017-03-21 06:00 | 398 | 394
2017-03-21 06:30 | 366 | 361
2017-03-21 07:00 | 393 | 388
2017-03-21 07:30 | 388 | 383
2017-03-21 08:00 | 408 | 403
2017-03-21 08:30 | 412 | 408
2017-03-21 09:00 | 407 | 403
2017-03-21 09:30 | 419 | 415
2017-03-21 10:00 | 423 | 419
2017-03-21 10:30 | 428 | 424
2017-03-21 11:00 | 445 | 441
2017-03-21 11:30 | 459 | 455
2017-03-21 12:00 | 459 | 456
2017-03-21 12:30 | 456 | 453
2017-03-21 13:00 | 470 | 467
2017-03-21 13:30 | 468 | 466
2017-03-21 14:00 | 474 | 471
2017-03-21 14:30 | 491 | 489
2017-03-21 15:00 | 500 | 499
2017-03-21 15:30 | 508 | 506
2017-03-21 16:00 | 512 | 511
2017-03-21 16:30 | 524 | 522
2017-03-21 17:00 | 505 | 503
2017-03-21 17:30 | 493 | 491
2017-03-21 18:00 | 495 | 493
2017-03-21 18:30 | 506 | 504
2017-03-21 19:00 | 525 | 524
2017-03-21 19:30 | 518 | 517
2017-03-21 20:00 | 523 | 521
2017-03-21 20:30 | 503 | 501
2017-03-21 21:00 | 474 | 472
2017-03-21 21:30 | 563 | 561
2017-03-21 22:00 | 565 | 565
2017-03-21 22:30 | 558 | 557
2017-03-21 23:00 | 537 | 537
2017-03-21 23:30 | 512 | 511
2017-03-22 | 492 | 490
2017-03-22 00:30 | 483 | 481
2017-03-22 01:00 | 473 | 471
2017-03-22 01:30 | 459 | 457
2017-03-22 02:00 | 455 | 452
2017-03-22 02:30 | 452 | 449
2017-03-22 03:00 | 448 | 445
2017-03-22 03:30 | 445 | 442
2017-03-22 04:00 | 444 | 441
2017-03-22 04:30 | 445 | 442
2017-03-22 05:00 | 447 | 444
2017-03-22 05:30 | 461 | 458
2017-03-22 06:00 | 480 | 478
2017-03-22 06:30 | 511 | 509
2017-03-22 07:00 | 536 | 535
2017-03-22 07:30 | 539 | 538
2017-03-22 08:00 | 533 | 532
2017-03-22 08:30 | 534 | 533
2017-03-22 09:00 | 539 | 538
2017-03-22 09:30 | 478 | 477
2017-03-22 10:00 | 399 | 397
2017-03-22 10:30 | 408 | 404
2017-03-22 11:00 | 418 | 414
2017-03-22 11:30 | 425 | 420
2017-03-22 12:00 | 442 | 438
2017-03-22 12:30 | 450 | 446
2017-03-22 13:00 | 450 | 447
2017-03-22 13:30 | 466 | 463
2017-03-22 14:00 | 477 | 476
2017-03-22 14:30 | 489 | 488
2017-03-22 15:00 | 496 | 495
2017-03-22 15:30 | 499 | 498
2017-03-22 16:00 | 506 | 505
2017-03-22 16:30 | 524 | 524
2017-03-22 17:00 | 529 | 529
2017-03-22 17:30 | 524 | 524
2017-03-22 18:00 | 523 | 523
2017-03-22 18:30 | 520 | 520
2017-03-22 19:00 | 535 | 535
2017-03-22 19:30 | 529 | 529
2017-03-22 20:00 | 512 | 512
2017-03-22 20:30 | 494 | 494
2017-03-22 21:00 | 480 | 479
2017-03-22 21:30 | 462 | 461
2017-03-22 22:00 | 441 | 440
2017-03-22 22:30 | 398 | 397
2017-03-22 23:00 | 472 | 470
2017-03-22 23:30 | 493 | 492
2017-03-23 | 472 | 471
2017-03-23 00:30 | 458 | 457
2017-03-23 01:00 | 444 | 443
2017-03-23 01:30 | 434 | 432
2017-03-23 02:00 | 425 | 424
2017-03-23 02:30 | 417 | 416
2017-03-23 03:00 | 415 | 413
2017-03-23 03:30 | 414 | 413
2017-03-23 04:00 | 414 | 413
2017-03-23 04:30 | 416 | 414
2017-03-23 05:00 | 427 | 426
2017-03-23 05:30 | 430 | 429
2017-03-23 06:00 | 446 | 445
2017-03-23 06:30 | 478 | 477
2017-03-23 07:00 | 502 | 501
2017-03-23 07:30 | 531 | 530
2017-03-23 08:00 | 526 | 525
2017-03-23 08:30 | 539 | 539
2017-03-23 09:00 | 543 | 543
2017-03-23 09:30 | 479 | 478
2017-03-23 10:00 | 412 | 410
2017-03-23 10:30 | 405 | 403
2017-03-23 11:00 | 402 | 400
2017-03-23 11:30 | 408 | 406
2017-03-23 12:00 | 414 | 412
2017-03-23 12:30 | 429 | 427
2017-03-23 13:00 | 431 | 429
2017-03-23 13:30 | 429 | 427
2017-03-23 14:00 | 453 | 451
2017-03-23 14:30 | 472 | 471
2017-03-23 15:00 | 480 | 479
2017-03-23 15:30 | 481 | 480
2017-03-23 16:00 | 483 | 482
2017-03-23 16:30 | 481 | 480
2017-03-23 17:00 | 490 | 489
2017-03-23 17:30 | 493 | 492
2017-03-23 18:00 | 499 | 498
2017-03-23 18:30 | 511 | 511
2017-03-23 19:00 | 537 | 537
2017-03-23 19:30 | 537 | 536
2017-03-23 20:00 | 517 | 516
2017-03-23 20:30 | 500 | 499
2017-03-23 21:00 | 472 | 471
2017-03-23 21:30 | 441 | 439
2017-03-23 22:00 | 429 | 428
2017-03-23 22:30 | 398 | 396
2017-03-23 23:00 | 477 | 475
2017-03-23 23:30 | 478 | 477
2017-03-24 | 458 | 456
2017-03-24 00:30 | 467 | 466
2017-03-24 01:00 | 461 | 460
2017-03-24 01:30 | 452 | 451
2017-03-24 02:00 | 450 | 448
2017-03-24 02:30 | 445 | 443
2017-03-24 03:00 | 441 | 439
2017-03-24 03:30 | 437 | 435
2017-03-24 04:00 | 438 | 436
2017-03-24 04:30 | 407 | 405
2017-03-24 05:00 | 385 | 383
2017-03-24 05:30 | 396 | 392
2017-03-24 06:00 | 413 | 410
2017-03-24 06:30 | 437 | 435
2017-03-24 07:00 | 377 | 375
2017-03-24 07:30 | 365 | 361
2017-03-24 08:00 | 385 | 382
2017-03-24 08:30 | 394 | 391
2017-03-24 09:00 | 397 | 394
2017-03-24 09:30 | 406 | 404
2017-03-24 10:00 | 399 | 396
2017-03-24 10:30 | 401 | 398
2017-03-24 11:00 | 406 | 404
2017-03-24 11:30 | 412 | 409
2017-03-24 12:00 | 410 | 408
2017-03-24 12:30 | 411 | 409
2017-03-24 13:00 | 412 | 410
2017-03-24 13:30 | 414 | 412
2017-03-24 14:00 | 412 | 410
2017-03-24 14:30 | 417 | 414
2017-03-24 15:00 | 427 | 424
2017-03-24 15:30 | 425 | 423
2017-03-24 16:00 | 435 | 433
2017-03-24 16:30 | 431 | 429
2017-03-24 17:00 | 434 | 432
2017-03-24 17:30 | 427 | 425
2017-03-24 18:00 | 433 | 431
2017-03-24 18:30 | 440 | 438
2017-03-24 19:00 | 455 | 454
2017-03-24 19:30 | 448 | 446
2017-03-24 20:00 | 426 | 425
2017-03-24 20:30 | 397 | 395
2017-03-24 21:00 | 377 | 374
2017-03-24 21:30 | 475 | 473
2017-03-24 22:00 | 489 | 488
2017-03-24 22:30 | 468 | 468
2017-03-24 23:00 | 455 | 454
2017-03-24 23:30 | 440 | 439
2017-03-25 | 426 | 424
2017-03-25 00:30 | 407 | 405
2017-03-25 01:00 | 386 | 384
2017-03-25 01:30 | 382 | 379
2017-03-25 02:00 | 377 | 374
2017-03-25 02:30 | 374 | 371
2017-03-25 03:00 | 372 | 369
2017-03-25 03:30 | 371 | 368
2017-03-25 04:00 | 367 | 363
2017-03-25 04:30 | 366 | 362
2017-03-25 05:00 | 362 | 358
2017-03-25 05:30 | 369 | 365
2017-03-25 06:00 | 378 | 375
2017-03-25 06:30 | 421 | 418
2017-03-25 07:00 | 430 | 428
2017-03-25 07:30 | 450 | 448
2017-03-25 08:00 | 468 | 467
2017-03-25 08:30 | 484 | 483
2017-03-25 09:00 | 495 | 494
2017-03-25 09:30 | 499 | 498
2017-03-25 10:00 | 496 | 495
2017-03-25 10:30 | 502 | 501
2017-03-25 11:00 | 508 | 507
2017-03-25 11:30 | 426 | 426
2017-03-25 12:00 | 387 | 385
2017-03-25 12:30 | 392 | 390
2017-03-25 13:00 | 407 | 405
2017-03-25 13:30 | 416 | 414
2017-03-25 14:00 | 427 | 424
2017-03-25 14:30 | 436 | 434
2017-03-25 15:00 | 451 | 449
2017-03-25 15:30 | 461 | 460
2017-03-25 16:00 | 478 | 477
2017-03-25 16:30 | 490 | 489
2017-03-25 17:00 | 500 | 499
2017-03-25 17:30 | 500 | 499
2017-03-25 18:00 | 495 | 494
2017-03-25 18:30 | 490 | 490
2017-03-25 19:00 | 512 | 512
2017-03-25 19:30 | 623 | 622
2017-03-25 20:00 | 627 | 627
2017-03-25 20:30 | 607 | 607
2017-03-25 21:00 | 602 | 602
2017-03-25 21:30 | 586 | 586
2017-03-25 22:00 | 563 | 563
2017-03-25 22:30 | 538 | 538
2017-03-25 23:00 | 509 | 509
2017-03-25 23:30 | 489 | 488
2017-03-26 | 474 | 473
2017-03-26 00:30 | 475 | 473
2017-03-26 01:00 | 460 | 458
2017-03-26 01:30 | 448 | 446
2017-03-26 02:00 | 439 | 437
2017-03-26 02:30 | 431 | 429
2017-03-26 03:00 | 426 | 425
2017-03-26 03:30 | 423 | 421
2017-03-26 04:00 | 421 | 419
2017-03-26 04:30 | 421 | 418
2017-03-26 05:00 | 420 | 417
2017-03-26 05:30 | 415 | 413
2017-03-26 06:00 | 392 | 389
2017-03-26 06:30 | 395 | 392
2017-03-26 07:00 | 397 | 394
2017-03-26 07:30 | 410 | 407
2017-03-26 08:00 | 433 | 430
2017-03-26 08:30 | 446 | 444
2017-03-26 09:00 | 455 | 454
2017-03-26 09:30 | 467 | 465
2017-03-26 10:00 | 470 | 468
2017-03-26 10:30 | 479 | 478
2017-03-26 11:00 | 498 | 497
2017-03-26 11:30 | 504 | 503
2017-03-26 12:00 | 503 | 502
2017-03-26 12:30 | 513 | 513
2017-03-26 13:00 | 540 | 540
2017-03-26 13:30 | 543 | 543
2017-03-26 14:00 | 552 | 552
2017-03-26 14:30 | 555 | 555
2017-03-26 15:00 | 571 | 571
2017-03-26 15:30 | 588 | 588
2017-03-26 16:00 | 562 | 562
2017-03-26 16:30 | 559 | 559
2017-03-26 17:00 | 540 | 540
2017-03-26 17:30 | 504 | 503
2017-03-26 18:00 | 431 | 430
2017-03-26 18:30 | 449 | 446
2017-03-26 19:00 | 458 | 456
2017-03-26 19:30 | 478 | 476
2017-03-26 20:00 | 464 | 462
2017-03-26 20:30 | 473 | 471
2017-03-26 21:00 | 458 | 456
2017-03-26 21:30 | 433 | 431
2017-03-26 22:00 | 406 | 403
2017-03-26 22:30 | 399 | 395
2017-03-26 23:00 | 378 | 373
2017-03-26 23:30 | 352 | 347
2017-03-27 | 337 | 330
2017-03-27 00:30 | 336 | 329
2017-03-27 01:00 | 318 | 310
2017-03-27 01:30 | 310 | 301
2017-03-27 02:00 | 303 | 294
2017-03-27 02:30 | 297 | 287
2017-03-27 03:00 | 295 | 285
2017-03-27 03:30 | 293 | 282
2017-03-27 04:00 | 290 | 279
2017-03-27 04:30 | 282 | 271
2017-03-27 05:00 | 287 | 276
2017-03-27 05:30 | 298 | 288
2017-03-27 06:00 | 311 | 301
2017-03-27 06:30 | 337 | 329
2017-03-27 07:00 | 355 | 348
2017-03-27 07:30 | 372 | 367
2017-03-27 08:00 | 384 | 379
2017-03-27 08:30 | 383 | 378
2017-03-27 09:00 | 382 | 378
2017-03-27 09:30 | 398 | 393
2017-03-27 10:00 | 404 | 400
2017-03-27 10:30 | 400 | 397
2017-03-27 11:00 | 399 | 395
2017-03-27 11:30 | 409 | 405
2017-03-27 12:00 | 411 | 407
2017-03-27 12:30 | 396 | 393
2017-03-27 13:00 | 409 | 405
2017-03-27 13:30 | 388 | 384
2017-03-27 14:00 | 397 | 393
2017-03-27 14:30 | 401 | 397
2017-03-27 15:00 | 410 | 406
2017-03-27 15:30 | 412 | 408
2017-03-27 16:00 | 419 | 416
2017-03-27 16:30 | 420 | 417
2017-03-27 17:00 | 422 | 418
2017-03-27 17:30 | 426 | 423
2017-03-27 18:00 | 432 | 429
2017-03-27 18:30 | 439 | 436
2017-03-27 19:00 | 455 | 452
2017-03-27 19:30 | 446 | 443
2017-03-27 20:00 | 430 | 427
2017-03-27 20:30 | 413 | 410
2017-03-27 21:00 | 395 | 391
2017-03-27 21:30 | 359 | 354
2017-03-27 22:00 | 327 | 321
2017-03-27 22:30 | 295 | 287
2017-03-27 23:00 | 269 | 259
2017-03-27 23:30 | 249 | 237
2017-03-28 | 228 | 213
2017-03-28 00:30 | 222 | 200
2017-03-28 01:00 | 311 | 293
2017-03-28 01:30 | 327 | 314
2017-03-28 02:00 | 315 | 304
2017-03-28 02:30 | 313 | 301
2017-03-28 03:00 | 310 | 298
2017-03-28 03:30 | 306 | 294
2017-03-28 04:00 | 299 | 286
2017-03-28 04:30 | 299 | 285
2017-03-28 05:00 | 298 | 285
2017-03-28 05:30 | 306 | 291
2017-03-28 06:00 | 315 | 302
2017-03-28 06:30 | 335 | 324
2017-03-28 07:00 | 356 | 345
2017-03-28 07:30 | 379 | 370
2017-03-28 08:00 | 401 | 394
2017-03-28 08:30 | 415 | 408
2017-03-28 09:00 | 422 | 416
2017-03-28 09:30 | 424 | 418
2017-03-28 10:00 | 421 | 415
2017-03-28 10:30 | 424 | 418
2017-03-28 11:00 | 427 | 421
2017-03-28 11:30 | 428 | 421
2017-03-28 12:00 | 431 | 425
2017-03-28 12:30 | 343 | 334
2017-03-28 13:00 | 300 | 287
2017-03-28 13:30 | 307 | 292
2017-03-28 14:00 | 316 | 302
2017-03-28 14:30 | 321 | 307
2017-03-28 15:00 | 299 | 284
2017-03-28 15:30 | 292 | 276
2017-03-28 16:00 | 293 | 274
2017-03-28 16:30 | 272 | 247
2017-03-28 17:00 | 262 | 233
2017-03-28 17:30 | 267 | 238
2017-03-28 18:00 | 277 | 250
2017-03-28 18:30 | 289 | 263
2017-03-28 19:00 | 292 | 267
2017-03-28 19:30 | 288 | 263
2017-03-28 20:00 | 273 | 246
2017-03-28 20:30 | 278 | 251
2017-03-28 21:00 | 273 | 245
2017-03-28 21:30 | 274 | 245
2017-03-28 22:00 | 275 | 246
2017-03-28 22:30 | 271 | 243
2017-03-28 23:00 | 261 | 230
2017-03-28 23:30 | 277 | 252
2017-03-29 | 280 | 254
2017-03-29 00:30 | 272 | 245
2017-03-29 01:00 | 268 | 240
2017-03-29 01:30 | 273 | 245
2017-03-29 02:00 | 274 | 246
2017-03-29 02:30 | 269 | 241
2017-03-29 03:00 | 271 | 244
2017-03-29 03:30 | 272 | 244
2017-03-29 04:00 | 273 | 245
2017-03-29 04:30 | 315 | 291
2017-03-29 05:00 | 332 | 313
2017-03-29 05:30 | 338 | 321
2017-03-29 06:00 | 353 | 336
2017-03-29 06:30 | 385 | 370
2017-03-29 07:00 | 411 | 399
2017-03-29 07:30 | 441 | 430
2017-03-29 08:00 | 469 | 460
2017-03-29 08:30 | 482 | 475
2017-03-29 09:00 | 495 | 489
2017-03-29 09:30 | 506 | 500
2017-03-29 10:00 | 496 | 490
2017-03-29 10:30 | 447 | 440
2017-03-29 11:00 | 453 | 444
2017-03-29 11:30 | 456 | 448
2017-03-29 12:00 | 459 | 451
2017-03-29 12:30 | 479 | 471
2017-03-29 13:00 | 494 | 486
2017-03-29 13:30 | 483 | 476
2017-03-29 14:00 | 453 | 445
2017-03-29 14:30 | 468 | 460
2017-03-29 15:00 | 489 | 481
2017-03-29 15:30 | 485 | 478
2017-03-29 16:00 | 499 | 492
2017-03-29 16:30 | 495 | 489
2017-03-29 17:00 | 483 | 477
2017-03-29 17:30 | 493 | 487
2017-03-29 18:00 | 474 | 469
2017-03-29 18:30 | 473 | 468
2017-03-29 19:00 | 507 | 502
2017-03-29 19:30 | 569 | 565
2017-03-29 20:00 | 566 | 563
2017-03-29 20:30 | 554 | 551
2017-03-29 21:00 | 538 | 535
2017-03-29 21:30 | 515 | 512
2017-03-29 22:00 | 496 | 492
2017-03-29 22:30 | 582 | 578
2017-03-29 23:00 | 572 | 570
2017-03-29 23:30 | 546 | 544
2017-03-30 | 528 | 525
2017-03-30 00:30 | 507 | 503
2017-03-30 01:00 | 496 | 491
2017-03-30 01:30 | 481 | 476
2017-03-30 02:00 | 470 | 465
2017-03-30 02:30 | 464 | 459
2017-03-30 03:00 | 457 | 451
2017-03-30 03:30 | 454 | 448
2017-03-30 04:00 | 451 | 445
2017-03-30 04:30 | 437 | 431
2017-03-30 05:00 | 442 | 435
2017-03-30 05:30 | 452 | 445
2017-03-30 06:00 | 466 | 459
2017-03-30 06:30 | 405 | 398
2017-03-30 07:00 | 377 | 368
2017-03-30 07:30 | 415 | 405
2017-03-30 08:00 | 437 | 428
2017-03-30 08:30 | 457 | 450
2017-03-30 09:00 | 468 | 462
2017-03-30 09:30 | 476 | 471
2017-03-30 10:00 | 484 | 479
2017-03-30 10:30 | 486 | 481
2017-03-30 11:00 | 467 | 463
2017-03-30 11:30 | 397 | 392
2017-03-30 12:00 | 446 | 438
2017-03-30 12:30 | 450 | 445
2017-03-30 13:00 | 461 | 456
2017-03-30 13:30 | 486 | 482
2017-03-30 14:00 | 536 | 532
2017-03-30 14:30 | 553 | 551
2017-03-30 15:00 | 556 | 554
2017-03-30 15:30 | 552 | 551
2017-03-30 16:00 | 540 | 538
2017-03-30 16:30 | 530 | 528
2017-03-30 17:00 | 509 | 507
2017-03-30 17:30 | 514 | 512
2017-03-30 18:00 | 534 | 531
2017-03-30 18:30 | 545 | 543
2017-03-30 19:00 | 563 | 561
2017-03-30 19:30 | 558 | 557
2017-03-30 20:00 | 563 | 562
2017-03-30 20:30 | 574 | 572
2017-03-30 21:00 | 567 | 566
2017-03-30 21:30 | 531 | 530
2017-03-30 22:00 | 508 | 506
2017-03-30 22:30 | 461 | 457
2017-03-30 23:00 | 425 | 420
2017-03-30 23:30 | 399 | 392
2017-03-31 | 434 | 426
2017-03-31 00:30 | 487 | 482
2017-03-31 01:00 | 482 | 477
2017-03-31 01:30 | 472 | 468
2017-03-31 02:00 | 465 | 460
2017-03-31 02:30 | 470 | 465
2017-03-31 03:00 | 465 | 459
2017-03-31 03:30 | 461 | 456
2017-03-31 04:00 | 458 | 452
2017-03-31 04:30 | 449 | 443
2017-03-31 05:00 | 453 | 447
2017-03-31 05:30 | 462 | 456
2017-03-31 06:00 | 477 | 472
2017-03-31 06:30 | 412 | 406
2017-03-31 07:00 | 385 | 376
2017-03-31 07:30 | 421 | 411
2017-03-31 08:00 | 425 | 417
2017-03-31 08:30 | 433 | 425
2017-03-31 09:00 | 450 | 444
2017-03-31 09:30 | 449 | 444
2017-03-31 10:00 | 449 | 444
2017-03-31 10:30 | 452 | 447
2017-03-31 11:00 | 459 | 454
2017-03-31 11:30 | 497 | 492
2017-03-31 12:00 | 518 | 515
2017-03-31 12:30 | 502 | 499
2017-03-31 13:00 | 493 | 490
2017-03-31 13:30 | 482 | 478
2017-03-31 14:00 | 485 | 482
2017-03-31 14:30 | 495 | 491
2017-03-31 15:00 | 503 | 499
2017-03-31 15:30 | 507 | 504
2017-03-31 16:00 | 526 | 524
2017-03-31 16:30 | 524 | 522
2017-03-31 17:00 | 473 | 471
2017-03-31 17:30 | 469 | 466
2017-03-31 18:00 | 489 | 487
2017-03-31 18:30 | 482 | 479
2017-03-31 19:00 | 493 | 491
2017-03-31 19:30 | 486 | 483
2017-03-31 20:00 | 467 | 464
2017-03-31 20:30 | 445 | 442
2017-03-31 21:00 | 425 | 421
2017-03-31 21:30 | 425 | 421
2017-03-31 22:00 | 436 | 431
2017-03-31 22:30 | 421 | 416
2017-03-31 23:00 | 399 | 393
2017-03-31 23:30 | 378 | 371
2017-04-01 | 359 | 351
2017-04-01 00:30 | 453 | 446
2017-04-01 01:00 | 468 | 463
2017-04-01 01:30 | 454 | 451
2017-04-01 02:00 | 445 | 441
2017-04-01 02:30 | 438 | 433
2017-04-01 03:00 | 431 | 426
2017-04-01 03:30 | 426 | 421
2017-04-01 04:00 | 423 | 418
2017-04-01 04:30 | 420 | 415
2017-04-01 05:00 | 419 | 414
2017-04-01 05:30 | 422 | 417
2017-04-01 06:00 | 423 | 418
2017-04-01 06:30 | 429 | 423
2017-04-01 07:00 | 434 | 429
2017-04-01 07:30 | 450 | 445
2017-04-01 08:00 | 463 | 458
2017-04-01 08:30 | 479 | 475
2017-04-01 09:00 | 486 | 482
2017-04-01 09:30 | 491 | 488
2017-04-01 10:00 | 494 | 490
2017-04-01 10:30 | 497 | 494
2017-04-01 11:00 | 496 | 493
2017-04-01 11:30 | 495 | 492
2017-04-01 12:00 | 500 | 497
2017-04-01 12:30 | 504 | 501
2017-04-01 13:00 | 512 | 509
2017-04-01 13:30 | 519 | 516
2017-04-01 14:00 | 523 | 520
2017-04-01 14:30 | 512 | 510
2017-04-01 15:00 | 513 | 511
2017-04-01 15:30 | 523 | 521
2017-04-01 16:00 | 530 | 528
2017-04-01 16:30 | 535 | 533
2017-04-01 17:00 | 532 | 530
2017-04-01 17:30 | 539 | 537
2017-04-01 18:00 | 547 | 545
2017-04-01 18:30 | 550 | 548
2017-04-01 19:00 | 564 | 563
2017-04-01 19:30 | 564 | 563
2017-04-01 20:00 | 566 | 564
2017-04-01 20:30 | 576 | 575
2017-04-01 21:00 | 568 | 567
2017-04-01 21:30 | 554 | 552
2017-04-01 22:00 | 537 | 535
2017-04-01 22:30 | 514 | 512
2017-04-01 23:00 | 492 | 490
2017-04-01 23:30 | 475 | 471
2017-04-02 | 465 | 461
2017-04-02 00:30 | 455 | 450
2017-04-02 01:00 | 441 | 436
2017-04-02 01:30 | 429 | 424
2017-04-02 02:00 | 423 | 418
2017-04-02 02:30 | 416 | 411
2017-04-02 03:00 | 413 | 407
2017-04-02 03:30 | 410 | 405
2017-04-02 04:00 | 407 | 401
2017-04-02 04:30 | 402 | 396
2017-04-02 05:00 | 400 | 394
2017-04-02 05:30 | 404 | 398
2017-04-02 06:00 | 404 | 398
2017-04-02 06:30 | 407 | 401
2017-04-02 07:00 | 406 | 400
2017-04-02 07:30 | 421 | 415
2017-04-02 08:00 | 430 | 425
2017-04-02 08:30 | 441 | 436
2017-04-02 09:00 | 444 | 440
2017-04-02 09:30 | 449 | 445
2017-04-02 10:00 | 456 | 453
2017-04-02 10:30 | 466 | 462
2017-04-02 11:00 | 470 | 466
2017-04-02 11:30 | 472 | 469
2017-04-02 12:00 | 481 | 477
2017-04-02 12:30 | 487 | 484
2017-04-02 13:00 | 491 | 488
2017-04-02 13:30 | 499 | 497
2017-04-02 14:00 | 503 | 500
2017-04-02 14:30 | 489 | 486
2017-04-02 15:00 | 492 | 489
2017-04-02 15:30 | 511 | 508
2017-04-02 16:00 | 522 | 520
2017-04-02 16:30 | 529 | 527
2017-04-02 17:00 | 531 | 529
2017-04-02 17:30 | 549 | 547
2017-04-02 18:00 | 561 | 560
2017-04-02 18:30 | 580 | 579
2017-04-02 19:00 | 608 | 607
2017-04-02 19:30 | 606 | 605
2017-04-02 20:00 | 604 | 603
2017-04-02 20:30 | 613 | 612
2017-04-02 21:00 | 608 | 607
2017-04-02 21:30 | 584 | 583
2017-04-02 22:00 | 560 | 559
2017-04-02 22:30 | 533 | 531
2017-04-02 23:00 | 511 | 508
2017-04-02 23:30 | 486 | 483
2017-04-03 | 472 | 468
2017-04-03 00:30 | 458 | 454
2017-04-03 01:00 | 451 | 446
2017-04-03 01:30 | 446 | 441
2017-04-03 02:00 | 439 | 435
2017-04-03 02:30 | 435 | 430
2017-04-03 03:00 | 429 | 424
2017-04-03 03:30 | 427 | 422
2017-04-03 04:00 | 424 | 419
2017-04-03 04:30 | 409 | 403
2017-04-03 05:00 | 370 | 363
2017-04-03 05:30 | 375 | 366
2017-04-03 06:00 | 390 | 382
2017-04-03 06:30 | 417 | 410
2017-04-03 07:00 | 443 | 437
2017-04-03 07:30 | 457 | 453
2017-04-03 08:00 | 458 | 454
2017-04-03 08:30 | 403 | 402
2017-04-03 09:00 | 396 | 395
2017-04-03 09:30 | 401 | 399
2017-04-03 10:00 | 402 | 401
2017-04-03 10:30 | 402 | 401
2017-04-03 11:00 | 399 | 397
2017-04-03 11:30 | 402 | 401
2017-04-03 12:00 | 410 | 409
2017-04-03 12:30 | 420 | 419
2017-04-03 13:00 | 430 | 429
2017-04-03 13:30 | 440 | 439
2017-04-03 14:00 | 441 | 440
2017-04-03 14:30 | 442 | 441
2017-04-03 15:00 | 448 | 447
2017-04-03 15:30 | 399 | 397
2017-04-03 16:00 | 419 | 417
2017-04-03 16:30 | 400 | 398
2017-04-03 17:00 | 367 | 364
2017-04-03 17:30 | 368 | 365
2017-04-03 18:00 | 372 | 369
2017-04-03 18:30 | 382 | 379
2017-04-03 19:00 | 401 | 398
2017-04-03 19:30 | 390 | 387
2017-04-03 20:00 | 390 | 388
2017-04-03 20:30 | 392 | 389
2017-04-03 21:00 | 374 | 371
2017-04-03 21:30 | 424 | 421
2017-04-03 22:00 | 416 | 415
2017-04-03 22:30 | 398 | 397
2017-04-03 23:00 | 379 | 376
2017-04-03 23:30 | 360 | 357
2017-04-04 | 341 | 337
2017-04-04 00:30 | 327 | 322
2017-04-04 01:00 | 313 | 307
2017-04-04 01:30 | 305 | 298
2017-04-04 02:00 | 297 | 290
2017-04-04 02:30 | 294 | 286
2017-04-04 03:00 | 293 | 285
2017-04-04 03:30 | 291 | 284
2017-04-04 04:00 | 289 | 281
2017-04-04 04:30 | 292 | 284
2017-04-04 05:00 | 291 | 283
2017-04-04 05:30 | 306 | 299
2017-04-04 06:00 | 318 | 311
2017-04-04 06:30 | 336 | 330
2017-04-04 07:00 | 280 | 274
2017-04-04 07:30 | 306 | 299
2017-04-04 08:00 | 327 | 320
2017-04-04 08:30 | 406 | 402
2017-04-04 09:00 | 407 | 405
2017-04-04 09:30 | 393 | 391
2017-04-04 10:00 | 378 | 375
2017-04-04 10:30 | 372 | 369
2017-04-04 11:00 | 331 | 327
2017-04-04 11:30 | 342 | 337
2017-04-04 12:00 | 335 | 330
2017-04-04 12:30 | 338 | 333
2017-04-04 13:00 | 378 | 373
2017-04-04 13:30 | 360 | 357
2017-04-04 14:00 | 368 | 364
2017-04-04 14:30 | 354 | 350
2017-04-04 15:00 | 367 | 364
2017-04-04 15:30 | 391 | 388
2017-04-04 16:00 | 359 | 356
2017-04-04 16:30 | 349 | 345
2017-04-04 17:00 | 335 | 330
2017-04-04 17:30 | 337 | 332
2017-04-04 18:00 | 343 | 338
2017-04-04 18:30 | 352 | 348
2017-04-04 19:00 | 372 | 368
2017-04-04 19:30 | 359 | 356
2017-04-04 20:00 | 344 | 340
2017-04-04 20:30 | 338 | 333
2017-04-04 21:00 | 315 | 310
2017-04-04 21:30 | 324 | 318
2017-04-04 22:00 | 315 | 309
2017-04-04 22:30 | 306 | 300
2017-04-04 23:00 | 280 | 273
2017-04-04 23:30 | 256 | 247
2017-04-05 | 246 | 234
2017-04-05 00:30 | 301 | 290
2017-04-05 01:00 | 310 | 301
2017-04-05 01:30 | 303 | 295
2017-04-05 02:00 | 298 | 290
2017-04-05 02:30 | 291 | 282
2017-04-05 03:00 | 289 | 280
2017-04-05 03:30 | 286 | 277
2017-04-05 04:00 | 286 | 277
2017-04-05 04:30 | 292 | 282
2017-04-05 05:00 | 295 | 285
2017-04-05 05:30 | 301 | 291
2017-04-05 06:00 | 311 | 302
2017-04-05 06:30 | 289 | 280
2017-04-05 07:00 | 262 | 251
2017-04-05 07:30 | 290 | 278
2017-04-05 08:00 | 311 | 301
2017-04-05 08:30 | 318 | 309
2017-04-05 09:00 | 321 | 313
2017-04-05 09:30 | 304 | 296
2017-04-05 10:00 | 288 | 279
2017-04-05 10:30 | 287 | 278
2017-04-05 11:00 | 281 | 271
2017-04-05 11:30 | 280 | 270
2017-04-05 12:00 | 277 | 267
2017-04-05 12:30 | 282 | 272
2017-04-05 13:00 | 291 | 282
2017-04-05 13:30 | 293 | 284
2017-04-05 14:00 | 303 | 295
2017-04-05 14:30 | 306 | 298
2017-04-05 15:00 | 305 | 298
2017-04-05 15:30 | 326 | 319
2017-04-05 16:00 | 339 | 332
2017-04-05 16:30 | 337 | 331
2017-04-05 17:00 | 328 | 322
2017-04-05 17:30 | 323 | 317
2017-04-05 18:00 | 331 | 325
2017-04-05 18:30 | 345 | 339
2017-04-05 19:00 | 367 | 362
2017-04-05 19:30 | 360 | 355
2017-04-05 20:00 | 343 | 338
2017-04-05 20:30 | 318 | 312
2017-04-05 21:00 | 337 | 331
2017-04-05 21:30 | 344 | 338
2017-04-05 22:00 | 347 | 341
2017-04-05 22:30 | 263 | 256
2017-04-05 23:00 | 231 | 219
2017-04-05 23:30 | 214 | 200
2017-04-06 | 262 | 249
2017-04-06 00:30 | 273 | 263
2017-04-06 01:00 | 293 | 284
2017-04-06 01:30 | 291 | 283
2017-04-06 02:00 | 282 | 274
2017-04-06 02:30 | 279 | 270
2017-04-06 03:00 | 276 | 267
2017-04-06 03:30 | 272 | 262
2017-04-06 04:00 | 272 | 263
2017-04-06 04:30 | 279 | 270
2017-04-06 05:00 | 281 | 272
2017-04-06 05:30 | 288 | 279
2017-04-06 06:00 | 307 | 299
2017-04-06 06:30 | 314 | 307
2017-04-06 07:00 | 262 | 253
2017-04-06 07:30 | 302 | 292
2017-04-06 08:00 | 313 | 306
2017-04-06 08:30 | 395 | 390
2017-04-06 09:00 | 394 | 391
2017-04-06 09:30 | 378 | 375
2017-04-06 10:00 | 372 | 369
2017-04-06 10:30 | 371 | 368
2017-04-06 11:00 | 371 | 368
2017-04-06 11:30 | 362 | 358
2017-04-06 12:00 | 351 | 348
2017-04-06 12:30 | 349 | 345
2017-04-06 13:00 | 358 | 354
2017-04-06 13:30 | 366 | 362
2017-04-06 14:00 | 373 | 370
2017-04-06 14:30 | 378 | 375
2017-04-06 15:00 | 384 | 382
2017-04-06 15:30 | 314 | 311
2017-04-06 16:00 | 314 | 309
2017-04-06 16:30 | 319 | 313
2017-04-06 17:00 | 326 | 321
2017-04-06 17:30 | 332 | 327
2017-04-06 18:00 | 339 | 335
2017-04-06 18:30 | 357 | 353
2017-04-06 19:00 | 383 | 380
2017-04-06 19:30 | 369 | 366
2017-04-06 20:00 | 346 | 343
2017-04-06 20:30 | 326 | 322
2017-04-06 21:00 | 309 | 304
2017-04-06 21:30 | 347 | 342
2017-04-06 22:00 | 339 | 335
2017-04-06 22:30 | 331 | 327
2017-04-06 23:00 | 312 | 307
2017-04-06 23:30 | 294 | 288
2017-04-07 | 278 | 271
2017-04-07 00:30 | 265 | 257
2017-04-07 01:00 | 255 | 245
2017-04-07 01:30 | 250 | 239
2017-04-07 02:00 | 241 | 230
2017-04-07 02:30 | 257 | 247
2017-04-07 03:00 | 256 | 246
2017-04-07 03:30 | 255 | 245
2017-04-07 04:00 | 254 | 243
2017-04-07 04:30 | 255 | 244
2017-04-07 05:00 | 261 | 250
2017-04-07 05:30 | 271 | 261
2017-04-07 06:00 | 284 | 275
2017-04-07 06:30 | 297 | 290
2017-04-07 07:00 | 292 | 285
2017-04-07 07:30 | 347 | 341
2017-04-07 08:00 | 365 | 360
2017-04-07 08:30 | 379 | 375
2017-04-07 09:00 | 383 | 380
2017-04-07 09:30 | 386 | 383
2017-04-07 10:00 | 384 | 382
2017-04-07 10:30 | 383 | 382
2017-04-07 11:00 | 381 | 379
2017-04-07 11:30 | 376 | 374
2017-04-07 12:00 | 389 | 387
2017-04-07 12:30 | 391 | 387
2017-04-07 13:00 | 394 | 389
2017-04-07 13:30 | 406 | 402
2017-04-07 14:00 | 400 | 396
2017-04-07 14:30 | 399 | 396
2017-04-07 15:00 | 406 | 402
2017-04-07 15:30 | 415 | 411
2017-04-07 16:00 | 421 | 417
2017-04-07 16:30 | 413 | 410
2017-04-07 17:00 | 398 | 394
2017-04-07 17:30 | 397 | 393
2017-04-07 18:00 | 403 | 399
2017-04-07 18:30 | 411 | 407
2017-04-07 19:00 | 425 | 421
2017-04-07 19:30 | 414 | 410
2017-04-07 20:00 | 419 | 416
2017-04-07 20:30 | 409 | 405
2017-04-07 21:00 | 395 | 391
2017-04-07 21:30 | 378 | 373
2017-04-07 22:00 | 366 | 360
2017-04-07 22:30 | 386 | 380
2017-04-07 23:00 | 372 | 367
2017-04-07 23:30 | 352 | 347
2017-04-08 | 337 | 331
2017-04-08 00:30 | 377 | 371
2017-04-08 01:00 | 442 | 437
2017-04-08 01:30 | 433 | 430
2017-04-08 02:00 | 420 | 417
2017-04-08 02:30 | 415 | 412
2017-04-08 03:00 | 416 | 413
2017-04-08 03:30 | 422 | 419
2017-04-08 04:00 | 420 | 417
2017-04-08 04:30 | 420 | 417
2017-04-08 05:00 | 415 | 412
2017-04-08 05:30 | 418 | 414
2017-04-08 06:00 | 423 | 420
2017-04-08 06:30 | 432 | 429
2017-04-08 07:00 | 440 | 437
2017-04-08 07:30 | 459 | 456
2017-04-08 08:00 | 476 | 474
2017-04-08 08:30 | 466 | 464
2017-04-08 09:00 | 475 | 472
2017-04-08 09:30 | 484 | 482
2017-04-08 10:00 | 494 | 491
2017-04-08 10:30 | 486 | 484
2017-04-08 11:00 | 481 | 479
2017-04-08 11:30 | 483 | 481
2017-04-08 12:00 | 490 | 488
2017-04-08 12:30 | 492 | 490
2017-04-08 13:00 | 498 | 497
2017-04-08 13:30 | 497 | 496
2017-04-08 14:00 | 498 | 497
2017-04-08 14:30 | 503 | 501
2017-04-08 15:00 | 509 | 507
2017-04-08 15:30 | 521 | 520
2017-04-08 16:00 | 530 | 529
2017-04-08 16:30 | 523 | 522
2017-04-08 17:00 | 510 | 509
2017-04-08 17:30 | 524 | 523
2017-04-08 18:00 | 533 | 532
2017-04-08 18:30 | 545 | 544
2017-04-08 19:00 | 561 | 560
2017-04-08 19:30 | 551 | 551
2017-04-08 20:00 | 549 | 548
2017-04-08 20:30 | 560 | 559
2017-04-08 21:00 | 553 | 552
2017-04-08 21:30 | 539 | 538
2017-04-08 22:00 | 526 | 525
2017-04-08 22:30 | 516 | 515
2017-04-08 23:00 | 500 | 499
2017-04-08 23:30 | 484 | 482
2017-04-09 | 468 | 466
2017-04-09 00:30 | 451 | 448
2017-04-09 01:00 | 437 | 434
2017-04-09 01:30 | 430 | 426
2017-04-09 02:00 | 430 | 426
2017-04-09 02:30 | 435 | 431
2017-04-09 03:00 | 429 | 426
2017-04-09 03:30 | 424 | 421
2017-04-09 04:00 | 424 | 421
2017-04-09 04:30 | 424 | 420
2017-04-09 05:00 | 422 | 418
2017-04-09 05:30 | 424 | 420
2017-04-09 06:00 | 425 | 422
2017-04-09 06:30 | 426 | 422
2017-04-09 07:00 | 412 | 408
2017-04-09 07:30 | 425 | 422
2017-04-09 08:00 | 432 | 429
2017-04-09 08:30 | 447 | 444
2017-04-09 09:00 | 438 | 435
2017-04-09 09:30 | 448 | 446
2017-04-09 10:00 | 450 | 447
2017-04-09 10:30 | 450 | 447
2017-04-09 11:00 | 448 | 445
2017-04-09 11:30 | 447 | 444
2017-04-09 12:00 | 447 | 444
2017-04-09 12:30 | 449 | 446
2017-04-09 13:00 | 458 | 455
2017-04-09 13:30 | 461 | 458
2017-04-09 14:00 | 472 | 469
2017-04-09 14:30 | 483 | 480
2017-04-09 15:00 | 491 | 488
2017-04-09 15:30 | 504 | 502
2017-04-09 16:00 | 521 | 520
2017-04-09 16:30 | 523 | 522
2017-04-09 17:00 | 525 | 524
2017-04-09 17:30 | 542 | 541
2017-04-09 18:00 | 554 | 553
2017-04-09 18:30 | 582 | 582
2017-04-09 19:00 | 610 | 610
2017-04-09 19:30 | 598 | 598
2017-04-09 20:00 | 619 | 618
2017-04-09 20:30 | 611 | 610
2017-04-09 21:00 | 595 | 595
2017-04-09 21:30 | 575 | 575
2017-04-09 22:00 | 550 | 550
2017-04-09 22:30 | 524 | 524
2017-04-09 23:00 | 501 | 501
2017-04-09 23:30 | 477 | 476
2017-04-10 | 456 | 456
2017-04-10 00:30 | 445 | 445
2017-04-10 01:00 | 436 | 435
2017-04-10 01:30 | 429 | 428
2017-04-10 02:00 | 423 | 422
2017-04-10 02:30 | 418 | 417
2017-04-10 03:00 | 415 | 414
2017-04-10 03:30 | 411 | 410
2017-04-10 04:00 | 413 | 412
2017-04-10 04:30 | 398 | 397
2017-04-10 05:00 | 356 | 354
2017-04-10 05:30 | 361 | 359
2017-04-10 06:00 | 363 | 361
2017-04-10 06:30 | 365 | 363
2017-04-10 07:00 | 371 | 369
2017-04-10 07:30 | 410 | 408
2017-04-10 08:00 | 412 | 411
2017-04-10 08:30 | 370 | 369
2017-04-10 09:00 | 370 | 368
2017-04-10 09:30 | 325 | 322
2017-04-10 10:00 | 344 | 341
2017-04-10 10:30 | 372 | 370
2017-04-10 11:00 | 373 | 372
2017-04-10 11:30 | 368 | 367
2017-04-10 12:00 | 372 | 370
2017-04-10 12:30 | 382 | 381
2017-04-10 13:00 | 390 | 388
2017-04-10 13:30 | 403 | 402
2017-04-10 14:00 | 412 | 411
2017-04-10 14:30 | 422 | 421
2017-04-10 15:00 | 437 | 436
2017-04-10 15:30 | 445 | 445
2017-04-10 16:00 | 458 | 457
2017-04-10 16:30 | 455 | 455
2017-04-10 17:00 | 449 | 449
2017-04-10 17:30 | 452 | 452
2017-04-10 18:00 | 438 | 437
2017-04-10 18:30 | 387 | 387
2017-04-10 19:00 | 452 | 451
2017-04-10 19:30 | 485 | 484
2017-04-10 20:00 | 481 | 481
2017-04-10 20:30 | 488 | 487
2017-04-10 21:00 | 472 | 472
2017-04-10 21:30 | 449 | 449
2017-04-10 22:00 | 428 | 428
2017-04-10 22:30 | 411 | 410
2017-04-10 23:00 | 386 | 385
2017-04-10 23:30 | 362 | 361
2017-04-11 | 345 | 342
2017-04-11 00:30 | 332 | 328
2017-04-11 01:00 | 321 | 317
2017-04-11 01:30 | 315 | 311
2017-04-11 02:00 | 305 | 300
2017-04-11 02:30 | 304 | 299
2017-04-11 03:00 | 299 | 294
2017-04-11 03:30 | 299 | 294
2017-04-11 04:00 | 294 | 289
2017-04-11 04:30 | 297 | 291
2017-04-11 05:00 | 303 | 298
2017-04-11 05:30 | 317 | 312
2017-04-11 06:00 | 329 | 324
2017-04-11 06:30 | 349 | 344
2017-04-11 07:00 | 314 | 306
2017-04-11 07:30 | 385 | 379
2017-04-11 08:00 | 403 | 399
2017-04-11 08:30 | 411 | 409
2017-04-11 09:00 | 413 | 410
2017-04-11 09:30 | 410 | 407
2017-04-11 10:00 | 404 | 402
2017-04-11 10:30 | 408 | 405
2017-04-11 11:00 | 416 | 414
2017-04-11 11:30 | 424 | 422
2017-04-11 12:00 | 430 | 427
2017-04-11 12:30 | 436 | 433
2017-04-11 13:00 | 439 | 437
2017-04-11 13:30 | 449 | 447
2017-04-11 14:00 | 458 | 456
2017-04-11 14:30 | 447 | 446
2017-04-11 15:00 | 452 | 450
2017-04-11 15:30 | 464 | 462
2017-04-11 16:00 | 475 | 474
2017-04-11 16:30 | 438 | 436
2017-04-11 17:00 | 404 | 402
2017-04-11 17:30 | 402 | 400
2017-04-11 18:00 | 377 | 374
2017-04-11 18:30 | 335 | 332
2017-04-11 19:00 | 384 | 380
2017-04-11 19:30 | 461 | 458
2017-04-11 20:00 | 453 | 451
2017-04-11 20:30 | 440 | 438
2017-04-11 21:00 | 436 | 434
2017-04-11 21:30 | 434 | 432
2017-04-11 22:00 | 446 | 443
2017-04-11 22:30 | 428 | 426
2017-04-11 23:00 | 415 | 412
2017-04-11 23:30 | 388 | 385
2017-04-12 | 371 | 367
2017-04-12 00:30 | 413 | 409
2017-04-12 01:00 | 476 | 473
2017-04-12 01:30 | 463 | 462
2017-04-12 02:00 | 452 | 450
2017-04-12 02:30 | 448 | 446
2017-04-12 03:00 | 440 | 437
2017-04-12 03:30 | 440 | 438
2017-04-12 04:00 | 444 | 441
2017-04-12 04:30 | 446 | 444
2017-04-12 05:00 | 444 | 442
2017-04-12 05:30 | 456 | 453
2017-04-12 06:00 | 469 | 467
2017-04-12 06:30 | 457 | 455
2017-04-12 07:00 | 438 | 436
2017-04-12 07:30 | 469 | 466
2017-04-12 08:00 | 461 | 459
2017-04-12 08:30 | 387 | 385
2017-04-12 09:00 | 396 | 392
2017-04-12 09:30 | 401 | 398
2017-04-12 10:00 | 391 | 388
2017-04-12 10:30 | 373 | 369
2017-04-12 11:00 | 346 | 342
2017-04-12 11:30 | 313 | 307
2017-04-12 12:00 | 309 | 302
2017-04-12 12:30 | 311 | 304
2017-04-12 13:00 | 313 | 306
2017-04-12 13:30 | 319 | 312
2017-04-12 14:00 | 321 | 315
2017-04-12 14:30 | 326 | 320
2017-04-12 15:00 | 333 | 327
2017-04-12 15:30 | 352 | 348
2017-04-12 16:00 | 362 | 358
2017-04-12 16:30 | 355 | 351
2017-04-12 17:00 | 352 | 347
2017-04-12 17:30 | 351 | 347
2017-04-12 18:00 | 358 | 353
2017-04-12 18:30 | 373 | 369
2017-04-12 19:00 | 398 | 395
2017-04-12 19:30 | 390 | 387
2017-04-12 20:00 | 391 | 388
2017-04-12 20:30 | 399 | 395
2017-04-12 21:00 | 388 | 385
2017-04-12 21:30 | 369 | 365
2017-04-12 22:00 | 351 | 347
2017-04-12 22:30 | 344 | 339
2017-04-12 23:00 | 343 | 338
2017-04-12 23:30 | 327 | 321
2017-04-13 | 355 | 349
2017-04-13 00:30 | 346 | 340
2017-04-13 01:00 | 329 | 323
2017-04-13 01:30 | 324 | 317
2017-04-13 02:00 | 315 | 308
2017-04-13 02:30 | 310 | 302
2017-04-13 03:00 | 304 | 296
2017-04-13 03:30 | 304 | 295
2017-04-13 04:00 | 301 | 293
2017-04-13 04:30 | 303 | 294
2017-04-13 05:00 | 305 | 297
2017-04-13 05:30 | 316 | 308
2017-04-13 06:00 | 328 | 320
2017-04-13 06:30 | 280 | 272
2017-04-13 07:00 | 291 | 281
2017-04-13 07:30 | 304 | 294
2017-04-13 08:00 | 314 | 306
2017-04-13 08:30 | 323 | 316
2017-04-13 09:00 | 327 | 321
2017-04-13 09:30 | 327 | 321
2017-04-13 10:00 | 327 | 321
2017-04-13 10:30 | 323 | 317
2017-04-13 11:00 | 324 | 317
2017-04-13 11:30 | 323 | 317
2017-04-13 12:00 | 326 | 320
2017-04-13 12:30 | 337 | 331
2017-04-13 13:00 | 343 | 338
2017-04-13 13:30 | 347 | 342
2017-04-13 14:00 | 351 | 346
2017-04-13 14:30 | 340 | 335
2017-04-13 15:00 | 338 | 333
2017-04-13 15:30 | 343 | 338
2017-04-13 16:00 | 359 | 354
2017-04-13 16:30 | 362 | 358
2017-04-13 17:00 | 354 | 350
2017-04-13 17:30 | 352 | 347
2017-04-13 18:00 | 357 | 353
2017-04-13 18:30 | 376 | 371
2017-04-13 19:00 | 391 | 388
2017-04-13 19:30 | 372 | 369
2017-04-13 20:00 | 384 | 380
2017-04-13 20:30 | 396 | 393
2017-04-13 21:00 | 386 | 382
2017-04-13 21:30 | 360 | 357
2017-04-13 22:00 | 367 | 363
2017-04-13 22:30 | 330 | 326
2017-04-13 23:00 | 301 | 295
2017-04-13 23:30 | 285 | 277
2017-04-14 | 335 | 328
2017-04-14 00:30 | 386 | 381
2017-04-14 01:00 | 452 | 449
2017-04-14 01:30 | 443 | 441
2017-04-14 02:00 | 435 | 433
2017-04-14 02:30 | 432 | 430
2017-04-14 03:00 | 423 | 421
2017-04-14 03:30 | 418 | 416
2017-04-14 04:00 | 418 | 416
2017-04-14 04:30 | 432 | 429
2017-04-14 05:00 | 436 | 434
2017-04-14 05:30 | 438 | 436
2017-04-14 06:00 | 443 | 441
2017-04-14 06:30 | 413 | 411
2017-04-14 07:00 | 389 | 386
2017-04-14 07:30 | 403 | 399
2017-04-14 08:00 | 414 | 411
2017-04-14 08:30 | 384 | 381
2017-04-14 09:00 | 346 | 343
2017-04-14 09:30 | 357 | 352
2017-04-14 10:00 | 355 | 351
2017-04-14 10:30 | 356 | 351
2017-04-14 11:00 | 351 | 347
2017-04-14 11:30 | 351 | 347
2017-04-14 12:00 | 364 | 360
2017-04-14 12:30 | 374 | 370
2017-04-14 13:00 | 385 | 381
2017-04-14 13:30 | 386 | 383
2017-04-14 14:00 | 375 | 372
2017-04-14 14:30 | 353 | 349
2017-04-14 15:00 | 341 | 337
2017-04-14 15:30 | 341 | 337
2017-04-14 16:00 | 362 | 358
2017-04-14 16:30 | 360 | 357
2017-04-14 17:00 | 362 | 358
2017-04-14 17:30 | 375 | 372
2017-04-14 18:00 | 385 | 382
2017-04-14 18:30 | 398 | 395
2017-04-14 19:00 | 422 | 420
2017-04-14 19:30 | 411 | 409
2017-04-14 20:00 | 413 | 411
2017-04-14 20:30 | 423 | 421
2017-04-14 21:00 | 415 | 413
2017-04-14 21:30 | 406 | 403
2017-04-14 22:00 | 395 | 393
2017-04-14 22:30 | 381 | 378
2017-04-14 23:00 | 362 | 358
2017-04-14 23:30 | 374 | 370
2017-04-15 | 442 | 438
2017-04-15 00:30 | 451 | 449
2017-04-15 01:00 | 446 | 445
2017-04-15 01:30 | 438 | 436
2017-04-15 02:00 | 431 | 429
2017-04-15 02:30 | 425 | 423
2017-04-15 03:00 | 422 | 420
2017-04-15 03:30 | 420 | 418
2017-04-15 04:00 | 421 | 418
2017-04-15 04:30 | 417 | 415
2017-04-15 05:00 | 422 | 420
2017-04-15 05:30 | 421 | 419
2017-04-15 06:00 | 421 | 419
2017-04-15 06:30 | 431 | 429
2017-04-15 07:00 | 439 | 437
2017-04-15 07:30 | 464 | 462
2017-04-15 08:00 | 476 | 475
2017-04-15 08:30 | 488 | 487
2017-04-15 09:00 | 497 | 496
2017-04-15 09:30 | 498 | 498
2017-04-15 10:00 | 495 | 494
2017-04-15 10:30 | 490 | 489
2017-04-15 11:00 | 480 | 479
2017-04-15 11:30 | 478 | 477
2017-04-15 12:00 | 491 | 490
2017-04-15 12:30 | 493 | 492
2017-04-15 13:00 | 487 | 487
2017-04-15 13:30 | 482 | 481
2017-04-15 14:00 | 477 | 476
2017-04-15 14:30 | 466 | 465
2017-04-15 15:00 | 472 | 471
2017-04-15 15:30 | 489 | 488
2017-04-15 16:00 | 499 | 499
2017-04-15 16:30 | 504 | 504
2017-04-15 17:00 | 504 | 503
2017-04-15 17:30 | 523 | 523
2017-04-15 18:00 | 530 | 530
2017-04-15 18:30 | 551 | 550
2017-04-15 19:00 | 566 | 566
2017-04-15 19:30 | 551 | 551
2017-04-15 20:00 | 529 | 528
2017-04-15 20:30 | 532 | 532
2017-04-15 21:00 | 551 | 551
2017-04-15 21:30 | 540 | 540
2017-04-15 22:00 | 529 | 528
2017-04-15 22:30 | 508 | 508
2017-04-15 23:00 | 491 | 491
2017-04-15 23:30 | 477 | 476
2017-04-16 | 462 | 461
2017-04-16 00:30 | 454 | 452
2017-04-16 01:00 | 441 | 439
2017-04-16 01:30 | 432 | 430
2017-04-16 02:00 | 426 | 424
2017-04-16 02:30 | 421 | 419
2017-04-16 03:00 | 418 | 416
2017-04-16 03:30 | 415 | 413
2017-04-16 04:00 | 415 | 413
2017-04-16 04:30 | 412 | 410
2017-04-16 05:00 | 408 | 406
2017-04-16 05:30 | 411 | 409
2017-04-16 06:00 | 412 | 410
2017-04-16 06:30 | 415 | 412
2017-04-16 07:00 | 423 | 420
2017-04-16 07:30 | 438 | 436
2017-04-16 08:00 | 447 | 445
2017-04-16 08:30 | 461 | 459
2017-04-16 09:00 | 462 | 461
2017-04-16 09:30 | 466 | 465
2017-04-16 10:00 | 476 | 475
2017-04-16 10:30 | 479 | 477
2017-04-16 11:00 | 473 | 472
2017-04-16 11:30 | 476 | 475
2017-04-16 12:00 | 474 | 473
2017-04-16 12:30 | 476 | 475
2017-04-16 13:00 | 470 | 469
2017-04-16 13:30 | 480 | 479
2017-04-16 14:00 | 478 | 477
2017-04-16 14:30 | 454 | 453
2017-04-16 15:00 | 456 | 455
2017-04-16 15:30 | 467 | 466
2017-04-16 16:00 | 482 | 481
2017-04-16 16:30 | 484 | 483
2017-04-16 17:00 | 488 | 487
2017-04-16 17:30 | 504 | 503
2017-04-16 18:00 | 515 | 515
2017-04-16 18:30 | 534 | 533
2017-04-16 19:00 | 549 | 549
2017-04-16 19:30 | 535 | 535
2017-04-16 20:00 | 538 | 538
2017-04-16 20:30 | 550 | 550
2017-04-16 21:00 | 538 | 538
2017-04-16 21:30 | 526 | 526
2017-04-16 22:00 | 512 | 512
2017-04-16 22:30 | 491 | 490
2017-04-16 23:00 | 473 | 472
2017-04-16 23:30 | 457 | 456
2017-04-17 | 448 | 447
2017-04-17 00:30 | 434 | 432
2017-04-17 01:00 | 422 | 421
2017-04-17 01:30 | 417 | 415
2017-04-17 02:00 | 413 | 411
2017-04-17 02:30 | 410 | 407
2017-04-17 03:00 | 403 | 400
2017-04-17 03:30 | 400 | 398
2017-04-17 04:00 | 402 | 399
2017-04-17 04:30 | 400 | 397
2017-04-17 05:00 | 400 | 397
2017-04-17 05:30 | 407 | 404
2017-04-17 06:00 | 412 | 409
2017-04-17 06:30 | 418 | 416
2017-04-17 07:00 | 423 | 421
2017-04-17 07:30 | 441 | 438
2017-04-17 08:00 | 454 | 453
2017-04-17 08:30 | 464 | 462
2017-04-17 09:00 | 475 | 474
2017-04-17 09:30 | 480 | 479
2017-04-17 10:00 | 481 | 480
2017-04-17 10:30 | 484 | 483
2017-04-17 11:00 | 480 | 479
2017-04-17 11:30 | 482 | 481
2017-04-17 12:00 | 493 | 492
2017-04-17 12:30 | 498 | 497
2017-04-17 13:00 | 497 | 496
2017-04-17 13:30 | 489 | 488
2017-04-17 14:00 | 488 | 487
2017-04-17 14:30 | 474 | 473
2017-04-17 15:00 | 483 | 482
2017-04-17 15:30 | 498 | 497
2017-04-17 16:00 | 510 | 510
2017-04-17 16:30 | 516 | 516
2017-04-17 17:00 | 519 | 519
2017-04-17 17:30 | 543 | 542
2017-04-17 18:00 | 559 | 559
2017-04-17 18:30 | 584 | 583
2017-04-17 19:00 | 599 | 599
2017-04-17 19:30 | 586 | 586
2017-04-17 20:00 | 584 | 584
2017-04-17 20:30 | 590 | 590
2017-04-17 21:00 | 578 | 578
2017-04-17 21:30 | 562 | 562
2017-04-17 22:00 | 538 | 538
2017-04-17 22:30 | 517 | 516
2017-04-17 23:00 | 493 | 493
2017-04-17 23:30 | 474 | 473
2017-04-18 | 459 | 458
2017-04-18 00:30 | 445 | 444
2017-04-18 01:00 | 438 | 436
2017-04-18 01:30 | 429 | 427
2017-04-18 02:00 | 417 | 415
2017-04-18 02:30 | 418 | 416
2017-04-18 03:00 | 412 | 410
2017-04-18 03:30 | 410 | 408
2017-04-18 04:00 | 412 | 410
2017-04-18 04:30 | 419 | 417
2017-04-18 05:00 | 426 | 423
2017-04-18 05:30 | 437 | 435
2017-04-18 06:00 | 450 | 448
2017-04-18 06:30 | 483 | 482
2017-04-18 07:00 | 507 | 506
2017-04-18 07:30 | 544 | 543
2017-04-18 08:00 | 557 | 557
2017-04-18 08:30 | 554 | 554
2017-04-18 09:00 | 552 | 551
2017-04-18 09:30 | 550 | 550
2017-04-18 10:00 | 543 | 543
2017-04-18 10:30 | 546 | 546
2017-04-18 11:00 | 550 | 550
2017-04-18 11:30 | 546 | 546
2017-04-18 12:00 | 542 | 542
2017-04-18 12:30 | 556 | 555
2017-04-18 13:00 | 573 | 573
2017-04-18 13:30 | 575 | 575
2017-04-18 14:00 | 572 | 572
2017-04-18 14:30 | 557 | 557
2017-04-18 15:00 | 556 | 556
2017-04-18 15:30 | 563 | 563
2017-04-18 16:00 | 576 | 576
2017-04-18 16:30 | 576 | 576
2017-04-18 17:00 | 569 | 569
2017-04-18 17:30 | 570 | 570
2017-04-18 18:00 | 579 | 579
2017-04-18 18:30 | 605 | 605
2017-04-18 19:00 | 620 | 620
2017-04-18 19:30 | 604 | 604
2017-04-18 20:00 | 604 | 604
2017-04-18 20:30 | 617 | 617
2017-04-18 21:00 | 602 | 602
2017-04-18 21:30 | 574 | 574
2017-04-18 22:00 | 548 | 548
2017-04-18 22:30 | 530 | 530
2017-04-18 23:00 | 507 | 507
2017-04-18 23:30 | 487 | 487
2017-04-19 | 466 | 465
2017-04-19 00:30 | 455 | 454
2017-04-19 01:00 | 447 | 446
2017-04-19 01:30 | 435 | 433
2017-04-19 02:00 | 427 | 426
2017-04-19 02:30 | 416 | 414
2017-04-19 03:00 | 411 | 410
2017-04-19 03:30 | 407 | 406
2017-04-19 04:00 | 407 | 405
2017-04-19 04:30 | 377 | 375
2017-04-19 05:00 | 377 | 375
2017-04-19 05:30 | 364 | 361
2017-04-19 06:00 | 385 | 382
2017-04-19 06:30 | 406 | 403
2017-04-19 07:00 | 435 | 433
2017-04-19 07:30 | 474 | 473
2017-04-19 08:00 | 490 | 489
2017-04-19 08:30 | 492 | 491
2017-04-19 09:00 | 488 | 487
2017-04-19 09:30 | 500 | 500
2017-04-19 10:00 | 495 | 495
2017-04-19 10:30 | 477 | 477
2017-04-19 11:00 | 427 | 426
2017-04-19 11:30 | 425 | 424
2017-04-19 12:00 | 433 | 432
2017-04-19 12:30 | 417 | 416
2017-04-19 13:00 | 413 | 411
2017-04-19 13:30 | 398 | 397
2017-04-19 14:00 | 384 | 382
2017-04-19 14:30 | 314 | 311
2017-04-19 15:00 | 315 | 311
2017-04-19 15:30 | 318 | 314
2017-04-19 16:00 | 326 | 322
2017-04-19 16:30 | 324 | 320
2017-04-19 17:00 | 312 | 307
2017-04-19 17:30 | 321 | 317
2017-04-19 18:00 | 366 | 363
2017-04-19 18:30 | 386 | 383
2017-04-19 19:00 | 406 | 404
2017-04-19 19:30 | 412 | 410
2017-04-19 20:00 | 422 | 421
2017-04-19 20:30 | 442 | 441
2017-04-19 21:00 | 424 | 422
2017-04-19 21:30 | 417 | 415
2017-04-19 22:00 | 402 | 401
2017-04-19 22:30 | 372 | 370
2017-04-19 23:00 | 355 | 352
2017-04-19 23:30 | 337 | 333
2017-04-20 | 329 | 324
2017-04-20 00:30 | 319 | 314
2017-04-20 01:00 | 316 | 310
2017-04-20 01:30 | 314 | 308
2017-04-20 02:00 | 309 | 303
2017-04-20 02:30 | 305 | 298
2017-04-20 03:00 | 304 | 297
2017-04-20 03:30 | 302 | 295
2017-04-20 04:00 | 299 | 292
2017-04-20 04:30 | 301 | 294
2017-04-20 05:00 | 304 | 298
2017-04-20 05:30 | 323 | 316
2017-04-20 06:00 | 340 | 334
2017-04-20 06:30 | 365 | 361
2017-04-20 07:00 | 397 | 393
2017-04-20 07:30 | 441 | 438
2017-04-20 08:00 | 451 | 449
2017-04-20 08:30 | 448 | 447
2017-04-20 09:00 | 445 | 444
2017-04-20 09:30 | 440 | 439
2017-04-20 10:00 | 431 | 429
2017-04-20 10:30 | 451 | 449
2017-04-20 11:00 | 443 | 441
2017-04-20 11:30 | 430 | 428
2017-04-20 12:00 | 436 | 435
2017-04-20 12:30 | 450 | 448
2017-04-20 13:00 | 433 | 433
2017-04-20 13:30 | 432 | 432
2017-04-20 14:00 | 440 | 440
2017-04-20 14:30 | 432 | 432
2017-04-20 15:00 | 430 | 430
2017-04-20 15:30 | 436 | 436
2017-04-20 16:00 | 370 | 370
2017-04-20 16:30 | 360 | 360
2017-04-20 17:00 | 348 | 345
2017-04-20 17:30 | 350 | 346
2017-04-20 18:00 | 364 | 360
2017-04-20 18:30 | 388 | 385
2017-04-20 19:00 | 397 | 395
2017-04-20 19:30 | 406 | 404
2017-04-20 20:00 | 418 | 416
2017-04-20 20:30 | 407 | 405
2017-04-20 21:00 | 389 | 387
2017-04-20 21:30 | 430 | 428
2017-04-20 22:00 | 422 | 420
2017-04-20 22:30 | 397 | 396
2017-04-20 23:00 | 374 | 372
2017-04-20 23:30 | 354 | 350
2017-04-21 | 335 | 332
2017-04-21 00:30 | 326 | 321
2017-04-21 01:00 | 318 | 312
2017-04-21 01:30 | 308 | 302
2017-04-21 02:00 | 302 | 295
2017-04-21 02:30 | 295 | 288
2017-04-21 03:00 | 292 | 285
2017-04-21 03:30 | 296 | 289
2017-04-21 04:00 | 296 | 289
2017-04-21 04:30 | 298 | 291
2017-04-21 05:00 | 302 | 295
2017-04-21 05:30 | 317 | 310
2017-04-21 06:00 | 335 | 329
2017-04-21 06:30 | 371 | 366
2017-04-21 07:00 | 395 | 391
2017-04-21 07:30 | 436 | 434
2017-04-21 08:00 | 456 | 454
2017-04-21 08:30 | 454 | 452
2017-04-21 09:00 | 445 | 443
2017-04-21 09:30 | 442 | 440
2017-04-21 10:00 | 443 | 441
2017-04-21 10:30 | 438 | 436
2017-04-21 11:00 | 433 | 431
2017-04-21 11:30 | 430 | 428
2017-04-21 12:00 | 429 | 427
2017-04-21 12:30 | 434 | 431
2017-04-21 13:00 | 436 | 434
2017-04-21 13:30 | 443 | 441
2017-04-21 14:00 | 438 | 436
2017-04-21 14:30 | 427 | 425
2017-04-21 15:00 | 422 | 420
2017-04-21 15:30 | 415 | 413
2017-04-21 16:00 | 349 | 346
2017-04-21 16:30 | 339 | 334
2017-04-21 17:00 | 337 | 332
2017-04-21 17:30 | 342 | 337
2017-04-21 18:00 | 341 | 336
2017-04-21 18:30 | 361 | 356
2017-04-21 19:00 | 370 | 366
2017-04-21 19:30 | 354 | 351
2017-04-21 20:00 | 355 | 351
2017-04-21 20:30 | 367 | 363
2017-04-21 21:00 | 360 | 356
2017-04-21 21:30 | 412 | 409
2017-04-21 22:00 | 415 | 413
2017-04-21 22:30 | 396 | 394
2017-04-21 23:00 | 378 | 375
2017-04-21 23:30 | 361 | 358
2017-04-22 | 344 | 340
2017-04-22 00:30 | 386 | 382
2017-04-22 01:00 | 451 | 448
2017-04-22 01:30 | 438 | 436
2017-04-22 02:00 | 428 | 426
2017-04-22 02:30 | 421 | 419
2017-04-22 03:00 | 418 | 416
2017-04-22 03:30 | 420 | 417
2017-04-22 04:00 | 416 | 414
2017-04-22 04:30 | 417 | 415
2017-04-22 05:00 | 420 | 418
2017-04-22 05:30 | 423 | 421
2017-04-22 06:00 | 430 | 428
2017-04-22 06:30 | 486 | 485
2017-04-22 07:00 | 507 | 506
2017-04-22 07:30 | 517 | 516
2017-04-22 08:00 | 524 | 524
2017-04-22 08:30 | 529 | 528
2017-04-22 09:00 | 537 | 536
2017-04-22 09:30 | 536 | 535
2017-04-22 10:00 | 534 | 533
2017-04-22 10:30 | 532 | 532
2017-04-22 11:00 | 531 | 530
2017-04-22 11:30 | 520 | 519
2017-04-22 12:00 | 522 | 521
2017-04-22 12:30 | 520 | 519
2017-04-22 13:00 | 514 | 513
2017-04-22 13:30 | 518 | 517
2017-04-22 14:00 | 510 | 509
2017-04-22 14:30 | 490 | 489
2017-04-22 15:00 | 481 | 480
2017-04-22 15:30 | 492 | 491
2017-04-22 16:00 | 505 | 504
2017-04-22 16:30 | 514 | 513
2017-04-22 17:00 | 515 | 514
2017-04-22 17:30 | 522 | 521
2017-04-22 18:00 | 537 | 536
2017-04-22 18:30 | 559 | 558
2017-04-22 19:00 | 566 | 565
2017-04-22 19:30 | 547 | 547
2017-04-22 20:00 | 552 | 552
2017-04-22 20:30 | 559 | 559
2017-04-22 21:00 | 534 | 533
2017-04-22 21:30 | 523 | 522
2017-04-22 22:00 | 504 | 503
2017-04-22 22:30 | 494 | 493
2017-04-22 23:00 | 486 | 485
2017-04-22 23:30 | 469 | 468
2017-04-23 | 451 | 450
2017-04-23 00:30 | 442 | 440
2017-04-23 01:00 | 433 | 432
2017-04-23 01:30 | 422 | 421
2017-04-23 02:00 | 416 | 414
2017-04-23 02:30 | 410 | 408
2017-04-23 03:00 | 406 | 404
2017-04-23 03:30 | 405 | 402
2017-04-23 04:00 | 404 | 401
2017-04-23 04:30 | 405 | 403
2017-04-23 05:00 | 405 | 403
2017-04-23 05:30 | 411 | 408
2017-04-23 06:00 | 411 | 409
2017-04-23 06:30 | 419 | 416
2017-04-23 07:00 | 423 | 420
2017-04-23 07:30 | 433 | 430
2017-04-23 08:00 | 440 | 438
2017-04-23 08:30 | 451 | 449
2017-04-23 09:00 | 464 | 462
2017-04-23 09:30 | 483 | 482
2017-04-23 10:00 | 489 | 488
2017-04-23 10:30 | 485 | 484
2017-04-23 11:00 | 486 | 485
2017-04-23 11:30 | 477 | 476
2017-04-23 12:00 | 478 | 477
2017-04-23 12:30 | 476 | 474
2017-04-23 13:00 | 473 | 472
2017-04-23 13:30 | 482 | 480
2017-04-23 14:00 | 471 | 470
2017-04-23 14:30 | 451 | 450
2017-04-23 15:00 | 449 | 448
2017-04-23 15:30 | 483 | 481
2017-04-23 16:00 | 496 | 495
2017-04-23 16:30 | 504 | 503
2017-04-23 17:00 | 501 | 500
2017-04-23 17:30 | 523 | 522
2017-04-23 18:00 | 543 | 543
2017-04-23 18:30 | 580 | 580
2017-04-23 19:00 | 592 | 592
2017-04-23 19:30 | 595 | 595
2017-04-23 20:00 | 602 | 602
2017-04-23 20:30 | 585 | 585
2017-04-23 21:00 | 570 | 570
2017-04-23 21:30 | 548 | 547
2017-04-23 22:00 | 526 | 525
2017-04-23 22:30 | 498 | 498
2017-04-23 23:00 | 482 | 481
2017-04-23 23:30 | 464 | 462
2017-04-24 | 448 | 446
2017-04-24 00:30 | 434 | 432
2017-04-24 01:00 | 423 | 421
2017-04-24 01:30 | 417 | 414
2017-04-24 02:00 | 411 | 408
2017-04-24 02:30 | 410 | 408
2017-04-24 03:00 | 410 | 407
2017-04-24 03:30 | 412 | 409
2017-04-24 04:00 | 415 | 412
2017-04-24 04:30 | 417 | 414
2017-04-24 05:00 | 424 | 421
2017-04-24 05:30 | 436 | 434
2017-04-24 06:00 | 453 | 451
2017-04-24 06:30 | 481 | 480
2017-04-24 07:00 | 516 | 515
2017-04-24 07:30 | 553 | 552
2017-04-24 08:00 | 570 | 569
2017-04-24 08:30 | 570 | 570
2017-04-24 09:00 | 567 | 566
2017-04-24 09:30 | 563 | 563
2017-04-24 10:00 | 557 | 557
2017-04-24 10:30 | 560 | 559
2017-04-24 11:00 | 559 | 558
2017-04-24 11:30 | 559 | 559
2017-04-24 12:00 | 566 | 565
2017-04-24 12:30 | 570 | 570
2017-04-24 13:00 | 566 | 566
2017-04-24 13:30 | 565 | 565
2017-04-24 14:00 | 565 | 565
2017-04-24 14:30 | 558 | 558
2017-04-24 15:00 | 558 | 558
2017-04-24 15:30 | 562 | 562
2017-04-24 16:00 | 573 | 572
2017-04-24 16:30 | 573 | 573
2017-04-24 17:00 | 571 | 571
2017-04-24 17:30 | 572 | 572
2017-04-24 18:00 | 581 | 581
2017-04-24 18:30 | 610 | 610
2017-04-24 19:00 | 638 | 638
2017-04-24 19:30 | 655 | 655
2017-04-24 20:00 | 640 | 640
2017-04-24 20:30 | 613 | 613
2017-04-24 21:00 | 592 | 592
2017-04-24 21:30 | 573 | 573
2017-04-24 22:00 | 554 | 554
2017-04-24 22:30 | 531 | 531
2017-04-24 23:00 | 511 | 510
2017-04-24 23:30 | 491 | 490
2017-04-25 | 474 | 473
2017-04-25 00:30 | 461 | 459
2017-04-25 01:00 | 446 | 444
2017-04-25 01:30 | 438 | 436
2017-04-25 02:00 | 429 | 427
2017-04-25 02:30 | 426 | 424
2017-04-25 03:00 | 418 | 416
2017-04-25 03:30 | 417 | 415
2017-04-25 04:00 | 421 | 419
2017-04-25 04:30 | 426 | 423
2017-04-25 05:00 | 427 | 424
2017-04-25 05:30 | 426 | 424
2017-04-25 06:00 | 429 | 426
2017-04-25 06:30 | 437 | 435
2017-04-25 07:00 | 446 | 444
2017-04-25 07:30 | 457 | 455
2017-04-25 08:00 | 460 | 458
2017-04-25 08:30 | 466 | 465
2017-04-25 09:00 | 470 | 468
2017-04-25 09:30 | 474 | 473
2017-04-25 10:00 | 472 | 471
2017-04-25 10:30 | 476 | 475
2017-04-25 11:00 | 475 | 473
2017-04-25 11:30 | 475 | 473
2017-04-25 12:00 | 480 | 479
2017-04-25 12:30 | 479 | 477
2017-04-25 13:00 | 477 | 476
2017-04-25 13:30 | 481 | 480
2017-04-25 14:00 | 483 | 482
2017-04-25 14:30 | 471 | 469
2017-04-25 15:00 | 473 | 472
2017-04-25 15:30 | 487 | 486
2017-04-25 16:00 | 502 | 500
2017-04-25 16:30 | 513 | 511
2017-04-25 17:00 | 515 | 514
2017-04-25 17:30 | 533 | 532
2017-04-25 18:00 | 555 | 555
2017-04-25 18:30 | 587 | 587
2017-04-25 19:00 | 625 | 625
2017-04-25 19:30 | 634 | 634
2017-04-25 20:00 | 620 | 620
2017-04-25 20:30 | 598 | 598
2017-04-25 21:00 | 579 | 579
2017-04-25 21:30 | 562 | 562
2017-04-25 22:00 | 543 | 542
2017-04-25 22:30 | 520 | 519
2017-04-25 23:00 | 501 | 500
2017-04-25 23:30 | 487 | 486
2017-04-26 | 467 | 466
2017-04-26 00:30 | 457 | 456
2017-04-26 01:00 | 440 | 438
2017-04-26 01:30 | 433 | 430
2017-04-26 02:00 | 425 | 423
2017-04-26 02:30 | 422 | 420
2017-04-26 03:00 | 423 | 420
2017-04-26 03:30 | 417 | 413
2017-04-26 04:00 | 419 | 415
2017-04-26 04:30 | 422 | 419
2017-04-26 05:00 | 426 | 423
2017-04-26 05:30 | 442 | 440
2017-04-26 06:00 | 462 | 460
2017-04-26 06:30 | 496 | 494
2017-04-26 07:00 | 530 | 529
2017-04-26 07:30 | 565 | 564
2017-04-26 08:00 | 584 | 584
2017-04-26 08:30 | 578 | 578
2017-04-26 09:00 | 570 | 570
2017-04-26 09:30 | 571 | 571
2017-04-26 10:00 | 568 | 568
2017-04-26 10:30 | 551 | 551
2017-04-26 11:00 | 509 | 508
2017-04-26 11:30 | 508 | 507
2017-04-26 12:00 | 521 | 520
2017-04-26 12:30 | 520 | 519
2017-04-26 13:00 | 528 | 528
2017-04-26 13:30 | 525 | 525
2017-04-26 14:00 | 516 | 516
2017-04-26 14:30 | 443 | 442
2017-04-26 15:00 | 445 | 444
2017-04-26 15:30 | 444 | 443
2017-04-26 16:00 | 462 | 461
2017-04-26 16:30 | 446 | 444
2017-04-26 17:00 | 375 | 373
2017-04-26 17:30 | 370 | 366
2017-04-26 18:00 | 391 | 387
2017-04-26 18:30 | 414 | 411
2017-04-26 19:00 | 422 | 420
2017-04-26 19:30 | 417 | 415
2017-04-26 20:00 | 414 | 411
2017-04-26 20:30 | 411 | 409
2017-04-26 21:00 | 411 | 408
2017-04-26 21:30 | 388 | 385
2017-04-26 22:00 | 436 | 433
2017-04-26 22:30 | 417 | 415
2017-04-26 23:00 | 392 | 390
2017-04-26 23:30 | 368 | 365
2017-04-27 | 352 | 348
2017-04-27 00:30 | 338 | 333
2017-04-27 01:00 | 332 | 327
2017-04-27 01:30 | 326 | 320
2017-04-27 02:00 | 315 | 309
2017-04-27 02:30 | 313 | 306
2017-04-27 03:00 | 308 | 301
2017-04-27 03:30 | 310 | 302
2017-04-27 04:00 | 307 | 299
2017-04-27 04:30 | 312 | 304
2017-04-27 05:00 | 314 | 306
2017-04-27 05:30 | 332 | 325
2017-04-27 06:00 | 348 | 341
2017-04-27 06:30 | 367 | 362
2017-04-27 07:00 | 369 | 364
2017-04-27 07:30 | 437 | 433
2017-04-27 08:00 | 459 | 457
2017-04-27 08:30 | 455 | 453
2017-04-27 09:00 | 452 | 450
2017-04-27 09:30 | 441 | 439
2017-04-27 10:00 | 432 | 430
2017-04-27 10:30 | 434 | 432
2017-04-27 11:00 | 437 | 434
2017-04-27 11:30 | 433 | 430
2017-04-27 12:00 | 434 | 432
2017-04-27 12:30 | 444 | 442
2017-04-27 13:00 | 451 | 448
2017-04-27 13:30 | 455 | 453
2017-04-27 14:00 | 461 | 459
2017-04-27 14:30 | 458 | 456
2017-04-27 15:00 | 455 | 453
2017-04-27 15:30 | 465 | 463
2017-04-27 16:00 | 476 | 475
2017-04-27 16:30 | 423 | 421
2017-04-27 17:00 | 393 | 391
2017-04-27 17:30 | 389 | 386
2017-04-27 18:00 | 387 | 383
2017-04-27 18:30 | 361 | 357
2017-04-27 19:00 | 432 | 428
2017-04-27 19:30 | 459 | 457
2017-04-27 20:00 | 444 | 442
2017-04-27 20:30 | 424 | 422
2017-04-27 21:00 | 411 | 408
2017-04-27 21:30 | 468 | 465
2017-04-27 22:00 | 448 | 446
2017-04-27 22:30 | 422 | 420
2017-04-27 23:00 | 392 | 389
2017-04-27 23:30 | 374 | 370
2017-04-28 | 357 | 353
2017-04-28 00:30 | 390 | 385
2017-04-28 01:00 | 455 | 452
2017-04-28 01:30 | 452 | 450
2017-04-28 02:00 | 442 | 439
2017-04-28 02:30 | 434 | 432
2017-04-28 03:00 | 435 | 432
2017-04-28 03:30 | 430 | 427
2017-04-28 04:00 | 428 | 425
2017-04-28 04:30 | 428 | 425
2017-04-28 05:00 | 430 | 427
2017-04-28 05:30 | 445 | 442
2017-04-28 06:00 | 460 | 458
2017-04-28 06:30 | 485 | 483
2017-04-28 07:00 | 491 | 489
2017-04-28 07:30 | 539 | 538
2017-04-28 08:00 | 553 | 552
2017-04-28 08:30 | 543 | 543
2017-04-28 09:00 | 529 | 528
2017-04-28 09:30 | 521 | 520
2017-04-28 10:00 | 508 | 507
2017-04-28 10:30 | 498 | 497
2017-04-28 11:00 | 494 | 493
2017-04-28 11:30 | 488 | 487
2017-04-28 12:00 | 490 | 489
2017-04-28 12:30 | 490 | 488
2017-04-28 13:00 | 498 | 496
2017-04-28 13:30 | 509 | 508
2017-04-28 14:00 | 511 | 510
2017-04-28 14:30 | 499 | 499
2017-04-28 15:00 | 498 | 498
2017-04-28 15:30 | 502 | 502
2017-04-28 16:00 | 514 | 514
2017-04-28 16:30 | 533 | 532
2017-04-28 17:00 | 550 | 549
2017-04-28 17:30 | 557 | 556
2017-04-28 18:00 | 561 | 561
2017-04-28 18:30 | 583 | 583
2017-04-28 19:00 | 593 | 593
2017-04-28 19:30 | 576 | 576
2017-04-28 20:00 | 557 | 557
2017-04-28 20:30 | 562 | 562
2017-04-28 21:00 | 550 | 550
2017-04-28 21:30 | 538 | 538
2017-04-28 22:00 | 521 | 521
2017-04-28 22:30 | 499 | 498
2017-04-28 23:00 | 480 | 479
2017-04-28 23:30 | 456 | 455
2017-04-29 | 444 | 442
2017-04-29 00:30 | 431 | 428
2017-04-29 01:00 | 420 | 417
2017-04-29 01:30 | 409 | 406
2017-04-29 02:00 | 406 | 402
2017-04-29 02:30 | 400 | 396
2017-04-29 03:00 | 397 | 392
2017-04-29 03:30 | 396 | 392
2017-04-29 04:00 | 395 | 391
2017-04-29 04:30 | 396 | 392
2017-04-29 05:00 | 396 | 391
2017-04-29 05:30 | 404 | 400
2017-04-29 06:00 | 407 | 403
2017-04-29 06:30 | 416 | 412
2017-04-29 07:00 | 427 | 424
2017-04-29 07:30 | 455 | 452
2017-04-29 08:00 | 465 | 463
2017-04-29 08:30 | 474 | 472
2017-04-29 09:00 | 474 | 473
2017-04-29 09:30 | 469 | 467
2017-04-29 10:00 | 463 | 461
2017-04-29 10:30 | 462 | 460
2017-04-29 11:00 | 460 | 458
2017-04-29 11:30 | 453 | 451
2017-04-29 12:00 | 446 | 444
2017-04-29 12:30 | 444 | 441
2017-04-29 13:00 | 445 | 443
2017-04-29 13:30 | 444 | 442
2017-04-29 14:00 | 441 | 438
2017-04-29 14:30 | 428 | 426
2017-04-29 15:00 | 425 | 423
2017-04-29 15:30 | 436 | 433
2017-04-29 16:00 | 455 | 453
2017-04-29 16:30 | 479 | 477
2017-04-29 17:00 | 505 | 503
2017-04-29 17:30 | 524 | 523
2017-04-29 18:00 | 546 | 545
2017-04-29 18:30 | 566 | 565
2017-04-29 19:00 | 573 | 573
2017-04-29 19:30 | 558 | 557
2017-04-29 20:00 | 539 | 538
2017-04-29 20:30 | 540 | 540
2017-04-29 21:00 | 531 | 531
2017-04-29 21:30 | 515 | 514
2017-04-29 22:00 | 495 | 494
2017-04-29 22:30 | 477 | 476
2017-04-29 23:00 | 467 | 466
2017-04-29 23:30 | 450 | 448
2017-04-30 | 433 | 431
2017-04-30 00:30 | 425 | 422
2017-04-30 01:00 | 417 | 413
2017-04-30 01:30 | 408 | 405
2017-04-30 02:00 | 406 | 402
2017-04-30 02:30 | 399 | 395
2017-04-30 03:00 | 400 | 396
2017-04-30 03:30 | 400 | 396
2017-04-30 04:00 | 398 | 394
2017-04-30 04:30 | 400 | 396
2017-04-30 05:00 | 397 | 394
2017-04-30 05:30 | 403 | 399
2017-04-30 06:00 | 409 | 405
2017-04-30 06:30 | 416 | 412
2017-04-30 07:00 | 423 | 420
2017-04-30 07:30 | 435 | 431
2017-04-30 08:00 | 440 | 437
2017-04-30 08:30 | 452 | 449
2017-04-30 09:00 | 458 | 456
2017-04-30 09:30 | 461 | 459
2017-04-30 10:00 | 456 | 454
2017-04-30 10:30 | 456 | 454
2017-04-30 11:00 | 454 | 452
2017-04-30 11:30 | 453 | 451
2017-04-30 12:00 | 457 | 455
2017-04-30 12:30 | 467 | 465
2017-04-30 13:00 | 476 | 474
2017-04-30 13:30 | 483 | 481
2017-04-30 14:00 | 488 | 486
2017-04-30 14:30 | 468 | 467
2017-04-30 15:00 | 464 | 463
2017-04-30 15:30 | 472 | 470
2017-04-30 16:00 | 479 | 478
2017-04-30 16:30 | 488 | 487
2017-04-30 17:00 | 505 | 504
2017-04-30 17:30 | 526 | 525
2017-04-30 18:00 | 529 | 529
2017-04-30 18:30 | 539 | 539
2017-04-30 19:00 | 589 | 589
2017-04-30 19:30 | 573 | 573
2017-04-30 20:00 | 554 | 554
2017-04-30 20:30 | 555 | 555
2017-04-30 21:00 | 548 | 548
2017-04-30 21:30 | 532 | 532
2017-04-30 22:00 | 518 | 518
2017-04-30 22:30 | 497 | 497
2017-04-30 23:00 | 483 | 482
2017-04-30 23:30 | 465 | 464
2017-05-01 | 449 | 448
2017-05-01 00:30 | 442 | 440
2017-05-01 01:00 | 432 | 429
2017-05-01 01:30 | 429 | 426
2017-05-01 02:00 | 424 | 422
2017-05-01 02:30 | 419 | 417
2017-05-01 03:00 | 413 | 410
2017-05-01 03:30 | 412 | 409
2017-05-01 04:00 | 405 | 402
2017-05-01 04:30 | 407 | 404
2017-05-01 05:00 | 412 | 409
2017-05-01 05:30 | 422 | 419
2017-05-01 06:00 | 423 | 421
2017-05-01 06:30 | 436 | 433
2017-05-01 07:00 | 439 | 437
2017-05-01 07:30 | 455 | 452
2017-05-01 08:00 | 465 | 463
2017-05-01 08:30 | 479 | 477
2017-05-01 09:00 | 482 | 480
2017-05-01 09:30 | 490 | 488
2017-05-01 10:00 | 498 | 496
2017-05-01 10:30 | 502 | 501
2017-05-01 11:00 | 494 | 493
2017-05-01 11:30 | 484 | 483
2017-05-01 12:00 | 478 | 477
2017-05-01 12:30 | 479 | 478
2017-05-01 13:00 | 485 | 484
2017-05-01 13:30 | 488 | 487
2017-05-01 14:00 | 485 | 484
2017-05-01 14:30 | 474 | 473
2017-05-01 15:00 | 475 | 473
2017-05-01 15:30 | 484 | 483
2017-05-01 16:00 | 497 | 496
2017-05-01 16:30 | 515 | 514
2017-05-01 17:00 | 532 | 531
2017-05-01 17:30 | 555 | 555
2017-05-01 18:00 | 571 | 571
2017-05-01 18:30 | 616 | 616
2017-05-01 19:00 | 619 | 619
2017-05-01 19:30 | 600 | 600
2017-05-01 20:00 | 581 | 580
2017-05-01 20:30 | 584 | 584
2017-05-01 21:00 | 567 | 567
2017-05-01 21:30 | 550 | 550
2017-05-01 22:00 | 529 | 529
2017-05-01 22:30 | 507 | 507
2017-05-01 23:00 | 486 | 486
2017-05-01 23:30 | 465 | 464
2017-05-02 | 451 | 450
2017-05-02 00:30 | 445 | 443
2017-05-02 01:00 | 432 | 431
2017-05-02 01:30 | 422 | 420
2017-05-02 02:00 | 416 | 414
2017-05-02 02:30 | 418 | 415
2017-05-02 03:00 | 415 | 412
2017-05-02 03:30 | 411 | 409
2017-05-02 04:00 | 405 | 402
2017-05-02 04:30 | 406 | 403
2017-05-02 05:00 | 413 | 410
2017-05-02 05:30 | 434 | 431
2017-05-02 06:00 | 451 | 449
2017-05-02 06:30 | 485 | 483
2017-05-02 07:00 | 480 | 478
2017-05-02 07:30 | 537 | 536
2017-05-02 08:00 | 569 | 569
2017-05-02 08:30 | 568 | 568
2017-05-02 09:00 | 561 | 561
2017-05-02 09:30 | 556 | 556
2017-05-02 10:00 | 555 | 554
2017-05-02 10:30 | 558 | 558
2017-05-02 11:00 | 559 | 559
2017-05-02 11:30 | 566 | 566
2017-05-02 12:00 | 567 | 567
2017-05-02 12:30 | 571 | 571
2017-05-02 13:00 | 571 | 571
2017-05-02 13:30 | 569 | 568
2017-05-02 14:00 | 571 | 571
2017-05-02 14:30 | 567 | 567
2017-05-02 15:00 | 564 | 563
2017-05-02 15:30 | 569 | 569
2017-05-02 16:00 | 584 | 583
2017-05-02 16:30 | 596 | 595
2017-05-02 17:00 | 605 | 605
2017-05-02 17:30 | 607 | 607
2017-05-02 18:00 | 574 | 574
2017-05-02 18:30 | 593 | 593
2017-05-02 19:00 | 632 | 632
2017-05-02 19:30 | 640 | 640
2017-05-02 20:00 | 619 | 619
2017-05-02 20:30 | 623 | 622
2017-05-02 21:00 | 604 | 604
2017-05-02 21:30 | 577 | 577
2017-05-02 22:00 | 554 | 554
2017-05-02 22:30 | 530 | 529
2017-05-02 23:00 | 502 | 501
2017-05-02 23:30 | 480 | 479
2017-05-03 | 458 | 456
2017-05-03 00:30 | 445 | 443
2017-05-03 01:00 | 435 | 432
2017-05-03 01:30 | 429 | 427
2017-05-03 02:00 | 421 | 418
2017-05-03 02:30 | 422 | 419
2017-05-03 03:00 | 421 | 418
2017-05-03 03:30 | 417 | 414
2017-05-03 04:00 | 419 | 416
2017-05-03 04:30 | 423 | 420
2017-05-03 05:00 | 428 | 425
2017-05-03 05:30 | 446 | 444
2017-05-03 06:00 | 469 | 467
2017-05-03 06:30 | 497 | 495
2017-05-03 07:00 | 477 | 476
2017-05-03 07:30 | 527 | 525
2017-05-03 08:00 | 577 | 576
2017-05-03 08:30 | 575 | 575
2017-05-03 09:00 | 568 | 568
2017-05-03 09:30 | 565 | 565
2017-05-03 10:00 | 560 | 560
2017-05-03 10:30 | 554 | 554
2017-05-03 11:00 | 508 | 508
2017-05-03 11:30 | 496 | 496
2017-05-03 12:00 | 496 | 495
2017-05-03 12:30 | 496 | 496
2017-05-03 13:00 | 511 | 510
2017-05-03 13:30 | 509 | 509
2017-05-03 14:00 | 509 | 508
2017-05-03 14:30 | 438 | 437
2017-05-03 15:00 | 423 | 421
2017-05-03 15:30 | 435 | 433
2017-05-03 16:00 | 444 | 442
2017-05-03 16:30 | 458 | 456
2017-05-03 17:00 | 472 | 471
2017-05-03 17:30 | 499 | 498
2017-05-03 18:00 | 404 | 403
2017-05-03 18:30 | 461 | 459
2017-05-03 19:00 | 557 | 556
2017-05-03 19:30 | 545 | 545
2017-05-03 20:00 | 523 | 523
2017-05-03 20:30 | 501 | 500
2017-05-03 21:00 | 478 | 477
2017-05-03 21:30 | 456 | 455
2017-05-03 22:00 | 440 | 438
2017-05-03 22:30 | 407 | 405
2017-05-03 23:00 | 380 | 377
2017-05-03 23:30 | 358 | 354
2017-05-04 | 343 | 339
2017-05-04 00:30 | 324 | 319
2017-05-04 01:00 | 315 | 309
2017-05-04 01:30 | 308 | 301
2017-05-04 02:00 | 306 | 297
2017-05-04 02:30 | 306 | 297
2017-05-04 03:00 | 301 | 292
2017-05-04 03:30 | 300 | 291
2017-05-04 04:00 | 307 | 298
2017-05-04 04:30 | 310 | 301
2017-05-04 05:00 | 312 | 304
2017-05-04 05:30 | 324 | 316
2017-05-04 06:00 | 338 | 330
2017-05-04 06:30 | 363 | 357
2017-05-04 07:00 | 366 | 361
2017-05-04 07:30 | 426 | 421
2017-05-04 08:00 | 447 | 445
2017-05-04 08:30 | 459 | 457
2017-05-04 09:00 | 450 | 448
2017-05-04 09:30 | 440 | 438
2017-05-04 10:00 | 429 | 427
2017-05-04 10:30 | 413 | 410
2017-05-04 11:00 | 410 | 407
2017-05-04 11:30 | 418 | 414
2017-05-04 12:00 | 423 | 420
2017-05-04 12:30 | 416 | 413
2017-05-04 13:00 | 423 | 420
2017-05-04 13:30 | 426 | 423
2017-05-04 14:00 | 426 | 424
2017-05-04 14:30 | 428 | 426
2017-05-04 15:00 | 444 | 442
2017-05-04 15:30 | 442 | 440
2017-05-04 16:00 | 451 | 449
2017-05-04 16:30 | 461 | 459
2017-05-04 17:00 | 474 | 473
2017-05-04 17:30 | 503 | 501
2017-05-04 18:00 | 436 | 435
2017-05-04 18:30 | 412 | 411
2017-05-04 19:00 | 451 | 449
2017-05-04 19:30 | 533 | 532
2017-05-04 20:00 | 519 | 519
2017-05-04 20:30 | 497 | 496
2017-05-04 21:00 | 481 | 480
2017-05-04 21:30 | 458 | 457
2017-05-04 22:00 | 430 | 428
2017-05-04 22:30 | 400 | 397
2017-05-04 23:00 | 383 | 379
2017-05-04 23:30 | 362 | 358
2017-05-05 | 351 | 346
2017-05-05 00:30 | 385 | 380
2017-05-05 01:00 | 451 | 448
2017-05-05 01:30 | 445 | 443
2017-05-05 02:00 | 435 | 433
2017-05-05 02:30 | 430 | 428
2017-05-05 03:00 | 432 | 430
2017-05-05 03:30 | 427 | 425
2017-05-05 04:00 | 429 | 427
2017-05-05 04:30 | 433 | 431
2017-05-05 05:00 | 446 | 444
2017-05-05 05:30 | 455 | 453
2017-05-05 06:00 | 472 | 471
2017-05-05 06:30 | 501 | 500
2017-05-05 07:00 | 535 | 534
2017-05-05 07:30 | 578 | 578
2017-05-05 08:00 | 596 | 596
2017-05-05 08:30 | 602 | 602
2017-05-05 09:00 | 593 | 593
2017-05-05 09:30 | 583 | 583
2017-05-05 10:00 | 577 | 576
2017-05-05 10:30 | 564 | 564
2017-05-05 11:00 | 570 | 569
2017-05-05 11:30 | 576 | 576
2017-05-05 12:00 | 573 | 573
2017-05-05 12:30 | 568 | 568
2017-05-05 13:00 | 580 | 580
2017-05-05 13:30 | 578 | 577
2017-05-05 14:00 | 591 | 590
2017-05-05 14:30 | 567 | 567
2017-05-05 15:00 | 553 | 553
2017-05-05 15:30 | 548 | 548
2017-05-05 16:00 | 557 | 556
2017-05-05 16:30 | 559 | 559
2017-05-05 17:00 | 573 | 573
2017-05-05 17:30 | 575 | 575
2017-05-05 18:00 | 588 | 588
2017-05-05 18:30 | 604 | 604
2017-05-05 19:00 | 603 | 603
2017-05-05 19:30 | 592 | 592
2017-05-05 20:00 | 575 | 574
2017-05-05 20:30 | 589 | 589
2017-05-05 21:00 | 577 | 576
2017-05-05 21:30 | 562 | 562
2017-05-05 22:00 | 541 | 541
2017-05-05 22:30 | 524 | 523
2017-05-05 23:00 | 508 | 507
2017-05-05 23:30 | 491 | 490
2017-05-06 | 470 | 469
2017-05-06 00:30 | 459 | 458
2017-05-06 01:00 | 447 | 446
2017-05-06 01:30 | 437 | 435
2017-05-06 02:00 | 430 | 428
2017-05-06 02:30 | 423 | 421
2017-05-06 03:00 | 420 | 418
2017-05-06 03:30 | 417 | 414
2017-05-06 04:00 | 415 | 413
2017-05-06 04:30 | 417 | 415
2017-05-06 05:00 | 418 | 416
2017-05-06 05:30 | 431 | 429
2017-05-06 06:00 | 441 | 439
2017-05-06 06:30 | 451 | 449
2017-05-06 07:00 | 461 | 460
2017-05-06 07:30 | 480 | 479
2017-05-06 08:00 | 506 | 505
2017-05-06 08:30 | 528 | 527
2017-05-06 09:00 | 541 | 540
2017-05-06 09:30 | 540 | 540
2017-05-06 10:00 | 541 | 541
2017-05-06 10:30 | 538 | 538
2017-05-06 11:00 | 526 | 525
2017-05-06 11:30 | 534 | 534
2017-05-06 12:00 | 526 | 526
2017-05-06 12:30 | 524 | 524
2017-05-06 13:00 | 518 | 518
2017-05-06 13:30 | 514 | 513
2017-05-06 14:00 | 511 | 511
2017-05-06 14:30 | 491 | 491
2017-05-06 15:00 | 501 | 501
2017-05-06 15:30 | 514 | 514
2017-05-06 16:00 | 527 | 527
2017-05-06 16:30 | 537 | 537
2017-05-06 17:00 | 553 | 552
2017-05-06 17:30 | 567 | 567
2017-05-06 18:00 | 581 | 581
2017-05-06 18:30 | 605 | 605
2017-05-06 19:00 | 604 | 604
2017-05-06 19:30 | 583 | 583
2017-05-06 20:00 | 574 | 574
2017-05-06 20:30 | 575 | 575
2017-05-06 21:00 | 562 | 562
2017-05-06 21:30 | 544 | 544
2017-05-06 22:00 | 531 | 531
2017-05-06 22:30 | 518 | 518
2017-05-06 23:00 | 502 | 502
2017-05-06 23:30 | 478 | 478
2017-05-07 | 463 | 462
2017-05-07 00:30 | 452 | 451
2017-05-07 01:00 | 447 | 445
2017-05-07 01:30 | 444 | 442
2017-05-07 02:00 | 435 | 433
2017-05-07 02:30 | 432 | 431
2017-05-07 03:00 | 428 | 426
2017-05-07 03:30 | 426 | 424
2017-05-07 04:00 | 425 | 423
2017-05-07 04:30 | 426 | 424
2017-05-07 05:00 | 426 | 424
2017-05-07 05:30 | 435 | 433
2017-05-07 06:00 | 431 | 430
2017-05-07 06:30 | 442 | 440
2017-05-07 07:00 | 450 | 449
2017-05-07 07:30 | 466 | 465
2017-05-07 08:00 | 481 | 480
2017-05-07 08:30 | 497 | 496
2017-05-07 09:00 | 502 | 501
2017-05-07 09:30 | 514 | 513
2017-05-07 10:00 | 514 | 514
2017-05-07 10:30 | 519 | 519
2017-05-07 11:00 | 513 | 513
2017-05-07 11:30 | 501 | 500
2017-05-07 12:00 | 504 | 503
2017-05-07 12:30 | 506 | 506
2017-05-07 13:00 | 509 | 509
2017-05-07 13:30 | 509 | 509
2017-05-07 14:00 | 491 | 491
2017-05-07 14:30 | 483 | 483
2017-05-07 15:00 | 486 | 486
2017-05-07 15:30 | 495 | 494
2017-05-07 16:00 | 509 | 508
2017-05-07 16:30 | 517 | 516
2017-05-07 17:00 | 534 | 534
2017-05-07 17:30 | 559 | 559
2017-05-07 18:00 | 590 | 590
2017-05-07 18:30 | 613 | 613
2017-05-07 19:00 | 611 | 611
2017-05-07 19:30 | 592 | 592
2017-05-07 20:00 | 572 | 572
2017-05-07 20:30 | 573 | 573
2017-05-07 21:00 | 560 | 560
2017-05-07 21:30 | 543 | 543
2017-05-07 22:00 | 521 | 521
2017-05-07 22:30 | 495 | 495
2017-05-07 23:00 | 476 | 475
2017-05-07 23:30 | 459 | 458
2017-05-08 | 445 | 443
2017-05-08 00:30 | 430 | 428
2017-05-08 01:00 | 424 | 422
2017-05-08 01:30 | 418 | 416
2017-05-08 02:00 | 410 | 407
2017-05-08 02:30 | 407 | 404
2017-05-08 03:00 | 405 | 402
2017-05-08 03:30 | 405 | 403
2017-05-08 04:00 | 404 | 402
2017-05-08 04:30 | 407 | 404
2017-05-08 05:00 | 415 | 412
2017-05-08 05:30 | 429 | 427
2017-05-08 06:00 | 452 | 450
2017-05-08 06:30 | 486 | 484
2017-05-08 07:00 | 504 | 503
2017-05-08 07:30 | 546 | 546
2017-05-08 08:00 | 567 | 567
2017-05-08 08:30 | 562 | 562
2017-05-08 09:00 | 549 | 549
2017-05-08 09:30 | 541 | 541
2017-05-08 10:00 | 533 | 533
2017-05-08 10:30 | 534 | 534
2017-05-08 11:00 | 529 | 529
2017-05-08 11:30 | 527 | 527
2017-05-08 12:00 | 525 | 525
2017-05-08 12:30 | 528 | 528
2017-05-08 13:00 | 544 | 543
2017-05-08 13:30 | 546 | 546
2017-05-08 14:00 | 547 | 547
2017-05-08 14:30 | 534 | 534
2017-05-08 15:00 | 540 | 540
2017-05-08 15:30 | 546 | 546
2017-05-08 16:00 | 559 | 559
2017-05-08 16:30 | 568 | 568
2017-05-08 17:00 | 575 | 575
2017-05-08 17:30 | 543 | 543
2017-05-08 18:00 | 538 | 538
2017-05-08 18:30 | 555 | 555
2017-05-08 19:00 | 577 | 577
2017-05-08 19:30 | 596 | 596
2017-05-08 20:00 | 585 | 585
2017-05-08 20:30 | 583 | 583
2017-05-08 21:00 | 582 | 582
2017-05-08 21:30 | 569 | 569
2017-05-08 22:00 | 541 | 541
2017-05-08 22:30 | 469 | 468
2017-05-08 23:00 | 459 | 458
2017-05-08 23:30 | 449 | 448
2017-05-09 | 434 | 433
2017-05-09 00:30 | 436 | 435
2017-05-09 01:00 | 428 | 426
2017-05-09 01:30 | 418 | 417
2017-05-09 02:00 | 411 | 409
2017-05-09 02:30 | 403 | 401
2017-05-09 03:00 | 407 | 404
2017-05-09 03:30 | 404 | 401
2017-05-09 04:00 | 406 | 403
2017-05-09 04:30 | 409 | 406
2017-05-09 05:00 | 416 | 414
2017-05-09 05:30 | 424 | 422
2017-05-09 06:00 | 429 | 427
2017-05-09 06:30 | 464 | 462
2017-05-09 07:00 | 467 | 466
2017-05-09 07:30 | 494 | 492
2017-05-09 08:00 | 504 | 503
2017-05-09 08:30 | 502 | 502
2017-05-09 09:00 | 539 | 538
2017-05-09 09:30 | 552 | 552
2017-05-09 10:00 | 545 | 545
2017-05-09 10:30 | 541 | 541
2017-05-09 11:00 | 529 | 528
2017-05-09 11:30 | 529 | 528
2017-05-09 12:00 | 537 | 536
2017-05-09 12:30 | 536 | 535
2017-05-09 13:00 | 536 | 535
2017-05-09 13:30 | 545 | 545
2017-05-09 14:00 | 555 | 555
2017-05-09 14:30 | 549 | 549
2017-05-09 15:00 | 551 | 550
2017-05-09 15:30 | 556 | 555
2017-05-09 16:00 | 571 | 571
2017-05-09 16:30 | 581 | 581
2017-05-09 17:00 | 587 | 587
2017-05-09 17:30 | 592 | 592
2017-05-09 18:00 | 554 | 554
2017-05-09 18:30 | 595 | 595
2017-05-09 19:00 | 621 | 621
2017-05-09 19:30 | 612 | 612
2017-05-09 20:00 | 576 | 576
2017-05-09 20:30 | 586 | 586
2017-05-09 21:00 | 589 | 588
2017-05-09 21:30 | 567 | 567
2017-05-09 22:00 | 544 | 544
2017-05-09 22:30 | 474 | 474
2017-05-09 23:00 | 438 | 437
2017-05-09 23:30 | 465 | 463
2017-05-10 | 444 | 443
2017-05-10 00:30 | 432 | 430
2017-05-10 01:00 | 422 | 420
2017-05-10 01:30 | 412 | 410
2017-05-10 02:00 | 411 | 409
2017-05-10 02:30 | 405 | 402
2017-05-10 03:00 | 401 | 399
2017-05-10 03:30 | 403 | 401
2017-05-10 04:00 | 400 | 397
2017-05-10 04:30 | 405 | 402
2017-05-10 05:00 | 413 | 410
2017-05-10 05:30 | 433 | 430
2017-05-10 06:00 | 442 | 440
2017-05-10 06:30 | 428 | 427
2017-05-10 07:00 | 449 | 447
2017-05-10 07:30 | 494 | 493
2017-05-10 08:00 | 486 | 485
2017-05-10 08:30 | 488 | 487
2017-05-10 09:00 | 498 | 497
2017-05-10 09:30 | 504 | 503
2017-05-10 10:00 | 486 | 486
2017-05-10 10:30 | 485 | 485
2017-05-10 11:00 | 454 | 453
2017-05-10 11:30 | 463 | 462
2017-05-10 12:00 | 475 | 474
2017-05-10 12:30 | 478 | 477
2017-05-10 13:00 | 484 | 483
2017-05-10 13:30 | 490 | 489
2017-05-10 14:00 | 479 | 478
2017-05-10 14:30 | 422 | 421
2017-05-10 15:00 | 390 | 388
2017-05-10 15:30 | 409 | 406
2017-05-10 16:00 | 417 | 414
2017-05-10 16:30 | 430 | 428
2017-05-10 17:00 | 361 | 359
2017-05-10 17:30 | 333 | 329
2017-05-10 18:00 | 316 | 311
2017-05-10 18:30 | 344 | 339
2017-05-10 19:00 | 349 | 344
2017-05-10 19:30 | 385 | 382
2017-05-10 20:00 | 369 | 366
2017-05-10 20:30 | 355 | 351
2017-05-10 21:00 | 386 | 382
2017-05-10 21:30 | 376 | 372
2017-05-10 22:00 | 373 | 369
2017-05-10 22:30 | 299 | 294
2017-05-10 23:00 | 333 | 327
2017-05-10 23:30 | 329 | 323
2017-05-11 | 311 | 305
2017-05-11 00:30 | 301 | 294
2017-05-11 01:00 | 290 | 282
2017-05-11 01:30 | 292 | 283
2017-05-11 02:00 | 281 | 273
2017-05-11 02:30 | 277 | 267
2017-05-11 03:00 | 275 | 265
2017-05-11 03:30 | 271 | 261
2017-05-11 04:00 | 274 | 264
2017-05-11 04:30 | 279 | 269
2017-05-11 05:00 | 283 | 274
2017-05-11 05:30 | 297 | 288
2017-05-11 06:00 | 317 | 310
2017-05-11 06:30 | 348 | 342
2017-05-11 07:00 | 375 | 371
2017-05-11 07:30 | 413 | 410
2017-05-11 08:00 | 422 | 419
2017-05-11 08:30 | 416 | 413
2017-05-11 09:00 | 400 | 398
2017-05-11 09:30 | 388 | 385
2017-05-11 10:00 | 373 | 369
2017-05-11 10:30 | 372 | 367
2017-05-11 11:00 | 368 | 363
2017-05-11 11:30 | 368 | 363
2017-05-11 12:00 | 369 | 364
2017-05-11 12:30 | 367 | 362
2017-05-11 13:00 | 366 | 361
2017-05-11 13:30 | 376 | 371
2017-05-11 14:00 | 386 | 382
2017-05-11 14:30 | 376 | 372
2017-05-11 15:00 | 369 | 365
2017-05-11 15:30 | 377 | 373
2017-05-11 16:00 | 397 | 393
2017-05-11 16:30 | 408 | 405
2017-05-11 17:00 | 409 | 406
2017-05-11 17:30 | 362 | 358
2017-05-11 18:00 | 320 | 315
2017-05-11 18:30 | 344 | 339
2017-05-11 19:00 | 351 | 347
2017-05-11 19:30 | 337 | 332
2017-05-11 20:00 | 319 | 313
2017-05-11 20:30 | 327 | 321
2017-05-11 21:00 | 408 | 403
2017-05-11 21:30 | 387 | 384
2017-05-11 22:00 | 358 | 354
2017-05-11 22:30 | 338 | 333
2017-05-11 23:00 | 319 | 313
2017-05-11 23:30 | 312 | 305
2017-05-12 | 306 | 298
2017-05-12 00:30 | 352 | 345
2017-05-12 01:00 | 418 | 413
2017-05-12 01:30 | 407 | 404
2017-05-12 02:00 | 404 | 400
2017-05-12 02:30 | 407 | 403
2017-05-12 03:00 | 410 | 407
2017-05-12 03:30 | 400 | 397
2017-05-12 04:00 | 365 | 361
2017-05-12 04:30 | 357 | 352
2017-05-12 05:00 | 362 | 358
2017-05-12 05:30 | 377 | 373
2017-05-12 06:00 | 392 | 389
2017-05-12 06:30 | 424 | 421
2017-05-12 07:00 | 490 | 488
2017-05-12 07:30 | 520 | 519
2017-05-12 08:00 | 507 | 507
2017-05-12 08:30 | 531 | 530
2017-05-12 09:00 | 536 | 536
2017-05-12 09:30 | 518 | 517
2017-05-12 10:00 | 493 | 493
2017-05-12 10:30 | 483 | 483
2017-05-12 11:00 | 516 | 516
2017-05-12 11:30 | 539 | 539
2017-05-12 12:00 | 540 | 540
2017-05-12 12:30 | 547 | 547
2017-05-12 13:00 | 549 | 549
2017-05-12 13:30 | 526 | 526
2017-05-12 14:00 | 539 | 539
2017-05-12 14:30 | 486 | 486
2017-05-12 15:00 | 474 | 473
2017-05-12 15:30 | 471 | 470
2017-05-12 16:00 | 476 | 475
2017-05-12 16:30 | 487 | 486
2017-05-12 17:00 | 498 | 497
2017-05-12 17:30 | 506 | 506
2017-05-12 18:00 | 519 | 518
2017-05-12 18:30 | 536 | 536
2017-05-12 19:00 | 538 | 538
2017-05-12 19:30 | 545 | 545
2017-05-12 20:00 | 555 | 555
2017-05-12 20:30 | 561 | 561
2017-05-12 21:00 | 552 | 552
2017-05-12 21:30 | 535 | 535
2017-05-12 22:00 | 517 | 517
2017-05-12 22:30 | 457 | 457
2017-05-12 23:00 | 471 | 470
2017-05-12 23:30 | 466 | 465
2017-05-13 | 453 | 452
2017-05-13 00:30 | 445 | 444
2017-05-13 01:00 | 431 | 430
2017-05-13 01:30 | 418 | 416
2017-05-13 02:00 | 410 | 409
2017-05-13 02:30 | 408 | 407
2017-05-13 03:00 | 407 | 405
2017-05-13 03:30 | 403 | 401
2017-05-13 04:00 | 402 | 400
2017-05-13 04:30 | 407 | 406
2017-05-13 05:00 | 408 | 406
2017-05-13 05:30 | 417 | 415
2017-05-13 06:00 | 419 | 418
2017-05-13 06:30 | 435 | 433
2017-05-13 07:00 | 451 | 450
2017-05-13 07:30 | 466 | 465
2017-05-13 08:00 | 448 | 447
2017-05-13 08:30 | 464 | 464
2017-05-13 09:00 | 468 | 468
2017-05-13 09:30 | 463 | 462
2017-05-13 10:00 | 457 | 456
2017-05-13 10:30 | 457 | 456
2017-05-13 11:00 | 453 | 453
2017-05-13 11:30 | 445 | 444
2017-05-13 12:00 | 484 | 484
2017-05-13 12:30 | 498 | 498
2017-05-13 13:00 | 482 | 481
2017-05-13 13:30 | 477 | 477
2017-05-13 14:00 | 478 | 477
2017-05-13 14:30 | 460 | 460
2017-05-13 15:00 | 462 | 461
2017-05-13 15:30 | 475 | 474
2017-05-13 16:00 | 475 | 474
2017-05-13 16:30 | 501 | 500
2017-05-13 17:00 | 480 | 479
2017-05-13 17:30 | 481 | 480
2017-05-13 18:00 | 499 | 499
2017-05-13 18:30 | 524 | 523
2017-05-13 19:00 | 525 | 525
2017-05-13 19:30 | 540 | 540
2017-05-13 20:00 | 541 | 541
2017-05-13 20:30 | 552 | 552
2017-05-13 21:00 | 544 | 544
2017-05-13 21:30 | 534 | 534
2017-05-13 22:00 | 514 | 514
2017-05-13 22:30 | 497 | 497
2017-05-13 23:00 | 482 | 481
2017-05-13 23:30 | 468 | 467
2017-05-14 | 451 | 450
2017-05-14 00:30 | 439 | 438
2017-05-14 01:00 | 429 | 428
2017-05-14 01:30 | 417 | 416
2017-05-14 02:00 | 411 | 409
2017-05-14 02:30 | 409 | 407
2017-05-14 03:00 | 404 | 402
2017-05-14 03:30 | 406 | 403
2017-05-14 04:00 | 407 | 405
2017-05-14 04:30 | 408 | 406
2017-05-14 05:00 | 407 | 406
2017-05-14 05:30 | 410 | 409
2017-05-14 06:00 | 416 | 414
2017-05-14 06:30 | 424 | 422
2017-05-14 07:00 | 431 | 429
2017-05-14 07:30 | 450 | 448
2017-05-14 08:00 | 461 | 460
2017-05-14 08:30 | 463 | 462
2017-05-14 09:00 | 460 | 459
2017-05-14 09:30 | 486 | 485
2017-05-14 10:00 | 482 | 481
2017-05-14 10:30 | 491 | 491
2017-05-14 11:00 | 491 | 490
2017-05-14 11:30 | 486 | 485
2017-05-14 12:00 | 481 | 480
2017-05-14 12:30 | 471 | 470
2017-05-14 13:00 | 444 | 443
2017-05-14 13:30 | 464 | 462
2017-05-14 14:00 | 468 | 467
2017-05-14 14:30 | 457 | 456
2017-05-14 15:00 | 460 | 459
2017-05-14 15:30 | 477 | 476
2017-05-14 16:00 | 493 | 492
2017-05-14 16:30 | 508 | 508
2017-05-14 17:00 | 528 | 527
2017-05-14 17:30 | 546 | 546
2017-05-14 18:00 | 527 | 527
2017-05-14 18:30 | 590 | 590
2017-05-14 19:00 | 607 | 607
2017-05-14 19:30 | 589 | 589
2017-05-14 20:00 | 567 | 567
2017-05-14 20:30 | 567 | 566
2017-05-14 21:00 | 556 | 556
2017-05-14 21:30 | 542 | 542
2017-05-14 22:00 | 517 | 517
2017-05-14 22:30 | 496 | 496
2017-05-14 23:00 | 475 | 475
2017-05-14 23:30 | 455 | 454
2017-05-15 | 444 | 443
2017-05-15 00:30 | 431 | 430
2017-05-15 01:00 | 424 | 423
2017-05-15 01:30 | 414 | 412
2017-05-15 02:00 | 410 | 408
2017-05-15 02:30 | 405 | 403
2017-05-15 03:00 | 407 | 404
2017-05-15 03:30 | 406 | 404
2017-05-15 04:00 | 406 | 404
2017-05-15 04:30 | 406 | 404
2017-05-15 05:00 | 415 | 413
2017-05-15 05:30 | 431 | 430
2017-05-15 06:00 | 448 | 446
2017-05-15 06:30 | 483 | 482
2017-05-15 07:00 | 476 | 475
2017-05-15 07:30 | 530 | 530
2017-05-15 08:00 | 513 | 513
2017-05-15 08:30 | 545 | 544
2017-05-15 09:00 | 551 | 551
2017-05-15 09:30 | 546 | 545
2017-05-15 10:00 | 547 | 547
2017-05-15 10:30 | 550 | 550
2017-05-15 11:00 | 524 | 524
2017-05-15 11:30 | 524 | 523
2017-05-15 12:00 | 524 | 523
2017-05-15 12:30 | 546 | 545
2017-05-15 13:00 | 555 | 555
2017-05-15 13:30 | 525 | 525
2017-05-15 14:00 | 537 | 537
2017-05-15 14:30 | 499 | 498
2017-05-15 15:00 | 530 | 530
2017-05-15 15:30 | 514 | 514
2017-05-15 16:00 | 547 | 547
2017-05-15 16:30 | 542 | 541
2017-05-15 17:00 | 538 | 538
2017-05-15 17:30 | 544 | 544
2017-05-15 18:00 | 557 | 557
2017-05-15 18:30 | 589 | 589
2017-05-15 19:00 | 618 | 618
2017-05-15 19:30 | 647 | 647
2017-05-15 20:00 | 632 | 632
2017-05-15 20:30 | 607 | 607
2017-05-15 21:00 | 582 | 582
2017-05-15 21:30 | 567 | 567
2017-05-15 22:00 | 539 | 538
2017-05-15 22:30 | 467 | 467
2017-05-15 23:00 | 477 | 475
2017-05-15 23:30 | 467 | 465
2017-05-16 | 449 | 447
2017-05-16 00:30 | 439 | 437
2017-05-16 01:00 | 430 | 428
2017-05-16 01:30 | 418 | 416
2017-05-16 02:00 | 413 | 410
2017-05-16 02:30 | 409 | 406
2017-05-16 03:00 | 409 | 406
2017-05-16 03:30 | 406 | 403
2017-05-16 04:00 | 408 | 405
2017-05-16 04:30 | 411 | 408
2017-05-16 05:00 | 415 | 412
2017-05-16 05:30 | 432 | 429
2017-05-16 06:00 | 453 | 451
2017-05-16 06:30 | 457 | 455
2017-05-16 07:00 | 442 | 440
2017-05-16 07:30 | 494 | 492
2017-05-16 08:00 | 504 | 503
2017-05-16 08:30 | 539 | 538
2017-05-16 09:00 | 544 | 543
2017-05-16 09:30 | 516 | 516
2017-05-16 10:00 | 532 | 532
2017-05-16 10:30 | 525 | 525
2017-05-16 11:00 | 523 | 523
2017-05-16 11:30 | 524 | 524
2017-05-16 12:00 | 532 | 532
2017-05-16 12:30 | 528 | 528
2017-05-16 13:00 | 533 | 533
2017-05-16 13:30 | 540 | 540
2017-05-16 14:00 | 542 | 541
2017-05-16 14:30 | 533 | 532
2017-05-16 15:00 | 532 | 532
2017-05-16 15:30 | 547 | 547
2017-05-16 16:00 | 537 | 537
2017-05-16 16:30 | 552 | 552
2017-05-16 17:00 | 571 | 571
2017-05-16 17:30 | 589 | 589
2017-05-16 18:00 | 553 | 553
2017-05-16 18:30 | 597 | 597
2017-05-16 19:00 | 617 | 617
2017-05-16 19:30 | 629 | 628
2017-05-16 20:00 | 622 | 622
2017-05-16 20:30 | 567 | 567
2017-05-16 21:00 | 536 | 536
2017-05-16 21:30 | 510 | 510
2017-05-16 22:00 | 514 | 514
2017-05-16 22:30 | 471 | 470
2017-05-16 23:00 | 436 | 435
2017-05-16 23:30 | 415 | 414
2017-05-17 | 430 | 428
2017-05-17 00:30 | 430 | 427
2017-05-17 01:00 | 423 | 420
2017-05-17 01:30 | 416 | 413
2017-05-17 02:00 | 413 | 409
2017-05-17 02:30 | 411 | 407
2017-05-17 03:00 | 409 | 405
2017-05-17 03:30 | 410 | 407
2017-05-17 04:00 | 410 | 406
2017-05-17 04:30 | 415 | 411
2017-05-17 05:00 | 424 | 421
2017-05-17 05:30 | 404 | 400
2017-05-17 06:00 | 409 | 406
2017-05-17 06:30 | 443 | 440
2017-05-17 07:00 | 471 | 469
2017-05-17 07:30 | 521 | 520
2017-05-17 08:00 | 519 | 519
2017-05-17 08:30 | 552 | 551
2017-05-17 09:00 | 549 | 549
2017-05-17 09:30 | 567 | 567
2017-05-17 10:00 | 570 | 570
2017-05-17 10:30 | 566 | 566
2017-05-17 11:00 | 515 | 515
2017-05-17 11:30 | 523 | 522
2017-05-17 12:00 | 507 | 507
2017-05-17 12:30 | 529 | 528
2017-05-17 13:00 | 525 | 525
2017-05-17 13:30 | 551 | 551
2017-05-17 14:00 | 536 | 536
2017-05-17 14:30 | 511 | 511
2017-05-17 15:00 | 514 | 514
2017-05-17 15:30 | 513 | 513
2017-05-17 16:00 | 522 | 522
2017-05-17 16:30 | 527 | 527
2017-05-17 17:00 | 517 | 517
2017-05-17 17:30 | 528 | 528
2017-05-17 18:00 | 574 | 574
2017-05-17 18:30 | 605 | 605
2017-05-17 19:00 | 610 | 610
2017-05-17 19:30 | 595 | 595
2017-05-17 20:00 | 577 | 577
2017-05-17 20:30 | 558 | 558
2017-05-17 21:00 | 535 | 535
2017-05-17 21:30 | 518 | 518
2017-05-17 22:00 | 492 | 492
2017-05-17 22:30 | 467 | 467
2017-05-17 23:00 | 444 | 444
2017-05-17 23:30 | 426 | 426
2017-05-18 | 410 | 410
2017-05-18 00:30 | 402 | 402
2017-05-18 01:00 | 384 | 383
2017-05-18 01:30 | 376 | 374
2017-05-18 02:00 | 370 | 368
2017-05-18 02:30 | 399 | 397
2017-05-18 03:00 | 403 | 401
2017-05-18 03:30 | 402 | 401
2017-05-18 04:00 | 399 | 398
2017-05-18 04:30 | 405 | 403
2017-05-18 05:00 | 410 | 409
2017-05-18 05:30 | 424 | 423
2017-05-18 06:00 | 406 | 405
2017-05-18 06:30 | 416 | 415
2017-05-18 07:00 | 449 | 448
2017-05-18 07:30 | 487 | 486
2017-05-18 08:00 | 523 | 522
2017-05-18 08:30 | 515 | 515
2017-05-18 09:00 | 512 | 512
2017-05-18 09:30 | 525 | 525
2017-05-18 10:00 | 530 | 530
2017-05-18 10:30 | 529 | 529
2017-05-18 11:00 | 527 | 527
2017-05-18 11:30 | 528 | 528
2017-05-18 12:00 | 523 | 523
2017-05-18 12:30 | 522 | 522
2017-05-18 13:00 | 522 | 522
2017-05-18 13:30 | 526 | 526
2017-05-18 14:00 | 537 | 537
2017-05-18 14:30 | 523 | 523
2017-05-18 15:00 | 501 | 501
2017-05-18 15:30 | 502 | 502
2017-05-18 16:00 | 502 | 502
2017-05-18 16:30 | 492 | 492
2017-05-18 17:00 | 494 | 494
2017-05-18 17:30 | 505 | 505
2017-05-18 18:00 | 543 | 543
2017-05-18 18:30 | 572 | 572
2017-05-18 19:00 | 574 | 574
2017-05-18 19:30 | 553 | 553
2017-05-18 20:00 | 534 | 534
2017-05-18 20:30 | 554 | 554
2017-05-18 21:00 | 557 | 557
2017-05-18 21:30 | 537 | 537
2017-05-18 22:00 | 512 | 512
2017-05-18 22:30 | 491 | 491
2017-05-18 23:00 | 417 | 417
2017-05-18 23:30 | 397 | 396
2017-05-19 | 412 | 410
2017-05-19 00:30 | 425 | 423
2017-05-19 01:00 | 415 | 413
2017-05-19 01:30 | 404 | 403
2017-05-19 02:00 | 402 | 401
2017-05-19 02:30 | 401 | 399
2017-05-19 03:00 | 399 | 397
2017-05-19 03:30 | 393 | 392
2017-05-19 04:00 | 392 | 390
2017-05-19 04:30 | 400 | 398
2017-05-19 05:00 | 403 | 402
2017-05-19 05:30 | 411 | 410
2017-05-19 06:00 | 430 | 429
2017-05-19 06:30 | 433 | 432
2017-05-19 07:00 | 466 | 465
2017-05-19 07:30 | 526 | 526
2017-05-19 08:00 | 542 | 542
2017-05-19 08:30 | 549 | 549
2017-05-19 09:00 | 549 | 549
2017-05-19 09:30 | 542 | 542
2017-05-19 10:00 | 537 | 537
2017-05-19 10:30 | 531 | 531
2017-05-19 11:00 | 521 | 521
2017-05-19 11:30 | 445 | 445
2017-05-19 12:00 | 417 | 416
2017-05-19 12:30 | 418 | 418
2017-05-19 13:00 | 423 | 423
2017-05-19 13:30 | 482 | 482
2017-05-19 14:00 | 493 | 493
2017-05-19 14:30 | 473 | 472
2017-05-19 15:00 | 467 | 467
2017-05-19 15:30 | 461 | 460
2017-05-19 16:00 | 451 | 451
2017-05-19 16:30 | 461 | 461
2017-05-19 17:00 | 468 | 467
2017-05-19 17:30 | 473 | 473
2017-05-19 18:00 | 494 | 493
2017-05-19 18:30 | 515 | 515
2017-05-19 19:00 | 530 | 530
2017-05-19 19:30 | 525 | 525
2017-05-19 20:00 | 505 | 505
2017-05-19 20:30 | 511 | 511
2017-05-19 21:00 | 495 | 495
2017-05-19 21:30 | 473 | 473
2017-05-19 22:00 | 469 | 469
2017-05-19 22:30 | 430 | 430
2017-05-19 23:00 | 403 | 403
2017-05-19 23:30 | 388 | 387
2017-05-20 | 382 | 381
2017-05-20 00:30 | 382 | 380
2017-05-20 01:00 | 377 | 375
2017-05-20 01:30 | 377 | 375
2017-05-20 02:00 | 371 | 369
2017-05-20 02:30 | 364 | 363
2017-05-20 03:00 | 362 | 360
2017-05-20 03:30 | 360 | 358
2017-05-20 04:00 | 350 | 348
2017-05-20 04:30 | 326 | 323
2017-05-20 05:00 | 330 | 327
2017-05-20 05:30 | 333 | 330
2017-05-20 06:00 | 337 | 334
2017-05-20 06:30 | 351 | 349
2017-05-20 07:00 | 364 | 362
2017-05-20 07:30 | 384 | 382
2017-05-20 08:00 | 397 | 396
2017-05-20 08:30 | 426 | 425
2017-05-20 09:00 | 435 | 434
2017-05-20 09:30 | 434 | 433
2017-05-20 10:00 | 427 | 426
2017-05-20 10:30 | 427 | 426
2017-05-20 11:00 | 421 | 420
2017-05-20 11:30 | 409 | 408
2017-05-20 12:00 | 410 | 409
2017-05-20 12:30 | 404 | 403
2017-05-20 13:00 | 409 | 407
2017-05-20 13:30 | 403 | 402
2017-05-20 14:00 | 402 | 401
2017-05-20 14:30 | 391 | 390
2017-05-20 15:00 | 395 | 394
2017-05-20 15:30 | 398 | 397
2017-05-20 16:00 | 409 | 408
2017-05-20 16:30 | 427 | 426
2017-05-20 17:00 | 448 | 447
2017-05-20 17:30 | 458 | 457
2017-05-20 18:00 | 476 | 475
2017-05-20 18:30 | 506 | 506
2017-05-20 19:00 | 511 | 511
2017-05-20 19:30 | 492 | 492
2017-05-20 20:00 | 474 | 474
2017-05-20 20:30 | 477 | 477
2017-05-20 21:00 | 473 | 472
2017-05-20 21:30 | 457 | 457
2017-05-20 22:00 | 440 | 440
2017-05-20 22:30 | 419 | 418
2017-05-20 23:00 | 402 | 401
2017-05-20 23:30 | 385 | 384
2017-05-21 | 378 | 377
2017-05-21 00:30 | 367 | 366
2017-05-21 01:00 | 352 | 350
2017-05-21 01:30 | 344 | 341
2017-05-21 02:00 | 334 | 331
2017-05-21 02:30 | 328 | 326
2017-05-21 03:00 | 322 | 319
2017-05-21 03:30 | 325 | 322
2017-05-21 04:00 | 328 | 323
2017-05-21 04:30 | 332 | 327
2017-05-21 05:00 | 333 | 329
2017-05-21 05:30 | 336 | 331
2017-05-21 06:00 | 335 | 331
2017-05-21 06:30 | 348 | 344
2017-05-21 07:00 | 351 | 347
2017-05-21 07:30 | 368 | 364
2017-05-21 08:00 | 380 | 377
2017-05-21 08:30 | 393 | 390
2017-05-21 09:00 | 398 | 396
2017-05-21 09:30 | 401 | 400
2017-05-21 10:00 | 404 | 403
2017-05-21 10:30 | 409 | 407
2017-05-21 11:00 | 403 | 401
2017-05-21 11:30 | 398 | 397
2017-05-21 12:00 | 397 | 395
2017-05-21 12:30 | 401 | 399
2017-05-21 13:00 | 400 | 398
2017-05-21 13:30 | 392 | 390
2017-05-21 14:00 | 395 | 392
2017-05-21 14:30 | 383 | 381
2017-05-21 15:00 | 389 | 386
2017-05-21 15:30 | 399 | 397
2017-05-21 16:00 | 414 | 412
2017-05-21 16:30 | 427 | 426
2017-05-21 17:00 | 450 | 449
2017-05-21 17:30 | 472 | 471
2017-05-21 18:00 | 503 | 502
2017-05-21 18:30 | 531 | 531
2017-05-21 19:00 | 539 | 539
2017-05-21 19:30 | 515 | 515
2017-05-21 20:00 | 492 | 491
2017-05-21 20:30 | 492 | 492
2017-05-21 21:00 | 479 | 478
2017-05-21 21:30 | 458 | 458
2017-05-21 22:00 | 440 | 439
2017-05-21 22:30 | 414 | 413
2017-05-21 23:00 | 395 | 393
2017-05-21 23:30 | 380 | 377
2017-05-22 | 361 | 358
2017-05-22 00:30 | 355 | 352
2017-05-22 01:00 | 346 | 343
2017-05-22 01:30 | 337 | 334
2017-05-22 02:00 | 331 | 327
2017-05-22 02:30 | 328 | 324
2017-05-22 03:00 | 327 | 323
2017-05-22 03:30 | 331 | 327
2017-05-22 04:00 | 335 | 330
2017-05-22 04:30 | 341 | 337
2017-05-22 05:00 | 347 | 343
2017-05-22 05:30 | 357 | 353
2017-05-22 06:00 | 370 | 368
2017-05-22 06:30 | 408 | 406
2017-05-22 07:00 | 445 | 443
2017-05-22 07:30 | 481 | 480
2017-05-22 08:00 | 496 | 496
2017-05-22 08:30 | 490 | 489
2017-05-22 09:00 | 482 | 481
2017-05-22 09:30 | 470 | 470
2017-05-22 10:00 | 466 | 465
2017-05-22 10:30 | 461 | 460
2017-05-22 11:00 | 456 | 455
2017-05-22 11:30 | 451 | 451
2017-05-22 12:00 | 460 | 460
2017-05-22 12:30 | 473 | 472
2017-05-22 13:00 | 470 | 470
2017-05-22 13:30 | 476 | 476
2017-05-22 14:00 | 485 | 484
2017-05-22 14:30 | 475 | 475
2017-05-22 15:00 | 481 | 481
2017-05-22 15:30 | 485 | 485
2017-05-22 16:00 | 492 | 492
2017-05-22 16:30 | 507 | 506
2017-05-22 17:00 | 515 | 515
2017-05-22 17:30 | 524 | 524
2017-05-22 18:00 | 540 | 540
2017-05-22 18:30 | 565 | 565
2017-05-22 19:00 | 572 | 572
2017-05-22 19:30 | 550 | 549
2017-05-22 20:00 | 532 | 532
2017-05-22 20:30 | 528 | 528
2017-05-22 21:00 | 511 | 511
2017-05-22 21:30 | 499 | 499
2017-05-22 22:00 | 479 | 479
2017-05-22 22:30 | 450 | 450
2017-05-22 23:00 | 430 | 429
2017-05-22 23:30 | 416 | 415
2017-05-23 | 405 | 403
2017-05-23 00:30 | 398 | 397
2017-05-23 01:00 | 389 | 387
2017-05-23 01:30 | 390 | 389
2017-05-23 02:00 | 391 | 389
2017-05-23 02:30 | 384 | 382
2017-05-23 03:00 | 385 | 382
2017-05-23 03:30 | 389 | 387
2017-05-23 04:00 | 389 | 387
2017-05-23 04:30 | 393 | 392
2017-05-23 05:00 | 401 | 400
2017-05-23 05:30 | 418 | 416
2017-05-23 06:00 | 439 | 437
2017-05-23 06:30 | 475 | 474
2017-05-23 07:00 | 472 | 472
2017-05-23 07:30 | 537 | 537
2017-05-23 08:00 | 570 | 569
2017-05-23 08:30 | 574 | 574
2017-05-23 09:00 | 566 | 566
2017-05-23 09:30 | 555 | 555
2017-05-23 10:00 | 552 | 552
2017-05-23 10:30 | 540 | 540
2017-05-23 11:00 | 496 | 496
2017-05-23 11:30 | 481 | 481
2017-05-23 12:00 | 480 | 479
2017-05-23 12:30 | 476 | 476
2017-05-23 13:00 | 481 | 481
2017-05-23 13:30 | 488 | 487
2017-05-23 14:00 | 494 | 494
2017-05-23 14:30 | 447 | 447
2017-05-23 15:00 | 404 | 403
2017-05-23 15:30 | 420 | 418
2017-05-23 16:00 | 427 | 426
2017-05-23 16:30 | 429 | 428
2017-05-23 17:00 | 442 | 441
2017-05-23 17:30 | 389 | 388
2017-05-23 18:00 | 368 | 366
2017-05-23 18:30 | 395 | 392
2017-05-23 19:00 | 403 | 402
2017-05-23 19:30 | 453 | 451
2017-05-23 20:00 | 446 | 445
2017-05-23 20:30 | 447 | 446
2017-05-23 21:00 | 403 | 402
2017-05-23 21:30 | 417 | 415
2017-05-23 22:00 | 390 | 389
2017-05-23 22:30 | 364 | 362
2017-05-23 23:00 | 337 | 334
2017-05-23 23:30 | 311 | 307
2017-05-24 | 290 | 286
2017-05-24 00:30 | 280 | 275
2017-05-24 01:00 | 271 | 265
2017-05-24 01:30 | 266 | 260
2017-05-24 02:00 | 260 | 254
2017-05-24 02:30 | 255 | 247
2017-05-24 03:00 | 253 | 244
2017-05-24 03:30 | 253 | 244
2017-05-24 04:00 | 251 | 243
2017-05-24 04:30 | 252 | 243
2017-05-24 05:00 | 259 | 251
2017-05-24 05:30 | 277 | 270
2017-05-24 06:00 | 295 | 288
2017-05-24 06:30 | 331 | 325
2017-05-24 07:00 | 362 | 359
2017-05-24 07:30 | 401 | 398
2017-05-24 08:00 | 403 | 401
2017-05-24 08:30 | 391 | 389
2017-05-24 09:00 | 399 | 397
2017-05-24 09:30 | 395 | 393
2017-05-24 10:00 | 391 | 389
2017-05-24 10:30 | 386 | 384
2017-05-24 11:00 | 379 | 377
2017-05-24 11:30 | 373 | 371
2017-05-24 12:00 | 376 | 375
2017-05-24 12:30 | 385 | 383
2017-05-24 13:00 | 393 | 391
2017-05-24 13:30 | 392 | 391
2017-05-24 14:00 | 392 | 391
2017-05-24 14:30 | 379 | 378
2017-05-24 15:00 | 382 | 380
2017-05-24 15:30 | 382 | 380
2017-05-24 16:00 | 386 | 384
2017-05-24 16:30 | 398 | 397
2017-05-24 17:00 | 398 | 397
2017-05-24 17:30 | 372 | 370
2017-05-24 18:00 | 346 | 345
2017-05-24 18:30 | 437 | 436
2017-05-24 19:00 | 435 | 434
2017-05-24 19:30 | 466 | 465
2017-05-24 20:00 | 454 | 453
2017-05-24 20:30 | 430 | 430
2017-05-24 21:00 | 411 | 410
2017-05-24 21:30 | 395 | 394
2017-05-24 22:00 | 374 | 373
2017-05-24 22:30 | 317 | 314
2017-05-24 23:00 | 270 | 267
2017-05-24 23:30 | 283 | 278
2017-05-25 | 284 | 279
2017-05-25 00:30 | 321 | 317
2017-05-25 01:00 | 389 | 386
2017-05-25 01:30 | 380 | 378
2017-05-25 02:00 | 375 | 373
2017-05-25 02:30 | 371 | 369
2017-05-25 03:00 | 372 | 370
2017-05-25 03:30 | 374 | 371
2017-05-25 04:00 | 372 | 370
2017-05-25 04:30 | 374 | 372
2017-05-25 05:00 | 380 | 378
2017-05-25 05:30 | 391 | 389
2017-05-25 06:00 | 415 | 413
2017-05-25 06:30 | 419 | 417
2017-05-25 07:00 | 434 | 433
2017-05-25 07:30 | 469 | 468
2017-05-25 08:00 | 480 | 480
2017-05-25 08:30 | 507 | 507
2017-05-25 09:00 | 513 | 512
2017-05-25 09:30 | 497 | 496
2017-05-25 10:00 | 485 | 484
2017-05-25 10:30 | 482 | 482
2017-05-25 11:00 | 483 | 482
2017-05-25 11:30 | 478 | 477
2017-05-25 12:00 | 477 | 477
2017-05-25 12:30 | 481 | 480
2017-05-25 13:00 | 491 | 490
2017-05-25 13:30 | 502 | 502
2017-05-25 14:00 | 504 | 504
2017-05-25 14:30 | 488 | 488
2017-05-25 15:00 | 488 | 488
2017-05-25 15:30 | 498 | 497
2017-05-25 16:00 | 514 | 514
2017-05-25 16:30 | 526 | 526
2017-05-25 17:00 | 542 | 542
2017-05-25 17:30 | 511 | 511
2017-05-25 18:00 | 514 | 514
2017-05-25 18:30 | 543 | 543
2017-05-25 19:00 | 554 | 554
2017-05-25 19:30 | 561 | 561
2017-05-25 20:00 | 546 | 546
2017-05-25 20:30 | 530 | 530
2017-05-25 21:00 | 505 | 505
2017-05-25 21:30 | 481 | 481
2017-05-25 22:00 | 458 | 458
2017-05-25 22:30 | 428 | 427
2017-05-25 23:00 | 410 | 409
2017-05-25 23:30 | 388 | 387
2017-05-26 | 369 | 368
2017-05-26 00:30 | 362 | 359
2017-05-26 01:00 | 353 | 350
2017-05-26 01:30 | 347 | 344
2017-05-26 02:00 | 378 | 375
2017-05-26 02:30 | 373 | 371
2017-05-26 03:00 | 372 | 369
2017-05-26 03:30 | 366 | 364
2017-05-26 04:00 | 376 | 373
2017-05-26 04:30 | 379 | 377
2017-05-26 05:00 | 387 | 384
2017-05-26 05:30 | 396 | 394
2017-05-26 06:00 | 420 | 418
2017-05-26 06:30 | 420 | 419
2017-05-26 07:00 | 442 | 441
2017-05-26 07:30 | 477 | 476
2017-05-26 08:00 | 482 | 482
2017-05-26 08:30 | 515 | 515
2017-05-26 09:00 | 518 | 518
2017-05-26 09:30 | 513 | 513
2017-05-26 10:00 | 507 | 507
2017-05-26 10:30 | 507 | 507
2017-05-26 11:00 | 504 | 504
2017-05-26 11:30 | 503 | 503
2017-05-26 12:00 | 507 | 507
2017-05-26 12:30 | 511 | 511
2017-05-26 13:00 | 508 | 508
2017-05-26 13:30 | 503 | 503
2017-05-26 14:00 | 500 | 500
2017-05-26 14:30 | 492 | 492
2017-05-26 15:00 | 488 | 488
2017-05-26 15:30 | 494 | 494
2017-05-26 16:00 | 507 | 507
2017-05-26 16:30 | 520 | 520
2017-05-26 17:00 | 530 | 530
2017-05-26 17:30 | 496 | 496
2017-05-26 18:00 | 496 | 496
2017-05-26 18:30 | 558 | 558
2017-05-26 19:00 | 598 | 598
2017-05-26 19:30 | 588 | 588
2017-05-26 20:00 | 570 | 570
2017-05-26 20:30 | 553 | 553
2017-05-26 21:00 | 540 | 540
2017-05-26 21:30 | 521 | 521
2017-05-26 22:00 | 505 | 505
2017-05-26 22:30 | 486 | 486
2017-05-26 23:00 | 468 | 468
2017-05-26 23:30 | 449 | 449
2017-05-27 | 432 | 431
2017-05-27 00:30 | 415 | 414
2017-05-27 01:00 | 406 | 405
2017-05-27 01:30 | 401 | 400
2017-05-27 02:00 | 395 | 393
2017-05-27 02:30 | 394 | 393
2017-05-27 03:00 | 389 | 387
2017-05-27 03:30 | 387 | 385
2017-05-27 04:00 | 390 | 388
2017-05-27 04:30 | 390 | 389
2017-05-27 05:00 | 391 | 389
2017-05-27 05:30 | 396 | 394
2017-05-27 06:00 | 407 | 405
2017-05-27 06:30 | 426 | 425
2017-05-27 07:00 | 437 | 436
2017-05-27 07:30 | 458 | 458
2017-05-27 08:00 | 474 | 474
2017-05-27 08:30 | 497 | 497
2017-05-27 09:00 | 494 | 494
2017-05-27 09:30 | 489 | 489
2017-05-27 10:00 | 485 | 485
2017-05-27 10:30 | 478 | 478
2017-05-27 11:00 | 477 | 477
2017-05-27 11:30 | 473 | 473
2017-05-27 12:00 | 469 | 469
2017-05-27 12:30 | 466 | 466
2017-05-27 13:00 | 465 | 465
2017-05-27 13:30 | 470 | 470
2017-05-27 14:00 | 470 | 470
2017-05-27 14:30 | 454 | 454
2017-05-27 15:00 | 451 | 450
2017-05-27 15:30 | 465 | 465
2017-05-27 16:00 | 478 | 478
2017-05-27 16:30 | 497 | 496
2017-05-27 17:00 | 512 | 512
2017-05-27 17:30 | 531 | 531
2017-05-27 18:00 | 533 | 533
2017-05-27 18:30 | 523 | 523
2017-05-27 19:00 | 568 | 568
2017-05-27 19:30 | 556 | 556
2017-05-27 20:00 | 535 | 535
2017-05-27 20:30 | 541 | 541
2017-05-27 21:00 | 533 | 533
2017-05-27 21:30 | 523 | 523
2017-05-27 22:00 | 513 | 513
2017-05-27 22:30 | 495 | 495
2017-05-27 23:00 | 478 | 478
2017-05-27 23:30 | 463 | 463
2017-05-28 | 451 | 451
2017-05-28 00:30 | 440 | 440
2017-05-28 01:00 | 432 | 431
2017-05-28 01:30 | 422 | 421
2017-05-28 02:00 | 416 | 415
2017-05-28 02:30 | 410 | 409
2017-05-28 03:00 | 407 | 406
2017-05-28 03:30 | 405 | 404
2017-05-28 04:00 | 403 | 402
2017-05-28 04:30 | 404 | 403
2017-05-28 05:00 | 403 | 402
2017-05-28 05:30 | 405 | 404
2017-05-28 06:00 | 409 | 409
2017-05-28 06:30 | 422 | 421
2017-05-28 07:00 | 429 | 428
2017-05-28 07:30 | 441 | 440
2017-05-28 08:00 | 453 | 452
2017-05-28 08:30 | 464 | 464
2017-05-28 09:00 | 469 | 468
2017-05-28 09:30 | 475 | 475
2017-05-28 10:00 | 474 | 474
2017-05-28 10:30 | 478 | 478
2017-05-28 11:00 | 474 | 474
2017-05-28 11:30 | 468 | 467
2017-05-28 12:00 | 468 | 468
2017-05-28 12:30 | 465 | 465
2017-05-28 13:00 | 467 | 467
2017-05-28 13:30 | 462 | 462
2017-05-28 14:00 | 459 | 458
2017-05-28 14:30 | 446 | 446
2017-05-28 15:00 | 448 | 448
2017-05-28 15:30 | 461 | 461
2017-05-28 16:00 | 486 | 486
2017-05-28 16:30 | 499 | 499
2017-05-28 17:00 | 513 | 513
2017-05-28 17:30 | 536 | 536
2017-05-28 18:00 | 574 | 574
2017-05-28 18:30 | 611 | 611
2017-05-28 19:00 | 633 | 632
2017-05-28 19:30 | 614 | 613
2017-05-28 20:00 | 587 | 586
2017-05-28 20:30 | 566 | 566
2017-05-28 21:00 | 545 | 545
2017-05-28 21:30 | 526 | 526
2017-05-28 22:00 | 508 | 508
2017-05-28 22:30 | 482 | 482
2017-05-28 23:00 | 464 | 463
2017-05-28 23:30 | 443 | 443
2017-05-29 | 429 | 428
2017-05-29 00:30 | 424 | 423
2017-05-29 01:00 | 412 | 411
2017-05-29 01:30 | 401 | 400
2017-05-29 02:00 | 404 | 402
2017-05-29 02:30 | 400 | 399
2017-05-29 03:00 | 399 | 397
2017-05-29 03:30 | 399 | 398
2017-05-29 04:00 | 402 | 400
2017-05-29 04:30 | 404 | 403
2017-05-29 05:00 | 408 | 406
2017-05-29 05:30 | 421 | 420
2017-05-29 06:00 | 442 | 442
2017-05-29 06:30 | 478 | 477
2017-05-29 07:00 | 459 | 459
2017-05-29 07:30 | 534 | 533
2017-05-29 08:00 | 557 | 557
2017-05-29 08:30 | 550 | 550
2017-05-29 09:00 | 542 | 542
2017-05-29 09:30 | 539 | 539
2017-05-29 10:00 | 523 | 523
2017-05-29 10:30 | 529 | 529
2017-05-29 11:00 | 523 | 523
2017-05-29 11:30 | 523 | 523
2017-05-29 12:00 | 514 | 514
2017-05-29 12:30 | 520 | 520
2017-05-29 13:00 | 530 | 530
2017-05-29 13:30 | 532 | 532
2017-05-29 14:00 | 532 | 532
2017-05-29 14:30 | 513 | 513
2017-05-29 15:00 | 520 | 520
2017-05-29 15:30 | 524 | 524
2017-05-29 16:00 | 538 | 538
2017-05-29 16:30 | 556 | 556
2017-05-29 17:00 | 550 | 550
2017-05-29 17:30 | 531 | 531
2017-05-29 18:00 | 553 | 553
2017-05-29 18:30 | 586 | 586
2017-05-29 19:00 | 610 | 610
2017-05-29 19:30 | 614 | 614
2017-05-29 20:00 | 606 | 606
2017-05-29 20:30 | 580 | 580
2017-05-29 21:00 | 558 | 558
2017-05-29 21:30 | 535 | 535
2017-05-29 22:00 | 511 | 511
2017-05-29 22:30 | 483 | 483
2017-05-29 23:00 | 460 | 460
2017-05-29 23:30 | 444 | 444
2017-05-30 | 429 | 427
2017-05-30 00:30 | 418 | 417
2017-05-30 01:00 | 407 | 406
2017-05-30 01:30 | 403 | 401
2017-05-30 02:00 | 396 | 394
2017-05-30 02:30 | 394 | 392
2017-05-30 03:00 | 389 | 387
2017-05-30 03:30 | 375 | 373
2017-05-30 04:00 | 323 | 320
2017-05-30 04:30 | 375 | 371
2017-05-30 05:00 | 397 | 394
2017-05-30 05:30 | 415 | 413
2017-05-30 06:00 | 430 | 428
2017-05-30 06:30 | 438 | 436
2017-05-30 07:00 | 464 | 463
2017-05-30 07:30 | 502 | 502
2017-05-30 08:00 | 519 | 519
2017-05-30 08:30 | 516 | 516
2017-05-30 09:00 | 518 | 518
2017-05-30 09:30 | 501 | 501
2017-05-30 10:00 | 502 | 502
2017-05-30 10:30 | 507 | 507
2017-05-30 11:00 | 503 | 503
2017-05-30 11:30 | 491 | 490
2017-05-30 12:00 | 498 | 498
2017-05-30 12:30 | 502 | 502
2017-05-30 13:00 | 516 | 516
2017-05-30 13:30 | 520 | 520
2017-05-30 14:00 | 529 | 529
2017-05-30 14:30 | 521 | 521
2017-05-30 15:00 | 516 | 516
2017-05-30 15:30 | 523 | 523
2017-05-30 16:00 | 526 | 526
2017-05-30 16:30 | 534 | 534
2017-05-30 17:00 | 529 | 529
2017-05-30 17:30 | 511 | 511
2017-05-30 18:00 | 535 | 535
2017-05-30 18:30 | 589 | 589
2017-05-30 19:00 | 596 | 596
2017-05-30 19:30 | 599 | 599
2017-05-30 20:00 | 565 | 565
2017-05-30 20:30 | 538 | 538
2017-05-30 21:00 | 539 | 539
2017-05-30 21:30 | 532 | 532
2017-05-30 22:00 | 509 | 509
2017-05-30 22:30 | 483 | 483
2017-05-30 23:00 | 461 | 461
2017-05-30 23:30 | 443 | 442
2017-05-31 | 424 | 423
2017-05-31 00:30 | 408 | 407
2017-05-31 01:00 | 406 | 403
2017-05-31 01:30 | 401 | 398
2017-05-31 02:00 | 396 | 393
2017-05-31 02:30 | 389 | 386
2017-05-31 03:00 | 393 | 389
2017-05-31 03:30 | 393 | 389
2017-05-31 04:00 | 390 | 387
2017-05-31 04:30 | 397 | 393
2017-05-31 05:00 | 402 | 399
2017-05-31 05:30 | 414 | 411
2017-05-31 06:00 | 438 | 435
2017-05-31 06:30 | 447 | 444
2017-05-31 07:00 | 457 | 455
2017-05-31 07:30 | 492 | 490
2017-05-31 08:00 | 510 | 509
2017-05-31 08:30 | 531 | 530
2017-05-31 09:00 | 533 | 532
2017-05-31 09:30 | 528 | 527
2017-05-31 10:00 | 523 | 523
2017-05-31 10:30 | 514 | 513
2017-05-31 11:00 | 461 | 460
2017-05-31 11:30 | 457 | 456
2017-05-31 12:00 | 466 | 465
2017-05-31 12:30 | 485 | 483
2017-05-31 13:00 | 491 | 490
2017-05-31 13:30 | 497 | 496
2017-05-31 14:00 | 488 | 487
2017-05-31 14:30 | 420 | 419
2017-05-31 15:00 | 376 | 374
2017-05-31 15:30 | 399 | 396
2017-05-31 16:00 | 416 | 413
2017-05-31 16:30 | 399 | 397
2017-05-31 17:00 | 355 | 353
2017-05-31 17:30 | 290 | 285
2017-05-31 18:00 | 313 | 307
2017-05-31 18:30 | 337 | 332
2017-05-31 19:00 | 332 | 328
2017-05-31 19:30 | 340 | 335
2017-05-31 20:00 | 325 | 320
2017-05-31 20:30 | 300 | 295
2017-05-31 21:00 | 275 | 268
2017-05-31 21:30 | 263 | 255
2017-05-31 22:00 | 244 | 234
2017-05-31 22:30 | 230 | 218
2017-05-31 23:00 | 213 | 199
2017-05-31 23:30 | 194 | 177
2017-06-01 | 213 | 195
2017-06-01 00:30 | 284 | 271
2017-06-01 01:00 | 279 | 269
2017-06-01 01:30 | 270 | 259
2017-06-01 02:00 | 262 | 251
2017-06-01 02:30 | 265 | 252
2017-06-01 03:00 | 262 | 249
2017-06-01 03:30 | 259 | 246
2017-06-01 04:00 | 258 | 245
2017-06-01 04:30 | 269 | 255
2017-06-01 05:00 | 269 | 256
2017-06-01 05:30 | 282 | 270
2017-06-01 06:00 | 276 | 265
2017-06-01 06:30 | 291 | 281
2017-06-01 07:00 | 237 | 224
2017-06-01 07:30 | 266 | 251
2017-06-01 08:00 | 262 | 248
2017-06-01 08:30 | 288 | 276
2017-06-01 09:00 | 389 | 381
2017-06-01 09:30 | 393 | 388
2017-06-01 10:00 | 388 | 384
2017-06-01 10:30 | 379 | 375
2017-06-01 11:00 | 374 | 369
2017-06-01 11:30 | 373 | 368
2017-06-01 12:00 | 378 | 373
2017-06-01 12:30 | 369 | 364
2017-06-01 13:00 | 363 | 358
2017-06-01 13:30 | 371 | 366
2017-06-01 14:00 | 372 | 367
2017-06-01 14:30 | 351 | 346
2017-06-01 15:00 | 350 | 345
2017-06-01 15:30 | 359 | 353
2017-06-01 16:00 | 369 | 364
2017-06-01 16:30 | 367 | 362
2017-06-01 17:00 | 298 | 293
2017-06-01 17:30 | 314 | 306
2017-06-01 18:00 | 328 | 320
2017-06-01 18:30 | 344 | 338
2017-06-01 19:00 | 378 | 373
2017-06-01 19:30 | 381 | 377
2017-06-01 20:00 | 362 | 358
2017-06-01 20:30 | 346 | 340
2017-06-01 21:00 | 321 | 315
2017-06-01 21:30 | 297 | 290
2017-06-01 22:00 | 303 | 295
2017-06-01 22:30 | 264 | 256
2017-06-01 23:00 | 242 | 230
2017-06-01 23:30 | 224 | 208
2017-06-02 | 247 | 230
2017-06-02 00:30 | 270 | 257
2017-06-02 01:00 | 262 | 249
2017-06-02 01:30 | 254 | 240
2017-06-02 02:00 | 252 | 238
2017-06-02 02:30 | 253 | 239
2017-06-02 03:00 | 251 | 237
2017-06-02 03:30 | 247 | 233
2017-06-02 04:00 | 246 | 232
2017-06-02 04:30 | 254 | 240
2017-06-02 05:00 | 265 | 252
2017-06-02 05:30 | 280 | 269
2017-06-02 06:00 | 301 | 291
2017-06-02 06:30 | 334 | 326
2017-06-02 07:00 | 294 | 286
2017-06-02 07:30 | 326 | 317
2017-06-02 08:00 | 345 | 338
2017-06-02 08:30 | 349 | 343
2017-06-02 09:00 | 415 | 409
2017-06-02 09:30 | 420 | 417
2017-06-02 10:00 | 410 | 407
2017-06-02 10:30 | 389 | 386
2017-06-02 11:00 | 382 | 378
2017-06-02 11:30 | 382 | 378
2017-06-02 12:00 | 384 | 380
2017-06-02 12:30 | 390 | 386
2017-06-02 13:00 | 392 | 388
2017-06-02 13:30 | 393 | 389
2017-06-02 14:00 | 387 | 383
2017-06-02 14:30 | 369 | 365
2017-06-02 15:00 | 369 | 365
2017-06-02 15:30 | 374 | 370
2017-06-02 16:00 | 374 | 370
2017-06-02 16:30 | 377 | 374
2017-06-02 17:00 | 308 | 304
2017-06-02 17:30 | 279 | 271
2017-06-02 18:00 | 334 | 327
2017-06-02 18:30 | 349 | 344
2017-06-02 19:00 | 343 | 339
2017-06-02 19:30 | 337 | 332
2017-06-02 20:00 | 323 | 318
2017-06-02 20:30 | 297 | 291
2017-06-02 21:00 | 359 | 353
2017-06-02 21:30 | 377 | 373
2017-06-02 22:00 | 365 | 361
2017-06-02 22:30 | 295 | 290
2017-06-02 23:00 | 321 | 314
2017-06-02 23:30 | 311 | 305
2017-06-03 | 296 | 288
2017-06-03 00:30 | 340 | 333
2017-06-03 01:00 | 408 | 402
2017-06-03 01:30 | 395 | 392
2017-06-03 02:00 | 387 | 384
2017-06-03 02:30 | 378 | 374
2017-06-03 03:00 | 377 | 373
2017-06-03 03:30 | 375 | 371
2017-06-03 04:00 | 374 | 369
2017-06-03 04:30 | 374 | 369
2017-06-03 05:00 | 382 | 378
2017-06-03 05:30 | 388 | 383
2017-06-03 06:00 | 395 | 391
2017-06-03 06:30 | 394 | 390
2017-06-03 07:00 | 427 | 423
2017-06-03 07:30 | 450 | 447
2017-06-03 08:00 | 477 | 475
2017-06-03 08:30 | 498 | 497
2017-06-03 09:00 | 507 | 506
2017-06-03 09:30 | 501 | 501
2017-06-03 10:00 | 496 | 495
2017-06-03 10:30 | 484 | 483
2017-06-03 11:00 | 479 | 478
2017-06-03 11:30 | 480 | 478
2017-06-03 12:00 | 470 | 469
2017-06-03 12:30 | 457 | 455
2017-06-03 13:00 | 466 | 464
2017-06-03 13:30 | 459 | 457
2017-06-03 14:00 | 450 | 448
2017-06-03 14:30 | 440 | 438
2017-06-03 15:00 | 430 | 428
2017-06-03 15:30 | 442 | 439
2017-06-03 16:00 | 464 | 462
2017-06-03 16:30 | 473 | 471
2017-06-03 17:00 | 487 | 486
2017-06-03 17:30 | 510 | 509
2017-06-03 18:00 | 544 | 543
2017-06-03 18:30 | 541 | 541
2017-06-03 19:00 | 577 | 577
2017-06-03 19:30 | 559 | 559
2017-06-03 20:00 | 539 | 539
2017-06-03 20:30 | 518 | 518
2017-06-03 21:00 | 505 | 505
2017-06-03 21:30 | 492 | 492
2017-06-03 22:00 | 477 | 476
2017-06-03 22:30 | 457 | 456
2017-06-03 23:00 | 440 | 439
2017-06-03 23:30 | 424 | 422
2017-06-04 | 413 | 410
2017-06-04 00:30 | 403 | 400
2017-06-04 01:00 | 391 | 387
2017-06-04 01:30 | 385 | 380
2017-06-04 02:00 | 381 | 376
2017-06-04 02:30 | 370 | 365
2017-06-04 03:00 | 371 | 365
2017-06-04 03:30 | 367 | 361
2017-06-04 04:00 | 370 | 364
2017-06-04 04:30 | 371 | 365
2017-06-04 05:00 | 371 | 366
2017-06-04 05:30 | 377 | 371
2017-06-04 06:00 | 381 | 376
2017-06-04 06:30 | 389 | 384
2017-06-04 07:00 | 395 | 391
2017-06-04 07:30 | 416 | 412
2017-06-04 08:00 | 430 | 427
2017-06-04 08:30 | 441 | 439
2017-06-04 09:00 | 447 | 444
2017-06-04 09:30 | 453 | 451
2017-06-04 10:00 | 452 | 450
2017-06-04 10:30 | 448 | 446
2017-06-04 11:00 | 443 | 441
2017-06-04 11:30 | 439 | 437
2017-06-04 12:00 | 442 | 439
2017-06-04 12:30 | 437 | 434
2017-06-04 13:00 | 433 | 431
2017-06-04 13:30 | 437 | 434
2017-06-04 14:00 | 433 | 431
2017-06-04 14:30 | 417 | 415
2017-06-04 15:00 | 421 | 418
2017-06-04 15:30 | 431 | 429
2017-06-04 16:00 | 449 | 447
2017-06-04 16:30 | 465 | 464
2017-06-04 17:00 | 481 | 479
2017-06-04 17:30 | 514 | 513
2017-06-04 18:00 | 578 | 577
2017-06-04 18:30 | 613 | 613
2017-06-04 19:00 | 608 | 608
2017-06-04 19:30 | 591 | 591
2017-06-04 20:00 | 567 | 567
2017-06-04 20:30 | 544 | 544
2017-06-04 21:00 | 526 | 526
2017-06-04 21:30 | 508 | 507
2017-06-04 22:00 | 490 | 489
2017-06-04 22:30 | 465 | 463
2017-06-04 23:00 | 449 | 446
2017-06-04 23:30 | 430 | 427
2017-06-05 | 415 | 412
2017-06-05 00:30 | 403 | 399
2017-06-05 01:00 | 391 | 387
2017-06-05 01:30 | 386 | 382
2017-06-05 02:00 | 384 | 380
2017-06-05 02:30 | 380 | 376
2017-06-05 03:00 | 379 | 374
2017-06-05 03:30 | 377 | 373
2017-06-05 04:00 | 379 | 374
2017-06-05 04:30 | 385 | 380
2017-06-05 05:00 | 396 | 392
2017-06-05 05:30 | 416 | 413
2017-06-05 06:00 | 433 | 430
2017-06-05 06:30 | 442 | 439
2017-06-05 07:00 | 470 | 468
2017-06-05 07:30 | 512 | 511
2017-06-05 08:00 | 526 | 525
2017-06-05 08:30 | 546 | 545
2017-06-05 09:00 | 538 | 537
2017-06-05 09:30 | 526 | 526
2017-06-05 10:00 | 512 | 511
2017-06-05 10:30 | 512 | 511
2017-06-05 11:00 | 510 | 509
2017-06-05 11:30 | 503 | 502
2017-06-05 12:00 | 500 | 499
2017-06-05 12:30 | 498 | 496
2017-06-05 13:00 | 498 | 497
2017-06-05 13:30 | 498 | 496
2017-06-05 14:00 | 499 | 498
2017-06-05 14:30 | 500 | 498
2017-06-05 15:00 | 492 | 490
2017-06-05 15:30 | 501 | 500
2017-06-05 16:00 | 514 | 513
2017-06-05 16:30 | 516 | 515
2017-06-05 17:00 | 531 | 529
2017-06-05 17:30 | 521 | 520
2017-06-05 18:00 | 564 | 563
2017-06-05 18:30 | 608 | 608
2017-06-05 19:00 | 610 | 609
2017-06-05 19:30 | 588 | 588
2017-06-05 20:00 | 560 | 560
2017-06-05 20:30 | 538 | 538
2017-06-05 21:00 | 547 | 546
2017-06-05 21:30 | 536 | 535
2017-06-05 22:00 | 515 | 514
2017-06-05 22:30 | 484 | 482
2017-06-05 23:00 | 458 | 456
2017-06-05 23:30 | 438 | 436
2017-06-06 | 424 | 421
2017-06-06 00:30 | 416 | 413
2017-06-06 01:00 | 408 | 404
2017-06-06 01:30 | 402 | 398
2017-06-06 02:00 | 394 | 390
2017-06-06 02:30 | 389 | 383
2017-06-06 03:00 | 389 | 384
2017-06-06 03:30 | 390 | 385
2017-06-06 04:00 | 385 | 380
2017-06-06 04:30 | 382 | 377
2017-06-06 05:00 | 392 | 387
2017-06-06 05:30 | 406 | 401
2017-06-06 06:00 | 422 | 417
2017-06-06 06:30 | 433 | 429
2017-06-06 07:00 | 465 | 462
2017-06-06 07:30 | 499 | 497
2017-06-06 08:00 | 524 | 522
2017-06-06 08:30 | 541 | 541
2017-06-06 09:00 | 528 | 527
2017-06-06 09:30 | 511 | 511
2017-06-06 10:00 | 505 | 504
2017-06-06 10:30 | 484 | 483
2017-06-06 11:00 | 423 | 422
2017-06-06 11:30 | 404 | 401
2017-06-06 12:00 | 408 | 405
2017-06-06 12:30 | 409 | 406
2017-06-06 13:00 | 417 | 413
2017-06-06 13:30 | 424 | 421
2017-06-06 14:00 | 416 | 413
2017-06-06 14:30 | 350 | 346
2017-06-06 15:00 | 333 | 326
2017-06-06 15:30 | 349 | 342
2017-06-06 16:00 | 356 | 350
2017-06-06 16:30 | 333 | 328
2017-06-06 17:00 | 314 | 307
2017-06-06 17:30 | 307 | 299
2017-06-06 18:00 | 329 | 322
2017-06-06 18:30 | 365 | 360
2017-06-06 19:00 | 363 | 359
2017-06-06 19:30 | 357 | 353
2017-06-06 20:00 | 356 | 351
2017-06-06 20:30 | 335 | 330
2017-06-06 21:00 | 335 | 330
2017-06-06 21:30 | 362 | 357
2017-06-06 22:00 | 488 | 485
2017-06-06 22:30 | 487 | 486
2017-06-06 23:00 | 462 | 461
2017-06-06 23:30 | 441 | 439
2017-06-07 | 420 | 418
2017-06-07 00:30 | 408 | 406
2017-06-07 01:00 | 397 | 394
2017-06-07 01:30 | 391 | 388
2017-06-07 02:00 | 387 | 383
2017-06-07 02:30 | 384 | 380
2017-06-07 03:00 | 384 | 379
2017-06-07 03:30 | 380 | 375
2017-06-07 04:00 | 382 | 377
2017-06-07 04:30 | 385 | 380
2017-06-07 05:00 | 393 | 389
2017-06-07 05:30 | 407 | 403
2017-06-07 06:00 | 427 | 423
2017-06-07 06:30 | 439 | 436
2017-06-07 07:00 | 470 | 467
2017-06-07 07:30 | 515 | 513
2017-06-07 08:00 | 514 | 513
2017-06-07 08:30 | 536 | 535
2017-06-07 09:00 | 521 | 521
2017-06-07 09:30 | 504 | 503
2017-06-07 10:00 | 487 | 486
2017-06-07 10:30 | 475 | 474
2017-06-07 11:00 | 467 | 466
2017-06-07 11:30 | 459 | 457
2017-06-07 12:00 | 461 | 459
2017-06-07 12:30 | 465 | 463
2017-06-07 13:00 | 466 | 464
2017-06-07 13:30 | 466 | 464
2017-06-07 14:00 | 468 | 466
2017-06-07 14:30 | 457 | 456
2017-06-07 15:00 | 457 | 455
2017-06-07 15:30 | 462 | 460
2017-06-07 16:00 | 483 | 481
2017-06-07 16:30 | 497 | 496
2017-06-07 17:00 | 510 | 509
2017-06-07 17:30 | 505 | 504
2017-06-07 18:00 | 557 | 556
2017-06-07 18:30 | 593 | 593
2017-06-07 19:00 | 599 | 599
2017-06-07 19:30 | 585 | 585
2017-06-07 20:00 | 565 | 565
2017-06-07 20:30 | 549 | 549
2017-06-07 21:00 | 548 | 548
2017-06-07 21:30 | 530 | 530
2017-06-07 22:00 | 510 | 509
2017-06-07 22:30 | 484 | 483
2017-06-07 23:00 | 461 | 460
2017-06-07 23:30 | 439 | 437
2017-06-08 | 419 | 417
2017-06-08 00:30 | 411 | 408
2017-06-08 01:00 | 394 | 391
2017-06-08 01:30 | 385 | 381
2017-06-08 02:00 | 381 | 376
2017-06-08 02:30 | 379 | 374
2017-06-08 03:00 | 377 | 372
2017-06-08 03:30 | 374 | 369
2017-06-08 04:00 | 376 | 371
2017-06-08 04:30 | 382 | 378
2017-06-08 05:00 | 393 | 388
2017-06-08 05:30 | 406 | 402
2017-06-08 06:00 | 430 | 426
2017-06-08 06:30 | 447 | 444
2017-06-08 07:00 | 465 | 463
2017-06-08 07:30 | 515 | 514
2017-06-08 08:00 | 520 | 520
2017-06-08 08:30 | 525 | 524
2017-06-08 09:00 | 503 | 502
2017-06-08 09:30 | 491 | 490
2017-06-08 10:00 | 480 | 479
2017-06-08 10:30 | 469 | 467
2017-06-08 11:00 | 459 | 458
2017-06-08 11:30 | 455 | 453
2017-06-08 12:00 | 450 | 448
2017-06-08 12:30 | 451 | 450
2017-06-08 13:00 | 455 | 454
2017-06-08 13:30 | 460 | 458
2017-06-08 14:00 | 459 | 457
2017-06-08 14:30 | 443 | 441
2017-06-08 15:00 | 450 | 448
2017-06-08 15:30 | 465 | 463
2017-06-08 16:00 | 485 | 483
2017-06-08 16:30 | 500 | 499
2017-06-08 17:00 | 519 | 518
2017-06-08 17:30 | 522 | 521
2017-06-08 18:00 | 535 | 535
2017-06-08 18:30 | 575 | 575
2017-06-08 19:00 | 585 | 585
2017-06-08 19:30 | 597 | 597
2017-06-08 20:00 | 583 | 583
2017-06-08 20:30 | 553 | 553
2017-06-08 21:00 | 556 | 556
2017-06-08 21:30 | 539 | 538
2017-06-08 22:00 | 515 | 514
2017-06-08 22:30 | 491 | 490
2017-06-08 23:00 | 458 | 457
2017-06-08 23:30 | 436 | 434
2017-06-09 | 422 | 419
2017-06-09 00:30 | 408 | 405
2017-06-09 01:00 | 402 | 398
2017-06-09 01:30 | 394 | 390
2017-06-09 02:00 | 386 | 382
2017-06-09 02:30 | 381 | 377
2017-06-09 03:00 | 378 | 374
2017-06-09 03:30 | 380 | 376
2017-06-09 04:00 | 383 | 380
2017-06-09 04:30 | 386 | 383
2017-06-09 05:00 | 390 | 387
2017-06-09 05:30 | 406 | 402
2017-06-09 06:00 | 419 | 416
2017-06-09 06:30 | 434 | 431
2017-06-09 07:00 | 467 | 465
2017-06-09 07:30 | 502 | 501
2017-06-09 08:00 | 507 | 506
2017-06-09 08:30 | 508 | 508
2017-06-09 09:00 | 527 | 526
2017-06-09 09:30 | 442 | 441
2017-06-09 10:00 | 364 | 363
2017-06-09 10:30 | 401 | 399
2017-06-09 11:00 | 414 | 412
2017-06-09 11:30 | 414 | 412
2017-06-09 12:00 | 418 | 416
2017-06-09 12:30 | 418 | 417
2017-06-09 13:00 | 418 | 416
2017-06-09 13:30 | 436 | 434
2017-06-09 14:00 | 438 | 436
2017-06-09 14:30 | 424 | 423
2017-06-09 15:00 | 423 | 421
2017-06-09 15:30 | 421 | 420
2017-06-09 16:00 | 446 | 445
2017-06-09 16:30 | 472 | 472
2017-06-09 17:00 | 492 | 491
2017-06-09 17:30 | 501 | 500
2017-06-09 18:00 | 516 | 516
2017-06-09 18:30 | 543 | 543
2017-06-09 19:00 | 564 | 564
2017-06-09 19:30 | 587 | 587
2017-06-09 20:00 | 573 | 573
2017-06-09 20:30 | 550 | 550
2017-06-09 21:00 | 535 | 534
2017-06-09 21:30 | 515 | 515
2017-06-09 22:00 | 509 | 509
2017-06-09 22:30 | 541 | 541
2017-06-09 23:00 | 522 | 522
2017-06-09 23:30 | 501 | 501
2017-06-10 | 484 | 484
2017-06-10 00:30 | 471 | 470
2017-06-10 01:00 | 464 | 463
2017-06-10 01:30 | 457 | 456
2017-06-10 02:00 | 448 | 447
2017-06-10 02:30 | 444 | 443
2017-06-10 03:00 | 437 | 436
2017-06-10 03:30 | 437 | 435
2017-06-10 04:00 | 434 | 433
2017-06-10 04:30 | 437 | 436
2017-06-10 05:00 | 442 | 441
2017-06-10 05:30 | 447 | 446
2017-06-10 06:00 | 456 | 455
2017-06-10 06:30 | 465 | 464
2017-06-10 07:00 | 464 | 463
2017-06-10 07:30 | 444 | 443
2017-06-10 08:00 | 465 | 464
2017-06-10 08:30 | 491 | 490
2017-06-10 09:00 | 494 | 494
2017-06-10 09:30 | 490 | 490
2017-06-10 10:00 | 482 | 481
2017-06-10 10:30 | 477 | 476
2017-06-10 11:00 | 456 | 455
2017-06-10 11:30 | 442 | 441
2017-06-10 12:00 | 445 | 444
2017-06-10 12:30 | 443 | 441
2017-06-10 13:00 | 432 | 431
2017-06-10 13:30 | 428 | 427
2017-06-10 14:00 | 423 | 421
2017-06-10 14:30 | 409 | 407
2017-06-10 15:00 | 407 | 405
2017-06-10 15:30 | 417 | 416
2017-06-10 16:00 | 435 | 434
2017-06-10 16:30 | 455 | 454
2017-06-10 17:00 | 474 | 473
2017-06-10 17:30 | 500 | 499
2017-06-10 18:00 | 556 | 555
2017-06-10 18:30 | 584 | 583
2017-06-10 19:00 | 578 | 578
2017-06-10 19:30 | 558 | 558
2017-06-10 20:00 | 534 | 534
2017-06-10 20:30 | 518 | 518
2017-06-10 21:00 | 508 | 508
2017-06-10 21:30 | 490 | 490
2017-06-10 22:00 | 495 | 495
2017-06-10 22:30 | 524 | 523
2017-06-10 23:00 | 508 | 508
2017-06-10 23:30 | 492 | 492
2017-06-11 | 474 | 474
2017-06-11 00:30 | 465 | 464
2017-06-11 01:00 | 458 | 457
2017-06-11 01:30 | 448 | 447
2017-06-11 02:00 | 446 | 445
2017-06-11 02:30 | 442 | 441
2017-06-11 03:00 | 440 | 438
2017-06-11 03:30 | 439 | 437
2017-06-11 04:00 | 438 | 436
2017-06-11 04:30 | 438 | 437
2017-06-11 05:00 | 437 | 436
2017-06-11 05:30 | 436 | 435
2017-06-11 06:00 | 443 | 442
2017-06-11 06:30 | 454 | 453
2017-06-11 07:00 | 450 | 449
2017-06-11 07:30 | 421 | 420
2017-06-11 08:00 | 439 | 438
2017-06-11 08:30 | 457 | 455
2017-06-11 09:00 | 474 | 473
2017-06-11 09:30 | 488 | 487
2017-06-11 10:00 | 500 | 500
2017-06-11 10:30 | 496 | 496
2017-06-11 11:00 | 500 | 500
2017-06-11 11:30 | 500 | 499
2017-06-11 12:00 | 494 | 493
2017-06-11 12:30 | 493 | 492
2017-06-11 13:00 | 491 | 490
2017-06-11 13:30 | 486 | 486
2017-06-11 14:00 | 477 | 476
2017-06-11 14:30 | 455 | 454
2017-06-11 15:00 | 448 | 447
2017-06-11 15:30 | 455 | 454
2017-06-11 16:00 | 471 | 470
2017-06-11 16:30 | 488 | 487
2017-06-11 17:00 | 509 | 509
2017-06-11 17:30 | 538 | 537
2017-06-11 18:00 | 595 | 594
2017-06-11 18:30 | 617 | 617
2017-06-11 19:00 | 606 | 606
2017-06-11 19:30 | 585 | 585
2017-06-11 20:00 | 566 | 566
2017-06-11 20:30 | 546 | 546
2017-06-11 21:00 | 527 | 527
2017-06-11 21:30 | 512 | 512
2017-06-11 22:00 | 504 | 504
2017-06-11 22:30 | 528 | 528
2017-06-11 23:00 | 507 | 507
2017-06-11 23:30 | 491 | 491
2017-06-12 | 473 | 472
2017-06-12 00:30 | 463 | 462
2017-06-12 01:00 | 446 | 445
2017-06-12 01:30 | 439 | 438
2017-06-12 02:00 | 435 | 433
2017-06-12 02:30 | 433 | 431
2017-06-12 03:00 | 428 | 426
2017-06-12 03:30 | 432 | 430
2017-06-12 04:00 | 438 | 437
2017-06-12 04:30 | 443 | 441
2017-06-12 05:00 | 449 | 447
2017-06-12 05:30 | 463 | 462
2017-06-12 06:00 | 481 | 480
2017-06-12 06:30 | 520 | 519
2017-06-12 07:00 | 548 | 547
2017-06-12 07:30 | 546 | 546
2017-06-12 08:00 | 558 | 558
2017-06-12 08:30 | 548 | 548
2017-06-12 09:00 | 523 | 522
2017-06-12 09:30 | 504 | 503
2017-06-12 10:00 | 494 | 493
2017-06-12 10:30 | 487 | 486
2017-06-12 11:00 | 478 | 477
2017-06-12 11:30 | 472 | 470
2017-06-12 12:00 | 469 | 468
2017-06-12 12:30 | 470 | 469
2017-06-12 13:00 | 465 | 464
2017-06-12 13:30 | 464 | 463
2017-06-12 14:00 | 468 | 467
2017-06-12 14:30 | 456 | 455
2017-06-12 15:00 | 458 | 456
2017-06-12 15:30 | 473 | 472
2017-06-12 16:00 | 486 | 485
2017-06-12 16:30 | 504 | 503
2017-06-12 17:00 | 518 | 517
2017-06-12 17:30 | 512 | 511
2017-06-12 18:00 | 534 | 533
2017-06-12 18:30 | 577 | 576
2017-06-12 19:00 | 587 | 587
2017-06-12 19:30 | 610 | 610
2017-06-12 20:00 | 598 | 598
2017-06-12 20:30 | 578 | 578
2017-06-12 21:00 | 558 | 558
2017-06-12 21:30 | 537 | 537
2017-06-12 22:00 | 525 | 525
2017-06-12 22:30 | 545 | 544
2017-06-12 23:00 | 518 | 518
2017-06-12 23:30 | 504 | 503
2017-06-13 | 482 | 481
2017-06-13 00:30 | 468 | 467
2017-06-13 01:00 | 457 | 455
2017-06-13 01:30 | 448 | 446
2017-06-13 02:00 | 445 | 444
2017-06-13 02:30 | 445 | 443
2017-06-13 03:00 | 440 | 438
2017-06-13 03:30 | 439 | 437
2017-06-13 04:00 | 435 | 433
2017-06-13 04:30 | 405 | 404
2017-06-13 05:00 | 386 | 383
2017-06-13 05:30 | 400 | 397
2017-06-13 06:00 | 408 | 405
2017-06-13 06:30 | 401 | 398
2017-06-13 07:00 | 431 | 429
2017-06-13 07:30 | 475 | 473
2017-06-13 08:00 | 485 | 484
2017-06-13 08:30 | 427 | 426
2017-06-13 09:00 | 351 | 349
2017-06-13 09:30 | 290 | 285
2017-06-13 10:00 | 271 | 262
2017-06-13 10:30 | 259 | 249
2017-06-13 11:00 | 249 | 238
2017-06-13 11:30 | 248 | 236
2017-06-13 12:00 | 245 | 233
2017-06-13 12:30 | 241 | 229
2017-06-13 13:00 | 244 | 232
2017-06-13 13:30 | 251 | 239
2017-06-13 14:00 | 243 | 232
2017-06-13 14:30 | 232 | 219
2017-06-13 15:00 | 244 | 232
2017-06-13 15:30 | 253 | 241
2017-06-13 16:00 | 261 | 250
2017-06-13 16:30 | 290 | 281
2017-06-13 17:00 | 382 | 376
2017-06-13 17:30 | 356 | 351
2017-06-13 18:00 | 366 | 360
2017-06-13 18:30 | 401 | 396
2017-06-13 19:00 | 427 | 423
2017-06-13 19:30 | 480 | 477
2017-06-13 20:00 | 465 | 463
2017-06-13 20:30 | 439 | 437
2017-06-13 21:00 | 426 | 423
2017-06-13 21:30 | 412 | 409
2017-06-13 22:00 | 395 | 391
2017-06-13 22:30 | 417 | 413
2017-06-13 23:00 | 396 | 392
2017-06-13 23:30 | 376 | 371
2017-06-14 | 361 | 356
2017-06-14 00:30 | 351 | 345
2017-06-14 01:00 | 341 | 334
2017-06-14 01:30 | 333 | 325
2017-06-14 02:00 | 334 | 326
2017-06-14 02:30 | 326 | 317
2017-06-14 03:00 | 324 | 315
2017-06-14 03:30 | 318 | 309
2017-06-14 04:00 | 321 | 313
2017-06-14 04:30 | 324 | 316
2017-06-14 05:00 | 330 | 321
2017-06-14 05:30 | 340 | 332
2017-06-14 06:00 | 364 | 357
2017-06-14 06:30 | 399 | 394
2017-06-14 07:00 | 378 | 373
2017-06-14 07:30 | 405 | 400
2017-06-14 08:00 | 437 | 434
2017-06-14 08:30 | 430 | 427
2017-06-14 09:00 | 404 | 401
2017-06-14 09:30 | 397 | 392
2017-06-14 10:00 | 383 | 379
2017-06-14 10:30 | 374 | 369
2017-06-14 11:00 | 366 | 361
2017-06-14 11:30 | 358 | 352
2017-06-14 12:00 | 352 | 346
2017-06-14 12:30 | 366 | 360
2017-06-14 13:00 | 381 | 376
2017-06-14 13:30 | 383 | 378
2017-06-14 14:00 | 384 | 379
2017-06-14 14:30 | 367 | 362
2017-06-14 15:00 | 364 | 359
2017-06-14 15:30 | 367 | 362
2017-06-14 16:00 | 375 | 370
2017-06-14 16:30 | 384 | 379
2017-06-14 17:00 | 402 | 398
2017-06-14 17:30 | 396 | 391
2017-06-14 18:00 | 387 | 383
2017-06-14 18:30 | 421 | 417
2017-06-14 19:00 | 431 | 428
2017-06-14 19:30 | 485 | 483
2017-06-14 20:00 | 471 | 470
2017-06-14 20:30 | 417 | 415
2017-06-14 21:00 | 429 | 426
2017-06-14 21:30 | 410 | 407
2017-06-14 22:00 | 397 | 394
2017-06-14 22:30 | 417 | 413
2017-06-14 23:00 | 395 | 391
2017-06-14 23:30 | 372 | 368
2017-06-15 | 358 | 352
2017-06-15 00:30 | 401 | 395
2017-06-15 01:00 | 467 | 463
2017-06-15 01:30 | 458 | 456
2017-06-15 02:00 | 451 | 448
2017-06-15 02:30 | 446 | 443
2017-06-15 03:00 | 443 | 440
2017-06-15 03:30 | 445 | 442
2017-06-15 04:00 | 444 | 441
2017-06-15 04:30 | 447 | 444
2017-06-15 05:00 | 446 | 444
2017-06-15 05:30 | 458 | 456
2017-06-15 06:00 | 481 | 479
2017-06-15 06:30 | 520 | 518
2017-06-15 07:00 | 532 | 531
2017-06-15 07:30 | 540 | 539
2017-06-15 08:00 | 544 | 543
2017-06-15 08:30 | 536 | 535
2017-06-15 09:00 | 505 | 504
2017-06-15 09:30 | 502 | 501
2017-06-15 10:00 | 496 | 495
2017-06-15 10:30 | 484 | 482
2017-06-15 11:00 | 476 | 474
2017-06-15 11:30 | 474 | 472
2017-06-15 12:00 | 465 | 464
2017-06-15 12:30 | 464 | 463
2017-06-15 13:00 | 467 | 465
2017-06-15 13:30 | 472 | 470
2017-06-15 14:00 | 476 | 474
2017-06-15 14:30 | 467 | 465
2017-06-15 15:00 | 471 | 470
2017-06-15 15:30 | 474 | 472
2017-06-15 16:00 | 485 | 484
2017-06-15 16:30 | 505 | 503
2017-06-15 17:00 | 518 | 517
2017-06-15 17:30 | 532 | 531
2017-06-15 18:00 | 587 | 587
2017-06-15 18:30 | 628 | 628
2017-06-15 19:00 | 634 | 634
2017-06-15 19:30 | 617 | 617
2017-06-15 20:00 | 601 | 601
2017-06-15 20:30 | 581 | 581
2017-06-15 21:00 | 565 | 565
2017-06-15 21:30 | 548 | 548
2017-06-15 22:00 | 531 | 531
2017-06-15 22:30 | 558 | 558
2017-06-15 23:00 | 539 | 538
2017-06-15 23:30 | 516 | 515
2017-06-16 | 497 | 496
2017-06-16 00:30 | 483 | 481
2017-06-16 01:00 | 473 | 471
2017-06-16 01:30 | 472 | 470
2017-06-16 02:00 | 459 | 458
2017-06-16 02:30 | 455 | 452
2017-06-16 03:00 | 448 | 445
2017-06-16 03:30 | 452 | 450
2017-06-16 04:00 | 449 | 447
2017-06-16 04:30 | 450 | 447
2017-06-16 05:00 | 459 | 457
2017-06-16 05:30 | 472 | 471
2017-06-16 06:00 | 488 | 487
2017-06-16 06:30 | 527 | 526
2017-06-16 07:00 | 545 | 544
2017-06-16 07:30 | 535 | 535
2017-06-16 08:00 | 546 | 545
2017-06-16 08:30 | 544 | 544
2017-06-16 09:00 | 531 | 531
2017-06-16 09:30 | 522 | 521
2017-06-16 10:00 | 508 | 508
2017-06-16 10:30 | 495 | 494
2017-06-16 11:00 | 498 | 497
2017-06-16 11:30 | 501 | 500
2017-06-16 12:00 | 498 | 497
2017-06-16 12:30 | 496 | 495
2017-06-16 13:00 | 498 | 497
2017-06-16 13:30 | 497 | 496
2017-06-16 14:00 | 496 | 495
2017-06-16 14:30 | 474 | 473
2017-06-16 15:00 | 474 | 473
2017-06-16 15:30 | 476 | 474
2017-06-16 16:00 | 496 | 494
2017-06-16 16:30 | 511 | 510
2017-06-16 17:00 | 533 | 532
2017-06-16 17:30 | 542 | 541
2017-06-16 18:00 | 576 | 576
2017-06-16 18:30 | 598 | 598
2017-06-16 19:00 | 602 | 602
2017-06-16 19:30 | 583 | 583
2017-06-16 20:00 | 567 | 567
2017-06-16 20:30 | 550 | 550
2017-06-16 21:00 | 536 | 535
2017-06-16 21:30 | 530 | 530
2017-06-16 22:00 | 531 | 531
2017-06-16 22:30 | 543 | 543
2017-06-16 23:00 | 530 | 530
2017-06-16 23:30 | 510 | 509
2017-06-17 | 491 | 490
2017-06-17 00:30 | 473 | 471
2017-06-17 01:00 | 457 | 455
2017-06-17 01:30 | 452 | 451
2017-06-17 02:00 | 438 | 436
2017-06-17 02:30 | 443 | 441
2017-06-17 03:00 | 440 | 438
2017-06-17 03:30 | 438 | 436
2017-06-17 04:00 | 435 | 433
2017-06-17 04:30 | 434 | 432
2017-06-17 05:00 | 439 | 437
2017-06-17 05:30 | 443 | 441
2017-06-17 06:00 | 451 | 449
2017-06-17 06:30 | 466 | 464
2017-06-17 07:00 | 470 | 469
2017-06-17 07:30 | 449 | 447
2017-06-17 08:00 | 462 | 460
2017-06-17 08:30 | 481 | 479
2017-06-17 09:00 | 483 | 482
2017-06-17 09:30 | 489 | 488
2017-06-17 10:00 | 480 | 479
2017-06-17 10:30 | 477 | 476
2017-06-17 11:00 | 453 | 452
2017-06-17 11:30 | 438 | 437
2017-06-17 12:00 | 436 | 434
2017-06-17 12:30 | 434 | 432
2017-06-17 13:00 | 435 | 433
2017-06-17 13:30 | 429 | 427
2017-06-17 14:00 | 430 | 428
2017-06-17 14:30 | 411 | 408
2017-06-17 15:00 | 413 | 410
2017-06-17 15:30 | 425 | 422
2017-06-17 16:00 | 442 | 440
2017-06-17 16:30 | 454 | 453
2017-06-17 17:00 | 474 | 473
2017-06-17 17:30 | 494 | 493
2017-06-17 18:00 | 517 | 517
2017-06-17 18:30 | 544 | 544
2017-06-17 19:00 | 544 | 544
2017-06-17 19:30 | 546 | 546
2017-06-17 20:00 | 537 | 537
2017-06-17 20:30 | 514 | 514
2017-06-17 21:00 | 499 | 499
2017-06-17 21:30 | 473 | 473
2017-06-17 22:00 | 458 | 457
2017-06-17 22:30 | 459 | 457
2017-06-17 23:00 | 450 | 449
2017-06-17 23:30 | 442 | 440
2017-06-18 | 477 | 475
2017-06-18 00:30 | 466 | 465
2017-06-18 01:00 | 454 | 452
2017-06-18 01:30 | 435 | 433
2017-06-18 02:00 | 432 | 430
2017-06-18 02:30 | 420 | 417
2017-06-18 03:00 | 416 | 413
2017-06-18 03:30 | 422 | 419
2017-06-18 04:00 | 416 | 413
2017-06-18 04:30 | 374 | 370
2017-06-18 05:00 | 384 | 380
2017-06-18 05:30 | 419 | 415
2017-06-18 06:00 | 446 | 443
2017-06-18 06:30 | 458 | 456
2017-06-18 07:00 | 450 | 448
2017-06-18 07:30 | 421 | 419
2017-06-18 08:00 | 430 | 427
2017-06-18 08:30 | 440 | 438
2017-06-18 09:00 | 446 | 444
2017-06-18 09:30 | 447 | 445
2017-06-18 10:00 | 446 | 444
2017-06-18 10:30 | 445 | 443
2017-06-18 11:00 | 442 | 440
2017-06-18 11:30 | 441 | 440
2017-06-18 12:00 | 434 | 432
2017-06-18 12:30 | 425 | 423
2017-06-18 13:00 | 419 | 417
2017-06-18 13:30 | 417 | 414
2017-06-18 14:00 | 423 | 420
2017-06-18 14:30 | 405 | 402
2017-06-18 15:00 | 407 | 404
2017-06-18 15:30 | 418 | 415
2017-06-18 16:00 | 442 | 440
2017-06-18 16:30 | 469 | 468
2017-06-18 17:00 | 489 | 488
2017-06-18 17:30 | 517 | 516
2017-06-18 18:00 | 572 | 571
2017-06-18 18:30 | 593 | 593
2017-06-18 19:00 | 614 | 614
2017-06-18 19:30 | 590 | 590
2017-06-18 20:00 | 569 | 569
2017-06-18 20:30 | 545 | 545
2017-06-18 21:00 | 522 | 522
2017-06-18 21:30 | 500 | 500
2017-06-18 22:00 | 485 | 484
2017-06-18 22:30 | 463 | 462
2017-06-18 23:00 | 440 | 438
2017-06-18 23:30 | 426 | 424
2017-06-19 | 469 | 467
2017-06-19 00:30 | 460 | 458
2017-06-19 01:00 | 444 | 442
2017-06-19 01:30 | 433 | 431
2017-06-19 02:00 | 429 | 426
2017-06-19 02:30 | 427 | 424
2017-06-19 03:00 | 423 | 420
2017-06-19 03:30 | 425 | 423
2017-06-19 04:00 | 425 | 423
2017-06-19 04:30 | 424 | 422
2017-06-19 05:00 | 389 | 386
2017-06-19 05:30 | 398 | 394
2017-06-19 06:00 | 416 | 413
2017-06-19 06:30 | 405 | 402
2017-06-19 07:00 | 424 | 421
2017-06-19 07:30 | 461 | 459
2017-06-19 08:00 | 457 | 455
2017-06-19 08:30 | 389 | 387
2017-06-19 09:00 | 352 | 349
2017-06-19 09:30 | 373 | 368
2017-06-19 10:00 | 356 | 352
2017-06-19 10:30 | 352 | 347
2017-06-19 11:00 | 346 | 341
2017-06-19 11:30 | 344 | 338
2017-06-19 12:00 | 342 | 336
2017-06-19 12:30 | 347 | 342
2017-06-19 13:00 | 352 | 346
2017-06-19 13:30 | 344 | 339
2017-06-19 14:00 | 347 | 342
2017-06-19 14:30 | 334 | 329
2017-06-19 15:00 | 321 | 315
2017-06-19 15:30 | 252 | 244
2017-06-19 16:00 | 255 | 243
2017-06-19 16:30 | 272 | 261
2017-06-19 17:00 | 284 | 278
2017-06-19 17:30 | 299 | 294
2017-06-19 18:00 | 349 | 345
2017-06-19 18:30 | 393 | 391
2017-06-19 19:00 | 392 | 389
2017-06-19 19:30 | 365 | 362
2017-06-19 20:00 | 344 | 340
2017-06-19 20:30 | 325 | 320
2017-06-19 21:00 | 308 | 302
2017-06-19 21:30 | 301 | 293
2017-06-19 22:00 | 302 | 294
2017-06-19 22:30 | 268 | 258
2017-06-19 23:00 | 312 | 302
2017-06-19 23:30 | 310 | 299
2017-06-20 | 311 | 296
2017-06-20 00:30 | 319 | 305
2017-06-20 01:00 | 307 | 294
2017-06-20 01:30 | 298 | 284
2017-06-20 02:00 | 289 | 274
2017-06-20 02:30 | 293 | 277
2017-06-20 03:00 | 286 | 270
2017-06-20 03:30 | 290 | 274
2017-06-20 04:00 | 286 | 268
2017-06-20 04:30 | 290 | 273
2017-06-20 05:00 | 292 | 276
2017-06-20 05:30 | 302 | 287
2017-06-20 06:00 | 320 | 306
2017-06-20 06:30 | 360 | 350
2017-06-20 07:00 | 388 | 383
2017-06-20 07:30 | 385 | 381
2017-06-20 08:00 | 387 | 382
2017-06-20 08:30 | 379 | 375
2017-06-20 09:00 | 370 | 366
2017-06-20 09:30 | 357 | 352
2017-06-20 10:00 | 353 | 347
2017-06-20 10:30 | 356 | 350
2017-06-20 11:00 | 343 | 337
2017-06-20 11:30 | 350 | 344
2017-06-20 12:00 | 344 | 337
2017-06-20 12:30 | 347 | 341
2017-06-20 13:00 | 353 | 347
2017-06-20 13:30 | 340 | 334
2017-06-20 14:00 | 308 | 302
2017-06-20 14:30 | 282 | 274
2017-06-20 15:00 | 277 | 267
2017-06-20 15:30 | 206 | 192
2017-06-20 16:00 | 203 | 183
2017-06-20 16:30 | 212 | 192
2017-06-20 17:00 | 226 | 208
2017-06-20 17:30 | 238 | 223
2017-06-20 18:00 | 286 | 274
2017-06-20 18:30 | 325 | 317
2017-06-20 19:00 | 328 | 322
2017-06-20 19:30 | 314 | 308
2017-06-20 20:00 | 294 | 287
2017-06-20 20:30 | 274 | 265
2017-06-20 21:00 | 263 | 253
2017-06-20 21:30 | 255 | 243
2017-06-20 22:00 | 243 | 229
2017-06-20 22:30 | 251 | 236
2017-06-20 23:00 | 287 | 274
2017-06-20 23:30 | 405 | 397
2017-06-21 | 392 | 388
2017-06-21 00:30 | 389 | 385
2017-06-21 01:00 | 375 | 371
2017-06-21 01:30 | 367 | 363
2017-06-21 02:00 | 364 | 360
2017-06-21 02:30 | 338 | 333
2017-06-21 03:00 | 335 | 329
2017-06-21 03:30 | 323 | 317
2017-06-21 04:00 | 321 | 314
2017-06-21 04:30 | 348 | 341
2017-06-21 05:00 | 387 | 382
2017-06-21 05:30 | 423 | 419
2017-06-21 06:00 | 443 | 440
2017-06-21 06:30 | 482 | 480
2017-06-21 07:00 | 499 | 497
2017-06-21 07:30 | 502 | 501
2017-06-21 08:00 | 523 | 522
2017-06-21 08:30 | 525 | 524
2017-06-21 09:00 | 511 | 510
2017-06-21 09:30 | 501 | 500
2017-06-21 10:00 | 494 | 493
2017-06-21 10:30 | 485 | 484
2017-06-21 11:00 | 466 | 465
2017-06-21 11:30 | 468 | 467
2017-06-21 12:00 | 464 | 462
2017-06-21 12:30 | 458 | 456
2017-06-21 13:00 | 465 | 463
2017-06-21 13:30 | 466 | 464
2017-06-21 14:00 | 457 | 455
2017-06-21 14:30 | 441 | 439
2017-06-21 15:00 | 440 | 438
2017-06-21 15:30 | 443 | 441
2017-06-21 16:00 | 461 | 459
2017-06-21 16:30 | 479 | 477
2017-06-21 17:00 | 486 | 485
2017-06-21 17:30 | 504 | 503
2017-06-21 18:00 | 555 | 555
2017-06-21 18:30 | 596 | 596
2017-06-21 19:00 | 602 | 602
2017-06-21 19:30 | 580 | 579
2017-06-21 20:00 | 559 | 558
2017-06-21 20:30 | 526 | 525
2017-06-21 21:00 | 504 | 503
2017-06-21 21:30 | 492 | 491
2017-06-21 22:00 | 482 | 481
2017-06-21 22:30 | 502 | 500
2017-06-21 23:00 | 492 | 490
2017-06-21 23:30 | 478 | 476
2017-06-22 | 459 | 456
2017-06-22 00:30 | 444 | 441
2017-06-22 01:00 | 422 | 420
2017-06-22 01:30 | 414 | 410
2017-06-22 02:00 | 404 | 400
2017-06-22 02:30 | 404 | 400
2017-06-22 03:00 | 408 | 404
2017-06-22 03:30 | 405 | 401
2017-06-22 04:00 | 404 | 400
2017-06-22 04:30 | 410 | 406
2017-06-22 05:00 | 417 | 414
2017-06-22 05:30 | 438 | 435
2017-06-22 06:00 | 445 | 442
2017-06-22 06:30 | 485 | 483
2017-06-22 07:00 | 524 | 522
2017-06-22 07:30 | 512 | 511
2017-06-22 08:00 | 514 | 513
2017-06-22 08:30 | 504 | 503
2017-06-22 09:00 | 457 | 456
2017-06-22 09:30 | 432 | 431
2017-06-22 10:00 | 423 | 421
2017-06-22 10:30 | 419 | 417
2017-06-22 11:00 | 420 | 418
2017-06-22 11:30 | 424 | 421
2017-06-22 12:00 | 429 | 426
2017-06-22 12:30 | 426 | 424
2017-06-22 13:00 | 460 | 458
2017-06-22 13:30 | 469 | 467
2017-06-22 14:00 | 454 | 453
2017-06-22 14:30 | 435 | 434
2017-06-22 15:00 | 437 | 435
2017-06-22 15:30 | 448 | 447
2017-06-22 16:00 | 468 | 467
2017-06-22 16:30 | 487 | 486
2017-06-22 17:00 | 504 | 503
2017-06-22 17:30 | 517 | 516
2017-06-22 18:00 | 562 | 561
2017-06-22 18:30 | 599 | 599
2017-06-22 19:00 | 607 | 607
2017-06-22 19:30 | 600 | 600
2017-06-22 20:00 | 580 | 580
2017-06-22 20:30 | 555 | 555
2017-06-22 21:00 | 578 | 578
2017-06-22 21:30 | 555 | 554
2017-06-22 22:00 | 530 | 530
2017-06-22 22:30 | 509 | 509
2017-06-22 23:00 | 484 | 483
2017-06-22 23:30 | 465 | 464
2017-06-23 | 446 | 445
2017-06-23 00:30 | 430 | 428
2017-06-23 01:00 | 424 | 421
2017-06-23 01:30 | 416 | 413
2017-06-23 02:00 | 405 | 402
2017-06-23 02:30 | 406 | 403
2017-06-23 03:00 | 395 | 392
2017-06-23 03:30 | 395 | 392
2017-06-23 04:00 | 400 | 397
2017-06-23 04:30 | 402 | 398
2017-06-23 05:00 | 409 | 406
2017-06-23 05:30 | 424 | 421
2017-06-23 06:00 | 450 | 448
2017-06-23 06:30 | 485 | 483
2017-06-23 07:00 | 505 | 504
2017-06-23 07:30 | 496 | 495
2017-06-23 08:00 | 508 | 507
2017-06-23 08:30 | 507 | 507
2017-06-23 09:00 | 489 | 488
2017-06-23 09:30 | 474 | 473
2017-06-23 10:00 | 462 | 460
2017-06-23 10:30 | 444 | 442
2017-06-23 11:00 | 438 | 437
2017-06-23 11:30 | 438 | 437
2017-06-23 12:00 | 432 | 430
2017-06-23 12:30 | 430 | 428
2017-06-23 13:00 | 443 | 440
2017-06-23 13:30 | 448 | 446
2017-06-23 14:00 | 452 | 451
2017-06-23 14:30 | 432 | 430
2017-06-23 15:00 | 437 | 435
2017-06-23 15:30 | 442 | 441
2017-06-23 16:00 | 448 | 446
2017-06-23 16:30 | 451 | 450
2017-06-23 17:00 | 462 | 460
2017-06-23 17:30 | 478 | 476
2017-06-23 18:00 | 524 | 523
2017-06-23 18:30 | 550 | 550
2017-06-23 19:00 | 554 | 554
2017-06-23 19:30 | 543 | 543
2017-06-23 20:00 | 522 | 522
2017-06-23 20:30 | 505 | 505
2017-06-23 21:00 | 491 | 490
2017-06-23 21:30 | 475 | 474
2017-06-23 22:00 | 456 | 455
2017-06-23 22:30 | 438 | 436
2017-06-23 23:00 | 427 | 425
2017-06-23 23:30 | 408 | 406
2017-06-24 | 396 | 393
2017-06-24 00:30 | 422 | 419
2017-06-24 01:00 | 422 | 419
2017-06-24 01:30 | 422 | 419
2017-06-24 02:00 | 407 | 405
2017-06-24 02:30 | 408 | 405
2017-06-24 03:00 | 410 | 407
2017-06-24 03:30 | 394 | 391
2017-06-24 04:00 | 388 | 384
2017-06-24 04:30 | 396 | 392
2017-06-24 05:00 | 397 | 394
2017-06-24 05:30 | 411 | 408
2017-06-24 06:00 | 416 | 413
2017-06-24 06:30 | 431 | 428
2017-06-24 07:00 | 436 | 433
2017-06-24 07:30 | 410 | 408
2017-06-24 08:00 | 428 | 425
2017-06-24 08:30 | 449 | 447
2017-06-24 09:00 | 457 | 456
2017-06-24 09:30 | 454 | 452
2017-06-24 10:00 | 443 | 441
2017-06-24 10:30 | 448 | 447
2017-06-24 11:00 | 444 | 443
2017-06-24 11:30 | 433 | 431
2017-06-24 12:00 | 433 | 432
2017-06-24 12:30 | 433 | 431
2017-06-24 13:00 | 421 | 419
2017-06-24 13:30 | 421 | 419
2017-06-24 14:00 | 418 | 417
2017-06-24 14:30 | 404 | 402
2017-06-24 15:00 | 403 | 402
2017-06-24 15:30 | 404 | 402
2017-06-24 16:00 | 412 | 410
2017-06-24 16:30 | 424 | 423
2017-06-24 17:00 | 447 | 447
2017-06-24 17:30 | 471 | 471
2017-06-24 18:00 | 516 | 515
2017-06-24 18:30 | 549 | 549
2017-06-24 19:00 | 538 | 538
2017-06-24 19:30 | 520 | 520
2017-06-24 20:00 | 502 | 502
2017-06-24 20:30 | 480 | 479
2017-06-24 21:00 | 464 | 463
2017-06-24 21:30 | 446 | 445
2017-06-24 22:00 | 430 | 430
2017-06-24 22:30 | 430 | 429
2017-06-24 23:00 | 417 | 416
2017-06-24 23:30 | 402 | 401
2017-06-25 | 386 | 385
2017-06-25 00:30 | 405 | 404
2017-06-25 01:00 | 399 | 398
2017-06-25 01:30 | 390 | 388
2017-06-25 02:00 | 379 | 377
2017-06-25 02:30 | 379 | 377
2017-06-25 03:00 | 380 | 378
2017-06-25 03:30 | 373 | 370
2017-06-25 04:00 | 376 | 374
2017-06-25 04:30 | 377 | 375
2017-06-25 05:00 | 383 | 381
2017-06-25 05:30 | 388 | 386
2017-06-25 06:00 | 390 | 388
2017-06-25 06:30 | 394 | 392
2017-06-25 07:00 | 364 | 362
2017-06-25 07:30 | 361 | 358
2017-06-25 08:00 | 371 | 368
2017-06-25 08:30 | 396 | 394
2017-06-25 09:00 | 412 | 410
2017-06-25 09:30 | 424 | 423
2017-06-25 10:00 | 414 | 413
2017-06-25 10:30 | 412 | 410
2017-06-25 11:00 | 414 | 412
2017-06-25 11:30 | 405 | 403
2017-06-25 12:00 | 401 | 399
2017-06-25 12:30 | 401 | 399
2017-06-25 13:00 | 393 | 391
2017-06-25 13:30 | 397 | 395
2017-06-25 14:00 | 398 | 396
2017-06-25 14:30 | 381 | 379
2017-06-25 15:00 | 374 | 372
2017-06-25 15:30 | 388 | 385
2017-06-25 16:00 | 403 | 400
2017-06-25 16:30 | 419 | 418
2017-06-25 17:00 | 434 | 433
2017-06-25 17:30 | 453 | 452
2017-06-25 18:00 | 503 | 502
2017-06-25 18:30 | 546 | 546
2017-06-25 19:00 | 542 | 542
2017-06-25 19:30 | 529 | 529
2017-06-25 20:00 | 506 | 505
2017-06-25 20:30 | 483 | 482
2017-06-25 21:00 | 465 | 465
2017-06-25 21:30 | 448 | 447
2017-06-25 22:00 | 444 | 443
2017-06-25 22:30 | 472 | 471
2017-06-25 23:00 | 448 | 447
2017-06-25 23:30 | 437 | 435
2017-06-26 | 419 | 418
2017-06-26 00:30 | 411 | 409
2017-06-26 01:00 | 397 | 395
2017-06-26 01:30 | 391 | 388
2017-06-26 02:00 | 383 | 381
2017-06-26 02:30 | 372 | 370
2017-06-26 03:00 | 364 | 360
2017-06-26 03:30 | 364 | 361
2017-06-26 04:00 | 370 | 367
2017-06-26 04:30 | 371 | 368
2017-06-26 05:00 | 378 | 375
2017-06-26 05:30 | 396 | 394
2017-06-26 06:00 | 415 | 412
2017-06-26 06:30 | 420 | 418
2017-06-26 07:00 | 412 | 411
2017-06-26 07:30 | 403 | 401
2017-06-26 08:00 | 419 | 417
2017-06-26 08:30 | 425 | 423
2017-06-26 09:00 | 422 | 420
2017-06-26 09:30 | 418 | 416
2017-06-26 10:00 | 413 | 411
2017-06-26 10:30 | 409 | 407
2017-06-26 11:00 | 396 | 394
2017-06-26 11:30 | 390 | 388
2017-06-26 12:00 | 390 | 387
2017-06-26 12:30 | 395 | 393
2017-06-26 13:00 | 405 | 403
2017-06-26 13:30 | 407 | 405
2017-06-26 14:00 | 412 | 410
2017-06-26 14:30 | 397 | 394
2017-06-26 15:00 | 390 | 387
2017-06-26 15:30 | 414 | 411
2017-06-26 16:00 | 421 | 419
2017-06-26 16:30 | 426 | 424
2017-06-26 17:00 | 442 | 440
2017-06-26 17:30 | 461 | 460
2017-06-26 18:00 | 490 | 489
2017-06-26 18:30 | 515 | 515
2017-06-26 19:00 | 519 | 519
2017-06-26 19:30 | 501 | 501
2017-06-26 20:00 | 510 | 509
2017-06-26 20:30 | 483 | 483
2017-06-26 21:00 | 460 | 459
2017-06-26 21:30 | 438 | 437
2017-06-26 22:00 | 423 | 422
2017-06-26 22:30 | 428 | 426
2017-06-26 23:00 | 457 | 455
2017-06-26 23:30 | 435 | 434
2017-06-27 | 407 | 406
2017-06-27 00:30 | 392 | 390
2017-06-27 01:00 | 368 | 366
2017-06-27 01:30 | 359 | 356
2017-06-27 02:00 | 350 | 347
2017-06-27 02:30 | 350 | 347
2017-06-27 03:00 | 347 | 343
2017-06-27 03:30 | 353 | 350
2017-06-27 04:00 | 349 | 345
2017-06-27 04:30 | 337 | 334
2017-06-27 05:00 | 300 | 296
2017-06-27 05:30 | 312 | 307
2017-06-27 06:00 | 329 | 324
2017-06-27 06:30 | 363 | 359
2017-06-27 07:00 | 386 | 383
2017-06-27 07:30 | 359 | 356
2017-06-27 08:00 | 366 | 363
2017-06-27 08:30 | 301 | 297
2017-06-27 09:00 | 237 | 228
2017-06-27 09:30 | 281 | 269
2017-06-27 10:00 | 317 | 308
2017-06-27 10:30 | 313 | 305
2017-06-27 11:00 | 309 | 302
2017-06-27 11:30 | 313 | 306
2017-06-27 12:00 | 288 | 281
2017-06-27 12:30 | 302 | 294
2017-06-27 13:00 | 299 | 291
2017-06-27 13:30 | 313 | 306
2017-06-27 14:00 | 313 | 307
2017-06-27 14:30 | 295 | 289
2017-06-27 15:00 | 285 | 278
2017-06-27 15:30 | 281 | 274
2017-06-27 16:00 | 290 | 282
2017-06-27 16:30 | 300 | 293
2017-06-27 17:00 | 271 | 264
2017-06-27 17:30 | 279 | 271
2017-06-27 18:00 | 231 | 221
2017-06-27 18:30 | 267 | 257
2017-06-27 19:00 | 282 | 274
2017-06-27 19:30 | 318 | 312
2017-06-27 20:00 | 337 | 333
2017-06-27 20:30 | 325 | 321
2017-06-27 21:00 | 301 | 297
2017-06-27 21:30 | 286 | 279
2017-06-27 22:00 | 283 | 275
2017-06-27 22:30 | 308 | 300
2017-06-27 23:00 | 277 | 269
2017-06-27 23:30 | 285 | 277
2017-06-28 | 292 | 284
2017-06-28 00:30 | 281 | 272
2017-06-28 01:00 | 265 | 255
2017-06-28 01:30 | 239 | 227
2017-06-28 02:00 | 244 | 231
2017-06-28 02:30 | 250 | 237
2017-06-28 03:00 | 250 | 238
2017-06-28 03:30 | 250 | 238
2017-06-28 04:00 | 255 | 243
2017-06-28 04:30 | 272 | 261
2017-06-28 05:00 | 294 | 284
2017-06-28 05:30 | 310 | 303
2017-06-28 06:00 | 329 | 322
2017-06-28 06:30 | 339 | 334
2017-06-28 07:00 | 301 | 295
2017-06-28 07:30 | 256 | 248
2017-06-28 08:00 | 280 | 270
2017-06-28 08:30 | 257 | 246
2017-06-28 09:00 | 295 | 284
2017-06-28 09:30 | 317 | 308
2017-06-28 10:00 | 324 | 317
2017-06-28 10:30 | 306 | 299
2017-06-28 11:00 | 299 | 291
2017-06-28 11:30 | 296 | 287
2017-06-28 12:00 | 300 | 291
2017-06-28 12:30 | 307 | 299
2017-06-28 13:00 | 315 | 307
2017-06-28 13:30 | 329 | 322
2017-06-28 14:00 | 341 | 336
2017-06-28 14:30 | 334 | 329
2017-06-28 15:00 | 327 | 321
2017-06-28 15:30 | 339 | 333
2017-06-28 16:00 | 339 | 334
2017-06-28 16:30 | 318 | 313
2017-06-28 17:00 | 267 | 260
2017-06-28 17:30 | 212 | 200
2017-06-28 18:00 | 225 | 210
2017-06-28 18:30 | 251 | 239
2017-06-28 19:00 | 257 | 246
2017-06-28 19:30 | 255 | 244
2017-06-28 20:00 | 284 | 274
2017-06-28 20:30 | 300 | 292
2017-06-28 21:00 | 337 | 331
2017-06-28 21:30 | 325 | 319
2017-06-28 22:00 | 316 | 310
2017-06-28 22:30 | 352 | 346
2017-06-28 23:00 | 328 | 323
2017-06-28 23:30 | 317 | 311
2017-06-29 | 303 | 296
2017-06-29 00:30 | 339 | 332
2017-06-29 01:00 | 406 | 402
2017-06-29 01:30 | 403 | 400
2017-06-29 02:00 | 403 | 400
2017-06-29 02:30 | 394 | 390
2017-06-29 03:00 | 390 | 386
2017-06-29 03:30 | 388 | 384
2017-06-29 04:00 | 388 | 384
2017-06-29 04:30 | 383 | 380
2017-06-29 05:00 | 387 | 383
2017-06-29 05:30 | 404 | 401
2017-06-29 06:00 | 416 | 413
2017-06-29 06:30 | 438 | 435
2017-06-29 07:00 | 449 | 447
2017-06-29 07:30 | 429 | 427
2017-06-29 08:00 | 433 | 431
2017-06-29 08:30 | 459 | 457
2017-06-29 09:00 | 457 | 456
2017-06-29 09:30 | 458 | 456
2017-06-29 10:00 | 448 | 447
2017-06-29 10:30 | 441 | 439
2017-06-29 11:00 | 439 | 437
2017-06-29 11:30 | 431 | 429
2017-06-29 12:00 | 427 | 425
2017-06-29 12:30 | 431 | 429
2017-06-29 13:00 | 440 | 438
2017-06-29 13:30 | 439 | 437
2017-06-29 14:00 | 439 | 437
2017-06-29 14:30 | 423 | 421
2017-06-29 15:00 | 416 | 414
2017-06-29 15:30 | 419 | 417
2017-06-29 16:00 | 428 | 426
2017-06-29 16:30 | 436 | 435
2017-06-29 17:00 | 431 | 429
2017-06-29 17:30 | 417 | 415
2017-06-29 18:00 | 449 | 447
2017-06-29 18:30 | 467 | 466
2017-06-29 19:00 | 502 | 501
2017-06-29 19:30 | 502 | 501
2017-06-29 20:00 | 507 | 506
2017-06-29 20:30 | 491 | 491
2017-06-29 21:00 | 475 | 474
2017-06-29 21:30 | 454 | 453
2017-06-29 22:00 | 433 | 432
2017-06-29 22:30 | 408 | 406
2017-06-29 23:00 | 402 | 399
2017-06-29 23:30 | 437 | 435
2017-06-30 | 419 | 417
2017-06-30 00:30 | 410 | 407
2017-06-30 01:00 | 400 | 397
2017-06-30 01:30 | 391 | 388
2017-06-30 02:00 | 388 | 384
2017-06-30 02:30 | 385 | 381
2017-06-30 03:00 | 382 | 379
2017-06-30 03:30 | 384 | 380
2017-06-30 04:00 | 383 | 379
2017-06-30 04:30 | 381 | 377
2017-06-30 05:00 | 391 | 387
2017-06-30 05:30 | 403 | 399
2017-06-30 06:00 | 415 | 412
2017-06-30 06:30 | 444 | 442
2017-06-30 07:00 | 413 | 411
2017-06-30 07:30 | 390 | 388
2017-06-30 08:00 | 400 | 397
2017-06-30 08:30 | 418 | 415
2017-06-30 09:00 | 455 | 453
2017-06-30 09:30 | 453 | 452
2017-06-30 10:00 | 443 | 442
2017-06-30 10:30 | 435 | 434
2017-06-30 11:00 | 431 | 429
2017-06-30 11:30 | 443 | 441
2017-06-30 12:00 | 452 | 451
2017-06-30 12:30 | 449 | 448
2017-06-30 13:00 | 442 | 441
2017-06-30 13:30 | 439 | 438
2017-06-30 14:00 | 433 | 432
2017-06-30 14:30 | 422 | 421
2017-06-30 15:00 | 422 | 421
2017-06-30 15:30 | 430 | 429
2017-06-30 16:00 | 428 | 427
2017-06-30 16:30 | 438 | 436
2017-06-30 17:00 | 443 | 442
2017-06-30 17:30 | 451 | 450
2017-06-30 18:00 | 444 | 444
2017-06-30 18:30 | 455 | 454
2017-06-30 19:00 | 481 | 480
2017-06-30 19:30 | 474 | 474
2017-06-30 20:00 | 477 | 476
2017-06-30 20:30 | 464 | 463
2017-06-30 21:00 | 454 | 454
2017-06-30 21:30 | 430 | 429
2017-06-30 22:00 | 429 | 427
2017-06-30 22:30 | 460 | 459
2017-06-30 23:00 | 433 | 432
2017-06-30 23:30 | 421 | 419
2017-07-01 | 405 | 403
2017-07-01 00:30 | 398 | 396
2017-07-01 01:00 | 387 | 384
2017-07-01 01:30 | 379 | 375
2017-07-01 02:00 | 373 | 370
2017-07-01 02:30 | 367 | 363
2017-07-01 03:00 | 357 | 353
2017-07-01 03:30 | 355 | 352
2017-07-01 04:00 | 363 | 360
2017-07-01 04:30 | 368 | 365
2017-07-01 05:00 | 363 | 360
2017-07-01 05:30 | 373 | 371
2017-07-01 06:00 | 357 | 355
2017-07-01 06:30 | 362 | 359
2017-07-01 07:00 | 378 | 375
2017-07-01 07:30 | 372 | 369
2017-07-01 08:00 | 391 | 389
2017-07-01 08:30 | 414 | 412
2017-07-01 09:00 | 426 | 424
2017-07-01 09:30 | 423 | 422
2017-07-01 10:00 | 414 | 412
2017-07-01 10:30 | 408 | 406
2017-07-01 11:00 | 405 | 403
2017-07-01 11:30 | 400 | 398
2017-07-01 12:00 | 409 | 407
2017-07-01 12:30 | 409 | 407
2017-07-01 13:00 | 402 | 400
2017-07-01 13:30 | 392 | 390
2017-07-01 14:00 | 389 | 387
2017-07-01 14:30 | 364 | 362
2017-07-01 15:00 | 369 | 366
2017-07-01 15:30 | 375 | 373
2017-07-01 16:00 | 384 | 382
2017-07-01 16:30 | 396 | 394
2017-07-01 17:00 | 412 | 410
2017-07-01 17:30 | 432 | 431
2017-07-01 18:00 | 471 | 470
2017-07-01 18:30 | 479 | 479
2017-07-01 19:00 | 489 | 488
2017-07-01 19:30 | 492 | 492
2017-07-01 20:00 | 477 | 477
2017-07-01 20:30 | 442 | 441
2017-07-01 21:00 | 440 | 439
2017-07-01 21:30 | 426 | 425
2017-07-01 22:00 | 422 | 420
2017-07-01 22:30 | 453 | 452
2017-07-01 23:00 | 440 | 439
2017-07-01 23:30 | 428 | 427
2017-07-02 | 417 | 416
2017-07-02 00:30 | 401 | 399
2017-07-02 01:00 | 396 | 394
2017-07-02 01:30 | 386 | 384
2017-07-02 02:00 | 378 | 376
2017-07-02 02:30 | 373 | 370
2017-07-02 03:00 | 367 | 364
2017-07-02 03:30 | 371 | 368
2017-07-02 04:00 | 371 | 367
2017-07-02 04:30 | 373 | 369
2017-07-02 05:00 | 380 | 377
2017-07-02 05:30 | 384 | 381
2017-07-02 06:00 | 367 | 364
2017-07-02 06:30 | 354 | 350
2017-07-02 07:00 | 349 | 345
2017-07-02 07:30 | 367 | 362
2017-07-02 08:00 | 385 | 381
2017-07-02 08:30 | 414 | 411
2017-07-02 09:00 | 431 | 429
2017-07-02 09:30 | 445 | 443
2017-07-02 10:00 | 444 | 442
2017-07-02 10:30 | 435 | 434
2017-07-02 11:00 | 424 | 423
2017-07-02 11:30 | 372 | 370
2017-07-02 12:00 | 358 | 354
2017-07-02 12:30 | 360 | 356
2017-07-02 13:00 | 374 | 370
2017-07-02 13:30 | 373 | 369
2017-07-02 14:00 | 364 | 360
2017-07-02 14:30 | 371 | 368
2017-07-02 15:00 | 397 | 393
2017-07-02 15:30 | 385 | 383
2017-07-02 16:00 | 394 | 392
2017-07-02 16:30 | 413 | 411
2017-07-02 17:00 | 428 | 426
2017-07-02 17:30 | 467 | 466
2017-07-02 18:00 | 475 | 474
2017-07-02 18:30 | 503 | 503
2017-07-02 19:00 | 509 | 509
2017-07-02 19:30 | 504 | 504
2017-07-02 20:00 | 487 | 486
2017-07-02 20:30 | 458 | 458
2017-07-02 21:00 | 444 | 443
2017-07-02 21:30 | 437 | 435
2017-07-02 22:00 | 427 | 425
2017-07-02 22:30 | 396 | 394
2017-07-02 23:00 | 393 | 391
2017-07-02 23:30 | 425 | 423
2017-07-03 | 409 | 407
2017-07-03 00:30 | 401 | 399
2017-07-03 01:00 | 398 | 396
2017-07-03 01:30 | 387 | 384
2017-07-03 02:00 | 379 | 375
2017-07-03 02:30 | 380 | 376
2017-07-03 03:00 | 382 | 378
2017-07-03 03:30 | 381 | 378
2017-07-03 04:00 | 380 | 377
2017-07-03 04:30 | 384 | 381
2017-07-03 05:00 | 355 | 351
2017-07-03 05:30 | 321 | 316
2017-07-03 06:00 | 325 | 319
2017-07-03 06:30 | 355 | 349
2017-07-03 07:00 | 383 | 378
2017-07-03 07:30 | 412 | 409
2017-07-03 08:00 | 425 | 423
2017-07-03 08:30 | 409 | 407
2017-07-03 09:00 | 442 | 440
2017-07-03 09:30 | 428 | 426
2017-07-03 10:00 | 457 | 455
2017-07-03 10:30 | 459 | 458
2017-07-03 11:00 | 451 | 449
2017-07-03 11:30 | 432 | 430
2017-07-03 12:00 | 437 | 435
2017-07-03 12:30 | 427 | 424
2017-07-03 13:00 | 445 | 443
2017-07-03 13:30 | 451 | 449
2017-07-03 14:00 | 444 | 442
2017-07-03 14:30 | 426 | 424
2017-07-03 15:00 | 421 | 418
2017-07-03 15:30 | 427 | 424
2017-07-03 16:00 | 424 | 422
2017-07-03 16:30 | 433 | 431
2017-07-03 17:00 | 454 | 452
2017-07-03 17:30 | 471 | 469
2017-07-03 18:00 | 517 | 516
2017-07-03 18:30 | 555 | 555
2017-07-03 19:00 | 554 | 554
2017-07-03 19:30 | 536 | 536
2017-07-03 20:00 | 515 | 515
2017-07-03 20:30 | 491 | 490
2017-07-03 21:00 | 471 | 470
2017-07-03 21:30 | 449 | 448
2017-07-03 22:00 | 418 | 416
2017-07-03 22:30 | 393 | 391
2017-07-03 23:00 | 389 | 386
2017-07-03 23:30 | 429 | 427
2017-07-04 | 414 | 412
2017-07-04 00:30 | 403 | 401
2017-07-04 01:00 | 391 | 388
2017-07-04 01:30 | 380 | 376
2017-07-04 02:00 | 374 | 370
2017-07-04 02:30 | 378 | 374
2017-07-04 03:00 | 376 | 372
2017-07-04 03:30 | 375 | 371
2017-07-04 04:00 | 378 | 375
2017-07-04 04:30 | 385 | 381
2017-07-04 05:00 | 392 | 388
2017-07-04 05:30 | 402 | 399
2017-07-04 06:00 | 419 | 417
2017-07-04 06:30 | 437 | 435
2017-07-04 07:00 | 404 | 402
2017-07-04 07:30 | 428 | 426
2017-07-04 08:00 | 451 | 449
2017-07-04 08:30 | 460 | 458
2017-07-04 09:00 | 454 | 453
2017-07-04 09:30 | 455 | 453
2017-07-04 10:00 | 455 | 454
2017-07-04 10:30 | 429 | 427
2017-07-04 11:00 | 383 | 381
2017-07-04 11:30 | 380 | 377
2017-07-04 12:00 | 367 | 364
2017-07-04 12:30 | 371 | 367
2017-07-04 13:00 | 380 | 377
2017-07-04 13:30 | 381 | 378
2017-07-04 14:00 | 367 | 364
2017-07-04 14:30 | 295 | 291
2017-07-04 15:00 | 270 | 262
2017-07-04 15:30 | 299 | 291
2017-07-04 16:00 | 306 | 299
2017-07-04 16:30 | 315 | 309
2017-07-04 17:00 | 329 | 324
2017-07-04 17:30 | 265 | 259
2017-07-04 18:00 | 274 | 266
2017-07-04 18:30 | 310 | 303
2017-07-04 19:00 | 321 | 315
2017-07-04 19:30 | 302 | 296
2017-07-04 20:00 | 285 | 279
2017-07-04 20:30 | 335 | 329
2017-07-04 21:00 | 358 | 354
2017-07-04 21:30 | 345 | 342
2017-07-04 22:00 | 331 | 327
2017-07-04 22:30 | 350 | 345
2017-07-04 23:00 | 332 | 328
2017-07-04 23:30 | 308 | 302
2017-07-05 | 292 | 285
2017-07-05 00:30 | 285 | 277
2017-07-05 01:00 | 266 | 256
2017-07-05 01:30 | 259 | 249
2017-07-05 02:00 | 255 | 243
2017-07-05 02:30 | 251 | 239
2017-07-05 03:00 | 252 | 240
2017-07-05 03:30 | 246 | 233
2017-07-05 04:00 | 242 | 229
2017-07-05 04:30 | 247 | 234
2017-07-05 05:00 | 260 | 248
2017-07-05 05:30 | 275 | 265
2017-07-05 06:00 | 272 | 263
2017-07-05 06:30 | 227 | 216
2017-07-05 07:00 | 250 | 237
2017-07-05 07:30 | 270 | 259
2017-07-05 08:00 | 281 | 272
2017-07-05 08:30 | 289 | 281
2017-07-05 09:00 | 286 | 278
2017-07-05 09:30 | 278 | 271
2017-07-05 10:00 | 263 | 255
2017-07-05 10:30 | 261 | 252
2017-07-05 11:00 | 254 | 245
2017-07-05 11:30 | 255 | 243
2017-07-05 12:00 | 246 | 235
2017-07-05 12:30 | 241 | 230
2017-07-05 13:00 | 238 | 226
2017-07-05 13:30 | 239 | 227
2017-07-05 14:00 | 249 | 238
2017-07-05 14:30 | 253 | 242
2017-07-05 15:00 | 256 | 246
2017-07-05 15:30 | 268 | 259
2017-07-05 16:00 | 287 | 278
2017-07-05 16:30 | 300 | 293
2017-07-05 17:00 | 316 | 310
2017-07-05 17:30 | 247 | 240
2017-07-05 18:00 | 282 | 273
2017-07-05 18:30 | 314 | 306
2017-07-05 19:00 | 321 | 314
2017-07-05 19:30 | 301 | 293
2017-07-05 20:00 | 283 | 275
2017-07-05 20:30 | 262 | 252
2017-07-05 21:00 | 247 | 233
2017-07-05 21:30 | 303 | 287
2017-07-05 22:00 | 316 | 303
2017-07-05 22:30 | 354 | 343
2017-07-05 23:00 | 334 | 324
2017-07-05 23:30 | 341 | 330
2017-07-06 | 316 | 304
2017-07-06 00:30 | 349 | 337
2017-07-06 01:00 | 414 | 405
2017-07-06 01:30 | 404 | 397
2017-07-06 02:00 | 373 | 365
2017-07-06 02:30 | 367 | 358
2017-07-06 03:00 | 368 | 358
2017-07-06 03:30 | 371 | 362
2017-07-06 04:00 | 377 | 368
2017-07-06 04:30 | 388 | 379
2017-07-06 05:00 | 389 | 382
2017-07-06 05:30 | 414 | 407
2017-07-06 06:00 | 434 | 428
2017-07-06 06:30 | 461 | 456
2017-07-06 07:00 | 487 | 483
2017-07-06 07:30 | 485 | 483
2017-07-06 08:00 | 503 | 501
2017-07-06 08:30 | 512 | 510
2017-07-06 09:00 | 502 | 500
2017-07-06 09:30 | 481 | 479
2017-07-06 10:00 | 475 | 472
2017-07-06 10:30 | 457 | 454
2017-07-06 11:00 | 450 | 447
2017-07-06 11:30 | 446 | 442
2017-07-06 12:00 | 437 | 434
2017-07-06 12:30 | 428 | 424
2017-07-06 13:00 | 432 | 428
2017-07-06 13:30 | 434 | 430
2017-07-06 14:00 | 426 | 422
2017-07-06 14:30 | 419 | 415
2017-07-06 15:00 | 421 | 417
2017-07-06 15:30 | 436 | 431
2017-07-06 16:00 | 450 | 446
2017-07-06 16:30 | 437 | 433
2017-07-06 17:00 | 450 | 446
2017-07-06 17:30 | 461 | 459
2017-07-06 18:00 | 482 | 480
2017-07-06 18:30 | 513 | 512
2017-07-06 19:00 | 528 | 526
2017-07-06 19:30 | 518 | 517
2017-07-06 20:00 | 496 | 495
2017-07-06 20:30 | 480 | 478
2017-07-06 21:00 | 455 | 453
2017-07-06 21:30 | 435 | 432
2017-07-06 22:00 | 421 | 419
2017-07-06 22:30 | 462 | 459
2017-07-06 23:00 | 447 | 445
2017-07-06 23:30 | 432 | 429
2017-07-07 | 413 | 410
2017-07-07 00:30 | 399 | 394
2017-07-07 01:00 | 390 | 385
2017-07-07 01:30 | 371 | 365
2017-07-07 02:00 | 367 | 361
2017-07-07 02:30 | 367 | 360
2017-07-07 03:00 | 367 | 360
2017-07-07 03:30 | 370 | 362
2017-07-07 04:00 | 379 | 372
2017-07-07 04:30 | 384 | 378
2017-07-07 05:00 | 378 | 372
2017-07-07 05:30 | 395 | 389
2017-07-07 06:00 | 419 | 414
2017-07-07 06:30 | 446 | 442
2017-07-07 07:00 | 457 | 454
2017-07-07 07:30 | 436 | 433
2017-07-07 08:00 | 442 | 439
2017-07-07 08:30 | 448 | 445
2017-07-07 09:00 | 451 | 447
2017-07-07 09:30 | 448 | 444
2017-07-07 10:00 | 438 | 435
2017-07-07 10:30 | 433 | 430
2017-07-07 11:00 | 418 | 414
2017-07-07 11:30 | 406 | 402
2017-07-07 12:00 | 404 | 399
2017-07-07 12:30 | 398 | 394
2017-07-07 13:00 | 398 | 394
2017-07-07 13:30 | 396 | 392
2017-07-07 14:00 | 394 | 390
2017-07-07 14:30 | 376 | 371
2017-07-07 15:00 | 397 | 391
2017-07-07 15:30 | 408 | 404
2017-07-07 16:00 | 421 | 417
2017-07-07 16:30 | 435 | 432
2017-07-07 17:00 | 453 | 449
2017-07-07 17:30 | 469 | 467
2017-07-07 18:00 | 499 | 497
2017-07-07 18:30 | 533 | 531
2017-07-07 19:00 | 552 | 551
2017-07-07 19:30 | 538 | 537
2017-07-07 20:00 | 516 | 515
2017-07-07 20:30 | 491 | 490
2017-07-07 21:00 | 482 | 481
2017-07-07 21:30 | 461 | 459
2017-07-07 22:00 | 447 | 444
2017-07-07 22:30 | 415 | 412
2017-07-07 23:00 | 390 | 386
2017-07-07 23:30 | 390 | 386
2017-07-08 | 429 | 425
2017-07-08 00:30 | 416 | 414
2017-07-08 01:00 | 404 | 401
2017-07-08 01:30 | 393 | 390
2017-07-08 02:00 | 389 | 386
2017-07-08 02:30 | 384 | 380
2017-07-08 03:00 | 380 | 376
2017-07-08 03:30 | 376 | 372
2017-07-08 04:00 | 389 | 385
2017-07-08 04:30 | 396 | 392
2017-07-08 05:00 | 396 | 392
2017-07-08 05:30 | 405 | 402
2017-07-08 06:00 | 395 | 391
2017-07-08 06:30 | 409 | 406
2017-07-08 07:00 | 402 | 399
2017-07-08 07:30 | 378 | 374
2017-07-08 08:00 | 416 | 412
2017-07-08 08:30 | 427 | 425
2017-07-08 09:00 | 430 | 428
2017-07-08 09:30 | 440 | 438
2017-07-08 10:00 | 434 | 433
2017-07-08 10:30 | 425 | 423
2017-07-08 11:00 | 386 | 383
2017-07-08 11:30 | 368 | 364
2017-07-08 12:00 | 361 | 356
2017-07-08 12:30 | 337 | 331
2017-07-08 13:00 | 333 | 326
2017-07-08 13:30 | 333 | 326
2017-07-08 14:00 | 330 | 323
2017-07-08 14:30 | 333 | 326
2017-07-08 15:00 | 343 | 337
2017-07-08 15:30 | 356 | 350
2017-07-08 16:00 | 369 | 365
2017-07-08 16:30 | 384 | 380
2017-07-08 17:00 | 417 | 414
2017-07-08 17:30 | 437 | 435
2017-07-08 18:00 | 454 | 453
2017-07-08 18:30 | 490 | 489
2017-07-08 19:00 | 505 | 504
2017-07-08 19:30 | 495 | 494
2017-07-08 20:00 | 495 | 494
2017-07-08 20:30 | 486 | 485
2017-07-08 21:00 | 469 | 468
2017-07-08 21:30 | 451 | 450
2017-07-08 22:00 | 450 | 448
2017-07-08 22:30 | 468 | 466
2017-07-08 23:00 | 459 | 457
2017-07-08 23:30 | 430 | 428
2017-07-09 | 414 | 411
2017-07-09 00:30 | 406 | 403
2017-07-09 01:00 | 395 | 390
2017-07-09 01:30 | 390 | 385
2017-07-09 02:00 | 377 | 371
2017-07-09 02:30 | 373 | 366
2017-07-09 03:00 | 370 | 363
2017-07-09 03:30 | 381 | 375
2017-07-09 04:00 | 375 | 369
2017-07-09 04:30 | 356 | 350
2017-07-09 05:00 | 321 | 313
2017-07-09 05:30 | 319 | 308
2017-07-09 06:00 | 323 | 313
2017-07-09 06:30 | 323 | 313
2017-07-09 07:00 | 330 | 320
2017-07-09 07:30 | 345 | 338
2017-07-09 08:00 | 350 | 344
2017-07-09 08:30 | 363 | 357
2017-07-09 09:00 | 364 | 359
2017-07-09 09:30 | 381 | 376
2017-07-09 10:00 | 377 | 372
2017-07-09 10:30 | 374 | 368
2017-07-09 11:00 | 373 | 367
2017-07-09 11:30 | 364 | 358
2017-07-09 12:00 | 354 | 347
2017-07-09 12:30 | 350 | 343
2017-07-09 13:00 | 353 | 346
2017-07-09 13:30 | 348 | 342
2017-07-09 14:00 | 344 | 337
2017-07-09 14:30 | 332 | 325
2017-07-09 15:00 | 336 | 329
2017-07-09 15:30 | 351 | 345
2017-07-09 16:00 | 359 | 353
2017-07-09 16:30 | 377 | 372
2017-07-09 17:00 | 396 | 392
2017-07-09 17:30 | 409 | 406
2017-07-09 18:00 | 457 | 455
2017-07-09 18:30 | 493 | 492
2017-07-09 19:00 | 506 | 505
2017-07-09 19:30 | 489 | 489
2017-07-09 20:00 | 457 | 456
2017-07-09 20:30 | 434 | 433
2017-07-09 21:00 | 421 | 419
2017-07-09 21:30 | 402 | 400
2017-07-09 22:00 | 385 | 382
2017-07-09 22:30 | 378 | 375
2017-07-09 23:00 | 414 | 410
2017-07-09 23:30 | 396 | 393
2017-07-10 | 384 | 381
2017-07-10 00:30 | 369 | 365
2017-07-10 01:00 | 361 | 356
2017-07-10 01:30 | 352 | 347
2017-07-10 02:00 | 349 | 343
2017-07-10 02:30 | 352 | 346
2017-07-10 03:00 | 355 | 349
2017-07-10 03:30 | 353 | 347
2017-07-10 04:00 | 354 | 348
2017-07-10 04:30 | 358 | 353
2017-07-10 05:00 | 364 | 359
2017-07-10 05:30 | 377 | 372
2017-07-10 06:00 | 394 | 389
2017-07-10 06:30 | 418 | 415
2017-07-10 07:00 | 433 | 431
2017-07-10 07:30 | 448 | 446
2017-07-10 08:00 | 475 | 473
2017-07-10 08:30 | 483 | 481
2017-07-10 09:00 | 475 | 474
2017-07-10 09:30 | 460 | 459
2017-07-10 10:00 | 450 | 448
2017-07-10 10:30 | 434 | 432
2017-07-10 11:00 | 424 | 421
2017-07-10 11:30 | 412 | 410
2017-07-10 12:00 | 414 | 411
2017-07-10 12:30 | 414 | 411
2017-07-10 13:00 | 415 | 412
2017-07-10 13:30 | 418 | 416
2017-07-10 14:00 | 424 | 421
2017-07-10 14:30 | 397 | 394
2017-07-10 15:00 | 402 | 399
2017-07-10 15:30 | 416 | 413
2017-07-10 16:00 | 425 | 423
2017-07-10 16:30 | 445 | 444
2017-07-10 17:00 | 457 | 456
2017-07-10 17:30 | 472 | 470
2017-07-10 18:00 | 473 | 472
2017-07-10 18:30 | 506 | 505
2017-07-10 19:00 | 520 | 519
2017-07-10 19:30 | 517 | 516
2017-07-10 20:00 | 504 | 503
2017-07-10 20:30 | 481 | 480
2017-07-10 21:00 | 453 | 452
2017-07-10 21:30 | 422 | 420
2017-07-10 22:00 | 408 | 405
2017-07-10 22:30 | 397 | 394
2017-07-10 23:00 | 423 | 420
2017-07-10 23:30 | 413 | 410
2017-07-11 | 395 | 392
2017-07-11 00:30 | 384 | 380
2017-07-11 01:00 | 376 | 371
2017-07-11 01:30 | 372 | 366
2017-07-11 02:00 | 365 | 359
2017-07-11 02:30 | 355 | 349
2017-07-11 03:00 | 352 | 345
2017-07-11 03:30 | 355 | 348
2017-07-11 04:00 | 353 | 346
2017-07-11 04:30 | 360 | 354
2017-07-11 05:00 | 374 | 368
2017-07-11 05:30 | 397 | 392
2017-07-11 06:00 | 406 | 402
2017-07-11 06:30 | 442 | 438
2017-07-11 07:00 | 462 | 460
2017-07-11 07:30 | 450 | 448
2017-07-11 08:00 | 456 | 454
2017-07-11 08:30 | 459 | 457
2017-07-11 09:00 | 448 | 446
2017-07-11 09:30 | 442 | 439
2017-07-11 10:00 | 437 | 435
2017-07-11 10:30 | 432 | 429
2017-07-11 11:00 | 377 | 374
2017-07-11 11:30 | 370 | 366
2017-07-11 12:00 | 368 | 363
2017-07-11 12:30 | 363 | 358
2017-07-11 13:00 | 370 | 365
2017-07-11 13:30 | 382 | 377
2017-07-11 14:00 | 367 | 363
2017-07-11 14:30 | 292 | 287
2017-07-11 15:00 | 284 | 275
2017-07-11 15:30 | 303 | 293
2017-07-11 16:00 | 305 | 296
2017-07-11 16:30 | 313 | 305
2017-07-11 17:00 | 323 | 315
2017-07-11 17:30 | 309 | 301
2017-07-11 18:00 | 269 | 259
2017-07-11 18:30 | 330 | 321
2017-07-11 19:00 | 333 | 325
2017-07-11 19:30 | 321 | 314
2017-07-11 20:00 | 331 | 324
2017-07-11 20:30 | 333 | 325
2017-07-11 21:00 | 335 | 328
2017-07-11 21:30 | 307 | 299
2017-07-11 22:00 | 290 | 281
2017-07-11 22:30 | 282 | 272
2017-07-11 23:00 | 322 | 312
2017-07-11 23:30 | 307 | 298
2017-07-12 | 295 | 284
2017-07-12 00:30 | 287 | 275
2017-07-12 01:00 | 268 | 255
2017-07-12 01:30 | 272 | 257
2017-07-12 02:00 | 273 | 258
2017-07-12 02:30 | 267 | 251
2017-07-12 03:00 | 264 | 249
2017-07-12 03:30 | 257 | 242
2017-07-12 04:00 | 266 | 251
2017-07-12 04:30 | 265 | 249
2017-07-12 05:00 | 277 | 262
2017-07-12 05:30 | 297 | 284
2017-07-12 06:00 | 310 | 299
2017-07-12 06:30 | 334 | 324
2017-07-12 07:00 | 352 | 344
2017-07-12 07:30 | 327 | 319
2017-07-12 08:00 | 266 | 256
2017-07-12 08:30 | 270 | 257
2017-07-12 09:00 | 337 | 328
2017-07-12 09:30 | 319 | 312
2017-07-12 10:00 | 307 | 299
2017-07-12 10:30 | 298 | 290
2017-07-12 11:00 | 297 | 287
2017-07-12 11:30 | 293 | 283
2017-07-12 12:00 | 302 | 292
2017-07-12 12:30 | 291 | 282
2017-07-12 13:00 | 289 | 279
2017-07-12 13:30 | 293 | 283
2017-07-12 14:00 | 290 | 280
2017-07-12 14:30 | 282 | 271
2017-07-12 15:00 | 279 | 268
2017-07-12 15:30 | 282 | 270
2017-07-12 16:00 | 298 | 287
2017-07-12 16:30 | 303 | 293
2017-07-12 17:00 | 326 | 317
2017-07-12 17:30 | 294 | 284
2017-07-12 18:00 | 291 | 280
2017-07-12 18:30 | 326 | 316
2017-07-12 19:00 | 334 | 326
2017-07-12 19:30 | 310 | 302
2017-07-12 20:00 | 289 | 280
2017-07-12 20:30 | 271 | 260
2017-07-12 21:00 | 244 | 230
2017-07-12 21:30 | 296 | 283
2017-07-12 22:00 | 309 | 299
2017-07-12 22:30 | 279 | 268
2017-07-12 23:00 | 262 | 249
2017-07-12 23:30 | 312 | 301
2017-07-13 | 321 | 312
2017-07-13 00:30 | 363 | 356
2017-07-13 01:00 | 410 | 405
2017-07-13 01:30 | 404 | 399
2017-07-13 02:00 | 392 | 387
2017-07-13 02:30 | 386 | 381
2017-07-13 03:00 | 380 | 374
2017-07-13 03:30 | 372 | 366
2017-07-13 04:00 | 371 | 365
2017-07-13 04:30 | 373 | 366
2017-07-13 05:00 | 372 | 366
2017-07-13 05:30 | 392 | 387
2017-07-13 06:00 | 397 | 392
2017-07-13 06:30 | 430 | 425
2017-07-13 07:00 | 414 | 410
2017-07-13 07:30 | 434 | 430
2017-07-13 08:00 | 453 | 451
2017-07-13 08:30 | 459 | 456
2017-07-13 09:00 | 446 | 444
2017-07-13 09:30 | 434 | 431
2017-07-13 10:00 | 425 | 422
2017-07-13 10:30 | 427 | 424
2017-07-13 11:00 | 413 | 409
2017-07-13 11:30 | 409 | 405
2017-07-13 12:00 | 412 | 408
2017-07-13 12:30 | 424 | 421
2017-07-13 13:00 | 425 | 421
2017-07-13 13:30 | 417 | 413
2017-07-13 14:00 | 415 | 411
2017-07-13 14:30 | 409 | 405
2017-07-13 15:00 | 402 | 399
2017-07-13 15:30 | 406 | 402
2017-07-13 16:00 | 414 | 411
2017-07-13 16:30 | 428 | 425
2017-07-13 17:00 | 442 | 439
2017-07-13 17:30 | 456 | 454
2017-07-13 18:00 | 492 | 490
2017-07-13 18:30 | 530 | 529
2017-07-13 19:00 | 531 | 531
2017-07-13 19:30 | 520 | 520
2017-07-13 20:00 | 499 | 498
2017-07-13 20:30 | 480 | 479
2017-07-13 21:00 | 460 | 459
2017-07-13 21:30 | 434 | 432
2017-07-13 22:00 | 415 | 413
2017-07-13 22:30 | 400 | 397
2017-07-13 23:00 | 438 | 435
2017-07-13 23:30 | 421 | 419
2017-07-14 | 407 | 405
2017-07-14 00:30 | 404 | 401
2017-07-14 01:00 | 388 | 385
2017-07-14 01:30 | 373 | 370
2017-07-14 02:00 | 365 | 361
2017-07-14 02:30 | 364 | 359
2017-07-14 03:00 | 357 | 352
2017-07-14 03:30 | 359 | 354
2017-07-14 04:00 | 362 | 357
2017-07-14 04:30 | 358 | 353
2017-07-14 05:00 | 366 | 361
2017-07-14 05:30 | 380 | 375
2017-07-14 06:00 | 399 | 395
2017-07-14 06:30 | 426 | 423
2017-07-14 07:00 | 442 | 439
2017-07-14 07:30 | 434 | 432
2017-07-14 08:00 | 447 | 445
2017-07-14 08:30 | 454 | 452
2017-07-14 09:00 | 445 | 443
2017-07-14 09:30 | 439 | 437
2017-07-14 10:00 | 428 | 426
2017-07-14 10:30 | 414 | 411
2017-07-14 11:00 | 404 | 400
2017-07-14 11:30 | 401 | 397
2017-07-14 12:00 | 406 | 402
2017-07-14 12:30 | 407 | 403
2017-07-14 13:00 | 413 | 410
2017-07-14 13:30 | 415 | 412
2017-07-14 14:00 | 405 | 402
2017-07-14 14:30 | 397 | 393
2017-07-14 15:00 | 383 | 380
2017-07-14 15:30 | 391 | 387
2017-07-14 16:00 | 414 | 411
2017-07-14 16:30 | 429 | 426
2017-07-14 17:00 | 432 | 429
2017-07-14 17:30 | 437 | 435
2017-07-14 18:00 | 454 | 452
2017-07-14 18:30 | 484 | 482
2017-07-14 19:00 | 486 | 485
2017-07-14 19:30 | 474 | 473
2017-07-14 20:00 | 457 | 456
2017-07-14 20:30 | 461 | 459
2017-07-14 21:00 | 454 | 452
2017-07-14 21:30 | 442 | 441
2017-07-14 22:00 | 437 | 435
2017-07-14 22:30 | 471 | 469
2017-07-14 23:00 | 452 | 451
2017-07-14 23:30 | 438 | 436
2017-07-15 | 420 | 418
2017-07-15 00:30 | 411 | 408
2017-07-15 01:00 | 389 | 386
2017-07-15 01:30 | 383 | 380
2017-07-15 02:00 | 374 | 370
2017-07-15 02:30 | 365 | 360
2017-07-15 03:00 | 367 | 363
2017-07-15 03:30 | 368 | 363
2017-07-15 04:00 | 375 | 371
2017-07-15 04:30 | 367 | 362
2017-07-15 05:00 | 337 | 332
2017-07-15 05:30 | 322 | 316
2017-07-15 06:00 | 323 | 317
2017-07-15 06:30 | 339 | 333
2017-07-15 07:00 | 358 | 352
2017-07-15 07:30 | 382 | 377
2017-07-15 08:00 | 398 | 394
2017-07-15 08:30 | 412 | 409
2017-07-15 09:00 | 419 | 417
2017-07-15 09:30 | 426 | 424
2017-07-15 10:00 | 408 | 406
2017-07-15 10:30 | 410 | 407
2017-07-15 11:00 | 410 | 407
2017-07-15 11:30 | 403 | 400
2017-07-15 12:00 | 398 | 395
2017-07-15 12:30 | 390 | 387
2017-07-15 13:00 | 397 | 394
2017-07-15 13:30 | 394 | 391
2017-07-15 14:00 | 393 | 389
2017-07-15 14:30 | 357 | 353
2017-07-15 15:00 | 357 | 352
2017-07-15 15:30 | 361 | 357
2017-07-15 16:00 | 376 | 372
2017-07-15 16:30 | 391 | 388
2017-07-15 17:00 | 413 | 411
2017-07-15 17:30 | 414 | 412
2017-07-15 18:00 | 463 | 461
2017-07-15 18:30 | 494 | 493
2017-07-15 19:00 | 485 | 484
2017-07-15 19:30 | 433 | 432
2017-07-15 20:00 | 417 | 416
2017-07-15 20:30 | 392 | 390
2017-07-15 21:00 | 378 | 375
2017-07-15 21:30 | 372 | 369
2017-07-15 22:00 | 367 | 364
2017-07-15 22:30 | 405 | 401
2017-07-15 23:00 | 402 | 399
2017-07-15 23:30 | 390 | 386
2017-07-16 | 376 | 373
2017-07-16 00:30 | 359 | 355
2017-07-16 01:00 | 345 | 341
2017-07-16 01:30 | 345 | 340
2017-07-16 02:00 | 338 | 332
2017-07-16 02:30 | 340 | 335
2017-07-16 03:00 | 332 | 325
2017-07-16 03:30 | 332 | 326
2017-07-16 04:00 | 331 | 324
2017-07-16 04:30 | 336 | 329
2017-07-16 05:00 | 340 | 333
2017-07-16 05:30 | 346 | 340
2017-07-16 06:00 | 347 | 341
2017-07-16 06:30 | 355 | 349
2017-07-16 07:00 | 352 | 346
2017-07-16 07:30 | 318 | 312
2017-07-16 08:00 | 332 | 324
2017-07-16 08:30 | 344 | 338
2017-07-16 09:00 | 346 | 341
2017-07-16 09:30 | 342 | 337
2017-07-16 10:00 | 340 | 335
2017-07-16 10:30 | 338 | 333
2017-07-16 11:00 | 336 | 330
2017-07-16 11:30 | 328 | 322
2017-07-16 12:00 | 328 | 322
2017-07-16 12:30 | 324 | 318
2017-07-16 13:00 | 314 | 307
2017-07-16 13:30 | 317 | 310
2017-07-16 14:00 | 317 | 310
2017-07-16 14:30 | 303 | 296
2017-07-16 15:00 | 310 | 303
2017-07-16 15:30 | 316 | 308
2017-07-16 16:00 | 328 | 321
2017-07-16 16:30 | 349 | 344
2017-07-16 17:00 | 367 | 363
2017-07-16 17:30 | 383 | 379
2017-07-16 18:00 | 425 | 422
2017-07-16 18:30 | 474 | 473
2017-07-16 19:00 | 470 | 469
2017-07-16 19:30 | 420 | 419
2017-07-16 20:00 | 397 | 395
2017-07-16 20:30 | 373 | 371
2017-07-16 21:00 | 360 | 358
2017-07-16 21:30 | 334 | 332
2017-07-16 22:00 | 315 | 312
2017-07-16 22:30 | 353 | 349
2017-07-16 23:00 | 347 | 344
2017-07-16 23:30 | 329 | 326
2017-07-17 | 317 | 314
2017-07-17 00:30 | 301 | 297
2017-07-17 01:00 | 302 | 297
2017-07-17 01:30 | 292 | 287
2017-07-17 02:00 | 288 | 283
2017-07-17 02:30 | 287 | 281
2017-07-17 03:00 | 280 | 274
2017-07-17 03:30 | 279 | 273
2017-07-17 04:00 | 291 | 285
2017-07-17 04:30 | 318 | 313
2017-07-17 05:00 | 321 | 317
2017-07-17 05:30 | 328 | 324
2017-07-17 06:00 | 346 | 343
2017-07-17 06:30 | 382 | 379
2017-07-17 07:00 | 366 | 364
2017-07-17 07:30 | 348 | 346
2017-07-17 08:00 | 352 | 350
2017-07-17 08:30 | 336 | 333
2017-07-17 09:00 | 325 | 322
2017-07-17 09:30 | 305 | 302
2017-07-17 10:00 | 297 | 293
2017-07-17 10:30 | 288 | 283
2017-07-17 11:00 | 288 | 283
2017-07-17 11:30 | 287 | 282
2017-07-17 12:00 | 283 | 279
2017-07-17 12:30 | 290 | 285
2017-07-17 13:00 | 284 | 279
2017-07-17 13:30 | 288 | 282
2017-07-17 14:00 | 284 | 279
2017-07-17 14:30 | 273 | 268
2017-07-17 15:00 | 279 | 273
2017-07-17 15:30 | 284 | 279
2017-07-17 16:00 | 304 | 300
2017-07-17 16:30 | 316 | 313
2017-07-17 17:00 | 327 | 324
2017-07-17 17:30 | 329 | 327
2017-07-17 18:00 | 331 | 329
2017-07-17 18:30 | 370 | 368
2017-07-17 19:00 | 384 | 382
2017-07-17 19:30 | 396 | 395
2017-07-17 20:00 | 393 | 392
2017-07-17 20:30 | 375 | 373
2017-07-17 21:00 | 353 | 352
2017-07-17 21:30 | 336 | 334
2017-07-17 22:00 | 313 | 310
2017-07-17 22:30 | 319 | 316
2017-07-17 23:00 | 338 | 335
2017-07-17 23:30 | 325 | 322
2017-07-18 | 307 | 303
2017-07-18 00:30 | 293 | 289
2017-07-18 01:00 | 278 | 273
2017-07-18 01:30 | 275 | 268
2017-07-18 02:00 | 268 | 261
2017-07-18 02:30 | 266 | 259
2017-07-18 03:00 | 273 | 265
2017-07-18 03:30 | 264 | 258
2017-07-18 04:00 | 268 | 261
2017-07-18 04:30 | 274 | 267
2017-07-18 05:00 | 276 | 270
2017-07-18 05:30 | 276 | 270
2017-07-18 06:00 | 260 | 253
2017-07-18 06:30 | 273 | 267
2017-07-18 07:00 | 304 | 298
2017-07-18 07:30 | 341 | 337
2017-07-18 08:00 | 355 | 351
2017-07-18 08:30 | 344 | 341
2017-07-18 09:00 | 324 | 320
2017-07-18 09:30 | 317 | 313
2017-07-18 10:00 | 313 | 304
2017-07-18 10:30 | 309 | 299
2017-07-18 11:00 | 300 | 289
2017-07-18 11:30 | 304 | 292
2017-07-18 12:00 | 301 | 289
2017-07-18 12:30 | 295 | 283
2017-07-18 13:00 | 295 | 283
2017-07-18 13:30 | 301 | 290
2017-07-18 14:00 | 312 | 301
2017-07-18 14:30 | 298 | 288
2017-07-18 15:00 | 300 | 289
2017-07-18 15:30 | 309 | 298
2017-07-18 16:00 | 322 | 311
2017-07-18 16:30 | 334 | 326
2017-07-18 17:00 | 343 | 335
2017-07-18 17:30 | 361 | 354
2017-07-18 18:00 | 394 | 388
2017-07-18 18:30 | 431 | 426
2017-07-18 19:00 | 442 | 439
2017-07-18 19:30 | 426 | 422
2017-07-18 20:00 | 406 | 402
2017-07-18 20:30 | 384 | 379
2017-07-18 21:00 | 370 | 365
2017-07-18 21:30 | 355 | 348
2017-07-18 22:00 | 334 | 326
2017-07-18 22:30 | 339 | 331
2017-07-18 23:00 | 362 | 355
2017-07-18 23:30 | 338 | 331
2017-07-19 | 323 | 314
2017-07-19 00:30 | 319 | 309
2017-07-19 01:00 | 313 | 303
2017-07-19 01:30 | 307 | 297
2017-07-19 02:00 | 301 | 290
2017-07-19 02:30 | 297 | 285
2017-07-19 03:00 | 291 | 278
2017-07-19 03:30 | 291 | 279
2017-07-19 04:00 | 289 | 277
2017-07-19 04:30 | 293 | 281
2017-07-19 05:00 | 297 | 285
2017-07-19 05:30 | 311 | 300
2017-07-19 06:00 | 328 | 319
2017-07-19 06:30 | 329 | 321
2017-07-19 07:00 | 317 | 308
2017-07-19 07:30 | 353 | 345
2017-07-19 08:00 | 362 | 355
2017-07-19 08:30 | 349 | 342
2017-07-19 09:00 | 323 | 315
2017-07-19 09:30 | 304 | 295
2017-07-19 10:00 | 294 | 283
2017-07-19 10:30 | 289 | 278
2017-07-19 11:00 | 295 | 283
2017-07-19 11:30 | 292 | 281
2017-07-19 12:00 | 288 | 276
2017-07-19 12:30 | 290 | 278
2017-07-19 13:00 | 296 | 284
2017-07-19 13:30 | 293 | 282
2017-07-19 14:00 | 294 | 282
2017-07-19 14:30 | 285 | 273
2017-07-19 15:00 | 284 | 272
2017-07-19 15:30 | 296 | 283
2017-07-19 16:00 | 313 | 302
2017-07-19 16:30 | 324 | 314
2017-07-19 17:00 | 339 | 331
2017-07-19 17:30 | 346 | 339
2017-07-19 18:00 | 384 | 378
2017-07-19 18:30 | 416 | 411
2017-07-19 19:00 | 435 | 431
2017-07-19 19:30 | 416 | 413
2017-07-19 20:00 | 392 | 388
2017-07-19 20:30 | 373 | 368
2017-07-19 21:00 | 357 | 351
2017-07-19 21:30 | 338 | 332
2017-07-19 22:00 | 315 | 307
2017-07-19 22:30 | 320 | 310
2017-07-19 23:00 | 342 | 333
2017-07-19 23:30 | 321 | 313
2017-07-20 | 306 | 295
2017-07-20 00:30 | 293 | 281
2017-07-20 01:00 | 284 | 271
2017-07-20 01:30 | 279 | 265
2017-07-20 02:00 | 270 | 255
2017-07-20 02:30 | 274 | 259
2017-07-20 03:00 | 262 | 247
2017-07-20 03:30 | 262 | 246
2017-07-20 04:00 | 270 | 254
2017-07-20 04:30 | 278 | 262
2017-07-20 05:00 | 279 | 264
2017-07-20 05:30 | 289 | 275
2017-07-20 06:00 | 304 | 291
2017-07-20 06:30 | 281 | 268
2017-07-20 07:00 | 296 | 283
2017-07-20 07:30 | 322 | 311
2017-07-20 08:00 | 336 | 327
2017-07-20 08:30 | 323 | 314
2017-07-20 09:00 | 310 | 300
2017-07-20 09:30 | 296 | 285
2017-07-20 10:00 | 278 | 265
2017-07-20 10:30 | 259 | 244
2017-07-20 11:00 | 221 | 200
2017-07-20 11:30 | 209 | 185
2017-07-20 12:00 | 204 | 176
2017-07-20 12:30 | 200 | 171
2017-07-20 13:00 | 199 | 170
2017-07-20 13:30 | 207 | 180
2017-07-20 14:00 | 205 | 178
2017-07-20 14:30 | 189 | 159
2017-07-20 15:00 | 150 | 108
2017-07-20 15:30 | 139 | 87
2017-07-20 16:00 | 119 | 43
2017-07-20 16:30 | 129 | 53
2017-07-20 17:00 | 135 | 68
2017-07-20 17:30 | 140 | 79
2017-07-20 18:00 | 174 | 131
2017-07-20 18:30 | 208 | 177
2017-07-20 19:00 | 220 | 195
2017-07-20 19:30 | 213 | 187
2017-07-20 20:00 | 187 | 157
2017-07-20 20:30 | 174 | 139
2017-07-20 21:00 | 167 | 127
2017-07-20 21:30 | 152 | 105
2017-07-20 22:00 | 141 | 86
2017-07-20 22:30 | 144 | 89
2017-07-20 23:00 | 212 | 179
2017-07-20 23:30 | 220 | 194
2017-07-21 | 200 | 172
2017-07-21 00:30 | 191 | 158
2017-07-21 01:00 | 181 | 144
2017-07-21 01:30 | 182 | 145
2017-07-21 02:00 | 174 | 134
2017-07-21 02:30 | 173 | 133
2017-07-21 03:00 | 170 | 131
2017-07-21 03:30 | 170 | 130
2017-07-21 04:00 | 174 | 135
2017-07-21 04:30 | 178 | 141
2017-07-21 05:00 | 180 | 145
2017-07-21 05:30 | 184 | 149
2017-07-21 06:00 | 148 | 104
2017-07-21 06:30 | 123 | 57
2017-07-21 07:00 | 126 | 52
2017-07-21 07:30 | 135 | 72
2017-07-21 08:00 | 135 | 75
2017-07-21 08:30 | 134 | 73
2017-07-21 09:00 | 134 | 67
2017-07-21 09:30 | 127 | 51
2017-07-21 10:00 | 151 | 95
2017-07-21 10:30 | 169 | 124
2017-07-21 11:00 | 120 | 37
2017-07-21 11:30 | 123 | 27
2017-07-21 12:00 | 124 | 24
2017-07-21 12:30 | 124 | 22
2017-07-21 13:00 | 123 | 14
2017-07-21 13:30 | 123 | 14
2017-07-21 14:00 | 123 | 18
2017-07-21 14:30 | 121 | 3
2017-07-21 15:00 | 123 | 10
2017-07-21 15:30 | 123 | 15
2017-07-21 16:00 | 125 | 32
2017-07-21 16:30 | 126 | 40
2017-07-21 17:00 | 136 | 65
2017-07-21 17:30 | 136 | 76
2017-07-21 18:00 | 162 | 116
2017-07-21 18:30 | 186 | 150
2017-07-21 19:00 | 189 | 157
2017-07-21 19:30 | 180 | 148
2017-07-21 20:00 | 166 | 129
2017-07-21 20:30 | 158 | 116
2017-07-21 21:00 | 150 | 103
2017-07-21 21:30 | 141 | 88
2017-07-21 22:00 | 131 | 71
2017-07-21 22:30 | 140 | 85
2017-07-21 23:00 | 159 | 114
2017-07-21 23:30 | 143 | 93
2017-07-22 | 184 | 147
2017-07-22 00:30 | 232 | 207
2017-07-22 01:00 | 287 | 271
2017-07-22 01:30 | 278 | 265
2017-07-22 02:00 | 275 | 261
2017-07-22 02:30 | 277 | 263
2017-07-22 03:00 | 271 | 257
2017-07-22 03:30 | 271 | 256
2017-07-22 04:00 | 269 | 254
2017-07-22 04:30 | 272 | 258
2017-07-22 05:00 | 275 | 261
2017-07-22 05:30 | 285 | 272
2017-07-22 06:00 | 293 | 280
2017-07-22 06:30 | 297 | 285
2017-07-22 07:00 | 295 | 283
2017-07-22 07:30 | 270 | 256
2017-07-22 08:00 | 286 | 273
2017-07-22 08:30 | 321 | 310
2017-07-22 09:00 | 326 | 316
2017-07-22 09:30 | 310 | 301
2017-07-22 10:00 | 290 | 279
2017-07-22 10:30 | 269 | 256
2017-07-22 11:00 | 265 | 251
2017-07-22 11:30 | 255 | 241
2017-07-22 12:00 | 254 | 238
2017-07-22 12:30 | 250 | 233
2017-07-22 13:00 | 253 | 236
2017-07-22 13:30 | 246 | 229
2017-07-22 14:00 | 246 | 229
2017-07-22 14:30 | 236 | 218
2017-07-22 15:00 | 235 | 216
2017-07-22 15:30 | 244 | 225
2017-07-22 16:00 | 259 | 242
2017-07-22 16:30 | 279 | 264
2017-07-22 17:00 | 297 | 285
2017-07-22 17:30 | 320 | 310
2017-07-22 18:00 | 352 | 345
2017-07-22 18:30 | 372 | 367
2017-07-22 19:00 | 376 | 371
2017-07-22 19:30 | 368 | 364
2017-07-22 20:00 | 351 | 346
2017-07-22 20:30 | 338 | 332
2017-07-22 21:00 | 326 | 319
2017-07-22 21:30 | 309 | 302
2017-07-22 22:00 | 295 | 287
2017-07-22 22:30 | 270 | 261
2017-07-22 23:00 | 260 | 248
2017-07-22 23:30 | 252 | 238
2017-07-23 | 247 | 233
2017-07-23 00:30 | 284 | 271
2017-07-23 01:00 | 280 | 268
2017-07-23 01:30 | 269 | 258
2017-07-23 02:00 | 260 | 248
2017-07-23 02:30 | 257 | 244
2017-07-23 03:00 | 253 | 240
2017-07-23 03:30 | 258 | 246
2017-07-23 04:00 | 259 | 249
2017-07-23 04:30 | 259 | 249
2017-07-23 05:00 | 265 | 255
2017-07-23 05:30 | 267 | 258
2017-07-23 06:00 | 264 | 256
2017-07-23 06:30 | 267 | 259
2017-07-23 07:00 | 263 | 255
2017-07-23 07:30 | 235 | 225
2017-07-23 08:00 | 245 | 234
2017-07-23 08:30 | 261 | 252
2017-07-23 09:00 | 268 | 259
2017-07-23 09:30 | 270 | 263
2017-07-23 10:00 | 270 | 262
2017-07-23 10:30 | 264 | 256
2017-07-23 11:00 | 259 | 251
2017-07-23 11:30 | 249 | 240
2017-07-23 12:00 | 249 | 240
2017-07-23 12:30 | 242 | 232
2017-07-23 13:00 | 242 | 232
2017-07-23 13:30 | 247 | 237
2017-07-23 14:00 | 246 | 236
2017-07-23 14:30 | 237 | 227
2017-07-23 15:00 | 233 | 221
2017-07-23 15:30 | 243 | 232
2017-07-23 16:00 | 256 | 246
2017-07-23 16:30 | 273 | 265
2017-07-23 17:00 | 290 | 284
2017-07-23 17:30 | 332 | 327
2017-07-23 18:00 | 393 | 390
2017-07-23 18:30 | 439 | 437
2017-07-23 19:00 | 440 | 439
2017-07-23 19:30 | 415 | 414
2017-07-23 20:00 | 393 | 392
2017-07-23 20:30 | 368 | 366
2017-07-23 21:00 | 344 | 341
2017-07-23 21:30 | 319 | 315
2017-07-23 22:00 | 312 | 307
2017-07-23 22:30 | 336 | 331
2017-07-23 23:00 | 322 | 318
2017-07-23 23:30 | 306 | 301
2017-07-24 | 291 | 285
2017-07-24 00:30 | 283 | 276
2017-07-24 01:00 | 280 | 272
2017-07-24 01:30 | 268 | 259
2017-07-24 02:00 | 259 | 251
2017-07-24 02:30 | 262 | 253
2017-07-24 03:00 | 264 | 255
2017-07-24 03:30 | 267 | 258
2017-07-24 04:00 | 267 | 259
2017-07-24 04:30 | 272 | 264
2017-07-24 05:00 | 276 | 268
2017-07-24 05:30 | 287 | 280
2017-07-24 06:00 | 294 | 287
2017-07-24 06:30 | 271 | 263
2017-07-24 07:00 | 279 | 271
2017-07-24 07:30 | 316 | 310
2017-07-24 08:00 | 329 | 324
2017-07-24 08:30 | 325 | 321
2017-07-24 09:00 | 305 | 300
2017-07-24 09:30 | 300 | 295
2017-07-24 10:00 | 294 | 288
2017-07-24 10:30 | 292 | 285
2017-07-24 11:00 | 284 | 277
2017-07-24 11:30 | 281 | 273
2017-07-24 12:00 | 289 | 281
2017-07-24 12:30 | 285 | 277
2017-07-24 13:00 | 285 | 278
2017-07-24 13:30 | 297 | 289
2017-07-24 14:00 | 300 | 293
2017-07-24 14:30 | 284 | 278
2017-07-24 15:00 | 285 | 277
2017-07-24 15:30 | 291 | 284
2017-07-24 16:00 | 299 | 292
2017-07-24 16:30 | 310 | 304
2017-07-24 17:00 | 331 | 326
2017-07-24 17:30 | 343 | 339
2017-07-24 18:00 | 386 | 383
2017-07-24 18:30 | 429 | 427
2017-07-24 19:00 | 448 | 447
2017-07-24 19:30 | 433 | 432
2017-07-24 20:00 | 405 | 404
2017-07-24 20:30 | 382 | 380
2017-07-24 21:00 | 365 | 363
2017-07-24 21:30 | 344 | 341
2017-07-24 22:00 | 326 | 322
2017-07-24 22:30 | 329 | 325
2017-07-24 23:00 | 328 | 324
2017-07-24 23:30 | 299 | 294
2017-07-25 | 317 | 311
2017-07-25 00:30 | 307 | 301
2017-07-25 01:00 | 295 | 289
2017-07-25 01:30 | 285 | 278
2017-07-25 02:00 | 274 | 266
2017-07-25 02:30 | 274 | 265
2017-07-25 03:00 | 264 | 255
2017-07-25 03:30 | 271 | 262
2017-07-25 04:00 | 285 | 276
2017-07-25 04:30 | 289 | 282
2017-07-25 05:00 | 309 | 303
2017-07-25 05:30 | 330 | 325
2017-07-25 06:00 | 353 | 349
2017-07-25 06:30 | 338 | 334
2017-07-25 07:00 | 347 | 343
2017-07-25 07:30 | 387 | 383
2017-07-25 08:00 | 390 | 387
2017-07-25 08:30 | 387 | 385
2017-07-25 09:00 | 368 | 366
2017-07-25 09:30 | 359 | 355
2017-07-25 10:00 | 351 | 347
2017-07-25 10:30 | 341 | 337
2017-07-25 11:00 | 338 | 333
2017-07-25 11:30 | 343 | 338
2017-07-25 12:00 | 339 | 334
2017-07-25 12:30 | 330 | 325
2017-07-25 13:00 | 333 | 327
2017-07-25 13:30 | 340 | 334
2017-07-25 14:00 | 343 | 338
2017-07-25 14:30 | 330 | 325
2017-07-25 15:00 | 325 | 320
2017-07-25 15:30 | 338 | 333
2017-07-25 16:00 | 356 | 351
2017-07-25 16:30 | 365 | 361
2017-07-25 17:00 | 374 | 370
2017-07-25 17:30 | 388 | 385
2017-07-25 18:00 | 430 | 428
2017-07-25 18:30 | 472 | 471
2017-07-25 19:00 | 492 | 491
2017-07-25 19:30 | 476 | 475
2017-07-25 20:00 | 455 | 454
2017-07-25 20:30 | 436 | 436
2017-07-25 21:00 | 403 | 402
2017-07-25 21:30 | 371 | 370
2017-07-25 22:00 | 358 | 356
2017-07-25 22:30 | 361 | 358
2017-07-25 23:00 | 374 | 371
2017-07-25 23:30 | 355 | 352
2017-07-26 | 336 | 333
2017-07-26 00:30 | 325 | 321
2017-07-26 01:00 | 322 | 317
2017-07-26 01:30 | 315 | 310
2017-07-26 02:00 | 313 | 307
2017-07-26 02:30 | 300 | 294
2017-07-26 03:00 | 303 | 296
2017-07-26 03:30 | 291 | 284
2017-07-26 04:00 | 267 | 258
2017-07-26 04:30 | 274 | 265
2017-07-26 05:00 | 283 | 274
2017-07-26 05:30 | 298 | 289
2017-07-26 06:00 | 311 | 304
2017-07-26 06:30 | 292 | 285
2017-07-26 07:00 | 299 | 292
2017-07-26 07:30 | 339 | 332
2017-07-26 08:00 | 344 | 339
2017-07-26 08:30 | 335 | 330
2017-07-26 09:00 | 324 | 319
2017-07-26 09:30 | 312 | 306
2017-07-26 10:00 | 308 | 301
2017-07-26 10:30 | 304 | 297
2017-07-26 11:00 | 296 | 289
2017-07-26 11:30 | 288 | 280
2017-07-26 12:00 | 297 | 290
2017-07-26 12:30 | 296 | 290
2017-07-26 13:00 | 295 | 288
2017-07-26 13:30 | 297 | 290
2017-07-26 14:00 | 301 | 294
2017-07-26 14:30 | 274 | 267
2017-07-26 15:00 | 277 | 270
2017-07-26 15:30 | 284 | 276
2017-07-26 16:00 | 295 | 288
2017-07-26 16:30 | 302 | 296
2017-07-26 17:00 | 315 | 310
2017-07-26 17:30 | 334 | 329
2017-07-26 18:00 | 386 | 382
2017-07-26 18:30 | 418 | 416
2017-07-26 19:00 | 440 | 438
2017-07-26 19:30 | 432 | 430
2017-07-26 20:00 | 407 | 406
2017-07-26 20:30 | 390 | 388
2017-07-26 21:00 | 374 | 373
2017-07-26 21:30 | 350 | 348
2017-07-26 22:00 | 336 | 333
2017-07-26 22:30 | 319 | 315
2017-07-26 23:00 | 321 | 317
2017-07-26 23:30 | 290 | 285
2017-07-27 | 310 | 304
2017-07-27 00:30 | 299 | 293
2017-07-27 01:00 | 298 | 292
2017-07-27 01:30 | 284 | 277
2017-07-27 02:00 | 275 | 267
2017-07-27 02:30 | 281 | 273
2017-07-27 03:00 | 284 | 277
2017-07-27 03:30 | 276 | 268
2017-07-27 04:00 | 277 | 269
2017-07-27 04:30 | 282 | 274
2017-07-27 05:00 | 288 | 281
2017-07-27 05:30 | 304 | 296
2017-07-27 06:00 | 313 | 306
2017-07-27 06:30 | 290 | 284
2017-07-27 07:00 | 298 | 291
2017-07-27 07:30 | 337 | 331
2017-07-27 08:00 | 355 | 351
2017-07-27 08:30 | 346 | 342
2017-07-27 09:00 | 329 | 325
2017-07-27 09:30 | 320 | 314
2017-07-27 10:00 | 309 | 303
2017-07-27 10:30 | 311 | 304
2017-07-27 11:00 | 308 | 302
2017-07-27 11:30 | 309 | 302
2017-07-27 12:00 | 309 | 302
2017-07-27 12:30 | 297 | 290
2017-07-27 13:00 | 299 | 291
2017-07-27 13:30 | 297 | 290
2017-07-27 14:00 | 305 | 298
2017-07-27 14:30 | 293 | 286
2017-07-27 15:00 | 276 | 268
2017-07-27 15:30 | 275 | 267
2017-07-27 16:00 | 282 | 274
2017-07-27 16:30 | 298 | 291
2017-07-27 17:00 | 314 | 308
2017-07-27 17:30 | 327 | 323
2017-07-27 18:00 | 396 | 392
2017-07-27 18:30 | 450 | 448
2017-07-27 19:00 | 441 | 440
2017-07-27 19:30 | 420 | 418
2017-07-27 20:00 | 407 | 406
2017-07-27 20:30 | 389 | 387
2017-07-27 21:00 | 373 | 371
2017-07-27 21:30 | 354 | 351
2017-07-27 22:00 | 336 | 332
2017-07-27 22:30 | 344 | 341
2017-07-27 23:00 | 370 | 367
2017-07-27 23:30 | 373 | 370
2017-07-28 | 347 | 344
2017-07-28 00:30 | 345 | 341
2017-07-28 01:00 | 333 | 329
2017-07-28 01:30 | 328 | 324
2017-07-28 02:00 | 323 | 318
2017-07-28 02:30 | 322 | 317
2017-07-28 03:00 | 320 | 315
2017-07-28 03:30 | 327 | 322
2017-07-28 04:00 | 326 | 322
2017-07-28 04:30 | 324 | 319
2017-07-28 05:00 | 331 | 327
2017-07-28 05:30 | 346 | 342
2017-07-28 06:00 | 358 | 354
2017-07-28 06:30 | 334 | 330
2017-07-28 07:00 | 365 | 361
2017-07-28 07:30 | 399 | 396
2017-07-28 08:00 | 404 | 402
2017-07-28 08:30 | 407 | 405
2017-07-28 09:00 | 418 | 416
2017-07-28 09:30 | 404 | 403
2017-07-28 10:00 | 366 | 365
2017-07-28 10:30 | 335 | 332
2017-07-28 11:00 | 377 | 374
2017-07-28 11:30 | 378 | 376
2017-07-28 12:00 | 376 | 374
2017-07-28 12:30 | 380 | 378
2017-07-28 13:00 | 360 | 358
2017-07-28 13:30 | 359 | 356
2017-07-28 14:00 | 362 | 359
2017-07-28 14:30 | 342 | 339
2017-07-28 15:00 | 345 | 342
2017-07-28 15:30 | 354 | 351
2017-07-28 16:00 | 369 | 366
2017-07-28 16:30 | 390 | 388
2017-07-28 17:00 | 403 | 401
2017-07-28 17:30 | 415 | 413
2017-07-28 18:00 | 453 | 452
2017-07-28 18:30 | 439 | 438
2017-07-28 19:00 | 430 | 429
2017-07-28 19:30 | 423 | 422
2017-07-28 20:00 | 394 | 392
2017-07-28 20:30 | 369 | 367
2017-07-28 21:00 | 360 | 358
2017-07-28 21:30 | 344 | 341
2017-07-28 22:00 | 319 | 315
2017-07-28 22:30 | 337 | 333
2017-07-28 23:00 | 363 | 360
2017-07-28 23:30 | 341 | 338
2017-07-29 | 330 | 327
2017-07-29 00:30 | 360 | 356
2017-07-29 01:00 | 349 | 346
2017-07-29 01:30 | 343 | 339
2017-07-29 02:00 | 338 | 335
2017-07-29 02:30 | 337 | 333
2017-07-29 03:00 | 329 | 326
2017-07-29 03:30 | 324 | 320
2017-07-29 04:00 | 328 | 324
2017-07-29 04:30 | 329 | 325
2017-07-29 05:00 | 331 | 326
2017-07-29 05:30 | 337 | 333
2017-07-29 06:00 | 315 | 311
2017-07-29 06:30 | 318 | 314
2017-07-29 07:00 | 331 | 326
2017-07-29 07:30 | 340 | 336
2017-07-29 08:00 | 346 | 343
2017-07-29 08:30 | 368 | 365
2017-07-29 09:00 | 371 | 368
2017-07-29 09:30 | 373 | 370
2017-07-29 10:00 | 367 | 365
2017-07-29 10:30 | 363 | 361
2017-07-29 11:00 | 353 | 351
2017-07-29 11:30 | 348 | 346
2017-07-29 12:00 | 341 | 338
2017-07-29 12:30 | 337 | 334
2017-07-29 13:00 | 333 | 330
2017-07-29 13:30 | 334 | 331
2017-07-29 14:00 | 330 | 327
2017-07-29 14:30 | 311 | 308
2017-07-29 15:00 | 310 | 306
2017-07-29 15:30 | 324 | 320
2017-07-29 16:00 | 354 | 351
2017-07-29 16:30 | 369 | 367
2017-07-29 17:00 | 378 | 375
2017-07-29 17:30 | 402 | 400
2017-07-29 18:00 | 408 | 406
2017-07-29 18:30 | 441 | 440
2017-07-29 19:00 | 449 | 448
2017-07-29 19:30 | 409 | 408
2017-07-29 20:00 | 415 | 414
2017-07-29 20:30 | 417 | 415
2017-07-29 21:00 | 406 | 405
2017-07-29 21:30 | 391 | 389
2017-07-29 22:00 | 346 | 344
2017-07-29 22:30 | 383 | 380
2017-07-29 23:00 | 359 | 357
2017-07-29 23:30 | 332 | 329
2017-07-30 | 340 | 337
2017-07-30 00:30 | 359 | 356
2017-07-30 01:00 | 347 | 344
2017-07-30 01:30 | 339 | 336
2017-07-30 02:00 | 339 | 335
2017-07-30 02:30 | 336 | 332
2017-07-30 03:00 | 339 | 335
2017-07-30 03:30 | 338 | 334
2017-07-30 04:00 | 334 | 330
2017-07-30 04:30 | 340 | 336
2017-07-30 05:00 | 336 | 332
2017-07-30 05:30 | 331 | 327
2017-07-30 06:00 | 310 | 306
2017-07-30 06:30 | 295 | 290
2017-07-30 07:00 | 299 | 293
2017-07-30 07:30 | 320 | 315
2017-07-30 08:00 | 333 | 329
2017-07-30 08:30 | 348 | 345
2017-07-30 09:00 | 357 | 354
2017-07-30 09:30 | 367 | 365
2017-07-30 10:00 | 365 | 363
2017-07-30 10:30 | 367 | 365
2017-07-30 11:00 | 369 | 366
2017-07-30 11:30 | 364 | 362
2017-07-30 12:00 | 347 | 345
2017-07-30 12:30 | 337 | 334
2017-07-30 13:00 | 340 | 337
2017-07-30 13:30 | 351 | 348
2017-07-30 14:00 | 355 | 352
2017-07-30 14:30 | 329 | 325
2017-07-30 15:00 | 333 | 330
2017-07-30 15:30 | 344 | 340
2017-07-30 16:00 | 355 | 352
2017-07-30 16:30 | 377 | 375
2017-07-30 17:00 | 397 | 395
2017-07-30 17:30 | 420 | 419
2017-07-30 18:00 | 468 | 467
2017-07-30 18:30 | 501 | 500
2017-07-30 19:00 | 519 | 519
2017-07-30 19:30 | 508 | 508
2017-07-30 20:00 | 493 | 493
2017-07-30 20:30 | 473 | 472
2017-07-30 21:00 | 450 | 450
2017-07-30 21:30 | 428 | 427
2017-07-30 22:00 | 418 | 417
2017-07-30 22:30 | 437 | 436
2017-07-30 23:00 | 406 | 405
2017-07-30 23:30 | 388 | 387
2017-07-31 | 379 | 377
2017-07-31 00:30 | 368 | 365
2017-07-31 01:00 | 354 | 351
2017-07-31 01:30 | 351 | 348
2017-07-31 02:00 | 349 | 345
2017-07-31 02:30 | 339 | 335
2017-07-31 03:00 | 341 | 336
2017-07-31 03:30 | 343 | 339
2017-07-31 04:00 | 343 | 339
2017-07-31 04:30 | 352 | 348
2017-07-31 05:00 | 361 | 358
2017-07-31 05:30 | 383 | 381
2017-07-31 06:00 | 376 | 374
2017-07-31 06:30 | 373 | 371
2017-07-31 07:00 | 394 | 391
2017-07-31 07:30 | 434 | 432
2017-07-31 08:00 | 456 | 455
2017-07-31 08:30 | 454 | 453
2017-07-31 09:00 | 447 | 446
2017-07-31 09:30 | 444 | 443
2017-07-31 10:00 | 430 | 429
2017-07-31 10:30 | 414 | 412
2017-07-31 11:00 | 408 | 407
2017-07-31 11:30 | 332 | 329
2017-07-31 12:00 | 313 | 308
2017-07-31 12:30 | 318 | 313
2017-07-31 13:00 | 319 | 314
2017-07-31 13:30 | 313 | 308
2017-07-31 14:00 | 309 | 304
2017-07-31 14:30 | 293 | 287
2017-07-31 15:00 | 251 | 243
2017-07-31 15:30 | 209 | 199
2017-07-31 16:00 | 197 | 190
2017-07-31 16:30 | 201 | 194
2017-07-31 17:00 | 235 | 230
2017-07-31 17:30 | 233 | 228
2017-07-31 18:00 | 189 | 183
2017-07-31 18:30 | 249 | 243
2017-07-31 19:00 | 257 | 253
2017-07-31 19:30 | 244 | 240
2017-07-31 20:00 | 266 | 262
2017-07-31 20:30 | 252 | 247
2017-07-31 21:00 | 231 | 226
2017-07-31 21:30 | 218 | 212
2017-07-31 22:00 | 204 | 197
2017-07-31 22:30 | 173 | 164
2017-07-31 23:00 | 141 | 128
2017-07-31 23:30 | 195 | 185
2017-08-01 | 260 | 254
2017-08-01 00:30 | 270 | 267
2017-08-01 01:00 | 252 | 248
2017-08-01 01:30 | 246 | 242
2017-08-01 02:00 | 243 | 238
2017-08-01 02:30 | 240 | 234
2017-08-01 03:00 | 239 | 232
2017-08-01 03:30 | 240 | 233
2017-08-01 04:00 | 237 | 230
2017-08-01 04:30 | 238 | 232
2017-08-01 05:00 | 245 | 238
2017-08-01 05:30 | 253 | 247
2017-08-01 06:00 | 269 | 263
2017-08-01 06:30 | 162 | 153
2017-08-01 07:00 | 148 | 131
2017-08-01 07:30 | 179 | 164
2017-08-01 08:00 | 210 | 199
2017-08-01 08:30 | 229 | 220
2017-08-01 09:00 | 203 | 194
2017-08-01 09:30 | 240 | 231
2017-08-01 10:00 | 309 | 303
2017-08-01 10:30 | 294 | 289
2017-08-01 11:00 | 272 | 266
2017-08-01 11:30 | 257 | 251
2017-08-01 12:00 | 235 | 228
2017-08-01 12:30 | 180 | 171
2017-08-01 13:00 | 180 | 169
2017-08-01 13:30 | 192 | 179
2017-08-01 14:00 | 195 | 184
2017-08-01 14:30 | 226 | 217
2017-08-01 15:00 | 231 | 222
2017-08-01 15:30 | 237 | 228
2017-08-01 16:00 | 252 | 246
2017-08-01 16:30 | 198 | 190
2017-08-01 17:00 | 202 | 193
2017-08-01 17:30 | 212 | 202
2017-08-01 18:00 | 233 | 225
2017-08-01 18:30 | 254 | 248
2017-08-01 19:00 | 254 | 248
2017-08-01 19:30 | 295 | 290
2017-08-01 20:00 | 291 | 286
2017-08-01 20:30 | 273 | 268
2017-08-01 21:00 | 247 | 241
2017-08-01 21:30 | 221 | 214
2017-08-01 22:00 | 202 | 193
2017-08-01 22:30 | 197 | 187
2017-08-01 23:00 | 208 | 199
2017-08-01 23:30 | 191 | 181
2017-08-02 | 245 | 237
2017-08-02 00:30 | 304 | 300
2017-08-02 01:00 | 367 | 363
2017-08-02 01:30 | 361 | 359
2017-08-02 02:00 | 349 | 347
2017-08-02 02:30 | 341 | 338
2017-08-02 03:00 | 341 | 339
2017-08-02 03:30 | 349 | 346
2017-08-02 04:00 | 351 | 348
2017-08-02 04:30 | 349 | 347
2017-08-02 05:00 | 360 | 358
2017-08-02 05:30 | 365 | 363
2017-08-02 06:00 | 380 | 378
2017-08-02 06:30 | 353 | 351
2017-08-02 07:00 | 329 | 327
2017-08-02 07:30 | 411 | 409
2017-08-02 08:00 | 454 | 453
2017-08-02 08:30 | 447 | 447
2017-08-02 09:00 | 411 | 411
2017-08-02 09:30 | 396 | 396
2017-08-02 10:00 | 384 | 383
2017-08-02 10:30 | 371 | 369
2017-08-02 11:00 | 370 | 368
2017-08-02 11:30 | 363 | 362
2017-08-02 12:00 | 365 | 364
2017-08-02 12:30 | 360 | 359
2017-08-02 13:00 | 365 | 364
2017-08-02 13:30 | 373 | 371
2017-08-02 14:00 | 383 | 381
2017-08-02 14:30 | 363 | 362
2017-08-02 15:00 | 357 | 355
2017-08-02 15:30 | 368 | 367
2017-08-02 16:00 | 391 | 389
2017-08-02 16:30 | 405 | 404
2017-08-02 17:00 | 428 | 427
2017-08-02 17:30 | 396 | 395
2017-08-02 18:00 | 351 | 350
2017-08-02 18:30 | 365 | 363
2017-08-02 19:00 | 371 | 369
2017-08-02 19:30 | 358 | 357
2017-08-02 20:00 | 339 | 337
2017-08-02 20:30 | 325 | 322
2017-08-02 21:00 | 304 | 301
2017-08-02 21:30 | 288 | 285
2017-08-02 22:00 | 256 | 252
2017-08-02 22:30 | 258 | 253
2017-08-02 23:00 | 275 | 270
2017-08-02 23:30 | 262 | 257
2017-08-03 | 307 | 303
2017-08-03 00:30 | 384 | 381
2017-08-03 01:00 | 369 | 367
2017-08-03 01:30 | 364 | 362
2017-08-03 02:00 | 362 | 359
2017-08-03 02:30 | 359 | 357
2017-08-03 03:00 | 361 | 359
2017-08-03 03:30 | 364 | 361
2017-08-03 04:00 | 361 | 358
2017-08-03 04:30 | 364 | 362
2017-08-03 05:00 | 360 | 357
2017-08-03 05:30 | 382 | 380
2017-08-03 06:00 | 406 | 404
2017-08-03 06:30 | 388 | 387
2017-08-03 07:00 | 378 | 375
2017-08-03 07:30 | 399 | 397
2017-08-03 08:00 | 370 | 368
2017-08-03 08:30 | 364 | 362
2017-08-03 09:00 | 350 | 348
2017-08-03 09:30 | 334 | 331
2017-08-03 10:00 | 322 | 320
2017-08-03 10:30 | 317 | 314
2017-08-03 11:00 | 318 | 315
2017-08-03 11:30 | 313 | 310
2017-08-03 12:00 | 314 | 311
2017-08-03 12:30 | 353 | 350
2017-08-03 13:00 | 386 | 383
2017-08-03 13:30 | 403 | 400
2017-08-03 14:00 | 415 | 413
2017-08-03 14:30 | 411 | 409
2017-08-03 15:00 | 409 | 407
2017-08-03 15:30 | 413 | 411
2017-08-03 16:00 | 408 | 406
2017-08-03 16:30 | 399 | 397
2017-08-03 17:00 | 409 | 407
2017-08-03 17:30 | 342 | 340
2017-08-03 18:00 | 284 | 280
2017-08-03 18:30 | 332 | 328
2017-08-03 19:00 | 362 | 359
2017-08-03 19:30 | 351 | 348
2017-08-03 20:00 | 332 | 329
2017-08-03 20:30 | 310 | 307
2017-08-03 21:00 | 289 | 286
2017-08-03 21:30 | 270 | 266
2017-08-03 22:00 | 242 | 237
2017-08-03 22:30 | 250 | 245
2017-08-03 23:00 | 327 | 323
2017-08-03 23:30 | 389 | 387
2017-08-04 | 388 | 386
2017-08-04 00:30 | 389 | 387
2017-08-04 01:00 | 374 | 372
2017-08-04 01:30 | 361 | 359
2017-08-04 02:00 | 354 | 352
2017-08-04 02:30 | 353 | 350
2017-08-04 03:00 | 347 | 345
2017-08-04 03:30 | 342 | 340
2017-08-04 04:00 | 342 | 339
2017-08-04 04:30 | 338 | 336
2017-08-04 05:00 | 340 | 337
2017-08-04 05:30 | 359 | 356
2017-08-04 06:00 | 371 | 368
2017-08-04 06:30 | 348 | 345
2017-08-04 07:00 | 360 | 357
2017-08-04 07:30 | 396 | 393
2017-08-04 08:00 | 395 | 393
2017-08-04 08:30 | 268 | 265
2017-08-04 09:00 | 256 | 251
2017-08-04 09:30 | 246 | 240
2017-08-04 10:00 | 265 | 259
2017-08-04 10:30 | 277 | 272
2017-08-04 11:00 | 269 | 264
2017-08-04 11:30 | 259 | 254
2017-08-04 12:00 | 261 | 256
2017-08-04 12:30 | 271 | 266
2017-08-04 13:00 | 276 | 271
2017-08-04 13:30 | 279 | 274
2017-08-04 14:00 | 275 | 270
2017-08-04 14:30 | 261 | 256
2017-08-04 15:00 | 260 | 255
2017-08-04 15:30 | 263 | 258
2017-08-04 16:00 | 266 | 262
2017-08-04 16:30 | 267 | 262
2017-08-04 17:00 | 279 | 275
2017-08-04 17:30 | 290 | 286
2017-08-04 18:00 | 324 | 321
2017-08-04 18:30 | 353 | 351
2017-08-04 19:00 | 361 | 359
2017-08-04 19:30 | 344 | 342
2017-08-04 20:00 | 385 | 383
2017-08-04 20:30 | 448 | 446
2017-08-04 21:00 | 442 | 441
2017-08-04 21:30 | 427 | 426
2017-08-04 22:00 | 411 | 410
2017-08-04 22:30 | 418 | 417
2017-08-04 23:00 | 439 | 439
2017-08-04 23:30 | 428 | 427
2017-08-05 | 409 | 409
2017-08-05 00:30 | 396 | 395
2017-08-05 01:00 | 395 | 395
2017-08-05 01:30 | 397 | 397
2017-08-05 02:00 | 400 | 400
2017-08-05 02:30 | 384 | 384
2017-08-05 03:00 | 366 | 365
2017-08-05 03:30 | 354 | 353
2017-08-05 04:00 | 353 | 353
2017-08-05 04:30 | 355 | 354
2017-08-05 05:00 | 362 | 362
2017-08-05 05:30 | 360 | 359
2017-08-05 06:00 | 370 | 370
2017-08-05 06:30 | 332 | 331
2017-08-05 07:00 | 319 | 318
2017-08-05 07:30 | 350 | 349
2017-08-05 08:00 | 392 | 391
2017-08-05 08:30 | 414 | 413
2017-08-05 09:00 | 423 | 423
2017-08-05 09:30 | 418 | 417
2017-08-05 10:00 | 393 | 393
2017-08-05 10:30 | 390 | 389
2017-08-05 11:00 | 387 | 386
2017-08-05 11:30 | 297 | 295
2017-08-05 12:00 | 245 | 242
2017-08-05 12:30 | 237 | 233
2017-08-05 13:00 | 231 | 227
2017-08-05 13:30 | 230 | 225
2017-08-05 14:00 | 232 | 227
2017-08-05 14:30 | 219 | 213
2017-08-05 15:00 | 277 | 271
2017-08-05 15:30 | 224 | 219
2017-08-05 16:00 | 233 | 226
2017-08-05 16:30 | 243 | 236
2017-08-05 17:00 | 256 | 250
2017-08-05 17:30 | 278 | 273
2017-08-05 18:00 | 302 | 299
2017-08-05 18:30 | 317 | 314
2017-08-05 19:00 | 321 | 319
2017-08-05 19:30 | 419 | 417
2017-08-05 20:00 | 429 | 428
2017-08-05 20:30 | 410 | 409
2017-08-05 21:00 | 402 | 402
2017-08-05 21:30 | 384 | 383
2017-08-05 22:00 | 366 | 365
2017-08-05 22:30 | 406 | 404
2017-08-05 23:00 | 434 | 434
2017-08-05 23:30 | 417 | 416
2017-08-06 | 401 | 400
2017-08-06 00:30 | 393 | 392
2017-08-06 01:00 | 385 | 384
2017-08-06 01:30 | 373 | 372
2017-08-06 02:00 | 372 | 370
2017-08-06 02:30 | 361 | 360
2017-08-06 03:00 | 355 | 353
2017-08-06 03:30 | 356 | 354
2017-08-06 04:00 | 363 | 361
2017-08-06 04:30 | 364 | 362
2017-08-06 05:00 | 363 | 361
2017-08-06 05:30 | 367 | 365
2017-08-06 06:00 | 350 | 348
2017-08-06 06:30 | 316 | 314
2017-08-06 07:00 | 314 | 311
2017-08-06 07:30 | 336 | 333
2017-08-06 08:00 | 349 | 346
2017-08-06 08:30 | 378 | 375
2017-08-06 09:00 | 389 | 387
2017-08-06 09:30 | 384 | 383
2017-08-06 10:00 | 381 | 380
2017-08-06 10:30 | 390 | 388
2017-08-06 11:00 | 388 | 387
2017-08-06 11:30 | 380 | 379
2017-08-06 12:00 | 394 | 393
2017-08-06 12:30 | 383 | 382
2017-08-06 13:00 | 373 | 372
2017-08-06 13:30 | 366 | 364
2017-08-06 14:00 | 384 | 382
2017-08-06 14:30 | 360 | 358
2017-08-06 15:00 | 356 | 354
2017-08-06 15:30 | 367 | 365
2017-08-06 16:00 | 382 | 380
2017-08-06 16:30 | 384 | 383
2017-08-06 17:00 | 391 | 390
2017-08-06 17:30 | 416 | 415
2017-08-06 18:00 | 458 | 457
2017-08-06 18:30 | 501 | 501
2017-08-06 19:00 | 519 | 519
2017-08-06 19:30 | 505 | 505
2017-08-06 20:00 | 482 | 482
2017-08-06 20:30 | 461 | 461
2017-08-06 21:00 | 447 | 447
2017-08-06 21:30 | 417 | 417
2017-08-06 22:00 | 400 | 399
2017-08-06 22:30 | 410 | 409
2017-08-06 23:00 | 425 | 424
2017-08-06 23:30 | 410 | 409
2017-08-07 | 399 | 398
2017-08-07 00:30 | 392 | 391
2017-08-07 01:00 | 375 | 374
2017-08-07 01:30 | 368 | 367
2017-08-07 02:00 | 356 | 355
2017-08-07 02:30 | 331 | 329
2017-08-07 03:00 | 326 | 323
2017-08-07 03:30 | 326 | 323
2017-08-07 04:00 | 332 | 329
2017-08-07 04:30 | 363 | 361
2017-08-07 05:00 | 379 | 378
2017-08-07 05:30 | 391 | 390
2017-08-07 06:00 | 407 | 406
2017-08-07 06:30 | 394 | 393
2017-08-07 07:00 | 399 | 398
2017-08-07 07:30 | 451 | 450
2017-08-07 08:00 | 471 | 471
2017-08-07 08:30 | 460 | 460
2017-08-07 09:00 | 433 | 433
2017-08-07 09:30 | 419 | 418
2017-08-07 10:00 | 409 | 408
2017-08-07 10:30 | 404 | 403
2017-08-07 11:00 | 408 | 407
2017-08-07 11:30 | 427 | 426
2017-08-07 12:00 | 427 | 427
2017-08-07 12:30 | 430 | 429
2017-08-07 13:00 | 452 | 451
2017-08-07 13:30 | 460 | 459
2017-08-07 14:00 | 464 | 464
2017-08-07 14:30 | 433 | 433
2017-08-07 15:00 | 433 | 432
2017-08-07 15:30 | 445 | 444
2017-08-07 16:00 | 451 | 451
2017-08-07 16:30 | 456 | 456
2017-08-07 17:00 | 469 | 469
2017-08-07 17:30 | 461 | 461
2017-08-07 18:00 | 455 | 455
2017-08-07 18:30 | 467 | 467
2017-08-07 19:00 | 511 | 511
2017-08-07 19:30 | 502 | 502
2017-08-07 20:00 | 508 | 508
2017-08-07 20:30 | 525 | 525
2017-08-07 21:00 | 490 | 490
2017-08-07 21:30 | 461 | 461
2017-08-07 22:00 | 435 | 435
2017-08-07 22:30 | 449 | 448
2017-08-07 23:00 | 459 | 458
2017-08-07 23:30 | 436 | 436
2017-08-08 | 425 | 424
2017-08-08 00:30 | 409 | 408
2017-08-08 01:00 | 398 | 396
2017-08-08 01:30 | 387 | 386
2017-08-08 02:00 | 379 | 377
2017-08-08 02:30 | 369 | 367
2017-08-08 03:00 | 356 | 353
2017-08-08 03:30 | 352 | 349
2017-08-08 04:00 | 344 | 341
2017-08-08 04:30 | 340 | 337
2017-08-08 05:00 | 340 | 336
2017-08-08 05:30 | 353 | 350
2017-08-08 06:00 | 372 | 369
2017-08-08 06:30 | 417 | 415
2017-08-08 07:00 | 409 | 407
2017-08-08 07:30 | 482 | 481
2017-08-08 08:00 | 500 | 500
2017-08-08 08:30 | 524 | 523
2017-08-08 09:00 | 489 | 488
2017-08-08 09:30 | 477 | 476
2017-08-08 10:00 | 472 | 471
2017-08-08 10:30 | 480 | 479
2017-08-08 11:00 | 476 | 476
2017-08-08 11:30 | 472 | 471
2017-08-08 12:00 | 484 | 483
2017-08-08 12:30 | 478 | 478
2017-08-08 13:00 | 478 | 478
2017-08-08 13:30 | 482 | 482
2017-08-08 14:00 | 486 | 485
2017-08-08 14:30 | 470 | 469
2017-08-08 15:00 | 480 | 479
2017-08-08 15:30 | 442 | 442
2017-08-08 16:00 | 454 | 453
2017-08-08 16:30 | 506 | 506
2017-08-08 17:00 | 515 | 515
2017-08-08 17:30 | 516 | 516
2017-08-08 18:00 | 547 | 547
2017-08-08 18:30 | 566 | 566
2017-08-08 19:00 | 569 | 568
2017-08-08 19:30 | 545 | 545
2017-08-08 20:00 | 529 | 529
2017-08-08 20:30 | 500 | 499
2017-08-08 21:00 | 483 | 482
2017-08-08 21:30 | 499 | 498
2017-08-08 22:00 | 481 | 480
2017-08-08 22:30 | 465 | 464
2017-08-08 23:00 | 444 | 442
2017-08-08 23:30 | 423 | 422
2017-08-09 | 411 | 409
2017-08-09 00:30 | 399 | 397
2017-08-09 01:00 | 382 | 380
2017-08-09 01:30 | 380 | 376
2017-08-09 02:00 | 366 | 363
2017-08-09 02:30 | 362 | 358
2017-08-09 03:00 | 367 | 363
2017-08-09 03:30 | 365 | 361
2017-08-09 04:00 | 364 | 360
2017-08-09 04:30 | 367 | 363
2017-08-09 05:00 | 379 | 375
2017-08-09 05:30 | 390 | 387
2017-08-09 06:00 | 416 | 413
2017-08-09 06:30 | 444 | 442
2017-08-09 07:00 | 430 | 428
2017-08-09 07:30 | 491 | 490
2017-08-09 08:00 | 523 | 522
2017-08-09 08:30 | 529 | 529
2017-08-09 09:00 | 525 | 524
2017-08-09 09:30 | 521 | 520
2017-08-09 10:00 | 514 | 514
2017-08-09 10:30 | 509 | 509
2017-08-09 11:00 | 499 | 498
2017-08-09 11:30 | 505 | 504
2017-08-09 12:00 | 505 | 504
2017-08-09 12:30 | 481 | 481
2017-08-09 13:00 | 460 | 460
2017-08-09 13:30 | 461 | 460
2017-08-09 14:00 | 463 | 462
2017-08-09 14:30 | 459 | 458
2017-08-09 15:00 | 468 | 467
2017-08-09 15:30 | 484 | 483
2017-08-09 16:00 | 494 | 493
2017-08-09 16:30 | 508 | 508
2017-08-09 17:00 | 512 | 511
2017-08-09 17:30 | 529 | 528
2017-08-09 18:00 | 543 | 543
2017-08-09 18:30 | 572 | 572
2017-08-09 19:00 | 559 | 559
2017-08-09 19:30 | 547 | 547
2017-08-09 20:00 | 557 | 557
2017-08-09 20:30 | 544 | 543
2017-08-09 21:00 | 523 | 522
2017-08-09 21:30 | 497 | 497
2017-08-09 22:00 | 469 | 467
2017-08-09 22:30 | 456 | 453
2017-08-09 23:00 | 436 | 433
2017-08-09 23:30 | 413 | 408
2017-08-10 | 404 | 399
2017-08-10 00:30 | 394 | 389
2017-08-10 01:00 | 382 | 376
2017-08-10 01:30 | 367 | 360
2017-08-10 02:00 | 374 | 367
2017-08-10 02:30 | 363 | 356
2017-08-10 03:00 | 364 | 356
2017-08-10 03:30 | 371 | 363
2017-08-10 04:00 | 382 | 375
2017-08-10 04:30 | 385 | 378
2017-08-10 05:00 | 392 | 386
2017-08-10 05:30 | 419 | 413
2017-08-10 06:00 | 446 | 440
2017-08-10 06:30 | 479 | 476
2017-08-10 07:00 | 463 | 459
2017-08-10 07:30 | 532 | 529
2017-08-10 08:00 | 527 | 525
2017-08-10 08:30 | 518 | 516
2017-08-10 09:00 | 495 | 494
2017-08-10 09:30 | 493 | 492
2017-08-10 10:00 | 471 | 469
2017-08-10 10:30 | 464 | 461
2017-08-10 11:00 | 471 | 468
2017-08-10 11:30 | 477 | 474
2017-08-10 12:00 | 481 | 478
2017-08-10 12:30 | 486 | 483
2017-08-10 13:00 | 493 | 490
2017-08-10 13:30 | 506 | 503
2017-08-10 14:00 | 504 | 502
2017-08-10 14:30 | 491 | 489
2017-08-10 15:00 | 488 | 485
2017-08-10 15:30 | 496 | 493
2017-08-10 16:00 | 505 | 503
2017-08-10 16:30 | 516 | 514
2017-08-10 17:00 | 534 | 533
2017-08-10 17:30 | 537 | 536
2017-08-10 18:00 | 549 | 548
2017-08-10 18:30 | 570 | 570
2017-08-10 19:00 | 588 | 588
2017-08-10 19:30 | 575 | 574
2017-08-10 20:00 | 555 | 555
2017-08-10 20:30 | 532 | 531
2017-08-10 21:00 | 508 | 507
2017-08-10 21:30 | 483 | 482
2017-08-10 22:00 | 456 | 454
2017-08-10 22:30 | 457 | 455
2017-08-10 23:00 | 446 | 443
2017-08-10 23:30 | 433 | 429
2017-08-11 | 410 | 406
2017-08-11 00:30 | 397 | 392
2017-08-11 01:00 | 380 | 374
2017-08-11 01:30 | 378 | 372
2017-08-11 02:00 | 377 | 370
2017-08-11 02:30 | 375 | 368
2017-08-11 03:00 | 365 | 359
2017-08-11 03:30 | 372 | 365
2017-08-11 04:00 | 372 | 366
2017-08-11 04:30 | 371 | 365
2017-08-11 05:00 | 376 | 369
2017-08-11 05:30 | 382 | 376
2017-08-11 06:00 | 350 | 344
2017-08-11 06:30 | 380 | 373
2017-08-11 07:00 | 408 | 403
2017-08-11 07:30 | 432 | 428
2017-08-11 08:00 | 472 | 469
2017-08-11 08:30 | 489 | 487
2017-08-11 09:00 | 472 | 470
2017-08-11 09:30 | 480 | 479
2017-08-11 10:00 | 478 | 476
2017-08-11 10:30 | 467 | 465
2017-08-11 11:00 | 469 | 467
2017-08-11 11:30 | 445 | 443
2017-08-11 12:00 | 443 | 440
2017-08-11 12:30 | 440 | 437
2017-08-11 13:00 | 442 | 440
2017-08-11 13:30 | 444 | 442
2017-08-11 14:00 | 451 | 448
2017-08-11 14:30 | 437 | 434
2017-08-11 15:00 | 438 | 436
2017-08-11 15:30 | 446 | 444
2017-08-11 16:00 | 465 | 463
2017-08-11 16:30 | 485 | 484
2017-08-11 17:00 | 495 | 494
2017-08-11 17:30 | 507 | 506
2017-08-11 18:00 | 519 | 518
2017-08-11 18:30 | 538 | 537
2017-08-11 19:00 | 572 | 572
2017-08-11 19:30 | 565 | 565
2017-08-11 20:00 | 553 | 552
2017-08-11 20:30 | 526 | 525
2017-08-11 21:00 | 509 | 508
2017-08-11 21:30 | 488 | 487
2017-08-11 22:00 | 470 | 469
2017-08-11 22:30 | 453 | 451
2017-08-11 23:00 | 432 | 430
2017-08-11 23:30 | 413 | 409
2017-08-12 | 397 | 393
2017-08-12 00:30 | 392 | 386
2017-08-12 01:00 | 377 | 370
2017-08-12 01:30 | 372 | 365
2017-08-12 02:00 | 368 | 362
2017-08-12 02:30 | 361 | 354
2017-08-12 03:00 | 360 | 353
2017-08-12 03:30 | 354 | 348
2017-08-12 04:00 | 360 | 354
2017-08-12 04:30 | 355 | 348
2017-08-12 05:00 | 365 | 357
2017-08-12 05:30 | 374 | 367
2017-08-12 06:00 | 384 | 377
2017-08-12 06:30 | 389 | 383
2017-08-12 07:00 | 399 | 393
2017-08-12 07:30 | 420 | 414
2017-08-12 08:00 | 437 | 432
2017-08-12 08:30 | 449 | 445
2017-08-12 09:00 | 453 | 450
2017-08-12 09:30 | 342 | 337
2017-08-12 10:00 | 320 | 311
2017-08-12 10:30 | 401 | 392
2017-08-12 11:00 | 425 | 419
2017-08-12 11:30 | 416 | 412
2017-08-12 12:00 | 419 | 414
2017-08-12 12:30 | 419 | 414
2017-08-12 13:00 | 415 | 410
2017-08-12 13:30 | 414 | 409
2017-08-12 14:00 | 417 | 412
2017-08-12 14:30 | 397 | 392
2017-08-12 15:00 | 390 | 384
2017-08-12 15:30 | 405 | 399
2017-08-12 16:00 | 426 | 421
2017-08-12 16:30 | 444 | 440
2017-08-12 17:00 | 463 | 460
2017-08-12 17:30 | 485 | 483
2017-08-12 18:00 | 499 | 498
2017-08-12 18:30 | 523 | 522
2017-08-12 19:00 | 542 | 541
2017-08-12 19:30 | 537 | 536
2017-08-12 20:00 | 529 | 528
2017-08-12 20:30 | 511 | 510
2017-08-12 21:00 | 498 | 497
2017-08-12 21:30 | 480 | 478
2017-08-12 22:00 | 468 | 466
2017-08-12 22:30 | 462 | 460
2017-08-12 23:00 | 449 | 446
2017-08-12 23:30 | 424 | 421
2017-08-13 | 417 | 413
2017-08-13 00:30 | 407 | 403
2017-08-13 01:00 | 396 | 391
2017-08-13 01:30 | 389 | 384
2017-08-13 02:00 | 386 | 381
2017-08-13 02:30 | 391 | 385
2017-08-13 03:00 | 374 | 368
2017-08-13 03:30 | 372 | 365
2017-08-13 04:00 | 373 | 366
2017-08-13 04:30 | 376 | 370
2017-08-13 05:00 | 379 | 372
2017-08-13 05:30 | 384 | 378
2017-08-13 06:00 | 380 | 374
2017-08-13 06:30 | 382 | 376
2017-08-13 07:00 | 389 | 383
2017-08-13 07:30 | 396 | 391
2017-08-13 08:00 | 422 | 417
2017-08-13 08:30 | 447 | 443
2017-08-13 09:00 | 455 | 451
2017-08-13 09:30 | 452 | 449
2017-08-13 10:00 | 447 | 444
2017-08-13 10:30 | 436 | 433
2017-08-13 11:00 | 427 | 423
2017-08-13 11:30 | 420 | 416
2017-08-13 12:00 | 411 | 407
2017-08-13 12:30 | 402 | 398
2017-08-13 13:00 | 400 | 396
2017-08-13 13:30 | 400 | 395
2017-08-13 14:00 | 404 | 395
2017-08-13 14:30 | 387 | 378
2017-08-13 15:00 | 392 | 382
2017-08-13 15:30 | 405 | 395
2017-08-13 16:00 | 423 | 415
2017-08-13 16:30 | 445 | 440
2017-08-13 17:00 | 470 | 467
2017-08-13 17:30 | 491 | 490
2017-08-13 18:00 | 513 | 512
2017-08-13 18:30 | 540 | 540
2017-08-13 19:00 | 557 | 557
2017-08-13 19:30 | 545 | 545
2017-08-13 20:00 | 521 | 521
2017-08-13 20:30 | 523 | 523
2017-08-13 21:00 | 505 | 505
2017-08-13 21:30 | 487 | 487
2017-08-13 22:00 | 467 | 466
2017-08-13 22:30 | 445 | 443
2017-08-13 23:00 | 422 | 419
2017-08-13 23:30 | 405 | 398
2017-08-14 | 393 | 385
2017-08-14 00:30 | 388 | 379
2017-08-14 01:00 | 389 | 380
2017-08-14 01:30 | 387 | 378
2017-08-14 02:00 | 381 | 371
2017-08-14 02:30 | 376 | 366
2017-08-14 03:00 | 368 | 357
2017-08-14 03:30 | 367 | 355
2017-08-14 04:00 | 361 | 348
2017-08-14 04:30 | 367 | 354
2017-08-14 05:00 | 376 | 364
2017-08-14 05:30 | 397 | 387
2017-08-14 06:00 | 411 | 403
2017-08-14 06:30 | 429 | 422
2017-08-14 07:00 | 430 | 424
2017-08-14 07:30 | 461 | 456
2017-08-14 08:00 | 485 | 482
2017-08-14 08:30 | 474 | 473
2017-08-14 09:00 | 458 | 457
2017-08-14 09:30 | 451 | 449
2017-08-14 10:00 | 439 | 436
2017-08-14 10:30 | 447 | 445
2017-08-14 11:00 | 442 | 439
2017-08-14 11:30 | 440 | 438
2017-08-14 12:00 | 442 | 440
2017-08-14 12:30 | 442 | 439
2017-08-14 13:00 | 435 | 432
2017-08-14 13:30 | 434 | 432
2017-08-14 14:00 | 442 | 441
2017-08-14 14:30 | 458 | 457
2017-08-14 15:00 | 466 | 465
2017-08-14 15:30 | 475 | 474
2017-08-14 16:00 | 489 | 489
2017-08-14 16:30 | 499 | 498
2017-08-14 17:00 | 518 | 518
2017-08-14 17:30 | 539 | 539
2017-08-14 18:00 | 541 | 541
2017-08-14 18:30 | 579 | 579
2017-08-14 19:00 | 668 | 668
2017-08-14 19:30 | 658 | 656
2017-08-14 20:00 | 636 | 634
2017-08-14 20:30 | 610 | 609
2017-08-14 21:00 | 588 | 587
2017-08-14 21:30 | 565 | 565
2017-08-14 22:00 | 525 | 525
2017-08-14 22:30 | 492 | 491
2017-08-14 23:00 | 469 | 469
2017-08-14 23:30 | 451 | 449
2017-08-15 | 427 | 424
2017-08-15 00:30 | 413 | 409
2017-08-15 01:00 | 400 | 395
2017-08-15 01:30 | 396 | 390
2017-08-15 02:00 | 395 | 388
2017-08-15 02:30 | 393 | 385
2017-08-15 03:00 | 391 | 383
2017-08-15 03:30 | 389 | 381
2017-08-15 04:00 | 389 | 381
2017-08-15 04:30 | 397 | 389
2017-08-15 05:00 | 398 | 390
2017-08-15 05:30 | 419 | 411
2017-08-15 06:00 | 434 | 429
2017-08-15 06:30 | 468 | 464
2017-08-15 07:00 | 469 | 466
2017-08-15 07:30 | 534 | 532
2017-08-15 08:00 | 539 | 538
2017-08-15 08:30 | 509 | 508
2017-08-15 09:00 | 489 | 487
2017-08-15 09:30 | 486 | 484
2017-08-15 10:00 | 490 | 489
2017-08-15 10:30 | 492 | 491
2017-08-15 11:00 | 486 | 485
2017-08-15 11:30 | 469 | 468
2017-08-15 12:00 | 470 | 468
2017-08-15 12:30 | 462 | 461
2017-08-15 13:00 | 465 | 464
2017-08-15 13:30 | 468 | 467
2017-08-15 14:00 | 476 | 475
2017-08-15 14:30 | 472 | 471
2017-08-15 15:00 | 478 | 477
2017-08-15 15:30 | 488 | 488
2017-08-15 16:00 | 510 | 509
2017-08-15 16:30 | 524 | 523
2017-08-15 17:00 | 544 | 543
2017-08-15 17:30 | 556 | 555
2017-08-15 18:00 | 584 | 584
2017-08-15 18:30 | 625 | 625
2017-08-15 19:00 | 639 | 639
2017-08-15 19:30 | 626 | 625
2017-08-15 20:00 | 621 | 621
2017-08-15 20:30 | 604 | 603
2017-08-15 21:00 | 573 | 572
2017-08-15 21:30 | 534 | 534
2017-08-15 22:00 | 510 | 510
2017-08-15 22:30 | 475 | 475
2017-08-15 23:00 | 448 | 447
2017-08-15 23:30 | 431 | 430
2017-08-16 | 425 | 425
2017-08-16 00:30 | 422 | 419
2017-08-16 01:00 | 406 | 402
2017-08-16 01:30 | 398 | 394
2017-08-16 02:00 | 389 | 385
2017-08-16 02:30 | 390 | 386
2017-08-16 03:00 | 387 | 383
2017-08-16 03:30 | 390 | 385
2017-08-16 04:00 | 388 | 384
2017-08-16 04:30 | 395 | 391
2017-08-16 05:00 | 396 | 391
2017-08-16 05:30 | 411 | 407
2017-08-16 06:00 | 421 | 417
2017-08-16 06:30 | 459 | 456
2017-08-16 07:00 | 499 | 497
2017-08-16 07:30 | 537 | 535
2017-08-16 08:00 | 566 | 566
2017-08-16 08:30 | 567 | 566
2017-08-16 09:00 | 547 | 546
2017-08-16 09:30 | 534 | 533
2017-08-16 10:00 | 525 | 525
2017-08-16 10:30 | 527 | 527
2017-08-16 11:00 | 518 | 517
2017-08-16 11:30 | 518 | 517
2017-08-16 12:00 | 519 | 519
2017-08-16 12:30 | 510 | 509
2017-08-16 13:00 | 488 | 487
2017-08-16 13:30 | 486 | 484
2017-08-16 14:00 | 488 | 487
2017-08-16 14:30 | 477 | 476
2017-08-16 15:00 | 474 | 472
2017-08-16 15:30 | 482 | 481
2017-08-16 16:00 | 499 | 498
2017-08-16 16:30 | 512 | 511
2017-08-16 17:00 | 531 | 530
2017-08-16 17:30 | 547 | 547
2017-08-16 18:00 | 568 | 568
2017-08-16 18:30 | 571 | 571
2017-08-16 19:00 | 583 | 583
2017-08-16 19:30 | 607 | 607
2017-08-16 20:00 | 586 | 586
2017-08-16 20:30 | 562 | 562
2017-08-16 21:00 | 563 | 563
2017-08-16 21:30 | 539 | 539
2017-08-16 22:00 | 514 | 513
2017-08-16 22:30 | 505 | 504
2017-08-16 23:00 | 490 | 489
2017-08-16 23:30 | 459 | 457
2017-08-17 | 426 | 424
2017-08-17 00:30 | 402 | 398
2017-08-17 01:00 | 385 | 381
2017-08-17 01:30 | 395 | 390
2017-08-17 02:00 | 383 | 378
2017-08-17 02:30 | 377 | 372
2017-08-17 03:00 | 372 | 367
2017-08-17 03:30 | 376 | 370
2017-08-17 04:00 | 371 | 365
2017-08-17 04:30 | 379 | 373
2017-08-17 05:00 | 388 | 382
2017-08-17 05:30 | 400 | 395
2017-08-17 06:00 | 421 | 417
2017-08-17 06:30 | 461 | 457
2017-08-17 07:00 | 502 | 499
2017-08-17 07:30 | 529 | 528
2017-08-17 08:00 | 536 | 535
2017-08-17 08:30 | 520 | 519
2017-08-17 09:00 | 502 | 501
2017-08-17 09:30 | 501 | 500
2017-08-17 10:00 | 499 | 498
2017-08-17 10:30 | 501 | 500
2017-08-17 11:00 | 489 | 488
2017-08-17 11:30 | 502 | 501
2017-08-17 12:00 | 499 | 498
2017-08-17 12:30 | 497 | 496
2017-08-17 13:00 | 495 | 494
2017-08-17 13:30 | 503 | 502
2017-08-17 14:00 | 504 | 503
2017-08-17 14:30 | 488 | 487
2017-08-17 15:00 | 498 | 496
2017-08-17 15:30 | 503 | 502
2017-08-17 16:00 | 516 | 515
2017-08-17 16:30 | 526 | 525
2017-08-17 17:00 | 504 | 504
2017-08-17 17:30 | 514 | 513
2017-08-17 18:00 | 527 | 527
2017-08-17 18:30 | 573 | 572
2017-08-17 19:00 | 651 | 651
2017-08-17 19:30 | 644 | 644
2017-08-17 20:00 | 613 | 613
2017-08-17 20:30 | 586 | 586
2017-08-17 21:00 | 568 | 568
2017-08-17 21:30 | 524 | 524
2017-08-17 22:00 | 495 | 495
2017-08-17 22:30 | 487 | 487
2017-08-17 23:00 | 468 | 467
2017-08-17 23:30 | 445 | 444
2017-08-18 | 431 | 429
2017-08-18 00:30 | 419 | 418
2017-08-18 01:00 | 401 | 398
2017-08-18 01:30 | 393 | 390
2017-08-18 02:00 | 384 | 380
2017-08-18 02:30 | 380 | 377
2017-08-18 03:00 | 379 | 375
2017-08-18 03:30 | 383 | 379
2017-08-18 04:00 | 382 | 379
2017-08-18 04:30 | 384 | 381
2017-08-18 05:00 | 391 | 388
2017-08-18 05:30 | 412 | 409
2017-08-18 06:00 | 429 | 427
2017-08-18 06:30 | 463 | 461
2017-08-18 07:00 | 496 | 495
2017-08-18 07:30 | 525 | 524
2017-08-18 08:00 | 532 | 531
2017-08-18 08:30 | 531 | 531
2017-08-18 09:00 | 508 | 508
2017-08-18 09:30 | 488 | 487
2017-08-18 10:00 | 481 | 480
2017-08-18 10:30 | 480 | 479
2017-08-18 11:00 | 477 | 476
2017-08-18 11:30 | 473 | 472
2017-08-18 12:00 | 467 | 466
2017-08-18 12:30 | 466 | 465
2017-08-18 13:00 | 438 | 436
2017-08-18 13:30 | 413 | 412
2017-08-18 14:00 | 433 | 432
2017-08-18 14:30 | 423 | 422
2017-08-18 15:00 | 421 | 420
2017-08-18 15:30 | 430 | 429
2017-08-18 16:00 | 449 | 447
2017-08-18 16:30 | 462 | 461
2017-08-18 17:00 | 487 | 487
2017-08-18 17:30 | 521 | 520
2017-08-18 18:00 | 555 | 554
2017-08-18 18:30 | 549 | 549
2017-08-18 19:00 | 536 | 536
2017-08-18 19:30 | 522 | 522
2017-08-18 20:00 | 502 | 502
2017-08-18 20:30 | 499 | 498
2017-08-18 21:00 | 494 | 493
2017-08-18 21:30 | 469 | 468
2017-08-18 22:00 | 436 | 435
2017-08-18 22:30 | 466 | 465
2017-08-18 23:00 | 453 | 453
2017-08-18 23:30 | 437 | 436
2017-08-19 | 427 | 426
2017-08-19 00:30 | 417 | 416
2017-08-19 01:00 | 408 | 406
2017-08-19 01:30 | 395 | 392
2017-08-19 02:00 | 389 | 386
2017-08-19 02:30 | 385 | 381
2017-08-19 03:00 | 385 | 381
2017-08-19 03:30 | 381 | 378
2017-08-19 04:00 | 377 | 373
2017-08-19 04:30 | 375 | 372
2017-08-19 05:00 | 367 | 363
2017-08-19 05:30 | 376 | 372
2017-08-19 06:00 | 383 | 380
2017-08-19 06:30 | 352 | 348
2017-08-19 07:00 | 340 | 335
2017-08-19 07:30 | 383 | 378
2017-08-19 08:00 | 400 | 397
2017-08-19 08:30 | 407 | 404
2017-08-19 09:00 | 405 | 402
2017-08-19 09:30 | 403 | 400
2017-08-19 10:00 | 394 | 391
2017-08-19 10:30 | 384 | 381
2017-08-19 11:00 | 385 | 382
2017-08-19 11:30 | 387 | 383
2017-08-19 12:00 | 381 | 377
2017-08-19 12:30 | 382 | 379
2017-08-19 13:00 | 380 | 376
2017-08-19 13:30 | 380 | 376
2017-08-19 14:00 | 377 | 373
2017-08-19 14:30 | 360 | 355
2017-08-19 15:00 | 362 | 358
2017-08-19 15:30 | 373 | 369
2017-08-19 16:00 | 384 | 380
2017-08-19 16:30 | 401 | 398
2017-08-19 17:00 | 423 | 420
2017-08-19 17:30 | 437 | 435
2017-08-19 18:00 | 449 | 448
2017-08-19 18:30 | 475 | 474
2017-08-19 19:00 | 501 | 500
2017-08-19 19:30 | 488 | 488
2017-08-19 20:00 | 469 | 468
2017-08-19 20:30 | 454 | 453
2017-08-19 21:00 | 443 | 442
2017-08-19 21:30 | 428 | 426
2017-08-19 22:00 | 414 | 412
2017-08-19 22:30 | 431 | 429
2017-08-19 23:00 | 423 | 421
2017-08-19 23:30 | 398 | 396
2017-08-20 | 380 | 377
2017-08-20 00:30 | 390 | 387
2017-08-20 01:00 | 387 | 383
2017-08-20 01:30 | 385 | 382
2017-08-20 02:00 | 382 | 378
2017-08-20 02:30 | 375 | 370
2017-08-20 03:00 | 378 | 374
2017-08-20 03:30 | 376 | 371
2017-08-20 04:00 | 371 | 366
2017-08-20 04:30 | 370 | 365
2017-08-20 05:00 | 371 | 366
2017-08-20 05:30 | 369 | 364
2017-08-20 06:00 | 371 | 366
2017-08-20 06:30 | 335 | 329
2017-08-20 07:00 | 313 | 306
2017-08-20 07:30 | 328 | 321
2017-08-20 08:00 | 344 | 337
2017-08-20 08:30 | 355 | 348
2017-08-20 09:00 | 354 | 348
2017-08-20 09:30 | 352 | 345
2017-08-20 10:00 | 351 | 344
2017-08-20 10:30 | 354 | 347
2017-08-20 11:00 | 349 | 343
2017-08-20 11:30 | 343 | 337
2017-08-20 12:00 | 335 | 328
2017-08-20 12:30 | 329 | 323
2017-08-20 13:00 | 326 | 319
2017-08-20 13:30 | 317 | 310
2017-08-20 14:00 | 314 | 306
2017-08-20 14:30 | 308 | 300
2017-08-20 15:00 | 316 | 308
2017-08-20 15:30 | 324 | 317
2017-08-20 16:00 | 345 | 338
2017-08-20 16:30 | 365 | 360
2017-08-20 17:00 | 381 | 377
2017-08-20 17:30 | 407 | 403
2017-08-20 18:00 | 467 | 465
2017-08-20 18:30 | 505 | 504
2017-08-20 19:00 | 523 | 522
2017-08-20 19:30 | 510 | 510
2017-08-20 20:00 | 481 | 481
2017-08-20 20:30 | 440 | 439
2017-08-20 21:00 | 426 | 424
2017-08-20 21:30 | 412 | 410
2017-08-20 22:00 | 395 | 392
2017-08-20 22:30 | 425 | 422
2017-08-20 23:00 | 423 | 421
2017-08-20 23:30 | 410 | 408
2017-08-21 | 389 | 387
2017-08-21 00:30 | 385 | 382
2017-08-21 01:00 | 381 | 378
2017-08-21 01:30 | 371 | 368
2017-08-21 02:00 | 368 | 365
2017-08-21 02:30 | 361 | 357
2017-08-21 03:00 | 360 | 356
2017-08-21 03:30 | 365 | 360
2017-08-21 04:00 | 365 | 361
2017-08-21 04:30 | 372 | 367
2017-08-21 05:00 | 366 | 362
2017-08-21 05:30 | 383 | 379
2017-08-21 06:00 | 403 | 399
2017-08-21 06:30 | 388 | 385
2017-08-21 07:00 | 383 | 379
2017-08-21 07:30 | 420 | 417
2017-08-21 08:00 | 427 | 425
2017-08-21 08:30 | 423 | 421
2017-08-21 09:00 | 404 | 402
2017-08-21 09:30 | 408 | 406
2017-08-21 10:00 | 408 | 406
2017-08-21 10:30 | 405 | 402
2017-08-21 11:00 | 394 | 391
2017-08-21 11:30 | 379 | 376
2017-08-21 12:00 | 371 | 368
2017-08-21 12:30 | 372 | 368
2017-08-21 13:00 | 376 | 372
2017-08-21 13:30 | 375 | 371
2017-08-21 14:00 | 367 | 364
2017-08-21 14:30 | 379 | 375
2017-08-21 15:00 | 381 | 377
2017-08-21 15:30 | 377 | 374
2017-08-21 16:00 | 391 | 388
2017-08-21 16:30 | 420 | 417
2017-08-21 17:00 | 456 | 455
2017-08-21 17:30 | 485 | 483
2017-08-21 18:00 | 488 | 488
2017-08-21 18:30 | 520 | 519
2017-08-21 19:00 | 523 | 522
2017-08-21 19:30 | 530 | 530
2017-08-21 20:00 | 512 | 512
2017-08-21 20:30 | 493 | 493
2017-08-21 21:00 | 492 | 492
2017-08-21 21:30 | 478 | 477
2017-08-21 22:00 | 449 | 448
2017-08-21 22:30 | 448 | 446
2017-08-21 23:00 | 436 | 434
2017-08-21 23:30 | 421 | 420
2017-08-22 | 411 | 409
2017-08-22 00:30 | 403 | 400
2017-08-22 01:00 | 389 | 386
2017-08-22 01:30 | 377 | 374
2017-08-22 02:00 | 369 | 366
2017-08-22 02:30 | 369 | 365
2017-08-22 03:00 | 365 | 361
2017-08-22 03:30 | 364 | 360
2017-08-22 04:00 | 366 | 362
2017-08-22 04:30 | 365 | 360
2017-08-22 05:00 | 377 | 372
2017-08-22 05:30 | 395 | 391
2017-08-22 06:00 | 406 | 403
2017-08-22 06:30 | 408 | 405
2017-08-22 07:00 | 412 | 409
2017-08-22 07:30 | 463 | 461
2017-08-22 08:00 | 468 | 466
2017-08-22 08:30 | 455 | 453
2017-08-22 09:00 | 437 | 436
2017-08-22 09:30 | 417 | 416
2017-08-22 10:00 | 405 | 403
2017-08-22 10:30 | 402 | 399
2017-08-22 11:00 | 391 | 389
2017-08-22 11:30 | 395 | 392
2017-08-22 12:00 | 403 | 400
2017-08-22 12:30 | 401 | 399
2017-08-22 13:00 | 406 | 404
2017-08-22 13:30 | 415 | 413
2017-08-22 14:00 | 419 | 417
2017-08-22 14:30 | 407 | 405
2017-08-22 15:00 | 400 | 397
2017-08-22 15:30 | 409 | 407
2017-08-22 16:00 | 433 | 431
2017-08-22 16:30 | 447 | 445
2017-08-22 17:00 | 455 | 454
2017-08-22 17:30 | 479 | 478
2017-08-22 18:00 | 502 | 501
2017-08-22 18:30 | 522 | 522
2017-08-22 19:00 | 545 | 545
2017-08-22 19:30 | 533 | 533
2017-08-22 20:00 | 507 | 507
2017-08-22 20:30 | 522 | 521
2017-08-22 21:00 | 547 | 546
2017-08-22 21:30 | 521 | 521
2017-08-22 22:00 | 494 | 494
2017-08-22 22:30 | 507 | 506
2017-08-22 23:00 | 489 | 489
2017-08-22 23:30 | 463 | 462
2017-08-23 | 437 | 435
2017-08-23 00:30 | 426 | 423
2017-08-23 01:00 | 415 | 411
2017-08-23 01:30 | 403 | 400
2017-08-23 02:00 | 398 | 394
2017-08-23 02:30 | 385 | 381
2017-08-23 03:00 | 376 | 372
2017-08-23 03:30 | 378 | 374
2017-08-23 04:00 | 378 | 375
2017-08-23 04:30 | 377 | 374
2017-08-23 05:00 | 380 | 376
2017-08-23 05:30 | 392 | 388
2017-08-23 06:00 | 406 | 403
2017-08-23 06:30 | 380 | 377
2017-08-23 07:00 | 396 | 392
2017-08-23 07:30 | 430 | 427
2017-08-23 08:00 | 442 | 440
2017-08-23 08:30 | 424 | 422
2017-08-23 09:00 | 417 | 415
2017-08-23 09:30 | 404 | 401
2017-08-23 10:00 | 418 | 415
2017-08-23 10:30 | 424 | 422
2017-08-23 11:00 | 413 | 411
2017-08-23 11:30 | 411 | 408
2017-08-23 12:00 | 405 | 403
2017-08-23 12:30 | 405 | 403
2017-08-23 13:00 | 406 | 404
2017-08-23 13:30 | 409 | 406
2017-08-23 14:00 | 413 | 411
2017-08-23 14:30 | 408 | 406
2017-08-23 15:00 | 409 | 407
2017-08-23 15:30 | 411 | 409
2017-08-23 16:00 | 426 | 425
2017-08-23 16:30 | 450 | 449
2017-08-23 17:00 | 458 | 457
2017-08-23 17:30 | 470 | 470
2017-08-23 18:00 | 479 | 479
2017-08-23 18:30 | 513 | 512
2017-08-23 19:00 | 537 | 537
2017-08-23 19:30 | 525 | 525
2017-08-23 20:00 | 507 | 507
2017-08-23 20:30 | 510 | 510
2017-08-23 21:00 | 493 | 493
2017-08-23 21:30 | 475 | 475
2017-08-23 22:00 | 451 | 450
2017-08-23 22:30 | 423 | 422
2017-08-23 23:00 | 402 | 400
2017-08-23 23:30 | 404 | 401
2017-08-24 | 407 | 404
2017-08-24 00:30 | 423 | 420
2017-08-24 01:00 | 414 | 412
2017-08-24 01:30 | 400 | 398
2017-08-24 02:00 | 393 | 390
2017-08-24 02:30 | 391 | 388
2017-08-24 03:00 | 389 | 386
2017-08-24 03:30 | 390 | 387
2017-08-24 04:00 | 387 | 384
2017-08-24 04:30 | 400 | 397
2017-08-24 05:00 | 403 | 400
2017-08-24 05:30 | 430 | 428
2017-08-24 06:00 | 443 | 441
2017-08-24 06:30 | 416 | 415
2017-08-24 07:00 | 417 | 415
2017-08-24 07:30 | 461 | 459
2017-08-24 08:00 | 473 | 472
2017-08-24 08:30 | 458 | 457
2017-08-24 09:00 | 437 | 435
2017-08-24 09:30 | 431 | 429
2017-08-24 10:00 | 421 | 419
2017-08-24 10:30 | 410 | 408
2017-08-24 11:00 | 412 | 410
2017-08-24 11:30 | 411 | 409
2017-08-24 12:00 | 412 | 409
2017-08-24 12:30 | 408 | 405
2017-08-24 13:00 | 404 | 402
2017-08-24 13:30 | 404 | 402
2017-08-24 14:00 | 415 | 412
2017-08-24 14:30 | 435 | 433
2017-08-24 15:00 | 434 | 432
2017-08-24 15:30 | 439 | 437
2017-08-24 16:00 | 463 | 462
2017-08-24 16:30 | 476 | 475
2017-08-24 17:00 | 486 | 485
2017-08-24 17:30 | 506 | 505
2017-08-24 18:00 | 538 | 537
2017-08-24 18:30 | 568 | 568
2017-08-24 19:00 | 599 | 599
2017-08-24 19:30 | 611 | 611
2017-08-24 20:00 | 581 | 581
2017-08-24 20:30 | 570 | 570
2017-08-24 21:00 | 557 | 557
2017-08-24 21:30 | 533 | 533
2017-08-24 22:00 | 500 | 500
2017-08-24 22:30 | 481 | 480
2017-08-24 23:00 | 456 | 456
2017-08-24 23:30 | 437 | 436
2017-08-25 | 423 | 422
2017-08-25 00:30 | 446 | 444
2017-08-25 01:00 | 447 | 446
2017-08-25 01:30 | 444 | 443
2017-08-25 02:00 | 440 | 439
2017-08-25 02:30 | 431 | 429
2017-08-25 03:00 | 429 | 428
2017-08-25 03:30 | 429 | 427
2017-08-25 04:00 | 428 | 426
2017-08-25 04:30 | 427 | 425
2017-08-25 05:00 | 433 | 431
2017-08-25 05:30 | 406 | 404
2017-08-25 06:00 | 396 | 394
2017-08-25 06:30 | 425 | 422
2017-08-25 07:00 | 413 | 411
2017-08-25 07:30 | 483 | 482
2017-08-25 08:00 | 494 | 494
2017-08-25 08:30 | 488 | 487
2017-08-25 09:00 | 468 | 467
2017-08-25 09:30 | 448 | 447
2017-08-25 10:00 | 421 | 419
2017-08-25 10:30 | 407 | 405
2017-08-25 11:00 | 398 | 395
2017-08-25 11:30 | 399 | 396
2017-08-25 12:00 | 397 | 394
2017-08-25 12:30 | 397 | 395
2017-08-25 13:00 | 403 | 400
2017-08-25 13:30 | 408 | 405
2017-08-25 14:00 | 404 | 401
2017-08-25 14:30 | 385 | 382
2017-08-25 15:00 | 388 | 384
2017-08-25 15:30 | 404 | 401
2017-08-25 16:00 | 419 | 416
2017-08-25 16:30 | 432 | 430
2017-08-25 17:00 | 457 | 456
2017-08-25 17:30 | 467 | 466
2017-08-25 18:00 | 475 | 474
2017-08-25 18:30 | 492 | 492
2017-08-25 19:00 | 512 | 511
2017-08-25 19:30 | 531 | 531
2017-08-25 20:00 | 526 | 526
2017-08-25 20:30 | 509 | 508
2017-08-25 21:00 | 492 | 492
2017-08-25 21:30 | 472 | 471
2017-08-25 22:00 | 454 | 454
2017-08-25 22:30 | 422 | 421
2017-08-25 23:00 | 398 | 396
2017-08-25 23:30 | 379 | 377
2017-08-26 | 368 | 365
2017-08-26 00:30 | 389 | 385
2017-08-26 01:00 | 400 | 396
2017-08-26 01:30 | 396 | 393
2017-08-26 02:00 | 389 | 386
2017-08-26 02:30 | 391 | 387
2017-08-26 03:00 | 391 | 387
2017-08-26 03:30 | 384 | 380
2017-08-26 04:00 | 372 | 368
2017-08-26 04:30 | 386 | 382
2017-08-26 05:00 | 390 | 386
2017-08-26 05:30 | 396 | 392
2017-08-26 06:00 | 403 | 400
2017-08-26 06:30 | 379 | 375
2017-08-26 07:00 | 370 | 366
2017-08-26 07:30 | 397 | 393
2017-08-26 08:00 | 406 | 403
2017-08-26 08:30 | 410 | 407
2017-08-26 09:00 | 405 | 402
2017-08-26 09:30 | 399 | 396
2017-08-26 10:00 | 398 | 395
2017-08-26 10:30 | 396 | 393
2017-08-26 11:00 | 391 | 388
2017-08-26 11:30 | 395 | 391
2017-08-26 12:00 | 388 | 384
2017-08-26 12:30 | 381 | 377
2017-08-26 13:00 | 381 | 377
2017-08-26 13:30 | 379 | 375
2017-08-26 14:00 | 365 | 361
2017-08-26 14:30 | 346 | 341
2017-08-26 15:00 | 349 | 344
2017-08-26 15:30 | 356 | 351
2017-08-26 16:00 | 373 | 368
2017-08-26 16:30 | 392 | 388
2017-08-26 17:00 | 413 | 410
2017-08-26 17:30 | 424 | 422
2017-08-26 18:00 | 474 | 472
2017-08-26 18:30 | 495 | 494
2017-08-26 19:00 | 480 | 479
2017-08-26 19:30 | 470 | 469
2017-08-26 20:00 | 456 | 455
2017-08-26 20:30 | 443 | 441
2017-08-26 21:00 | 422 | 421
2017-08-26 21:30 | 402 | 400
2017-08-26 22:00 | 392 | 389
2017-08-26 22:30 | 425 | 422
2017-08-26 23:00 | 437 | 435
2017-08-26 23:30 | 424 | 422
2017-08-27 | 404 | 401
2017-08-27 00:30 | 395 | 391
2017-08-27 01:00 | 390 | 386
2017-08-27 01:30 | 378 | 373
2017-08-27 02:00 | 367 | 362
2017-08-27 02:30 | 373 | 367
2017-08-27 03:00 | 371 | 366
2017-08-27 03:30 | 365 | 360
2017-08-27 04:00 | 367 | 362
2017-08-27 04:30 | 363 | 358
2017-08-27 05:00 | 366 | 361
2017-08-27 05:30 | 374 | 369
2017-08-27 06:00 | 380 | 375
2017-08-27 06:30 | 353 | 348
2017-08-27 07:00 | 336 | 330
2017-08-27 07:30 | 361 | 354
2017-08-27 08:00 | 373 | 367
2017-08-27 08:30 | 381 | 375
2017-08-27 09:00 | 389 | 384
2017-08-27 09:30 | 392 | 388
2017-08-27 10:00 | 398 | 393
2017-08-27 10:30 | 387 | 383
2017-08-27 11:00 | 376 | 372
2017-08-27 11:30 | 372 | 368
2017-08-27 12:00 | 370 | 366
2017-08-27 12:30 | 369 | 364
2017-08-27 13:00 | 366 | 361
2017-08-27 13:30 | 352 | 347
2017-08-27 14:00 | 342 | 337
2017-08-27 14:30 | 321 | 315
2017-08-27 15:00 | 317 | 310
2017-08-27 15:30 | 329 | 322
2017-08-27 16:00 | 342 | 336
2017-08-27 16:30 | 371 | 365
2017-08-27 17:00 | 399 | 395
2017-08-27 17:30 | 441 | 438
2017-08-27 18:00 | 466 | 465
2017-08-27 18:30 | 509 | 508
2017-08-27 19:00 | 541 | 540
2017-08-27 19:30 | 522 | 522
2017-08-27 20:00 | 485 | 485
2017-08-27 20:30 | 406 | 406
2017-08-27 21:00 | 436 | 434
2017-08-27 21:30 | 437 | 436
2017-08-27 22:00 | 412 | 410
2017-08-27 22:30 | 426 | 424
2017-08-27 23:00 | 438 | 436
2017-08-27 23:30 | 426 | 425
2017-08-28 | 407 | 405
2017-08-28 00:30 | 401 | 399
2017-08-28 01:00 | 386 | 383
2017-08-28 01:30 | 372 | 370
2017-08-28 02:00 | 367 | 363
2017-08-28 02:30 | 366 | 363
2017-08-28 03:00 | 360 | 357
2017-08-28 03:30 | 353 | 350
2017-08-28 04:00 | 356 | 353
2017-08-28 04:30 | 355 | 352
2017-08-28 05:00 | 361 | 357
2017-08-28 05:30 | 378 | 375
2017-08-28 06:00 | 397 | 395
2017-08-28 06:30 | 382 | 380
2017-08-28 07:00 | 349 | 346
2017-08-28 07:30 | 403 | 400
2017-08-28 08:00 | 406 | 403
2017-08-28 08:30 | 401 | 399
2017-08-28 09:00 | 383 | 380
2017-08-28 09:30 | 401 | 397
2017-08-28 10:00 | 405 | 402
2017-08-28 10:30 | 406 | 403
2017-08-28 11:00 | 407 | 404
2017-08-28 11:30 | 398 | 395
2017-08-28 12:00 | 402 | 399
2017-08-28 12:30 | 414 | 412
2017-08-28 13:00 | 422 | 420
2017-08-28 13:30 | 427 | 426
2017-08-28 14:00 | 428 | 426
2017-08-28 14:30 | 411 | 409
2017-08-28 15:00 | 413 | 411
2017-08-28 15:30 | 411 | 409
2017-08-28 16:00 | 429 | 427
2017-08-28 16:30 | 436 | 435
2017-08-28 17:00 | 463 | 461
2017-08-28 17:30 | 493 | 492
2017-08-28 18:00 | 511 | 510
2017-08-28 18:30 | 497 | 496
2017-08-28 19:00 | 504 | 504
2017-08-28 19:30 | 474 | 474
2017-08-28 20:00 | 443 | 442
2017-08-28 20:30 | 442 | 441
2017-08-28 21:00 | 450 | 449
2017-08-28 21:30 | 451 | 449
2017-08-28 22:00 | 427 | 426
2017-08-28 22:30 | 434 | 433
2017-08-28 23:00 | 436 | 435
2017-08-28 23:30 | 421 | 419
2017-08-29 | 401 | 398
2017-08-29 00:30 | 386 | 383
2017-08-29 01:00 | 378 | 374
2017-08-29 01:30 | 371 | 367
2017-08-29 02:00 | 366 | 362
2017-08-29 02:30 | 362 | 357
2017-08-29 03:00 | 358 | 352
2017-08-29 03:30 | 360 | 354
2017-08-29 04:00 | 359 | 353
2017-08-29 04:30 | 369 | 363
2017-08-29 05:00 | 388 | 383
2017-08-29 05:30 | 405 | 400
2017-08-29 06:00 | 402 | 399
2017-08-29 06:30 | 393 | 390
2017-08-29 07:00 | 356 | 352
2017-08-29 07:30 | 387 | 383
2017-08-29 08:00 | 434 | 431
2017-08-29 08:30 | 432 | 430
2017-08-29 09:00 | 416 | 414
2017-08-29 09:30 | 428 | 426
2017-08-29 10:00 | 433 | 430
2017-08-29 10:30 | 434 | 432
2017-08-29 11:00 | 444 | 442
2017-08-29 11:30 | 435 | 433
2017-08-29 12:00 | 440 | 438
2017-08-29 12:30 | 438 | 436
2017-08-29 13:00 | 446 | 445
2017-08-29 13:30 | 447 | 445
2017-08-29 14:00 | 448 | 446
2017-08-29 14:30 | 423 | 422
2017-08-29 15:00 | 425 | 423
2017-08-29 15:30 | 434 | 432
2017-08-29 16:00 | 445 | 443
2017-08-29 16:30 | 456 | 454
2017-08-29 17:00 | 459 | 458
2017-08-29 17:30 | 470 | 469
2017-08-29 18:00 | 489 | 488
2017-08-29 18:30 | 483 | 482
2017-08-29 19:00 | 500 | 500
2017-08-29 19:30 | 504 | 503
2017-08-29 20:00 | 505 | 505
2017-08-29 20:30 | 488 | 488
2017-08-29 21:00 | 464 | 464
2017-08-29 21:30 | 476 | 475
2017-08-29 22:00 | 459 | 458
2017-08-29 22:30 | 428 | 426
2017-08-29 23:00 | 385 | 383
2017-08-29 23:30 | 374 | 370
2017-08-30 | 375 | 371
2017-08-30 00:30 | 376 | 372
2017-08-30 01:00 | 384 | 380
2017-08-30 01:30 | 378 | 375
2017-08-30 02:00 | 367 | 363
2017-08-30 02:30 | 353 | 349
2017-08-30 03:00 | 351 | 346
2017-08-30 03:30 | 354 | 349
2017-08-30 04:00 | 358 | 353
2017-08-30 04:30 | 362 | 358
2017-08-30 05:00 | 351 | 346
2017-08-30 05:30 | 359 | 353
2017-08-30 06:00 | 358 | 353
2017-08-30 06:30 | 380 | 375
2017-08-30 07:00 | 345 | 340
2017-08-30 07:30 | 387 | 382
2017-08-30 08:00 | 419 | 415
2017-08-30 08:30 | 412 | 409
2017-08-30 09:00 | 391 | 388
2017-08-30 09:30 | 409 | 406
2017-08-30 10:00 | 414 | 410
2017-08-30 10:30 | 407 | 404
2017-08-30 11:00 | 396 | 392
2017-08-30 11:30 | 391 | 387
2017-08-30 12:00 | 397 | 393
2017-08-30 12:30 | 384 | 381
2017-08-30 13:00 | 376 | 372
2017-08-30 13:30 | 393 | 389
2017-08-30 14:00 | 396 | 393
2017-08-30 14:30 | 348 | 345
2017-08-30 15:00 | 386 | 381
2017-08-30 15:30 | 400 | 396
2017-08-30 16:00 | 408 | 404
2017-08-30 16:30 | 422 | 420
2017-08-30 17:00 | 431 | 428
2017-08-30 17:30 | 454 | 452
2017-08-30 18:00 | 496 | 494
2017-08-30 18:30 | 494 | 494
2017-08-30 19:00 | 520 | 519
2017-08-30 19:30 | 509 | 509
2017-08-30 20:00 | 493 | 493
2017-08-30 20:30 | 492 | 492
2017-08-30 21:00 | 478 | 477
2017-08-30 21:30 | 458 | 457
2017-08-30 22:00 | 435 | 434
2017-08-30 22:30 | 442 | 440
2017-08-30 23:00 | 435 | 433
2017-08-30 23:30 | 413 | 411
2017-08-31 | 398 | 395
2017-08-31 00:30 | 389 | 386
2017-08-31 01:00 | 377 | 374
2017-08-31 01:30 | 371 | 368
2017-08-31 02:00 | 364 | 360
2017-08-31 02:30 | 361 | 357
2017-08-31 03:00 | 352 | 348
2017-08-31 03:30 | 354 | 349
2017-08-31 04:00 | 357 | 352
2017-08-31 04:30 | 361 | 357
2017-08-31 05:00 | 363 | 358
2017-08-31 05:30 | 373 | 369
2017-08-31 06:00 | 393 | 390
2017-08-31 06:30 | 419 | 416
2017-08-31 07:00 | 390 | 387
2017-08-31 07:30 | 409 | 406
2017-08-31 08:00 | 419 | 416
2017-08-31 08:30 | 411 | 409
2017-08-31 09:00 | 400 | 398
2017-08-31 09:30 | 439 | 437
2017-08-31 10:00 | 436 | 435
2017-08-31 10:30 | 390 | 389
2017-08-31 11:00 | 380 | 377
2017-08-31 11:30 | 382 | 378
2017-08-31 12:00 | 381 | 378
2017-08-31 12:30 | 398 | 395
2017-08-31 13:00 | 388 | 386
2017-08-31 13:30 | 385 | 383
2017-08-31 14:00 | 387 | 385
2017-08-31 14:30 | 376 | 374
2017-08-31 15:00 | 366 | 364
2017-08-31 15:30 | 378 | 376
2017-08-31 16:00 | 393 | 391
2017-08-31 16:30 | 407 | 405
2017-08-31 17:00 | 423 | 422
2017-08-31 17:30 | 439 | 438
2017-08-31 18:00 | 460 | 459
2017-08-31 18:30 | 485 | 484
2017-08-31 19:00 | 518 | 518
2017-08-31 19:30 | 547 | 547
2017-08-31 20:00 | 549 | 549
2017-08-31 20:30 | 528 | 528
2017-08-31 21:00 | 506 | 506
2017-08-31 21:30 | 501 | 501
2017-08-31 22:00 | 490 | 489
2017-08-31 22:30 | 499 | 499
2017-08-31 23:00 | 487 | 487
2017-08-31 23:30 | 473 | 473
2017-09-01 | 453 | 453
2017-09-01 00:30 | 443 | 442
2017-09-01 01:00 | 433 | 433
2017-09-01 01:30 | 420 | 419
2017-09-01 02:00 | 413 | 412
2017-09-01 02:30 | 407 | 406
2017-09-01 03:00 | 405 | 404
2017-09-01 03:30 | 401 | 400
2017-09-01 04:00 | 407 | 405
2017-09-01 04:30 | 410 | 409
2017-09-01 05:00 | 409 | 407
2017-09-01 05:30 | 425 | 424
2017-09-01 06:00 | 436 | 435
2017-09-01 06:30 | 464 | 463
2017-09-01 07:00 | 460 | 459
2017-09-01 07:30 | 478 | 477
2017-09-01 08:00 | 447 | 446
2017-09-01 08:30 | 437 | 437
2017-09-01 09:00 | 426 | 425
2017-09-01 09:30 | 420 | 419
2017-09-01 10:00 | 415 | 414
2017-09-01 10:30 | 399 | 398
2017-09-01 11:00 | 407 | 406
2017-09-01 11:30 | 404 | 403
2017-09-01 12:00 | 406 | 404
2017-09-01 12:30 | 445 | 443
2017-09-01 13:00 | 444 | 443
2017-09-01 13:30 | 423 | 422
2017-09-01 14:00 | 422 | 421
2017-09-01 14:30 | 358 | 357
2017-09-01 15:00 | 322 | 320
2017-09-01 15:30 | 322 | 318
2017-09-01 16:00 | 338 | 335
2017-09-01 16:30 | 367 | 364
2017-09-01 17:00 | 376 | 374
2017-09-01 17:30 | 393 | 392
2017-09-01 18:00 | 398 | 397
2017-09-01 18:30 | 421 | 420
2017-09-01 19:00 | 471 | 470
2017-09-01 19:30 | 532 | 532
2017-09-01 20:00 | 536 | 536
2017-09-01 20:30 | 520 | 519
2017-09-01 21:00 | 508 | 508
2017-09-01 21:30 | 490 | 490
2017-09-01 22:00 | 468 | 468
2017-09-01 22:30 | 473 | 472
2017-09-01 23:00 | 480 | 479
2017-09-01 23:30 | 462 | 461
2017-09-02 | 447 | 447
2017-09-02 00:30 | 450 | 449
2017-09-02 01:00 | 438 | 438
2017-09-02 01:30 | 433 | 432
2017-09-02 02:00 | 428 | 428
2017-09-02 02:30 | 416 | 415
2017-09-02 03:00 | 415 | 414
2017-09-02 03:30 | 413 | 412
2017-09-02 04:00 | 413 | 412
2017-09-02 04:30 | 405 | 404
2017-09-02 05:00 | 410 | 409
2017-09-02 05:30 | 414 | 413
2017-09-02 06:00 | 410 | 409
2017-09-02 06:30 | 415 | 414
2017-09-02 07:00 | 397 | 396
2017-09-02 07:30 | 411 | 410
2017-09-02 08:00 | 417 | 416
2017-09-02 08:30 | 432 | 431
2017-09-02 09:00 | 434 | 433
2017-09-02 09:30 | 422 | 421
2017-09-02 10:00 | 325 | 324
2017-09-02 10:30 | 285 | 282
2017-09-02 11:00 | 272 | 267
2017-09-02 11:30 | 264 | 257
2017-09-02 12:00 | 264 | 258
2017-09-02 12:30 | 263 | 255
2017-09-02 13:00 | 263 | 251
2017-09-02 13:30 | 264 | 253
2017-09-02 14:00 | 261 | 249
2017-09-02 14:30 | 254 | 242
2017-09-02 15:00 | 265 | 254
2017-09-02 15:30 | 290 | 280
2017-09-02 16:00 | 290 | 284
2017-09-02 16:30 | 298 | 293
2017-09-02 17:00 | 319 | 314
2017-09-02 17:30 | 334 | 330
2017-09-02 18:00 | 391 | 389
2017-09-02 18:30 | 434 | 433
2017-09-02 19:00 | 396 | 395
2017-09-02 19:30 | 516 | 515
2017-09-02 20:00 | 520 | 520
2017-09-02 20:30 | 504 | 504
2017-09-02 21:00 | 494 | 494
2017-09-02 21:30 | 478 | 478
2017-09-02 22:00 | 467 | 466
2017-09-02 22:30 | 472 | 472
2017-09-02 23:00 | 470 | 470
2017-09-02 23:30 | 451 | 450
2017-09-03 | 441 | 440
2017-09-03 00:30 | 435 | 434
2017-09-03 01:00 | 422 | 420
2017-09-03 01:30 | 406 | 405
2017-09-03 02:00 | 404 | 403
2017-09-03 02:30 | 392 | 390
2017-09-03 03:00 | 393 | 391
2017-09-03 03:30 | 392 | 389
2017-09-03 04:00 | 395 | 393
2017-09-03 04:30 | 391 | 389
2017-09-03 05:00 | 388 | 386
2017-09-03 05:30 | 388 | 386
2017-09-03 06:00 | 392 | 390
2017-09-03 06:30 | 398 | 396
2017-09-03 07:00 | 377 | 374
2017-09-03 07:30 | 384 | 382
2017-09-03 08:00 | 394 | 392
2017-09-03 08:30 | 405 | 403
2017-09-03 09:00 | 411 | 409
2017-09-03 09:30 | 416 | 414
2017-09-03 10:00 | 410 | 409
2017-09-03 10:30 | 412 | 410
2017-09-03 11:00 | 409 | 408
2017-09-03 11:30 | 404 | 402
2017-09-03 12:00 | 398 | 397
2017-09-03 12:30 | 396 | 394
2017-09-03 13:00 | 392 | 390
2017-09-03 13:30 | 397 | 395
2017-09-03 14:00 | 395 | 393
2017-09-03 14:30 | 387 | 384
2017-09-03 15:00 | 400 | 398
2017-09-03 15:30 | 406 | 404
2017-09-03 16:00 | 423 | 421
2017-09-03 16:30 | 432 | 431
2017-09-03 17:00 | 448 | 447
2017-09-03 17:30 | 473 | 473
2017-09-03 18:00 | 517 | 516
2017-09-03 18:30 | 543 | 543
2017-09-03 19:00 | 562 | 562
2017-09-03 19:30 | 550 | 550
2017-09-03 20:00 | 500 | 500
2017-09-03 20:30 | 483 | 483
2017-09-03 21:00 | 471 | 471
2017-09-03 21:30 | 456 | 456
2017-09-03 22:00 | 433 | 432
2017-09-03 22:30 | 429 | 428
2017-09-03 23:00 | 433 | 431
2017-09-03 23:30 | 409 | 408
2017-09-04 | 393 | 390
2017-09-04 00:30 | 396 | 393
2017-09-04 01:00 | 383 | 381
2017-09-04 01:30 | 372 | 369
2017-09-04 02:00 | 366 | 363
2017-09-04 02:30 | 363 | 360
2017-09-04 03:00 | 369 | 366
2017-09-04 03:30 | 377 | 374
2017-09-04 04:00 | 380 | 377
2017-09-04 04:30 | 375 | 372
2017-09-04 05:00 | 379 | 376
2017-09-04 05:30 | 392 | 389
2017-09-04 06:00 | 406 | 403
2017-09-04 06:30 | 440 | 438
2017-09-04 07:00 | 444 | 443
2017-09-04 07:30 | 458 | 456
2017-09-04 08:00 | 464 | 463
2017-09-04 08:30 | 462 | 461
2017-09-04 09:00 | 448 | 448
2017-09-04 09:30 | 440 | 440
2017-09-04 10:00 | 435 | 434
2017-09-04 10:30 | 428 | 427
2017-09-04 11:00 | 411 | 410
2017-09-04 11:30 | 408 | 406
2017-09-04 12:00 | 411 | 409
2017-09-04 12:30 | 408 | 406
2017-09-04 13:00 | 408 | 406
2017-09-04 13:30 | 411 | 409
2017-09-04 14:00 | 414 | 412
2017-09-04 14:30 | 407 | 405
2017-09-04 15:00 | 415 | 413
2017-09-04 15:30 | 431 | 429
2017-09-04 16:00 | 436 | 435
2017-09-04 16:30 | 454 | 453
2017-09-04 17:00 | 467 | 466
2017-09-04 17:30 | 490 | 489
2017-09-04 18:00 | 525 | 525
2017-09-04 18:30 | 556 | 555
2017-09-04 19:00 | 564 | 564
2017-09-04 19:30 | 571 | 571
2017-09-04 20:00 | 551 | 551
2017-09-04 20:30 | 525 | 525
2017-09-04 21:00 | 505 | 505
2017-09-04 21:30 | 484 | 483
2017-09-04 22:00 | 466 | 465
2017-09-04 22:30 | 468 | 468
2017-09-04 23:00 | 461 | 460
2017-09-04 23:30 | 444 | 444
2017-09-05 | 429 | 429
2017-09-05 00:30 | 413 | 412
2017-09-05 01:00 | 402 | 400
2017-09-05 01:30 | 400 | 399
2017-09-05 02:00 | 387 | 385
2017-09-05 02:30 | 379 | 376
2017-09-05 03:00 | 378 | 375
2017-09-05 03:30 | 386 | 383
2017-09-05 04:00 | 380 | 377
2017-09-05 04:30 | 390 | 388
2017-09-05 05:00 | 403 | 400
2017-09-05 05:30 | 421 | 419
2017-09-05 06:00 | 441 | 440
2017-09-05 06:30 | 467 | 466
2017-09-05 07:00 | 469 | 468
2017-09-05 07:30 | 487 | 486
2017-09-05 08:00 | 490 | 490
2017-09-05 08:30 | 480 | 480
2017-09-05 09:00 | 469 | 468
2017-09-05 09:30 | 462 | 461
2017-09-05 10:00 | 454 | 453
2017-09-05 10:30 | 448 | 447
2017-09-05 11:00 | 447 | 446
2017-09-05 11:30 | 436 | 435
2017-09-05 12:00 | 434 | 433
2017-09-05 12:30 | 439 | 438
2017-09-05 13:00 | 446 | 445
2017-09-05 13:30 | 457 | 456
2017-09-05 14:00 | 460 | 459
2017-09-05 14:30 | 449 | 448
2017-09-05 15:00 | 449 | 448
2017-09-05 15:30 | 458 | 457
2017-09-05 16:00 | 488 | 487
2017-09-05 16:30 | 509 | 509
2017-09-05 17:00 | 518 | 517
2017-09-05 17:30 | 541 | 541
2017-09-05 18:00 | 559 | 559
2017-09-05 18:30 | 585 | 585
2017-09-05 19:00 | 613 | 613
2017-09-05 19:30 | 606 | 606
2017-09-05 20:00 | 584 | 584
2017-09-05 20:30 | 560 | 560
2017-09-05 21:00 | 544 | 544
2017-09-05 21:30 | 525 | 525
2017-09-05 22:00 | 495 | 495
2017-09-05 22:30 | 497 | 497
2017-09-05 23:00 | 489 | 489
2017-09-05 23:30 | 470 | 470
2017-09-06 | 444 | 443
2017-09-06 00:30 | 422 | 420
2017-09-06 01:00 | 415 | 414
2017-09-06 01:30 | 407 | 405
2017-09-06 02:00 | 405 | 403
2017-09-06 02:30 | 398 | 396
2017-09-06 03:00 | 394 | 392
2017-09-06 03:30 | 384 | 381
2017-09-06 04:00 | 388 | 385
2017-09-06 04:30 | 410 | 407
2017-09-06 05:00 | 430 | 427
2017-09-06 05:30 | 446 | 444
2017-09-06 06:00 | 453 | 451
2017-09-06 06:30 | 480 | 479
2017-09-06 07:00 | 472 | 471
2017-09-06 07:30 | 473 | 471
2017-09-06 08:00 | 473 | 471
2017-09-06 08:30 | 456 | 454
2017-09-06 09:00 | 431 | 428
2017-09-06 09:30 | 422 | 419
2017-09-06 10:00 | 411 | 408
2017-09-06 10:30 | 411 | 407
2017-09-06 11:00 | 407 | 403
2017-09-06 11:30 | 394 | 390
2017-09-06 12:00 | 393 | 389
2017-09-06 12:30 | 397 | 393
2017-09-06 13:00 | 407 | 403
2017-09-06 13:30 | 411 | 407
2017-09-06 14:00 | 420 | 416
2017-09-06 14:30 | 392 | 388
2017-09-06 15:00 | 396 | 392
2017-09-06 15:30 | 418 | 415
2017-09-06 16:00 | 440 | 437
2017-09-06 16:30 | 467 | 464
2017-09-06 17:00 | 465 | 463
2017-09-06 17:30 | 440 | 438
2017-09-06 18:00 | 404 | 401
2017-09-06 18:30 | 429 | 426
2017-09-06 19:00 | 455 | 453
2017-09-06 19:30 | 443 | 441
2017-09-06 20:00 | 424 | 422
2017-09-06 20:30 | 402 | 399
2017-09-06 21:00 | 385 | 382
2017-09-06 21:30 | 369 | 365
2017-09-06 22:00 | 342 | 337
2017-09-06 22:30 | 343 | 336
2017-09-06 23:00 | 330 | 324
2017-09-06 23:30 | 311 | 303
2017-09-07 | 294 | 285
2017-09-07 00:30 | 404 | 397
2017-09-07 01:00 | 421 | 417
2017-09-07 01:30 | 430 | 427
2017-09-07 02:00 | 439 | 436
2017-09-07 02:30 | 435 | 432
2017-09-07 03:00 | 428 | 425
2017-09-07 03:30 | 426 | 423
2017-09-07 04:00 | 423 | 420
2017-09-07 04:30 | 426 | 423
2017-09-07 05:00 | 431 | 428
2017-09-07 05:30 | 445 | 442
2017-09-07 06:00 | 461 | 459
2017-09-07 06:30 | 473 | 471
2017-09-07 07:00 | 460 | 459
2017-09-07 07:30 | 475 | 473
2017-09-07 08:00 | 471 | 470
2017-09-07 08:30 | 465 | 463
2017-09-07 09:00 | 452 | 450
2017-09-07 09:30 | 455 | 453
2017-09-07 10:00 | 450 | 448
2017-09-07 10:30 | 442 | 439
2017-09-07 11:00 | 444 | 442
2017-09-07 11:30 | 438 | 435
2017-09-07 12:00 | 428 | 425
2017-09-07 12:30 | 427 | 424
2017-09-07 13:00 | 435 | 432
2017-09-07 13:30 | 440 | 438
2017-09-07 14:00 | 446 | 444
2017-09-07 14:30 | 431 | 429
2017-09-07 15:00 | 448 | 446
2017-09-07 15:30 | 452 | 449
2017-09-07 16:00 | 458 | 456
2017-09-07 16:30 | 396 | 394
2017-09-07 17:00 | 343 | 340
2017-09-07 17:30 | 372 | 367
2017-09-07 18:00 | 391 | 387
2017-09-07 18:30 | 424 | 421
2017-09-07 19:00 | 447 | 445
2017-09-07 19:30 | 443 | 442
2017-09-07 20:00 | 434 | 433
2017-09-07 20:30 | 398 | 396
2017-09-07 21:00 | 367 | 366
2017-09-07 21:30 | 341 | 340
2017-09-07 22:00 | 328 | 326
2017-09-07 22:30 | 334 | 329
2017-09-07 23:00 | 332 | 325
2017-09-07 23:30 | 304 | 297
2017-09-08 | 285 | 275
2017-09-08 00:30 | 396 | 388
2017-09-08 01:00 | 406 | 403
2017-09-08 01:30 | 398 | 395
2017-09-08 02:00 | 393 | 389
2017-09-08 02:30 | 385 | 381
2017-09-08 03:00 | 377 | 373
2017-09-08 03:30 | 374 | 370
2017-09-08 04:00 | 377 | 373
2017-09-08 04:30 | 379 | 375
2017-09-08 05:00 | 384 | 380
2017-09-08 05:30 | 397 | 394
2017-09-08 06:00 | 413 | 410
2017-09-08 06:30 | 437 | 435
2017-09-08 07:00 | 445 | 443
2017-09-08 07:30 | 456 | 454
2017-09-08 08:00 | 465 | 463
2017-09-08 08:30 | 458 | 457
2017-09-08 09:00 | 455 | 454
2017-09-08 09:30 | 439 | 438
2017-09-08 10:00 | 429 | 427
2017-09-08 10:30 | 438 | 436
2017-09-08 11:00 | 426 | 424
2017-09-08 11:30 | 409 | 407
2017-09-08 12:00 | 408 | 405
2017-09-08 12:30 | 417 | 415
2017-09-08 13:00 | 426 | 424
2017-09-08 13:30 | 426 | 424
2017-09-08 14:00 | 433 | 432
2017-09-08 14:30 | 432 | 430
2017-09-08 15:00 | 427 | 425
2017-09-08 15:30 | 434 | 433
2017-09-08 16:00 | 452 | 451
2017-09-08 16:30 | 465 | 464
2017-09-08 17:00 | 409 | 409
2017-09-08 17:30 | 356 | 355
2017-09-08 18:00 | 387 | 384
2017-09-08 18:30 | 405 | 403
2017-09-08 19:00 | 410 | 409
2017-09-08 19:30 | 387 | 386
2017-09-08 20:00 | 366 | 365
2017-09-08 20:30 | 347 | 345
2017-09-08 21:00 | 330 | 328
2017-09-08 21:30 | 314 | 311
2017-09-08 22:00 | 295 | 291
2017-09-08 22:30 | 301 | 296
2017-09-08 23:00 | 306 | 300
2017-09-08 23:30 | 281 | 274
2017-09-09 | 272 | 264
2017-09-09 00:30 | 379 | 373
2017-09-09 01:00 | 386 | 382
2017-09-09 01:30 | 378 | 375
2017-09-09 02:00 | 374 | 371
2017-09-09 02:30 | 368 | 364
2017-09-09 03:00 | 359 | 356
2017-09-09 03:30 | 359 | 355
2017-09-09 04:00 | 353 | 349
2017-09-09 04:30 | 359 | 354
2017-09-09 05:00 | 367 | 363
2017-09-09 05:30 | 375 | 372
2017-09-09 06:00 | 380 | 377
2017-09-09 06:30 | 396 | 393
2017-09-09 07:00 | 372 | 369
2017-09-09 07:30 | 376 | 372
2017-09-09 08:00 | 379 | 376
2017-09-09 08:30 | 389 | 386
2017-09-09 09:00 | 391 | 388
2017-09-09 09:30 | 387 | 384
2017-09-09 10:00 | 383 | 380
2017-09-09 10:30 | 386 | 383
2017-09-09 11:00 | 374 | 370
2017-09-09 11:30 | 376 | 372
2017-09-09 12:00 | 379 | 376
2017-09-09 12:30 | 367 | 363
2017-09-09 13:00 | 353 | 349
2017-09-09 13:30 | 353 | 349
2017-09-09 14:00 | 344 | 340
2017-09-09 14:30 | 349 | 344
2017-09-09 15:00 | 355 | 351
2017-09-09 15:30 | 378 | 373
2017-09-09 16:00 | 401 | 398
2017-09-09 16:30 | 418 | 416
2017-09-09 17:00 | 438 | 436
2017-09-09 17:30 | 457 | 455
2017-09-09 18:00 | 473 | 472
2017-09-09 18:30 | 502 | 501
2017-09-09 19:00 | 519 | 519
2017-09-09 19:30 | 502 | 502
2017-09-09 20:00 | 486 | 485
2017-09-09 20:30 | 478 | 478
2017-09-09 21:00 | 472 | 471
2017-09-09 21:30 | 450 | 449
2017-09-09 22:00 | 432 | 431
2017-09-09 22:30 | 437 | 436
2017-09-09 23:00 | 447 | 446
2017-09-09 23:30 | 428 | 426
2017-09-10 | 403 | 400
2017-09-10 00:30 | 397 | 394
2017-09-10 01:00 | 382 | 378
2017-09-10 01:30 | 373 | 369
2017-09-10 02:00 | 364 | 359
2017-09-10 02:30 | 359 | 354
2017-09-10 03:00 | 355 | 350
2017-09-10 03:30 | 351 | 346
2017-09-10 04:00 | 350 | 344
2017-09-10 04:30 | 355 | 350
2017-09-10 05:00 | 354 | 349
2017-09-10 05:30 | 357 | 352
2017-09-10 06:00 | 361 | 356
2017-09-10 06:30 | 364 | 359
2017-09-10 07:00 | 338 | 333
2017-09-10 07:30 | 337 | 331
2017-09-10 08:00 | 353 | 346
2017-09-10 08:30 | 365 | 360
2017-09-10 09:00 | 370 | 366
2017-09-10 09:30 | 378 | 374
2017-09-10 10:00 | 374 | 370
2017-09-10 10:30 | 367 | 363
2017-09-10 11:00 | 357 | 352
2017-09-10 11:30 | 350 | 345
2017-09-10 12:00 | 350 | 344
2017-09-10 12:30 | 342 | 336
2017-09-10 13:00 | 337 | 332
2017-09-10 13:30 | 332 | 326
2017-09-10 14:00 | 336 | 330
2017-09-10 14:30 | 330 | 323
2017-09-10 15:00 | 339 | 332
2017-09-10 15:30 | 353 | 347
2017-09-10 16:00 | 377 | 372
2017-09-10 16:30 | 398 | 394
2017-09-10 17:00 | 412 | 409
2017-09-10 17:30 | 469 | 467
2017-09-10 18:00 | 511 | 510
2017-09-10 18:30 | 532 | 532
2017-09-10 19:00 | 558 | 558
2017-09-10 19:30 | 557 | 557
2017-09-10 20:00 | 530 | 529
2017-09-10 20:30 | 501 | 501
2017-09-10 21:00 | 477 | 476
2017-09-10 21:30 | 462 | 461
2017-09-10 22:00 | 443 | 442
2017-09-10 22:30 | 440 | 438
2017-09-10 23:00 | 433 | 431
2017-09-10 23:30 | 418 | 416
2017-09-11 | 403 | 400
2017-09-11 00:30 | 397 | 394
2017-09-11 01:00 | 390 | 387
2017-09-11 01:30 | 388 | 384
2017-09-11 02:00 | 377 | 374
2017-09-11 02:30 | 369 | 366
2017-09-11 03:00 | 370 | 366
2017-09-11 03:30 | 363 | 359
2017-09-11 04:00 | 387 | 383
2017-09-11 04:30 | 386 | 383
2017-09-11 05:00 | 385 | 381
2017-09-11 05:30 | 397 | 394
2017-09-11 06:00 | 414 | 411
2017-09-11 06:30 | 446 | 444
2017-09-11 07:00 | 448 | 447
2017-09-11 07:30 | 457 | 455
2017-09-11 08:00 | 466 | 465
2017-09-11 08:30 | 459 | 458
2017-09-11 09:00 | 448 | 447
2017-09-11 09:30 | 444 | 442
2017-09-11 10:00 | 429 | 428
2017-09-11 10:30 | 423 | 421
2017-09-11 11:00 | 423 | 422
2017-09-11 11:30 | 438 | 436
2017-09-11 12:00 | 424 | 422
2017-09-11 12:30 | 412 | 411
2017-09-11 13:00 | 424 | 423
2017-09-11 13:30 | 444 | 442
2017-09-11 14:00 | 450 | 449
2017-09-11 14:30 | 451 | 450
2017-09-11 15:00 | 450 | 449
2017-09-11 15:30 | 450 | 449
2017-09-11 16:00 | 454 | 454
2017-09-11 16:30 | 395 | 394
2017-09-11 17:00 | 326 | 324
2017-09-11 17:30 | 337 | 333
2017-09-11 18:00 | 370 | 366
2017-09-11 18:30 | 399 | 397
2017-09-11 19:00 | 426 | 424
2017-09-11 19:30 | 536 | 535
2017-09-11 20:00 | 554 | 554
2017-09-11 20:30 | 532 | 532
2017-09-11 21:00 | 513 | 513
2017-09-11 21:30 | 496 | 496
2017-09-11 22:00 | 475 | 474
2017-09-11 22:30 | 478 | 477
2017-09-11 23:00 | 458 | 457
2017-09-11 23:30 | 441 | 440
2017-09-12 | 431 | 429
2017-09-12 00:30 | 415 | 413
2017-09-12 01:00 | 397 | 394
2017-09-12 01:30 | 389 | 386
2017-09-12 02:00 | 387 | 384
2017-09-12 02:30 | 376 | 372
2017-09-12 03:00 | 370 | 365
2017-09-12 03:30 | 376 | 372
2017-09-12 04:00 | 378 | 375
2017-09-12 04:30 | 378 | 375
2017-09-12 05:00 | 374 | 371
2017-09-12 05:30 | 397 | 393
2017-09-12 06:00 | 421 | 419
2017-09-12 06:30 | 448 | 446
2017-09-12 07:00 | 457 | 455
2017-09-12 07:30 | 471 | 469
2017-09-12 08:00 | 480 | 479
2017-09-12 08:30 | 477 | 477
2017-09-12 09:00 | 462 | 462
2017-09-12 09:30 | 468 | 467
2017-09-12 10:00 | 462 | 461
2017-09-12 10:30 | 453 | 452
2017-09-12 11:00 | 449 | 448
2017-09-12 11:30 | 450 | 449
2017-09-12 12:00 | 446 | 444
2017-09-12 12:30 | 438 | 436
2017-09-12 13:00 | 433 | 431
2017-09-12 13:30 | 444 | 442
2017-09-12 14:00 | 446 | 444
2017-09-12 14:30 | 437 | 435
2017-09-12 15:00 | 443 | 441
2017-09-12 15:30 | 450 | 448
2017-09-12 16:00 | 463 | 461
2017-09-12 16:30 | 475 | 474
2017-09-12 17:00 | 485 | 484
2017-09-12 17:30 | 506 | 505
2017-09-12 18:00 | 525 | 524
2017-09-12 18:30 | 560 | 559
2017-09-12 19:00 | 582 | 582
2017-09-12 19:30 | 571 | 571
2017-09-12 20:00 | 548 | 548
2017-09-12 20:30 | 523 | 523
2017-09-12 21:00 | 508 | 508
2017-09-12 21:30 | 488 | 488
2017-09-12 22:00 | 468 | 468
2017-09-12 22:30 | 467 | 466
2017-09-12 23:00 | 452 | 452
2017-09-12 23:30 | 433 | 431
2017-09-13 | 419 | 415
2017-09-13 00:30 | 413 | 409
2017-09-13 01:00 | 402 | 398
2017-09-13 01:30 | 397 | 393
2017-09-13 02:00 | 385 | 380
2017-09-13 02:30 | 378 | 372
2017-09-13 03:00 | 374 | 368
2017-09-13 03:30 | 381 | 376
2017-09-13 04:00 | 370 | 365
2017-09-13 04:30 | 372 | 366
2017-09-13 05:00 | 377 | 371
2017-09-13 05:30 | 393 | 387
2017-09-13 06:00 | 410 | 405
2017-09-13 06:30 | 436 | 432
2017-09-13 07:00 | 418 | 415
2017-09-13 07:30 | 434 | 431
2017-09-13 08:00 | 431 | 428
2017-09-13 08:30 | 432 | 430
2017-09-13 09:00 | 432 | 431
2017-09-13 09:30 | 420 | 418
2017-09-13 10:00 | 417 | 415
2017-09-13 10:30 | 413 | 411
2017-09-13 11:00 | 405 | 403
2017-09-13 11:30 | 398 | 396
2017-09-13 12:00 | 394 | 392
2017-09-13 12:30 | 396 | 393
2017-09-13 13:00 | 400 | 398
2017-09-13 13:30 | 405 | 402
2017-09-13 14:00 | 409 | 405
2017-09-13 14:30 | 413 | 409
2017-09-13 15:00 | 423 | 420
2017-09-13 15:30 | 436 | 433
2017-09-13 16:00 | 446 | 444
2017-09-13 16:30 | 452 | 450
2017-09-13 17:00 | 468 | 466
2017-09-13 17:30 | 481 | 480
2017-09-13 18:00 | 491 | 490
2017-09-13 18:30 | 526 | 525
2017-09-13 19:00 | 550 | 550
2017-09-13 19:30 | 538 | 537
2017-09-13 20:00 | 520 | 520
2017-09-13 20:30 | 503 | 502
2017-09-13 21:00 | 488 | 487
2017-09-13 21:30 | 463 | 462
2017-09-13 22:00 | 441 | 439
2017-09-13 22:30 | 440 | 438
2017-09-13 23:00 | 437 | 436
2017-09-13 23:30 | 416 | 414
2017-09-14 | 409 | 406
2017-09-14 00:30 | 396 | 392
2017-09-14 01:00 | 375 | 371
2017-09-14 01:30 | 371 | 365
2017-09-14 02:00 | 368 | 362
2017-09-14 02:30 | 363 | 357
2017-09-14 03:00 | 364 | 358
2017-09-14 03:30 | 368 | 362
2017-09-14 04:00 | 361 | 355
2017-09-14 04:30 | 364 | 358
2017-09-14 05:00 | 371 | 365
2017-09-14 05:30 | 387 | 381
2017-09-14 06:00 | 401 | 396
2017-09-14 06:30 | 428 | 424
2017-09-14 07:00 | 441 | 438
2017-09-14 07:30 | 439 | 437
2017-09-14 08:00 | 457 | 455
2017-09-14 08:30 | 452 | 451
2017-09-14 09:00 | 430 | 429
2017-09-14 09:30 | 412 | 410
2017-09-14 10:00 | 403 | 401
2017-09-14 10:30 | 395 | 393
2017-09-14 11:00 | 381 | 378
2017-09-14 11:30 | 382 | 379
2017-09-14 12:00 | 386 | 383
2017-09-14 12:30 | 361 | 358
2017-09-14 13:00 | 333 | 329
2017-09-14 13:30 | 346 | 342
2017-09-14 14:00 | 363 | 359
2017-09-14 14:30 | 380 | 376
2017-09-14 15:00 | 381 | 378
2017-09-14 15:30 | 360 | 357
2017-09-14 16:00 | 378 | 374
2017-09-14 16:30 | 406 | 403
2017-09-14 17:00 | 446 | 444
2017-09-14 17:30 | 515 | 514
2017-09-14 18:00 | 517 | 517
2017-09-14 18:30 | 471 | 471
2017-09-14 19:00 | 479 | 478
2017-09-14 19:30 | 461 | 461
2017-09-14 20:00 | 442 | 441
2017-09-14 20:30 | 416 | 415
2017-09-14 21:00 | 397 | 396
2017-09-14 21:30 | 373 | 371
2017-09-14 22:00 | 347 | 344
2017-09-14 22:30 | 345 | 342
2017-09-14 23:00 | 333 | 329
2017-09-14 23:30 | 315 | 310
2017-09-15 | 294 | 287
2017-09-15 00:30 | 404 | 398
2017-09-15 01:00 | 417 | 414
2017-09-15 01:30 | 408 | 406
2017-09-15 02:00 | 398 | 395
2017-09-15 02:30 | 387 | 384
2017-09-15 03:00 | 386 | 383
2017-09-15 03:30 | 389 | 386
2017-09-15 04:00 | 386 | 382
2017-09-15 04:30 | 388 | 384
2017-09-15 05:00 | 392 | 389
2017-09-15 05:30 | 404 | 401
2017-09-15 06:00 | 424 | 422
2017-09-15 06:30 | 463 | 461
2017-09-15 07:00 | 474 | 473
2017-09-15 07:30 | 486 | 484
2017-09-15 08:00 | 503 | 502
2017-09-15 08:30 | 504 | 503
2017-09-15 09:00 | 496 | 496
2017-09-15 09:30 | 492 | 492
2017-09-15 10:00 | 478 | 477
2017-09-15 10:30 | 476 | 475
2017-09-15 11:00 | 472 | 470
2017-09-15 11:30 | 466 | 465
2017-09-15 12:00 | 464 | 462
2017-09-15 12:30 | 432 | 430
2017-09-15 13:00 | 396 | 393
2017-09-15 13:30 | 396 | 392
2017-09-15 14:00 | 405 | 401
2017-09-15 14:30 | 406 | 403
2017-09-15 15:00 | 455 | 451
2017-09-15 15:30 | 428 | 426
2017-09-15 16:00 | 422 | 420
2017-09-15 16:30 | 424 | 422
2017-09-15 17:00 | 459 | 456
2017-09-15 17:30 | 496 | 494
2017-09-15 18:00 | 508 | 507
2017-09-15 18:30 | 517 | 516
2017-09-15 19:00 | 537 | 537
2017-09-15 19:30 | 528 | 528
2017-09-15 20:00 | 508 | 507
2017-09-15 20:30 | 486 | 485
2017-09-15 21:00 | 476 | 475
2017-09-15 21:30 | 465 | 464
2017-09-15 22:00 | 442 | 440
2017-09-15 22:30 | 457 | 455
2017-09-15 23:00 | 452 | 450
2017-09-15 23:30 | 434 | 433
2017-09-16 | 421 | 418
2017-09-16 00:30 | 409 | 406
2017-09-16 01:00 | 398 | 395
2017-09-16 01:30 | 388 | 385
2017-09-16 02:00 | 383 | 379
2017-09-16 02:30 | 379 | 374
2017-09-16 03:00 | 377 | 372
2017-09-16 03:30 | 383 | 378
2017-09-16 04:00 | 390 | 386
2017-09-16 04:30 | 391 | 387
2017-09-16 05:00 | 389 | 385
2017-09-16 05:30 | 388 | 384
2017-09-16 06:00 | 399 | 395
2017-09-16 06:30 | 414 | 410
2017-09-16 07:00 | 392 | 389
2017-09-16 07:30 | 401 | 397
2017-09-16 08:00 | 405 | 402
2017-09-16 08:30 | 417 | 413
2017-09-16 09:00 | 415 | 412
2017-09-16 09:30 | 415 | 412
2017-09-16 10:00 | 397 | 394
2017-09-16 10:30 | 391 | 387
2017-09-16 11:00 | 337 | 332
2017-09-16 11:30 | 305 | 298
2017-09-16 12:00 | 296 | 287
2017-09-16 12:30 | 291 | 282
2017-09-16 13:00 | 291 | 283
2017-09-16 13:30 | 294 | 285
2017-09-16 14:00 | 296 | 288
2017-09-16 14:30 | 326 | 318
2017-09-16 15:00 | 365 | 359
2017-09-16 15:30 | 369 | 365
2017-09-16 16:00 | 388 | 384
2017-09-16 16:30 | 413 | 410
2017-09-16 17:00 | 428 | 426
2017-09-16 17:30 | 452 | 450
2017-09-16 18:00 | 474 | 472
2017-09-16 18:30 | 499 | 498
2017-09-16 19:00 | 523 | 523
2017-09-16 19:30 | 532 | 532
2017-09-16 20:00 | 511 | 511
2017-09-16 20:30 | 484 | 484
2017-09-16 21:00 | 469 | 469
2017-09-16 21:30 | 456 | 455
2017-09-16 22:00 | 442 | 441
2017-09-16 22:30 | 453 | 451
2017-09-16 23:00 | 447 | 446
2017-09-16 23:30 | 435 | 434
2017-09-17 | 413 | 411
2017-09-17 00:30 | 401 | 398
2017-09-17 01:00 | 395 | 392
2017-09-17 01:30 | 388 | 385
2017-09-17 02:00 | 374 | 371
2017-09-17 02:30 | 369 | 366
2017-09-17 03:00 | 368 | 364
2017-09-17 03:30 | 368 | 363
2017-09-17 04:00 | 361 | 357
2017-09-17 04:30 | 370 | 365
2017-09-17 05:00 | 370 | 365
2017-09-17 05:30 | 369 | 365
2017-09-17 06:00 | 366 | 361
2017-09-17 06:30 | 370 | 366
2017-09-17 07:00 | 362 | 358
2017-09-17 07:30 | 348 | 343
2017-09-17 08:00 | 357 | 351
2017-09-17 08:30 | 364 | 359
2017-09-17 09:00 | 373 | 368
2017-09-17 09:30 | 383 | 378
2017-09-17 10:00 | 388 | 384
2017-09-17 10:30 | 382 | 379
2017-09-17 11:00 | 380 | 376
2017-09-17 11:30 | 380 | 377
2017-09-17 12:00 | 362 | 358
2017-09-17 12:30 | 362 | 357
2017-09-17 13:00 | 359 | 354
2017-09-17 13:30 | 362 | 357
2017-09-17 14:00 | 358 | 353
2017-09-17 14:30 | 369 | 364
2017-09-17 15:00 | 392 | 388
2017-09-17 15:30 | 397 | 393
2017-09-17 16:00 | 418 | 414
2017-09-17 16:30 | 438 | 436
2017-09-17 17:00 | 445 | 443
2017-09-17 17:30 | 465 | 463
2017-09-17 18:00 | 488 | 487
2017-09-17 18:30 | 525 | 525
2017-09-17 19:00 | 537 | 537
2017-09-17 19:30 | 523 | 523
2017-09-17 20:00 | 502 | 502
2017-09-17 20:30 | 483 | 482
2017-09-17 21:00 | 471 | 470
2017-09-17 21:30 | 452 | 451
2017-09-17 22:00 | 431 | 429
2017-09-17 22:30 | 435 | 433
2017-09-17 23:00 | 430 | 428
2017-09-17 23:30 | 414 | 411
2017-09-18 | 404 | 401
2017-09-18 00:30 | 392 | 388
2017-09-18 01:00 | 395 | 391
2017-09-18 01:30 | 386 | 382
2017-09-18 02:00 | 390 | 386
2017-09-18 02:30 | 377 | 373
2017-09-18 03:00 | 376 | 372
2017-09-18 03:30 | 370 | 366
2017-09-18 04:00 | 373 | 368
2017-09-18 04:30 | 373 | 369
2017-09-18 05:00 | 374 | 369
2017-09-18 05:30 | 389 | 385
2017-09-18 06:00 | 398 | 395
2017-09-18 06:30 | 420 | 417
2017-09-18 07:00 | 414 | 411
2017-09-18 07:30 | 423 | 421
2017-09-18 08:00 | 440 | 438
2017-09-18 08:30 | 454 | 452
2017-09-18 09:00 | 458 | 457
2017-09-18 09:30 | 446 | 444
2017-09-18 10:00 | 444 | 442
2017-09-18 10:30 | 427 | 424
2017-09-18 11:00 | 366 | 363
2017-09-18 11:30 | 363 | 358
2017-09-18 12:00 | 366 | 361
2017-09-18 12:30 | 368 | 363
2017-09-18 13:00 | 373 | 368
2017-09-18 13:30 | 389 | 384
2017-09-18 14:00 | 394 | 390
2017-09-18 14:30 | 423 | 420
2017-09-18 15:00 | 405 | 402
2017-09-18 15:30 | 390 | 387
2017-09-18 16:00 | 380 | 376
2017-09-18 16:30 | 383 | 379
2017-09-18 17:00 | 426 | 423
2017-09-18 17:30 | 491 | 490
2017-09-18 18:00 | 501 | 501
2017-09-18 18:30 | 462 | 462
2017-09-18 19:00 | 450 | 449
2017-09-18 19:30 | 414 | 412
2017-09-18 20:00 | 391 | 389
2017-09-18 20:30 | 486 | 484
2017-09-18 21:00 | 497 | 496
2017-09-18 21:30 | 474 | 473
2017-09-18 22:00 | 452 | 451
2017-09-18 22:30 | 451 | 450
2017-09-18 23:00 | 447 | 446
2017-09-18 23:30 | 433 | 432
2017-09-19 | 423 | 421
2017-09-19 00:30 | 421 | 419
2017-09-19 01:00 | 410 | 408
2017-09-19 01:30 | 407 | 405
2017-09-19 02:00 | 407 | 405
2017-09-19 02:30 | 404 | 402
2017-09-19 03:00 | 391 | 389
2017-09-19 03:30 | 392 | 388
2017-09-19 04:00 | 390 | 387
2017-09-19 04:30 | 396 | 393
2017-09-19 05:00 | 407 | 404
2017-09-19 05:30 | 419 | 417
2017-09-19 06:00 | 446 | 444
2017-09-19 06:30 | 465 | 463
2017-09-19 07:00 | 448 | 447
2017-09-19 07:30 | 470 | 469
2017-09-19 08:00 | 486 | 485
2017-09-19 08:30 | 499 | 498
2017-09-19 09:00 | 506 | 505
2017-09-19 09:30 | 528 | 527
2017-09-19 10:00 | 480 | 480
2017-09-19 10:30 | 388 | 387
2017-09-19 11:00 | 388 | 385
2017-09-19 11:30 | 411 | 408
2017-09-19 12:00 | 508 | 505
2017-09-19 12:30 | 504 | 503
2017-09-19 13:00 | 504 | 504
2017-09-19 13:30 | 496 | 496
2017-09-19 14:00 | 510 | 509
2017-09-19 14:30 | 521 | 521
2017-09-19 15:00 | 518 | 517
2017-09-19 15:30 | 499 | 499
2017-09-19 16:00 | 491 | 490
2017-09-19 16:30 | 443 | 442
2017-09-19 17:00 | 452 | 451
2017-09-19 17:30 | 469 | 468
2017-09-19 18:00 | 507 | 506
2017-09-19 18:30 | 547 | 547
2017-09-19 19:00 | 560 | 560
2017-09-19 19:30 | 548 | 548
2017-09-19 20:00 | 558 | 558
2017-09-19 20:30 | 583 | 583
2017-09-19 21:00 | 565 | 565
2017-09-19 21:30 | 547 | 547
2017-09-19 22:00 | 508 | 508
2017-09-19 22:30 | 510 | 510
2017-09-19 23:00 | 514 | 513
2017-09-19 23:30 | 504 | 504
2017-09-20 | 475 | 474
2017-09-20 00:30 | 455 | 453
2017-09-20 01:00 | 437 | 436
2017-09-20 01:30 | 425 | 423
2017-09-20 02:00 | 418 | 416
2017-09-20 02:30 | 415 | 413
2017-09-20 03:00 | 413 | 410
2017-09-20 03:30 | 407 | 404
2017-09-20 04:00 | 401 | 398
2017-09-20 04:30 | 407 | 404
2017-09-20 05:00 | 411 | 408
2017-09-20 05:30 | 415 | 412
2017-09-20 06:00 | 373 | 371
2017-09-20 06:30 | 371 | 368
2017-09-20 07:00 | 372 | 367
2017-09-20 07:30 | 381 | 377
2017-09-20 08:00 | 399 | 395
2017-09-20 08:30 | 401 | 398
2017-09-20 09:00 | 394 | 391
2017-09-20 09:30 | 385 | 382
2017-09-20 10:00 | 392 | 389
2017-09-20 10:30 | 398 | 396
2017-09-20 11:00 | 385 | 382
2017-09-20 11:30 | 378 | 375
2017-09-20 12:00 | 354 | 351
2017-09-20 12:30 | 305 | 300
2017-09-20 13:00 | 320 | 314
2017-09-20 13:30 | 322 | 317
2017-09-20 14:00 | 332 | 327
2017-09-20 14:30 | 355 | 351
2017-09-20 15:00 | 358 | 354
2017-09-20 15:30 | 366 | 363
2017-09-20 16:00 | 363 | 361
2017-09-20 16:30 | 372 | 370
2017-09-20 17:00 | 387 | 384
2017-09-20 17:30 | 395 | 393
2017-09-20 18:00 | 385 | 383
2017-09-20 18:30 | 407 | 405
2017-09-20 19:00 | 448 | 447
2017-09-20 19:30 | 461 | 461
2017-09-20 20:00 | 475 | 474
2017-09-20 20:30 | 516 | 516
2017-09-20 21:00 | 506 | 506
2017-09-20 21:30 | 479 | 479
2017-09-20 22:00 | 467 | 466
2017-09-20 22:30 | 471 | 470
2017-09-20 23:00 | 464 | 463
2017-09-20 23:30 | 445 | 444
2017-09-21 | 435 | 433
2017-09-21 00:30 | 422 | 421
2017-09-21 01:00 | 422 | 419
2017-09-21 01:30 | 414 | 411
2017-09-21 02:00 | 407 | 404
2017-09-21 02:30 | 404 | 401
2017-09-21 03:00 | 400 | 397
2017-09-21 03:30 | 400 | 396
2017-09-21 04:00 | 393 | 389
2017-09-21 04:30 | 391 | 387
2017-09-21 05:00 | 391 | 388
2017-09-21 05:30 | 398 | 395
2017-09-21 06:00 | 415 | 411
2017-09-21 06:30 | 449 | 447
2017-09-21 07:00 | 460 | 458
2017-09-21 07:30 | 433 | 432
2017-09-21 08:00 | 437 | 435
2017-09-21 08:30 | 426 | 424
2017-09-21 09:00 | 383 | 380
2017-09-21 09:30 | 418 | 414
2017-09-21 10:00 | 366 | 362
2017-09-21 10:30 | 356 | 351
2017-09-21 11:00 | 360 | 355
2017-09-21 11:30 | 357 | 351
2017-09-21 12:00 | 361 | 356
2017-09-21 12:30 | 368 | 363
2017-09-21 13:00 | 381 | 377
2017-09-21 13:30 | 426 | 422
2017-09-21 14:00 | 429 | 427
2017-09-21 14:30 | 431 | 428
2017-09-21 15:00 | 434 | 432
2017-09-21 15:30 | 452 | 450
2017-09-21 16:00 | 463 | 461
2017-09-21 16:30 | 482 | 481
2017-09-21 17:00 | 491 | 490
2017-09-21 17:30 | 473 | 472
2017-09-21 18:00 | 504 | 503
2017-09-21 18:30 | 542 | 542
2017-09-21 19:00 | 563 | 563
2017-09-21 19:30 | 573 | 573
2017-09-21 20:00 | 612 | 612
2017-09-21 20:30 | 594 | 594
2017-09-21 21:00 | 566 | 566
2017-09-21 21:30 | 542 | 542
2017-09-21 22:00 | 519 | 519
2017-09-21 22:30 | 535 | 535
2017-09-21 23:00 | 518 | 518
2017-09-21 23:30 | 500 | 499
2017-09-22 | 485 | 484
2017-09-22 00:30 | 471 | 470
2017-09-22 01:00 | 456 | 455
2017-09-22 01:30 | 442 | 441
2017-09-22 02:00 | 439 | 437
2017-09-22 02:30 | 437 | 435
2017-09-22 03:00 | 427 | 425
2017-09-22 03:30 | 425 | 424
2017-09-22 04:00 | 425 | 423
2017-09-22 04:30 | 426 | 424
2017-09-22 05:00 | 426 | 424
2017-09-22 05:30 | 439 | 437
2017-09-22 06:00 | 452 | 450
2017-09-22 06:30 | 474 | 472
2017-09-22 07:00 | 494 | 493
2017-09-22 07:30 | 477 | 476
2017-09-22 08:00 | 483 | 482
2017-09-22 08:30 | 529 | 528
2017-09-22 09:00 | 537 | 537
2017-09-22 09:30 | 548 | 548
2017-09-22 10:00 | 540 | 539
2017-09-22 10:30 | 510 | 510
2017-09-22 11:00 | 509 | 508
2017-09-22 11:30 | 491 | 491
2017-09-22 12:00 | 475 | 475
2017-09-22 12:30 | 472 | 472
2017-09-22 13:00 | 470 | 469
2017-09-22 13:30 | 484 | 483
2017-09-22 14:00 | 519 | 518
2017-09-22 14:30 | 531 | 531
2017-09-22 15:00 | 546 | 546
2017-09-22 15:30 | 547 | 547
2017-09-22 16:00 | 558 | 558
2017-09-22 16:30 | 568 | 568
2017-09-22 17:00 | 562 | 562
2017-09-22 17:30 | 543 | 543
2017-09-22 18:00 | 572 | 571
2017-09-22 18:30 | 582 | 582
2017-09-22 19:00 | 606 | 606
2017-09-22 19:30 | 606 | 606
2017-09-22 20:00 | 580 | 580
2017-09-22 20:30 | 552 | 552
2017-09-22 21:00 | 537 | 537
2017-09-22 21:30 | 518 | 518
2017-09-22 22:00 | 497 | 496
2017-09-22 22:30 | 526 | 525
2017-09-22 23:00 | 513 | 512
2017-09-22 23:30 | 494 | 494
2017-09-23 | 473 | 472
2017-09-23 00:30 | 465 | 464
2017-09-23 01:00 | 447 | 447
2017-09-23 01:30 | 433 | 432
2017-09-23 02:00 | 424 | 423
2017-09-23 02:30 | 423 | 421
2017-09-23 03:00 | 416 | 413
2017-09-23 03:30 | 415 | 412
2017-09-23 04:00 | 418 | 416
2017-09-23 04:30 | 419 | 417
2017-09-23 05:00 | 415 | 413
2017-09-23 05:30 | 426 | 424
2017-09-23 06:00 | 430 | 428
2017-09-23 06:30 | 439 | 437
2017-09-23 07:00 | 444 | 442
2017-09-23 07:30 | 466 | 464
2017-09-23 08:00 | 473 | 472
2017-09-23 08:30 | 489 | 488
2017-09-23 09:00 | 496 | 495
2017-09-23 09:30 | 494 | 493
2017-09-23 10:00 | 451 | 450
2017-09-23 10:30 | 401 | 400
2017-09-23 11:00 | 345 | 342
2017-09-23 11:30 | 319 | 313
2017-09-23 12:00 | 320 | 313
2017-09-23 12:30 | 326 | 321
2017-09-23 13:00 | 371 | 366
2017-09-23 13:30 | 379 | 375
2017-09-23 14:00 | 393 | 390
2017-09-23 14:30 | 412 | 409
2017-09-23 15:00 | 426 | 424
2017-09-23 15:30 | 441 | 439
2017-09-23 16:00 | 452 | 450
2017-09-23 16:30 | 466 | 465
2017-09-23 17:00 | 486 | 485
2017-09-23 17:30 | 510 | 509
2017-09-23 18:00 | 463 | 463
2017-09-23 18:30 | 462 | 461
2017-09-23 19:00 | 482 | 480
2017-09-23 19:30 | 605 | 604
2017-09-23 20:00 | 630 | 630
2017-09-23 20:30 | 601 | 601
2017-09-23 21:00 | 577 | 577
2017-09-23 21:30 | 552 | 552
2017-09-23 22:00 | 522 | 522
2017-09-23 22:30 | 501 | 501
2017-09-23 23:00 | 486 | 485
2017-09-23 23:30 | 468 | 467
2017-09-24 | 451 | 450
2017-09-24 00:30 | 438 | 437
2017-09-24 01:00 | 426 | 425
2017-09-24 01:30 | 414 | 412
2017-09-24 02:00 | 408 | 405
2017-09-24 02:30 | 399 | 396
2017-09-24 03:00 | 392 | 389
2017-09-24 03:30 | 396 | 393
2017-09-24 04:00 | 390 | 387
2017-09-24 04:30 | 396 | 393
2017-09-24 05:00 | 399 | 396
2017-09-24 05:30 | 395 | 392
2017-09-24 06:00 | 393 | 390
2017-09-24 06:30 | 393 | 390
2017-09-24 07:00 | 409 | 406
2017-09-24 07:30 | 424 | 421
2017-09-24 08:00 | 431 | 429
2017-09-24 08:30 | 437 | 435
2017-09-24 09:00 | 440 | 439
2017-09-24 09:30 | 453 | 451
2017-09-24 10:00 | 415 | 414
2017-09-24 10:30 | 402 | 400
2017-09-24 11:00 | 395 | 392
2017-09-24 11:30 | 396 | 393
2017-09-24 12:00 | 393 | 390
2017-09-24 12:30 | 385 | 382
2017-09-24 13:00 | 381 | 378
2017-09-24 13:30 | 417 | 414
2017-09-24 14:00 | 434 | 432
2017-09-24 14:30 | 444 | 443
2017-09-24 15:00 | 458 | 457
2017-09-24 15:30 | 472 | 471
2017-09-24 16:00 | 480 | 479
2017-09-24 16:30 | 503 | 502
2017-09-24 17:00 | 532 | 532
2017-09-24 17:30 | 552 | 552
2017-09-24 18:00 | 572 | 572
2017-09-24 18:30 | 591 | 591
2017-09-24 19:00 | 620 | 620
2017-09-24 19:30 | 609 | 609
2017-09-24 20:00 | 588 | 588
2017-09-24 20:30 | 575 | 575
2017-09-24 21:00 | 557 | 557
2017-09-24 21:30 | 536 | 536
2017-09-24 22:00 | 514 | 514
2017-09-24 22:30 | 493 | 492
2017-09-24 23:00 | 467 | 466
2017-09-24 23:30 | 451 | 450
2017-09-25 | 443 | 441
2017-09-25 00:30 | 437 | 435
2017-09-25 01:00 | 424 | 422
2017-09-25 01:30 | 424 | 421
2017-09-25 02:00 | 415 | 412
2017-09-25 02:30 | 411 | 408
2017-09-25 03:00 | 408 | 405
2017-09-25 03:30 | 410 | 407
2017-09-25 04:00 | 407 | 404
2017-09-25 04:30 | 404 | 401
2017-09-25 05:00 | 411 | 408
2017-09-25 05:30 | 421 | 419
2017-09-25 06:00 | 427 | 425
2017-09-25 06:30 | 447 | 445
2017-09-25 07:00 | 460 | 458
2017-09-25 07:30 | 453 | 452
2017-09-25 08:00 | 466 | 465
2017-09-25 08:30 | 478 | 477
2017-09-25 09:00 | 474 | 473
2017-09-25 09:30 | 470 | 469
2017-09-25 10:00 | 460 | 459
2017-09-25 10:30 | 449 | 448
2017-09-25 11:00 | 423 | 421
2017-09-25 11:30 | 382 | 380
2017-09-25 12:00 | 386 | 383
2017-09-25 12:30 | 389 | 387
2017-09-25 13:00 | 388 | 385
2017-09-25 13:30 | 393 | 391
2017-09-25 14:00 | 406 | 403
2017-09-25 14:30 | 415 | 413
2017-09-25 15:00 | 414 | 412
2017-09-25 15:30 | 365 | 363
2017-09-25 16:00 | 333 | 330
2017-09-25 16:30 | 352 | 348
2017-09-25 17:00 | 362 | 359
2017-09-25 17:30 | 373 | 370
2017-09-25 18:00 | 397 | 394
2017-09-25 18:30 | 428 | 426
2017-09-25 19:00 | 459 | 458
2017-09-25 19:30 | 443 | 442
2017-09-25 20:00 | 420 | 419
2017-09-25 20:30 | 392 | 390
2017-09-25 21:00 | 370 | 367
2017-09-25 21:30 | 494 | 492
2017-09-25 22:00 | 499 | 499
2017-09-25 22:30 | 482 | 482
2017-09-25 23:00 | 478 | 477
2017-09-25 23:30 | 462 | 461
2017-09-26 | 440 | 439
2017-09-26 00:30 | 427 | 425
2017-09-26 01:00 | 423 | 421
2017-09-26 01:30 | 421 | 419
2017-09-26 02:00 | 416 | 414
2017-09-26 02:30 | 417 | 415
2017-09-26 03:00 | 421 | 419
2017-09-26 03:30 | 423 | 421
2017-09-26 04:00 | 426 | 424
2017-09-26 04:30 | 429 | 427
2017-09-26 05:00 | 438 | 437
2017-09-26 05:30 | 447 | 446
2017-09-26 06:00 | 455 | 453
2017-09-26 06:30 | 482 | 480
2017-09-26 07:00 | 483 | 482
2017-09-26 07:30 | 463 | 462
2017-09-26 08:00 | 496 | 495
2017-09-26 08:30 | 532 | 531
2017-09-26 09:00 | 531 | 531
2017-09-26 09:30 | 514 | 514
2017-09-26 10:00 | 496 | 496
2017-09-26 10:30 | 447 | 446
2017-09-26 11:00 | 429 | 427
2017-09-26 11:30 | 425 | 423
2017-09-26 12:00 | 478 | 476
2017-09-26 12:30 | 495 | 494
2017-09-26 13:00 | 482 | 481
2017-09-26 13:30 | 414 | 413
2017-09-26 14:00 | 403 | 401
2017-09-26 14:30 | 407 | 405
2017-09-26 15:00 | 416 | 414
2017-09-26 15:30 | 429 | 428
2017-09-26 16:00 | 447 | 446
2017-09-26 16:30 | 446 | 445
2017-09-26 17:00 | 476 | 475
2017-09-26 17:30 | 466 | 465
2017-09-26 18:00 | 504 | 503
2017-09-26 18:30 | 466 | 466
2017-09-26 19:00 | 533 | 532
2017-09-26 19:30 | 522 | 522
2017-09-26 20:00 | 489 | 489
2017-09-26 20:30 | 461 | 461
2017-09-26 21:00 | 443 | 442
2017-09-26 21:30 | 423 | 421
2017-09-26 22:00 | 459 | 457
2017-09-26 22:30 | 441 | 439
2017-09-26 23:00 | 384 | 382
2017-09-26 23:30 | 486 | 484
2017-09-27 | 476 | 476
2017-09-27 00:30 | 471 | 470
2017-09-27 01:00 | 453 | 452
2017-09-27 01:30 | 455 | 453
2017-09-27 02:00 | 432 | 431
2017-09-27 02:30 | 422 | 419
2017-09-27 03:00 | 413 | 411
2017-09-27 03:30 | 415 | 412
2017-09-27 04:00 | 415 | 413
2017-09-27 04:30 | 423 | 421
2017-09-27 05:00 | 424 | 421
2017-09-27 05:30 | 436 | 433
2017-09-27 06:00 | 442 | 439
2017-09-27 06:30 | 454 | 452
2017-09-27 07:00 | 479 | 477
2017-09-27 07:30 | 470 | 468
2017-09-27 08:00 | 479 | 477
2017-09-27 08:30 | 492 | 491
2017-09-27 09:00 | 488 | 488
2017-09-27 09:30 | 448 | 447
2017-09-27 10:00 | 417 | 414
2017-09-27 10:30 | 420 | 416
2017-09-27 11:00 | 409 | 403
2017-09-27 11:30 | 422 | 417
2017-09-27 12:00 | 417 | 413
2017-09-27 12:30 | 418 | 414
2017-09-27 13:00 | 427 | 424
2017-09-27 13:30 | 427 | 424
2017-09-27 14:00 | 431 | 427
2017-09-27 14:30 | 448 | 445
2017-09-27 15:00 | 503 | 501
2017-09-27 15:30 | 506 | 506
2017-09-27 16:00 | 531 | 531
2017-09-27 16:30 | 526 | 526
2017-09-27 17:00 | 542 | 542
2017-09-27 17:30 | 575 | 575
2017-09-27 18:00 | 598 | 597
2017-09-27 18:30 | 614 | 614
2017-09-27 19:00 | 632 | 631
2017-09-27 19:30 | 619 | 618
2017-09-27 20:00 | 596 | 596
2017-09-27 20:30 | 574 | 574
2017-09-27 21:00 | 558 | 558
2017-09-27 21:30 | 545 | 544
2017-09-27 22:00 | 518 | 518
2017-09-27 22:30 | 519 | 518
2017-09-27 23:00 | 498 | 497
2017-09-27 23:30 | 476 | 474
2017-09-28 | 458 | 456
2017-09-28 00:30 | 447 | 444
2017-09-28 01:00 | 438 | 434
2017-09-28 01:30 | 431 | 427
2017-09-28 02:00 | 426 | 422
2017-09-28 02:30 | 420 | 414
2017-09-28 03:00 | 417 | 411
2017-09-28 03:30 | 416 | 409
2017-09-28 04:00 | 421 | 413
2017-09-28 04:30 | 429 | 422
2017-09-28 05:00 | 427 | 421
2017-09-28 05:30 | 441 | 434
2017-09-28 06:00 | 454 | 448
2017-09-28 06:30 | 485 | 481
2017-09-28 07:00 | 487 | 484
2017-09-28 07:30 | 466 | 465
2017-09-28 08:00 | 484 | 482
2017-09-28 08:30 | 490 | 489
2017-09-28 09:00 | 489 | 488
2017-09-28 09:30 | 480 | 479
2017-09-28 10:00 | 469 | 468
2017-09-28 10:30 | 468 | 466
2017-09-28 11:00 | 458 | 457
2017-09-28 11:30 | 462 | 460
2017-09-28 12:00 | 463 | 462
2017-09-28 12:30 | 472 | 470
2017-09-28 13:00 | 429 | 428
2017-09-28 13:30 | 388 | 386
2017-09-28 14:00 | 400 | 397
2017-09-28 14:30 | 448 | 445
2017-09-28 15:00 | 459 | 457
2017-09-28 15:30 | 440 | 439
2017-09-28 16:00 | 437 | 436
2017-09-28 16:30 | 374 | 373
2017-09-28 17:00 | 350 | 347
2017-09-28 17:30 | 404 | 400
2017-09-28 18:00 | 408 | 406
2017-09-28 18:30 | 357 | 355
2017-09-28 19:00 | 385 | 382
2017-09-28 19:30 | 501 | 499
2017-09-28 20:00 | 522 | 521
2017-09-28 20:30 | 497 | 497
2017-09-28 21:00 | 507 | 507
2017-09-28 21:30 | 486 | 486
2017-09-28 22:00 | 457 | 456
2017-09-28 22:30 | 431 | 430
2017-09-28 23:00 | 407 | 405
2017-09-28 23:30 | 461 | 458
2017-09-29 | 457 | 456
2017-09-29 00:30 | 444 | 442
2017-09-29 01:00 | 430 | 428
2017-09-29 01:30 | 423 | 420
2017-09-29 02:00 | 416 | 413
2017-09-29 02:30 | 407 | 404
2017-09-29 03:00 | 402 | 399
2017-09-29 03:30 | 405 | 402
2017-09-29 04:00 | 401 | 397
2017-09-29 04:30 | 407 | 404
2017-09-29 05:00 | 406 | 403
2017-09-29 05:30 | 418 | 415
2017-09-29 06:00 | 430 | 427
2017-09-29 06:30 | 451 | 449
2017-09-29 07:00 | 476 | 474
2017-09-29 07:30 | 496 | 495
2017-09-29 08:00 | 504 | 504
2017-09-29 08:30 | 514 | 513
2017-09-29 09:00 | 515 | 514
2017-09-29 09:30 | 432 | 432
2017-09-29 10:00 | 341 | 338
2017-09-29 10:30 | 440 | 436
2017-09-29 11:00 | 462 | 460
2017-09-29 11:30 | 457 | 456
2017-09-29 12:00 | 457 | 455
2017-09-29 12:30 | 454 | 453
2017-09-29 13:00 | 402 | 400
2017-09-29 13:30 | 414 | 411
2017-09-29 14:00 | 433 | 431
2017-09-29 14:30 | 443 | 441
2017-09-29 15:00 | 451 | 450
2017-09-29 15:30 | 437 | 436
2017-09-29 16:00 | 405 | 403
2017-09-29 16:30 | 401 | 399
2017-09-29 17:00 | 344 | 341
2017-09-29 17:30 | 394 | 390
2017-09-29 18:00 | 440 | 437
2017-09-29 18:30 | 454 | 452
2017-09-29 19:00 | 474 | 473
2017-09-29 19:30 | 489 | 487
2017-09-29 20:00 | 481 | 480
2017-09-29 20:30 | 486 | 484
2017-09-29 21:00 | 536 | 534
2017-09-29 21:30 | 533 | 532
2017-09-29 22:00 | 516 | 515
2017-09-29 22:30 | 495 | 494
2017-09-29 23:00 | 475 | 474
2017-09-29 23:30 | 486 | 484
2017-09-30 | 471 | 470
2017-09-30 00:30 | 455 | 454
2017-09-30 01:00 | 440 | 438
2017-09-30 01:30 | 432 | 430
2017-09-30 02:00 | 424 | 422
2017-09-30 02:30 | 427 | 424
2017-09-30 03:00 | 430 | 427
2017-09-30 03:30 | 438 | 435
2017-09-30 04:00 | 436 | 433
2017-09-30 04:30 | 430 | 428
2017-09-30 05:00 | 429 | 426
2017-09-30 05:30 | 434 | 431
2017-09-30 06:00 | 438 | 435
2017-09-30 06:30 | 446 | 444
2017-09-30 07:00 | 456 | 453
2017-09-30 07:30 | 468 | 466
2017-09-30 08:00 | 481 | 479
2017-09-30 08:30 | 500 | 498
2017-09-30 09:00 | 506 | 506
2017-09-30 09:30 | 507 | 506
2017-09-30 10:00 | 474 | 473
2017-09-30 10:30 | 451 | 449
2017-09-30 11:00 | 449 | 448
2017-09-30 11:30 | 442 | 441
2017-09-30 12:00 | 438 | 436
2017-09-30 12:30 | 451 | 449
2017-09-30 13:00 | 460 | 458
2017-09-30 13:30 | 499 | 498
2017-09-30 14:00 | 526 | 525
2017-09-30 14:30 | 521 | 520
2017-09-30 15:00 | 526 | 526
2017-09-30 15:30 | 540 | 540
2017-09-30 16:00 | 496 | 495
2017-09-30 16:30 | 489 | 488
2017-09-30 17:00 | 496 | 495
2017-09-30 17:30 | 508 | 507
2017-09-30 18:00 | 520 | 520
2017-09-30 18:30 | 490 | 489
2017-09-30 19:00 | 485 | 484
2017-09-30 19:30 | 526 | 525
2017-09-30 20:00 | 538 | 538
2017-09-30 20:30 | 585 | 585
2017-09-30 21:00 | 577 | 577
2017-09-30 21:30 | 555 | 555
2017-09-30 22:00 | 547 | 547
2017-09-30 22:30 | 527 | 526
2017-09-30 23:00 | 514 | 513
2017-09-30 23:30 | 492 | 491
2017-10-01 | 474 | 473
2017-10-01 00:30 | 468 | 466
2017-10-01 01:00 | 449 | 448
2017-10-01 01:30 | 436 | 434
2017-10-01 02:00 | 437 | 435
2017-10-01 02:30 | 440 | 438
2017-10-01 03:00 | 434 | 432
2017-10-01 03:30 | 432 | 430
2017-10-01 04:00 | 431 | 429
2017-10-01 04:30 | 427 | 424
2017-10-01 05:00 | 427 | 424
2017-10-01 05:30 | 432 | 429
2017-10-01 06:00 | 435 | 432
2017-10-01 06:30 | 433 | 431
2017-10-01 07:00 | 437 | 435
2017-10-01 07:30 | 451 | 448
2017-10-01 08:00 | 470 | 469
2017-10-01 08:30 | 517 | 516
2017-10-01 09:00 | 539 | 538
2017-10-01 09:30 | 548 | 547
2017-10-01 10:00 | 516 | 516
2017-10-01 10:30 | 489 | 488
2017-10-01 11:00 | 480 | 478
2017-10-01 11:30 | 478 | 477
2017-10-01 12:00 | 489 | 487
2017-10-01 12:30 | 488 | 487
2017-10-01 13:00 | 493 | 492
2017-10-01 13:30 | 521 | 520
2017-10-01 14:00 | 536 | 535
2017-10-01 14:30 | 548 | 547
2017-10-01 15:00 | 554 | 553
2017-10-01 15:30 | 564 | 564
2017-10-01 16:00 | 578 | 578
2017-10-01 16:30 | 475 | 474
2017-10-01 17:00 | 480 | 478
2017-10-01 17:30 | 486 | 485
2017-10-01 18:00 | 490 | 489
2017-10-01 18:30 | 493 | 491
2017-10-01 19:00 | 498 | 497
2017-10-01 19:30 | 560 | 559
2017-10-01 20:00 | 578 | 578
2017-10-01 20:30 | 583 | 583
2017-10-01 21:00 | 579 | 579
2017-10-01 21:30 | 567 | 567
2017-10-01 22:00 | 549 | 549
2017-10-01 22:30 | 530 | 530
2017-10-01 23:00 | 514 | 514
2017-10-01 23:30 | 489 | 488
2017-10-02 | 472 | 471
2017-10-02 00:30 | 464 | 463
2017-10-02 01:00 | 454 | 452
2017-10-02 01:30 | 439 | 437
2017-10-02 02:00 | 433 | 430
2017-10-02 02:30 | 425 | 422
2017-10-02 03:00 | 419 | 416
2017-10-02 03:30 | 420 | 416
2017-10-02 04:00 | 419 | 416
2017-10-02 04:30 | 413 | 409
2017-10-02 05:00 | 420 | 417
2017-10-02 05:30 | 432 | 429
2017-10-02 06:00 | 434 | 432
2017-10-02 06:30 | 436 | 433
2017-10-02 07:00 | 448 | 445
2017-10-02 07:30 | 462 | 460
2017-10-02 08:00 | 477 | 475
2017-10-02 08:30 | 482 | 481
2017-10-02 09:00 | 481 | 479
2017-10-02 09:30 | 491 | 489
2017-10-02 10:00 | 458 | 456
2017-10-02 10:30 | 436 | 434
2017-10-02 11:00 | 432 | 429
2017-10-02 11:30 | 440 | 437
2017-10-02 12:00 | 437 | 434
2017-10-02 12:30 | 442 | 440
2017-10-02 13:00 | 435 | 432
2017-10-02 13:30 | 469 | 467
2017-10-02 14:00 | 490 | 488
2017-10-02 14:30 | 487 | 485
2017-10-02 15:00 | 501 | 499
2017-10-02 15:30 | 499 | 498
2017-10-02 16:00 | 523 | 522
2017-10-02 16:30 | 543 | 543
2017-10-02 17:00 | 562 | 562
2017-10-02 17:30 | 579 | 578
2017-10-02 18:00 | 622 | 622
2017-10-02 18:30 | 648 | 648
2017-10-02 19:00 | 671 | 671
2017-10-02 19:30 | 647 | 647
2017-10-02 20:00 | 601 | 601
2017-10-02 20:30 | 577 | 577
2017-10-02 21:00 | 567 | 567
2017-10-02 21:30 | 555 | 554
2017-10-02 22:00 | 531 | 530
2017-10-02 22:30 | 502 | 501
2017-10-02 23:00 | 481 | 480
2017-10-02 23:30 | 466 | 464
2017-10-03 | 468 | 466
2017-10-03 00:30 | 456 | 454
2017-10-03 01:00 | 451 | 448
2017-10-03 01:30 | 439 | 436
2017-10-03 02:00 | 435 | 432
2017-10-03 02:30 | 437 | 434
2017-10-03 03:00 | 431 | 428
2017-10-03 03:30 | 409 | 406
2017-10-03 04:00 | 410 | 406
2017-10-03 04:30 | 417 | 414
2017-10-03 05:00 | 418 | 415
2017-10-03 05:30 | 430 | 427
2017-10-03 06:00 | 438 | 435
2017-10-03 06:30 | 474 | 472
2017-10-03 07:00 | 503 | 501
2017-10-03 07:30 | 548 | 547
2017-10-03 08:00 | 574 | 573
2017-10-03 08:30 | 569 | 569
2017-10-03 09:00 | 562 | 562
2017-10-03 09:30 | 559 | 558
2017-10-03 10:00 | 524 | 524
2017-10-03 10:30 | 505 | 504
2017-10-03 11:00 | 496 | 495
2017-10-03 11:30 | 493 | 492
2017-10-03 12:00 | 489 | 488
2017-10-03 12:30 | 489 | 488
2017-10-03 13:00 | 485 | 484
2017-10-03 13:30 | 516 | 515
2017-10-03 14:00 | 541 | 540
2017-10-03 14:30 | 564 | 564
2017-10-03 15:00 | 565 | 564
2017-10-03 15:30 | 499 | 499
2017-10-03 16:00 | 494 | 493
2017-10-03 16:30 | 474 | 473
2017-10-03 17:00 | 486 | 485
2017-10-03 17:30 | 470 | 469
2017-10-03 18:00 | 495 | 494
2017-10-03 18:30 | 524 | 523
2017-10-03 19:00 | 591 | 591
2017-10-03 19:30 | 602 | 602
2017-10-03 20:00 | 577 | 577
2017-10-03 20:30 | 520 | 520
2017-10-03 21:00 | 535 | 534
2017-10-03 21:30 | 584 | 583
2017-10-03 22:00 | 559 | 558
2017-10-03 22:30 | 532 | 532
2017-10-03 23:00 | 510 | 509
2017-10-03 23:30 | 495 | 494
2017-10-04 | 479 | 478
2017-10-04 00:30 | 461 | 459
2017-10-04 01:00 | 457 | 456
2017-10-04 01:30 | 451 | 449
2017-10-04 02:00 | 442 | 441
2017-10-04 02:30 | 447 | 445
2017-10-04 03:00 | 447 | 446
2017-10-04 03:30 | 439 | 437
2017-10-04 04:00 | 446 | 444
2017-10-04 04:30 | 437 | 436
2017-10-04 05:00 | 442 | 440
2017-10-04 05:30 | 468 | 467
2017-10-04 06:00 | 484 | 483
2017-10-04 06:30 | 506 | 505
2017-10-04 07:00 | 528 | 527
2017-10-04 07:30 | 565 | 564
2017-10-04 08:00 | 572 | 571
2017-10-04 08:30 | 608 | 608
2017-10-04 09:00 | 591 | 591
2017-10-04 09:30 | 575 | 575
2017-10-04 10:00 | 557 | 557
2017-10-04 10:30 | 535 | 535
2017-10-04 11:00 | 524 | 524
2017-10-04 11:30 | 547 | 547
2017-10-04 12:00 | 542 | 542
2017-10-04 12:30 | 538 | 538
2017-10-04 13:00 | 546 | 546
2017-10-04 13:30 | 577 | 577
2017-10-04 14:00 | 604 | 604
2017-10-04 14:30 | 603 | 603
2017-10-04 15:00 | 625 | 625
2017-10-04 15:30 | 619 | 619
2017-10-04 16:00 | 635 | 635
2017-10-04 16:30 | 644 | 643
2017-10-04 17:00 | 630 | 630
2017-10-04 17:30 | 666 | 666
2017-10-04 18:00 | 672 | 672
2017-10-04 18:30 | 694 | 692
2017-10-04 19:00 | 715 | 714
2017-10-04 19:30 | 722 | 720
2017-10-04 20:00 | 695 | 693
2017-10-04 20:30 | 668 | 667
2017-10-04 21:00 | 644 | 643
2017-10-04 21:30 | 619 | 618
2017-10-04 22:00 | 596 | 596
2017-10-04 22:30 | 561 | 561
2017-10-04 23:00 | 549 | 549
2017-10-04 23:30 | 520 | 520
2017-10-05 | 498 | 498
2017-10-05 00:30 | 486 | 486
2017-10-05 01:00 | 476 | 476
2017-10-05 01:30 | 466 | 465
2017-10-05 02:00 | 463 | 463
2017-10-05 02:30 | 467 | 466
2017-10-05 03:00 | 453 | 453
2017-10-05 03:30 | 452 | 451
2017-10-05 04:00 | 476 | 475
2017-10-05 04:30 | 471 | 471
2017-10-05 05:00 | 469 | 469
2017-10-05 05:30 | 490 | 489
2017-10-05 06:00 | 506 | 506
2017-10-05 06:30 | 530 | 530
2017-10-05 07:00 | 570 | 570
2017-10-05 07:30 | 608 | 608
2017-10-05 08:00 | 622 | 622
2017-10-05 08:30 | 634 | 634
2017-10-05 09:00 | 635 | 635
2017-10-05 09:30 | 633 | 633
2017-10-05 10:00 | 609 | 609
2017-10-05 10:30 | 586 | 586
2017-10-05 11:00 | 581 | 581
2017-10-05 11:30 | 581 | 580
2017-10-05 12:00 | 580 | 580
2017-10-05 12:30 | 586 | 586
2017-10-05 13:00 | 591 | 591
2017-10-05 13:30 | 608 | 608
2017-10-05 14:00 | 640 | 640
2017-10-05 14:30 | 652 | 652
2017-10-05 15:00 | 642 | 641
2017-10-05 15:30 | 626 | 626
2017-10-05 16:00 | 646 | 646
2017-10-05 16:30 | 653 | 653
2017-10-05 17:00 | 635 | 635
2017-10-05 17:30 | 595 | 595
2017-10-05 18:00 | 639 | 639
2017-10-05 18:30 | 604 | 604
2017-10-05 19:00 | 645 | 645
2017-10-05 19:30 | 737 | 737
2017-10-05 20:00 | 725 | 724
2017-10-05 20:30 | 690 | 689
2017-10-05 21:00 | 672 | 672
2017-10-05 21:30 | 647 | 647
2017-10-05 22:00 | 612 | 612
2017-10-05 22:30 | 583 | 583
2017-10-05 23:00 | 562 | 562
2017-10-05 23:30 | 537 | 537
2017-10-06 | 519 | 519
2017-10-06 00:30 | 508 | 507
2017-10-06 01:00 | 476 | 476
2017-10-06 01:30 | 452 | 451
2017-10-06 02:00 | 449 | 448
2017-10-06 02:30 | 444 | 442
2017-10-06 03:00 | 435 | 433
2017-10-06 03:30 | 435 | 434
2017-10-06 04:00 | 431 | 429
2017-10-06 04:30 | 436 | 434
2017-10-06 05:00 | 440 | 438
2017-10-06 05:30 | 462 | 460
2017-10-06 06:00 | 487 | 486
2017-10-06 06:30 | 510 | 509
2017-10-06 07:00 | 536 | 535
2017-10-06 07:30 | 567 | 567
2017-10-06 08:00 | 582 | 582
2017-10-06 08:30 | 585 | 585
2017-10-06 09:00 | 582 | 582
2017-10-06 09:30 | 583 | 583
2017-10-06 10:00 | 561 | 561
2017-10-06 10:30 | 546 | 546
2017-10-06 11:00 | 542 | 541
2017-10-06 11:30 | 544 | 544
2017-10-06 12:00 | 550 | 550
2017-10-06 12:30 | 550 | 550
2017-10-06 13:00 | 555 | 555
2017-10-06 13:30 | 563 | 563
2017-10-06 14:00 | 581 | 581
2017-10-06 14:30 | 593 | 593
2017-10-06 15:00 | 572 | 572
2017-10-06 15:30 | 537 | 537
2017-10-06 16:00 | 533 | 533
2017-10-06 16:30 | 485 | 484
2017-10-06 17:00 | 543 | 542
2017-10-06 17:30 | 524 | 524
2017-10-06 18:00 | 566 | 565
2017-10-06 18:30 | 566 | 566
2017-10-06 19:00 | 539 | 539
2017-10-06 19:30 | 563 | 563
2017-10-06 20:00 | 572 | 572
2017-10-06 20:30 | 577 | 577
2017-10-06 21:00 | 546 | 546
2017-10-06 21:30 | 523 | 523
2017-10-06 22:00 | 525 | 524
2017-10-06 22:30 | 549 | 548
2017-10-06 23:00 | 541 | 540
2017-10-06 23:30 | 515 | 514
2017-10-07 | 493 | 492
2017-10-07 00:30 | 483 | 482
2017-10-07 01:00 | 465 | 465
2017-10-07 01:30 | 447 | 446
2017-10-07 02:00 | 443 | 441
2017-10-07 02:30 | 443 | 442
2017-10-07 03:00 | 444 | 443
2017-10-07 03:30 | 428 | 426
2017-10-07 04:00 | 422 | 421
2017-10-07 04:30 | 418 | 416
2017-10-07 05:00 | 417 | 416
2017-10-07 05:30 | 424 | 422
2017-10-07 06:00 | 431 | 429
2017-10-07 06:30 | 435 | 433
2017-10-07 07:00 | 442 | 440
2017-10-07 07:30 | 466 | 464
2017-10-07 08:00 | 488 | 487
2017-10-07 08:30 | 506 | 505
2017-10-07 09:00 | 512 | 511
2017-10-07 09:30 | 520 | 519
2017-10-07 10:00 | 502 | 501
2017-10-07 10:30 | 483 | 482
2017-10-07 11:00 | 476 | 475
2017-10-07 11:30 | 471 | 470
2017-10-07 12:00 | 472 | 471
2017-10-07 12:30 | 464 | 463
2017-10-07 13:00 | 475 | 475
2017-10-07 13:30 | 484 | 483
2017-10-07 14:00 | 507 | 506
2017-10-07 14:30 | 517 | 516
2017-10-07 15:00 | 522 | 522
2017-10-07 15:30 | 542 | 542
2017-10-07 16:00 | 560 | 560
2017-10-07 16:30 | 578 | 578
2017-10-07 17:00 | 589 | 589
2017-10-07 17:30 | 603 | 603
2017-10-07 18:00 | 617 | 617
2017-10-07 18:30 | 630 | 630
2017-10-07 19:00 | 648 | 648
2017-10-07 19:30 | 639 | 639
2017-10-07 20:00 | 622 | 621
2017-10-07 20:30 | 593 | 593
2017-10-07 21:00 | 575 | 575
2017-10-07 21:30 | 566 | 566
2017-10-07 22:00 | 550 | 550
2017-10-07 22:30 | 528 | 528
2017-10-07 23:00 | 505 | 505
2017-10-07 23:30 | 493 | 493
2017-10-08 | 468 | 467
2017-10-08 00:30 | 458 | 457
2017-10-08 01:00 | 443 | 441
2017-10-08 01:30 | 431 | 429
2017-10-08 02:00 | 432 | 429
2017-10-08 02:30 | 425 | 422
2017-10-08 03:00 | 427 | 425
2017-10-08 03:30 | 416 | 414
2017-10-08 04:00 | 421 | 418
2017-10-08 04:30 | 417 | 414
2017-10-08 05:00 | 411 | 408
2017-10-08 05:30 | 411 | 408
2017-10-08 06:00 | 412 | 409
2017-10-08 06:30 | 416 | 413
2017-10-08 07:00 | 415 | 412
2017-10-08 07:30 | 431 | 428
2017-10-08 08:00 | 441 | 439
2017-10-08 08:30 | 454 | 452
2017-10-08 09:00 | 475 | 474
2017-10-08 09:30 | 474 | 472
2017-10-08 10:00 | 456 | 455
2017-10-08 10:30 | 451 | 450
2017-10-08 11:00 | 451 | 449
2017-10-08 11:30 | 450 | 448
2017-10-08 12:00 | 450 | 448
2017-10-08 12:30 | 455 | 453
2017-10-08 13:00 | 465 | 463
2017-10-08 13:30 | 483 | 481
2017-10-08 14:00 | 517 | 516
2017-10-08 14:30 | 529 | 528
2017-10-08 15:00 | 536 | 535
2017-10-08 15:30 | 542 | 542
2017-10-08 16:00 | 559 | 558
2017-10-08 16:30 | 575 | 575
2017-10-08 17:00 | 583 | 583
2017-10-08 17:30 | 535 | 535
2017-10-08 18:00 | 519 | 519
2017-10-08 18:30 | 544 | 543
2017-10-08 19:00 | 564 | 564
2017-10-08 19:30 | 603 | 603
2017-10-08 20:00 | 598 | 598
2017-10-08 20:30 | 584 | 584
2017-10-08 21:00 | 589 | 589
2017-10-08 21:30 | 568 | 568
2017-10-08 22:00 | 541 | 541
2017-10-08 22:30 | 520 | 519
2017-10-08 23:00 | 485 | 484
2017-10-08 23:30 | 457 | 456
2017-10-09 | 447 | 446
2017-10-09 00:30 | 452 | 450
2017-10-09 01:00 | 440 | 438
2017-10-09 01:30 | 428 | 426
2017-10-09 02:00 | 420 | 418
2017-10-09 02:30 | 420 | 417
2017-10-09 03:00 | 414 | 411
2017-10-09 03:30 | 414 | 411
2017-10-09 04:00 | 413 | 410
2017-10-09 04:30 | 416 | 413
2017-10-09 05:00 | 416 | 413
2017-10-09 05:30 | 434 | 431
2017-10-09 06:00 | 443 | 441
2017-10-09 06:30 | 473 | 471
2017-10-09 07:00 | 499 | 498
2017-10-09 07:30 | 521 | 520
2017-10-09 08:00 | 499 | 498
2017-10-09 08:30 | 511 | 510
2017-10-09 09:00 | 510 | 509
2017-10-09 09:30 | 497 | 497
2017-10-09 10:00 | 491 | 490
2017-10-09 10:30 | 487 | 486
2017-10-09 11:00 | 479 | 479
2017-10-09 11:30 | 479 | 478
2017-10-09 12:00 | 481 | 480
2017-10-09 12:30 | 481 | 480
2017-10-09 13:00 | 492 | 491
2017-10-09 13:30 | 490 | 489
2017-10-09 14:00 | 507 | 506
2017-10-09 14:30 | 540 | 540
2017-10-09 15:00 | 590 | 589
2017-10-09 15:30 | 573 | 573
2017-10-09 16:00 | 593 | 593
2017-10-09 16:30 | 601 | 601
2017-10-09 17:00 | 558 | 557
2017-10-09 17:30 | 543 | 543
2017-10-09 18:00 | 576 | 576
2017-10-09 18:30 | 580 | 580
2017-10-09 19:00 | 572 | 572
2017-10-09 19:30 | 592 | 592
2017-10-09 20:00 | 587 | 587
2017-10-09 20:30 | 570 | 570
2017-10-09 21:00 | 603 | 603
2017-10-09 21:30 | 596 | 596
2017-10-09 22:00 | 566 | 566
2017-10-09 22:30 | 537 | 537
2017-10-09 23:00 | 501 | 501
2017-10-09 23:30 | 484 | 484
2017-10-10 | 472 | 471
2017-10-10 00:30 | 460 | 459
2017-10-10 01:00 | 448 | 446
2017-10-10 01:30 | 440 | 438
2017-10-10 02:00 | 435 | 433
2017-10-10 02:30 | 426 | 424
2017-10-10 03:00 | 421 | 419
2017-10-10 03:30 | 421 | 418
2017-10-10 04:00 | 415 | 412
2017-10-10 04:30 | 413 | 410
2017-10-10 05:00 | 418 | 415
2017-10-10 05:30 | 425 | 422
2017-10-10 06:00 | 439 | 436
2017-10-10 06:30 | 478 | 476
2017-10-10 07:00 | 510 | 508
2017-10-10 07:30 | 510 | 509
2017-10-10 08:00 | 476 | 475
2017-10-10 08:30 | 476 | 475
2017-10-10 09:00 | 464 | 463
2017-10-10 09:30 | 464 | 463
2017-10-10 10:00 | 462 | 461
2017-10-10 10:30 | 463 | 462
2017-10-10 11:00 | 454 | 453
2017-10-10 11:30 | 446 | 445
2017-10-10 12:00 | 461 | 460
2017-10-10 12:30 | 468 | 467
2017-10-10 13:00 | 445 | 444
2017-10-10 13:30 | 477 | 476
2017-10-10 14:00 | 492 | 491
2017-10-10 14:30 | 516 | 515
2017-10-10 15:00 | 567 | 567
2017-10-10 15:30 | 558 | 558
2017-10-10 16:00 | 505 | 505
2017-10-10 16:30 | 515 | 515
2017-10-10 17:00 | 456 | 456
2017-10-10 17:30 | 402 | 401
2017-10-10 18:00 | 467 | 465
2017-10-10 18:30 | 501 | 501
2017-10-10 19:00 | 481 | 481
2017-10-10 19:30 | 499 | 499
2017-10-10 20:00 | 497 | 497
2017-10-10 20:30 | 483 | 483
2017-10-10 21:00 | 522 | 521
2017-10-10 21:30 | 511 | 510
2017-10-10 22:00 | 487 | 486
2017-10-10 22:30 | 442 | 442
2017-10-10 23:00 | 492 | 491
2017-10-10 23:30 | 476 | 476
2017-10-11 | 457 | 456
2017-10-11 00:30 | 450 | 449
2017-10-11 01:00 | 436 | 434
2017-10-11 01:30 | 427 | 425
2017-10-11 02:00 | 426 | 424
2017-10-11 02:30 | 422 | 420
2017-10-11 03:00 | 419 | 417
2017-10-11 03:30 | 416 | 413
2017-10-11 04:00 | 415 | 412
2017-10-11 04:30 | 413 | 410
2017-10-11 05:00 | 422 | 419
2017-10-11 05:30 | 435 | 433
2017-10-11 06:00 | 448 | 446
2017-10-11 06:30 | 476 | 475
2017-10-11 07:00 | 463 | 462
2017-10-11 07:30 | 437 | 436
2017-10-11 08:00 | 421 | 419
2017-10-11 08:30 | 461 | 460
2017-10-11 09:00 | 470 | 469
2017-10-11 09:30 | 467 | 466
2017-10-11 10:00 | 461 | 460
2017-10-11 10:30 | 463 | 462
2017-10-11 11:00 | 421 | 420
2017-10-11 11:30 | 421 | 419
2017-10-11 12:00 | 468 | 466
2017-10-11 12:30 | 476 | 475
2017-10-11 13:00 | 484 | 483
2017-10-11 13:30 | 491 | 490
2017-10-11 14:00 | 496 | 496
2017-10-11 14:30 | 505 | 505
2017-10-11 15:00 | 570 | 569
2017-10-11 15:30 | 580 | 579
2017-10-11 16:00 | 581 | 580
2017-10-11 16:30 | 610 | 610
2017-10-11 17:00 | 572 | 571
2017-10-11 17:30 | 553 | 553
2017-10-11 18:00 | 562 | 562
2017-10-11 18:30 | 587 | 587
2017-10-11 19:00 | 619 | 618
2017-10-11 19:30 | 651 | 651
2017-10-11 20:00 | 635 | 635
2017-10-11 20:30 | 608 | 608
2017-10-11 21:00 | 613 | 613
2017-10-11 21:30 | 604 | 603
2017-10-11 22:00 | 577 | 577
2017-10-11 22:30 | 542 | 541
2017-10-11 23:00 | 520 | 519
2017-10-11 23:30 | 501 | 499
2017-10-12 | 486 | 484
2017-10-12 00:30 | 477 | 474
2017-10-12 01:00 | 463 | 460
2017-10-12 01:30 | 455 | 452
2017-10-12 02:00 | 450 | 446
2017-10-12 02:30 | 445 | 441
2017-10-12 03:00 | 435 | 431
2017-10-12 03:30 | 430 | 425
2017-10-12 04:00 | 440 | 435
2017-10-12 04:30 | 442 | 437
2017-10-12 05:00 | 441 | 437
2017-10-12 05:30 | 457 | 453
2017-10-12 06:00 | 471 | 468
2017-10-12 06:30 | 494 | 491
2017-10-12 07:00 | 458 | 455
2017-10-12 07:30 | 448 | 445
2017-10-12 08:00 | 414 | 411
2017-10-12 08:30 | 414 | 410
2017-10-12 09:00 | 432 | 428
2017-10-12 09:30 | 438 | 435
2017-10-12 10:00 | 444 | 441
2017-10-12 10:30 | 421 | 417
2017-10-12 11:00 | 421 | 416
2017-10-12 11:30 | 439 | 436
2017-10-12 12:00 | 442 | 439
2017-10-12 12:30 | 468 | 466
2017-10-12 13:00 | 467 | 466
2017-10-12 13:30 | 470 | 469
2017-10-12 14:00 | 455 | 454
2017-10-12 14:30 | 476 | 474
2017-10-12 15:00 | 537 | 536
2017-10-12 15:30 | 540 | 539
2017-10-12 16:00 | 542 | 541
2017-10-12 16:30 | 542 | 541
2017-10-12 17:00 | 564 | 564
2017-10-12 17:30 | 557 | 557
2017-10-12 18:00 | 590 | 590
2017-10-12 18:30 | 631 | 631
2017-10-12 19:00 | 633 | 633
2017-10-12 19:30 | 643 | 642
2017-10-12 20:00 | 651 | 651
2017-10-12 20:30 | 650 | 650
2017-10-12 21:00 | 628 | 628
2017-10-12 21:30 | 599 | 598
2017-10-12 22:00 | 568 | 568
2017-10-12 22:30 | 526 | 525
2017-10-12 23:00 | 511 | 510
2017-10-12 23:30 | 487 | 485
2017-10-13 | 470 | 468
2017-10-13 00:30 | 461 | 458
2017-10-13 01:00 | 450 | 447
2017-10-13 01:30 | 437 | 434
2017-10-13 02:00 | 433 | 430
2017-10-13 02:30 | 433 | 430
2017-10-13 03:00 | 428 | 425
2017-10-13 03:30 | 430 | 427
2017-10-13 04:00 | 431 | 427
2017-10-13 04:30 | 437 | 434
2017-10-13 05:00 | 439 | 436
2017-10-13 05:30 | 451 | 448
2017-10-13 06:00 | 465 | 463
2017-10-13 06:30 | 487 | 485
2017-10-13 07:00 | 504 | 503
2017-10-13 07:30 | 486 | 485
2017-10-13 08:00 | 501 | 499
2017-10-13 08:30 | 504 | 503
2017-10-13 09:00 | 501 | 499
2017-10-13 09:30 | 502 | 501
2017-10-13 10:00 | 494 | 493
2017-10-13 10:30 | 495 | 494
2017-10-13 11:00 | 489 | 488
2017-10-13 11:30 | 493 | 492
2017-10-13 12:00 | 492 | 491
2017-10-13 12:30 | 489 | 488
2017-10-13 13:00 | 490 | 489
2017-10-13 13:30 | 494 | 493
2017-10-13 14:00 | 508 | 507
2017-10-13 14:30 | 555 | 554
2017-10-13 15:00 | 577 | 577
2017-10-13 15:30 | 571 | 570
2017-10-13 16:00 | 550 | 550
2017-10-13 16:30 | 565 | 565
2017-10-13 17:00 | 577 | 576
2017-10-13 17:30 | 581 | 581
2017-10-13 18:00 | 604 | 604
2017-10-13 18:30 | 618 | 618
2017-10-13 19:00 | 590 | 590
2017-10-13 19:30 | 599 | 599
2017-10-13 20:00 | 600 | 600
2017-10-13 20:30 | 577 | 577
2017-10-13 21:00 | 594 | 594
2017-10-13 21:30 | 583 | 583
2017-10-13 22:00 | 559 | 559
2017-10-13 22:30 | 535 | 535
2017-10-13 23:00 | 518 | 517
2017-10-13 23:30 | 492 | 491
2017-10-14 | 469 | 467
2017-10-14 00:30 | 461 | 457
2017-10-14 01:00 | 454 | 452
2017-10-14 01:30 | 437 | 435
2017-10-14 02:00 | 439 | 436
2017-10-14 02:30 | 438 | 435
2017-10-14 03:00 | 422 | 419
2017-10-14 03:30 | 421 | 417
2017-10-14 04:00 | 411 | 406
2017-10-14 04:30 | 416 | 411
2017-10-14 05:00 | 419 | 414
2017-10-14 05:30 | 418 | 414
2017-10-14 06:00 | 412 | 408
2017-10-14 06:30 | 428 | 424
2017-10-14 07:00 | 436 | 433
2017-10-14 07:30 | 457 | 454
2017-10-14 08:00 | 482 | 480
2017-10-14 08:30 | 500 | 499
2017-10-14 09:00 | 519 | 518
2017-10-14 09:30 | 525 | 524
2017-10-14 10:00 | 508 | 508
2017-10-14 10:30 | 483 | 482
2017-10-14 11:00 | 464 | 463
2017-10-14 11:30 | 468 | 466
2017-10-14 12:00 | 450 | 449
2017-10-14 12:30 | 452 | 451
2017-10-14 13:00 | 457 | 456
2017-10-14 13:30 | 473 | 472
2017-10-14 14:00 | 495 | 494
2017-10-14 14:30 | 508 | 508
2017-10-14 15:00 | 518 | 518
2017-10-14 15:30 | 527 | 526
2017-10-14 16:00 | 540 | 540
2017-10-14 16:30 | 561 | 561
2017-10-14 17:00 | 579 | 579
2017-10-14 17:30 | 592 | 592
2017-10-14 18:00 | 606 | 606
2017-10-14 18:30 | 621 | 621
2017-10-14 19:00 | 641 | 641
2017-10-14 19:30 | 637 | 637
2017-10-14 20:00 | 610 | 610
2017-10-14 20:30 | 588 | 588
2017-10-14 21:00 | 583 | 583
2017-10-14 21:30 | 573 | 572
2017-10-14 22:00 | 551 | 551
2017-10-14 22:30 | 533 | 533
2017-10-14 23:00 | 516 | 515
2017-10-14 23:30 | 490 | 489
2017-10-15 | 472 | 472
2017-10-15 00:30 | 459 | 457
2017-10-15 01:00 | 445 | 444
2017-10-15 01:30 | 446 | 444
2017-10-15 02:00 | 441 | 440
2017-10-15 02:30 | 430 | 429
2017-10-15 03:00 | 426 | 424
2017-10-15 03:30 | 422 | 420
2017-10-15 04:00 | 419 | 417
2017-10-15 04:30 | 418 | 416
2017-10-15 05:00 | 416 | 414
2017-10-15 05:30 | 422 | 420
2017-10-15 06:00 | 420 | 418
2017-10-15 06:30 | 421 | 419
2017-10-15 07:00 | 429 | 427
2017-10-15 07:30 | 446 | 444
2017-10-15 08:00 | 459 | 458
2017-10-15 08:30 | 471 | 470
2017-10-15 09:00 | 492 | 491
2017-10-15 09:30 | 506 | 505
2017-10-15 10:00 | 483 | 482
2017-10-15 10:30 | 471 | 471
2017-10-15 11:00 | 470 | 469
2017-10-15 11:30 | 465 | 464
2017-10-15 12:00 | 454 | 453
2017-10-15 12:30 | 452 | 451
2017-10-15 13:00 | 454 | 453
2017-10-15 13:30 | 473 | 472
2017-10-15 14:00 | 516 | 515
2017-10-15 14:30 | 544 | 544
2017-10-15 15:00 | 543 | 543
2017-10-15 15:30 | 551 | 551
2017-10-15 16:00 | 564 | 564
2017-10-15 16:30 | 576 | 576
2017-10-15 17:00 | 580 | 580
2017-10-15 17:30 | 594 | 594
2017-10-15 18:00 | 613 | 613
2017-10-15 18:30 | 636 | 636
2017-10-15 19:00 | 645 | 645
2017-10-15 19:30 | 632 | 632
2017-10-15 20:00 | 610 | 610
2017-10-15 20:30 | 593 | 593
2017-10-15 21:00 | 582 | 582
2017-10-15 21:30 | 561 | 561
2017-10-15 22:00 | 548 | 548
2017-10-15 22:30 | 517 | 517
2017-10-15 23:00 | 498 | 498
2017-10-15 23:30 | 468 | 467
2017-10-16 | 445 | 445
2017-10-16 00:30 | 436 | 435
2017-10-16 01:00 | 426 | 425
2017-10-16 01:30 | 423 | 421
2017-10-16 02:00 | 415 | 413
2017-10-16 02:30 | 409 | 407
2017-10-16 03:00 | 415 | 413
2017-10-16 03:30 | 416 | 414
2017-10-16 04:00 | 408 | 406
2017-10-16 04:30 | 413 | 411
2017-10-16 05:00 | 421 | 419
2017-10-16 05:30 | 427 | 425
2017-10-16 06:00 | 439 | 437
2017-10-16 06:30 | 468 | 466
2017-10-16 07:00 | 487 | 486
2017-10-16 07:30 | 523 | 522
2017-10-16 08:00 | 557 | 557
2017-10-16 08:30 | 575 | 575
2017-10-16 09:00 | 581 | 581
2017-10-16 09:30 | 583 | 583
2017-10-16 10:00 | 562 | 562
2017-10-16 10:30 | 545 | 545
2017-10-16 11:00 | 554 | 554
2017-10-16 11:30 | 557 | 557
2017-10-16 12:00 | 568 | 567
2017-10-16 12:30 | 559 | 559
2017-10-16 13:00 | 571 | 570
2017-10-16 13:30 | 561 | 561
2017-10-16 14:00 | 522 | 522
2017-10-16 14:30 | 483 | 483
2017-10-16 15:00 | 483 | 483
2017-10-16 15:30 | 468 | 467
2017-10-16 16:00 | 466 | 466
2017-10-16 16:30 | 464 | 464
2017-10-16 17:00 | 473 | 472
2017-10-16 17:30 | 479 | 478
2017-10-16 18:00 | 547 | 546
2017-10-16 18:30 | 568 | 568
2017-10-16 19:00 | 577 | 577
2017-10-16 19:30 | 631 | 631
2017-10-16 20:00 | 624 | 624
2017-10-16 20:30 | 594 | 594
2017-10-16 21:00 | 570 | 570
2017-10-16 21:30 | 547 | 547
2017-10-16 22:00 | 527 | 527
2017-10-16 22:30 | 490 | 490
2017-10-16 23:00 | 469 | 468
2017-10-16 23:30 | 453 | 452
2017-10-17 | 436 | 435
2017-10-17 00:30 | 438 | 436
2017-10-17 01:00 | 425 | 423
2017-10-17 01:30 | 419 | 417
2017-10-17 02:00 | 406 | 403
2017-10-17 02:30 | 408 | 405
2017-10-17 03:00 | 398 | 395
2017-10-17 03:30 | 396 | 393
2017-10-17 04:00 | 397 | 394
2017-10-17 04:30 | 411 | 408
2017-10-17 05:00 | 417 | 415
2017-10-17 05:30 | 430 | 428
2017-10-17 06:00 | 450 | 448
2017-10-17 06:30 | 481 | 479
2017-10-17 07:00 | 509 | 508
2017-10-17 07:30 | 548 | 547
2017-10-17 08:00 | 570 | 569
2017-10-17 08:30 | 541 | 540
2017-10-17 09:00 | 478 | 477
2017-10-17 09:30 | 512 | 511
2017-10-17 10:00 | 491 | 490
2017-10-17 10:30 | 470 | 469
2017-10-17 11:00 | 489 | 488
2017-10-17 11:30 | 483 | 482
2017-10-17 12:00 | 463 | 463
2017-10-17 12:30 | 465 | 463
2017-10-17 13:00 | 468 | 467
2017-10-17 13:30 | 480 | 479
2017-10-17 14:00 | 514 | 513
2017-10-17 14:30 | 511 | 510
2017-10-17 15:00 | 477 | 476
2017-10-17 15:30 | 451 | 450
2017-10-17 16:00 | 458 | 456
2017-10-17 16:30 | 458 | 456
2017-10-17 17:00 | 467 | 466
2017-10-17 17:30 | 480 | 479
2017-10-17 18:00 | 518 | 517
2017-10-17 18:30 | 545 | 544
2017-10-17 19:00 | 555 | 555
2017-10-17 19:30 | 539 | 539
2017-10-17 20:00 | 532 | 531
2017-10-17 20:30 | 569 | 568
2017-10-17 21:00 | 583 | 582
2017-10-17 21:30 | 555 | 555
2017-10-17 22:00 | 523 | 523
2017-10-17 22:30 | 492 | 491
2017-10-17 23:00 | 468 | 467
2017-10-17 23:30 | 450 | 449
2017-10-18 | 439 | 437
2017-10-18 00:30 | 428 | 426
2017-10-18 01:00 | 426 | 424
2017-10-18 01:30 | 421 | 419
2017-10-18 02:00 | 413 | 410
2017-10-18 02:30 | 411 | 408
2017-10-18 03:00 | 403 | 400
2017-10-18 03:30 | 410 | 407
2017-10-18 04:00 | 411 | 408
2017-10-18 04:30 | 411 | 409
2017-10-18 05:00 | 417 | 415
2017-10-18 05:30 | 433 | 430
2017-10-18 06:00 | 454 | 452
2017-10-18 06:30 | 489 | 488
2017-10-18 07:00 | 507 | 506
2017-10-18 07:30 | 538 | 538
2017-10-18 08:00 | 561 | 560
2017-10-18 08:30 | 579 | 579
2017-10-18 09:00 | 525 | 525
2017-10-18 09:30 | 498 | 498
2017-10-18 10:00 | 483 | 482
2017-10-18 10:30 | 447 | 445
2017-10-18 11:00 | 419 | 417
2017-10-18 11:30 | 501 | 498
2017-10-18 12:00 | 517 | 516
2017-10-18 12:30 | 530 | 529
2017-10-18 13:00 | 541 | 541
2017-10-18 13:30 | 557 | 557
2017-10-18 14:00 | 583 | 583
2017-10-18 14:30 | 534 | 534
2017-10-18 15:00 | 535 | 534
2017-10-18 15:30 | 494 | 494
2017-10-18 16:00 | 480 | 479
2017-10-18 16:30 | 484 | 483
2017-10-18 17:00 | 502 | 501
2017-10-18 17:30 | 507 | 506
2017-10-18 18:00 | 527 | 526
2017-10-18 18:30 | 556 | 555
2017-10-18 19:00 | 575 | 575
2017-10-18 19:30 | 602 | 602
2017-10-18 20:00 | 644 | 644
2017-10-18 20:30 | 665 | 665
2017-10-18 21:00 | 647 | 646
2017-10-18 21:30 | 622 | 622
2017-10-18 22:00 | 596 | 596
2017-10-18 22:30 | 569 | 569
2017-10-18 23:00 | 554 | 553
2017-10-18 23:30 | 534 | 533
2017-10-19 | 513 | 512
2017-10-19 00:30 | 496 | 495
2017-10-19 01:00 | 487 | 485
2017-10-19 01:30 | 482 | 480
2017-10-19 02:00 | 487 | 486
2017-10-19 02:30 | 490 | 489
2017-10-19 03:00 | 485 | 484
2017-10-19 03:30 | 444 | 443
2017-10-19 04:00 | 418 | 416
2017-10-19 04:30 | 429 | 427
2017-10-19 05:00 | 436 | 434
2017-10-19 05:30 | 447 | 445
2017-10-19 06:00 | 462 | 461
2017-10-19 06:30 | 500 | 499
2017-10-19 07:00 | 516 | 515
2017-10-19 07:30 | 547 | 546
2017-10-19 08:00 | 575 | 574
2017-10-19 08:30 | 545 | 545
2017-10-19 09:00 | 482 | 481
2017-10-19 09:30 | 484 | 483
2017-10-19 10:00 | 457 | 456
2017-10-19 10:30 | 415 | 413
2017-10-19 11:00 | 415 | 412
2017-10-19 11:30 | 413 | 410
2017-10-19 12:00 | 410 | 407
2017-10-19 12:30 | 360 | 357
2017-10-19 13:00 | 322 | 317
2017-10-19 13:30 | 318 | 312
2017-10-19 14:00 | 331 | 325
2017-10-19 14:30 | 331 | 325
2017-10-19 15:00 | 327 | 321
2017-10-19 15:30 | 318 | 313
2017-10-19 16:00 | 336 | 330
2017-10-19 16:30 | 339 | 335
2017-10-19 17:00 | 342 | 338
2017-10-19 17:30 | 341 | 337
2017-10-19 18:00 | 356 | 351
2017-10-19 18:30 | 431 | 428
2017-10-19 19:00 | 396 | 394
2017-10-19 19:30 | 433 | 431
2017-10-19 20:00 | 567 | 565
2017-10-19 20:30 | 619 | 619
2017-10-19 21:00 | 601 | 601
2017-10-19 21:30 | 575 | 575
2017-10-19 22:00 | 555 | 555
2017-10-19 22:30 | 522 | 522
2017-10-19 23:00 | 503 | 502
2017-10-19 23:30 | 488 | 488
2017-10-20 | 473 | 472
2017-10-20 00:30 | 453 | 452
2017-10-20 01:00 | 438 | 437
2017-10-20 01:30 | 423 | 421
2017-10-20 02:00 | 419 | 418
2017-10-20 02:30 | 420 | 418
2017-10-20 03:00 | 419 | 417
2017-10-20 03:30 | 420 | 418
2017-10-20 04:00 | 416 | 414
2017-10-20 04:30 | 427 | 425
2017-10-20 05:00 | 429 | 428
2017-10-20 05:30 | 448 | 446
2017-10-20 06:00 | 477 | 475
2017-10-20 06:30 | 514 | 513
2017-10-20 07:00 | 540 | 540
2017-10-20 07:30 | 576 | 576
2017-10-20 08:00 | 603 | 603
2017-10-20 08:30 | 605 | 605
2017-10-20 09:00 | 543 | 543
2017-10-20 09:30 | 508 | 508
2017-10-20 10:00 | 489 | 488
2017-10-20 10:30 | 456 | 455
2017-10-20 11:00 | 433 | 432
2017-10-20 11:30 | 441 | 439
2017-10-20 12:00 | 438 | 436
2017-10-20 12:30 | 453 | 451
2017-10-20 13:00 | 509 | 507
2017-10-20 13:30 | 542 | 541
2017-10-20 14:00 | 510 | 509
2017-10-20 14:30 | 412 | 411
2017-10-20 15:00 | 371 | 368
2017-10-20 15:30 | 406 | 403
2017-10-20 16:00 | 508 | 506
2017-10-20 16:30 | 596 | 596
2017-10-20 17:00 | 600 | 600
2017-10-20 17:30 | 593 | 593
2017-10-20 18:00 | 602 | 602
2017-10-20 18:30 | 611 | 611
2017-10-20 19:00 | 631 | 631
2017-10-20 19:30 | 627 | 627
2017-10-20 20:00 | 603 | 603
2017-10-20 20:30 | 578 | 578
2017-10-20 21:00 | 566 | 566
2017-10-20 21:30 | 544 | 544
2017-10-20 22:00 | 519 | 519
2017-10-20 22:30 | 496 | 496
2017-10-20 23:00 | 479 | 479
2017-10-20 23:30 | 462 | 461
2017-10-21 | 447 | 446
2017-10-21 00:30 | 434 | 433
2017-10-21 01:00 | 425 | 422
2017-10-21 01:30 | 417 | 414
2017-10-21 02:00 | 410 | 408
2017-10-21 02:30 | 409 | 406
2017-10-21 03:00 | 401 | 398
2017-10-21 03:30 | 400 | 396
2017-10-21 04:00 | 397 | 394
2017-10-21 04:30 | 399 | 395
2017-10-21 05:00 | 397 | 394
2017-10-21 05:30 | 400 | 397
2017-10-21 06:00 | 408 | 404
2017-10-21 06:30 | 421 | 418
2017-10-21 07:00 | 430 | 428
2017-10-21 07:30 | 455 | 452
2017-10-21 08:00 | 472 | 470
2017-10-21 08:30 | 481 | 480
2017-10-21 09:00 | 501 | 499
2017-10-21 09:30 | 504 | 503
2017-10-21 10:00 | 485 | 485
2017-10-21 10:30 | 480 | 479
2017-10-21 11:00 | 477 | 476
2017-10-21 11:30 | 471 | 470
2017-10-21 12:00 | 467 | 465
2017-10-21 12:30 | 464 | 462
2017-10-21 13:00 | 462 | 461
2017-10-21 13:30 | 486 | 485
2017-10-21 14:00 | 517 | 516
2017-10-21 14:30 | 517 | 516
2017-10-21 15:00 | 516 | 515
2017-10-21 15:30 | 537 | 536
2017-10-21 16:00 | 566 | 565
2017-10-21 16:30 | 578 | 578
2017-10-21 17:00 | 589 | 589
2017-10-21 17:30 | 601 | 600
2017-10-21 18:00 | 612 | 612
2017-10-21 18:30 | 622 | 622
2017-10-21 19:00 | 628 | 628
2017-10-21 19:30 | 613 | 613
2017-10-21 20:00 | 596 | 596
2017-10-21 20:30 | 578 | 578
2017-10-21 21:00 | 561 | 561
2017-10-21 21:30 | 566 | 566
2017-10-21 22:00 | 563 | 563
2017-10-21 22:30 | 542 | 542
2017-10-21 23:00 | 527 | 527
2017-10-21 23:30 | 512 | 511
2017-10-22 | 497 | 497
2017-10-22 00:30 | 486 | 485
2017-10-22 01:00 | 474 | 473
2017-10-22 01:30 | 468 | 467
2017-10-22 02:00 | 461 | 459
2017-10-22 02:30 | 456 | 455
2017-10-22 03:00 | 454 | 452
2017-10-22 03:30 | 452 | 450
2017-10-22 04:00 | 448 | 446
2017-10-22 04:30 | 445 | 442
2017-10-22 05:00 | 448 | 446
2017-10-22 05:30 | 451 | 449
2017-10-22 06:00 | 453 | 451
2017-10-22 06:30 | 463 | 461
2017-10-22 07:00 | 472 | 470
2017-10-22 07:30 | 486 | 485
2017-10-22 08:00 | 503 | 502
2017-10-22 08:30 | 521 | 520
2017-10-22 09:00 | 522 | 521
2017-10-22 09:30 | 532 | 531
2017-10-22 10:00 | 512 | 511
2017-10-22 10:30 | 508 | 507
2017-10-22 11:00 | 517 | 516
2017-10-22 11:30 | 523 | 522
2017-10-22 12:00 | 522 | 521
2017-10-22 12:30 | 522 | 522
2017-10-22 13:00 | 520 | 520
2017-10-22 13:30 | 534 | 534
2017-10-22 14:00 | 553 | 552
2017-10-22 14:30 | 542 | 542
2017-10-22 15:00 | 553 | 552
2017-10-22 15:30 | 558 | 558
2017-10-22 16:00 | 570 | 569
2017-10-22 16:30 | 582 | 582
2017-10-22 17:00 | 602 | 602
2017-10-22 17:30 | 612 | 612
2017-10-22 18:00 | 629 | 629
2017-10-22 18:30 | 632 | 631
2017-10-22 19:00 | 652 | 652
2017-10-22 19:30 | 643 | 643
2017-10-22 20:00 | 622 | 621
2017-10-22 20:30 | 598 | 598
2017-10-22 21:00 | 591 | 590
2017-10-22 21:30 | 554 | 554
2017-10-22 22:00 | 506 | 506
2017-10-22 22:30 | 481 | 481
2017-10-22 23:00 | 466 | 465
2017-10-22 23:30 | 447 | 446
2017-10-23 | 429 | 428
2017-10-23 00:30 | 475 | 473
2017-10-23 01:00 | 479 | 478
2017-10-23 01:30 | 471 | 470
2017-10-23 02:00 | 464 | 463
2017-10-23 02:30 | 460 | 459
2017-10-23 03:00 | 459 | 458
2017-10-23 03:30 | 457 | 455
2017-10-23 04:00 | 462 | 460
2017-10-23 04:30 | 467 | 465
2017-10-23 05:00 | 470 | 469
2017-10-23 05:30 | 487 | 486
2017-10-23 06:00 | 502 | 501
2017-10-23 06:30 | 534 | 534
2017-10-23 07:00 | 566 | 566
2017-10-23 07:30 | 599 | 599
2017-10-23 08:00 | 608 | 608
2017-10-23 08:30 | 608 | 608
2017-10-23 09:00 | 588 | 588
2017-10-23 09:30 | 571 | 570
2017-10-23 10:00 | 552 | 552
2017-10-23 10:30 | 542 | 542
2017-10-23 11:00 | 539 | 539
2017-10-23 11:30 | 543 | 542
2017-10-23 12:00 | 539 | 538
2017-10-23 12:30 | 543 | 543
2017-10-23 13:00 | 555 | 554
2017-10-23 13:30 | 570 | 570
2017-10-23 14:00 | 587 | 586
2017-10-23 14:30 | 591 | 591
2017-10-23 15:00 | 603 | 603
2017-10-23 15:30 | 609 | 609
2017-10-23 16:00 | 621 | 621
2017-10-23 16:30 | 638 | 638
2017-10-23 17:00 | 655 | 655
2017-10-23 17:30 | 641 | 641
2017-10-23 18:00 | 632 | 632
2017-10-23 18:30 | 647 | 647
2017-10-23 19:00 | 674 | 674
2017-10-23 19:30 | 675 | 675
2017-10-23 20:00 | 653 | 653
2017-10-23 20:30 | 620 | 620
2017-10-23 21:00 | 653 | 653
2017-10-23 21:30 | 636 | 636
2017-10-23 22:00 | 612 | 612
2017-10-23 22:30 | 579 | 579
2017-10-23 23:00 | 554 | 554
2017-10-23 23:30 | 534 | 534
2017-10-24 | 519 | 518
2017-10-24 00:30 | 507 | 506
2017-10-24 01:00 | 493 | 492
2017-10-24 01:30 | 486 | 485
2017-10-24 02:00 | 476 | 475
2017-10-24 02:30 | 473 | 472
2017-10-24 03:00 | 471 | 469
2017-10-24 03:30 | 471 | 470
2017-10-24 04:00 | 469 | 467
2017-10-24 04:30 | 478 | 477
2017-10-24 05:00 | 484 | 483
2017-10-24 05:30 | 501 | 500
2017-10-24 06:00 | 534 | 533
2017-10-24 06:30 | 573 | 572
2017-10-24 07:00 | 598 | 597
2017-10-24 07:30 | 630 | 630
2017-10-24 08:00 | 637 | 637
2017-10-24 08:30 | 642 | 642
2017-10-24 09:00 | 633 | 633
2017-10-24 09:30 | 635 | 635
2017-10-24 10:00 | 594 | 594
2017-10-24 10:30 | 571 | 571
2017-10-24 11:00 | 564 | 564
2017-10-24 11:30 | 562 | 562
2017-10-24 12:00 | 567 | 567
2017-10-24 12:30 | 569 | 569
2017-10-24 13:00 | 576 | 575
2017-10-24 13:30 | 598 | 598
2017-10-24 14:00 | 617 | 617
2017-10-24 14:30 | 620 | 620
2017-10-24 15:00 | 614 | 614
2017-10-24 15:30 | 595 | 595
2017-10-24 16:00 | 605 | 605
2017-10-24 16:30 | 616 | 616
2017-10-24 17:00 | 631 | 631
2017-10-24 17:30 | 637 | 637
2017-10-24 18:00 | 638 | 638
2017-10-24 18:30 | 647 | 647
2017-10-24 19:00 | 668 | 668
2017-10-24 19:30 | 659 | 659
2017-10-24 20:00 | 629 | 629
2017-10-24 20:30 | 604 | 604
2017-10-24 21:00 | 574 | 574
2017-10-24 21:30 | 558 | 558
2017-10-24 22:00 | 527 | 527
2017-10-24 22:30 | 522 | 522
2017-10-24 23:00 | 535 | 535
2017-10-24 23:30 | 525 | 524
2017-10-25 | 504 | 504
2017-10-25 00:30 | 492 | 492
2017-10-25 01:00 | 475 | 474
2017-10-25 01:30 | 467 | 466
2017-10-25 02:00 | 464 | 463
2017-10-25 02:30 | 465 | 463
2017-10-25 03:00 | 456 | 454
2017-10-25 03:30 | 453 | 452
2017-10-25 04:00 | 452 | 450
2017-10-25 04:30 | 451 | 449
2017-10-25 05:00 | 453 | 451
2017-10-25 05:30 | 465 | 463
2017-10-25 06:00 | 477 | 475
2017-10-25 06:30 | 506 | 505
2017-10-25 07:00 | 529 | 528
2017-10-25 07:30 | 559 | 559
2017-10-25 08:00 | 573 | 572
2017-10-25 08:30 | 575 | 575
2017-10-25 09:00 | 570 | 570
2017-10-25 09:30 | 565 | 565
2017-10-25 10:00 | 538 | 538
2017-10-25 10:30 | 525 | 525
2017-10-25 11:00 | 528 | 528
2017-10-25 11:30 | 530 | 530
2017-10-25 12:00 | 539 | 539
2017-10-25 12:30 | 541 | 540
2017-10-25 13:00 | 543 | 542
2017-10-25 13:30 | 560 | 559
2017-10-25 14:00 | 584 | 583
2017-10-25 14:30 | 596 | 596
2017-10-25 15:00 | 605 | 605
2017-10-25 15:30 | 614 | 614
2017-10-25 16:00 | 629 | 629
2017-10-25 16:30 | 647 | 647
2017-10-25 17:00 | 654 | 653
2017-10-25 17:30 | 637 | 636
2017-10-25 18:00 | 644 | 643
2017-10-25 18:30 | 656 | 656
2017-10-25 19:00 | 680 | 680
2017-10-25 19:30 | 678 | 678
2017-10-25 20:00 | 661 | 661
2017-10-25 20:30 | 632 | 632
2017-10-25 21:00 | 635 | 635
2017-10-25 21:30 | 609 | 609
2017-10-25 22:00 | 590 | 590
2017-10-25 22:30 | 566 | 566
2017-10-25 23:00 | 541 | 541
2017-10-25 23:30 | 518 | 518
2017-10-26 | 499 | 498
2017-10-26 00:30 | 484 | 483
2017-10-26 01:00 | 463 | 461
2017-10-26 01:30 | 454 | 452
2017-10-26 02:00 | 447 | 445
2017-10-26 02:30 | 442 | 440
2017-10-26 03:00 | 439 | 436
2017-10-26 03:30 | 439 | 437
2017-10-26 04:00 | 439 | 436
2017-10-26 04:30 | 443 | 441
2017-10-26 05:00 | 452 | 450
2017-10-26 05:30 | 463 | 461
2017-10-26 06:00 | 474 | 472
2017-10-26 06:30 | 508 | 507
2017-10-26 07:00 | 530 | 529
2017-10-26 07:30 | 554 | 554
2017-10-26 08:00 | 563 | 563
2017-10-26 08:30 | 559 | 558
2017-10-26 09:00 | 550 | 550
2017-10-26 09:30 | 554 | 554
2017-10-26 10:00 | 525 | 525
2017-10-26 10:30 | 514 | 514
2017-10-26 11:00 | 522 | 522
2017-10-26 11:30 | 524 | 524
2017-10-26 12:00 | 539 | 538
2017-10-26 12:30 | 521 | 521
2017-10-26 13:00 | 542 | 542
2017-10-26 13:30 | 514 | 514
2017-10-26 14:00 | 440 | 439
2017-10-26 14:30 | 441 | 440
2017-10-26 15:00 | 455 | 454
2017-10-26 15:30 | 472 | 472
2017-10-26 16:00 | 482 | 482
2017-10-26 16:30 | 500 | 499
2017-10-26 17:00 | 531 | 531
2017-10-26 17:30 | 543 | 543
2017-10-26 18:00 | 558 | 558
2017-10-26 18:30 | 567 | 567
2017-10-26 19:00 | 533 | 533
2017-10-26 19:30 | 476 | 476
2017-10-26 20:00 | 452 | 451
2017-10-26 20:30 | 423 | 422
2017-10-26 21:00 | 467 | 465
2017-10-26 21:30 | 476 | 475
2017-10-26 22:00 | 457 | 456
2017-10-26 22:30 | 430 | 429
2017-10-26 23:00 | 454 | 453
2017-10-26 23:30 | 520 | 519
2017-10-27 | 501 | 501
2017-10-27 00:30 | 482 | 482
2017-10-27 01:00 | 471 | 470
2017-10-27 01:30 | 467 | 466
2017-10-27 02:00 | 458 | 457
2017-10-27 02:30 | 457 | 456
2017-10-27 03:00 | 453 | 452
2017-10-27 03:30 | 454 | 453
2017-10-27 04:00 | 447 | 446
2017-10-27 04:30 | 444 | 443
2017-10-27 05:00 | 444 | 443
2017-10-27 05:30 | 449 | 448
2017-10-27 06:00 | 456 | 454
2017-10-27 06:30 | 490 | 488
2017-10-27 07:00 | 520 | 519
2017-10-27 07:30 | 536 | 536
2017-10-27 08:00 | 545 | 545
2017-10-27 08:30 | 541 | 541
2017-10-27 09:00 | 533 | 532
2017-10-27 09:30 | 531 | 531
2017-10-27 10:00 | 503 | 503
2017-10-27 10:30 | 494 | 494
2017-10-27 11:00 | 498 | 497
2017-10-27 11:30 | 503 | 502
2017-10-27 12:00 | 509 | 509
2017-10-27 12:30 | 515 | 515
2017-10-27 13:00 | 518 | 518
2017-10-27 13:30 | 538 | 538
2017-10-27 14:00 | 559 | 559
2017-10-27 14:30 | 570 | 570
2017-10-27 15:00 | 578 | 578
2017-10-27 15:30 | 566 | 566
2017-10-27 16:00 | 587 | 587
2017-10-27 16:30 | 605 | 605
2017-10-27 17:00 | 626 | 626
2017-10-27 17:30 | 624 | 624
2017-10-27 18:00 | 645 | 645
2017-10-27 18:30 | 657 | 657
2017-10-27 19:00 | 675 | 674
2017-10-27 19:30 | 665 | 664
2017-10-27 20:00 | 625 | 624
2017-10-27 20:30 | 608 | 607
2017-10-27 21:00 | 586 | 586
2017-10-27 21:30 | 572 | 572
2017-10-27 22:00 | 549 | 549
2017-10-27 22:30 | 526 | 525
2017-10-27 23:00 | 499 | 498
2017-10-27 23:30 | 485 | 484
2017-10-28 | 487 | 486
2017-10-28 00:30 | 474 | 473
2017-10-28 01:00 | 464 | 463
2017-10-28 01:30 | 455 | 454
2017-10-28 02:00 | 448 | 447
2017-10-28 02:30 | 440 | 438
2017-10-28 03:00 | 438 | 436
2017-10-28 03:30 | 435 | 433
2017-10-28 04:00 | 437 | 435
2017-10-28 04:30 | 433 | 431
2017-10-28 05:00 | 433 | 432
2017-10-28 05:30 | 436 | 434
2017-10-28 06:00 | 438 | 436
2017-10-28 06:30 | 449 | 448
2017-10-28 07:00 | 458 | 457
2017-10-28 07:30 | 474 | 473
2017-10-28 08:00 | 482 | 481
2017-10-28 08:30 | 497 | 497
2017-10-28 09:00 | 503 | 502
2017-10-28 09:30 | 499 | 499
2017-10-28 10:00 | 482 | 481
2017-10-28 10:30 | 467 | 467
2017-10-28 11:00 | 469 | 469
2017-10-28 11:30 | 474 | 473
2017-10-28 12:00 | 478 | 477
2017-10-28 12:30 | 485 | 485
2017-10-28 13:00 | 490 | 489
2017-10-28 13:30 | 508 | 508
2017-10-28 14:00 | 511 | 510
2017-10-28 14:30 | 520 | 520
2017-10-28 15:00 | 533 | 533
2017-10-28 15:30 | 549 | 549
2017-10-28 16:00 | 572 | 572
2017-10-28 16:30 | 587 | 587
2017-10-28 17:00 | 613 | 613
2017-10-28 17:30 | 630 | 630
2017-10-28 18:00 | 633 | 633
2017-10-28 18:30 | 636 | 636
2017-10-28 19:00 | 657 | 657
2017-10-28 19:30 | 673 | 672
2017-10-28 20:00 | 660 | 659
2017-10-28 20:30 | 638 | 637
2017-10-28 21:00 | 621 | 621
2017-10-28 21:30 | 603 | 603
2017-10-28 22:00 | 583 | 583
2017-10-28 22:30 | 559 | 559
2017-10-28 23:00 | 545 | 545
2017-10-28 23:30 | 528 | 528
2017-10-29 | 520 | 520
2017-10-29 00:30 | 508 | 508
2017-10-29 01:00 | 489 | 489
2017-10-29 01:30 | 476 | 476
2017-10-29 02:00 | 465 | 464
2017-10-29 02:30 | 457 | 456
2017-10-29 03:00 | 454 | 453
2017-10-29 03:30 | 448 | 447
2017-10-29 04:00 | 446 | 445
2017-10-29 04:30 | 449 | 448
2017-10-29 05:00 | 448 | 447
2017-10-29 05:30 | 451 | 450
2017-10-29 06:00 | 449 | 448
2017-10-29 06:30 | 455 | 454
2017-10-29 07:00 | 461 | 460
2017-10-29 07:30 | 475 | 475
2017-10-29 08:00 | 483 | 483
2017-10-29 08:30 | 497 | 496
2017-10-29 09:00 | 511 | 511
2017-10-29 09:30 | 517 | 517
2017-10-29 10:00 | 501 | 501
2017-10-29 10:30 | 491 | 491
2017-10-29 11:00 | 497 | 497
2017-10-29 11:30 | 504 | 504
2017-10-29 12:00 | 510 | 510
2017-10-29 12:30 | 515 | 515
2017-10-29 13:00 | 519 | 519
2017-10-29 13:30 | 542 | 542
2017-10-29 14:00 | 563 | 563
2017-10-29 14:30 | 577 | 577
2017-10-29 15:00 | 595 | 595
2017-10-29 15:30 | 605 | 604
2017-10-29 16:00 | 623 | 623
2017-10-29 16:30 | 636 | 636
2017-10-29 17:00 | 658 | 658
2017-10-29 17:30 | 678 | 678
2017-10-29 18:00 | 687 | 686
2017-10-29 18:30 | 688 | 688
2017-10-29 19:00 | 717 | 717
2017-10-29 19:30 | 713 | 712
2017-10-29 20:00 | 689 | 688
2017-10-29 20:30 | 673 | 672
2017-10-29 21:00 | 651 | 650
2017-10-29 21:30 | 631 | 631
2017-10-29 22:00 | 608 | 607
2017-10-29 22:30 | 581 | 581
2017-10-29 23:00 | 551 | 551
2017-10-29 23:30 | 530 | 529
2017-10-30 | 506 | 506
2017-10-30 00:30 | 495 | 494
2017-10-30 01:00 | 484 | 484
2017-10-30 01:30 | 477 | 477
2017-10-30 02:00 | 468 | 467
2017-10-30 02:30 | 465 | 465
2017-10-30 03:00 | 461 | 460
2017-10-30 03:30 | 459 | 458
2017-10-30 04:00 | 462 | 461
2017-10-30 04:30 | 463 | 462
2017-10-30 05:00 | 467 | 466
2017-10-30 05:30 | 479 | 478
2017-10-30 06:00 | 491 | 490
2017-10-30 06:30 | 528 | 527
2017-10-30 07:00 | 552 | 552
2017-10-30 07:30 | 585 | 585
2017-10-30 08:00 | 603 | 603
2017-10-30 08:30 | 609 | 609
2017-10-30 09:00 | 616 | 616
2017-10-30 09:30 | 622 | 622
2017-10-30 10:00 | 595 | 595
2017-10-30 10:30 | 572 | 572
2017-10-30 11:00 | 596 | 596
2017-10-30 11:30 | 603 | 603
2017-10-30 12:00 | 621 | 621
2017-10-30 12:30 | 628 | 628
2017-10-30 13:00 | 631 | 631
2017-10-30 13:30 | 660 | 660
2017-10-30 14:00 | 670 | 670
2017-10-30 14:30 | 680 | 679
2017-10-30 15:00 | 682 | 681
2017-10-30 15:30 | 674 | 673
2017-10-30 16:00 | 676 | 676
2017-10-30 16:30 | 675 | 675
2017-10-30 17:00 | 670 | 669
2017-10-30 17:30 | 665 | 664
2017-10-30 18:00 | 698 | 697
2017-10-30 18:30 | 720 | 719
2017-10-30 19:00 | 735 | 735
2017-10-30 19:30 | 719 | 718
2017-10-30 20:00 | 695 | 694
2017-10-30 20:30 | 663 | 663
2017-10-30 21:00 | 651 | 651
2017-10-30 21:30 | 643 | 643
2017-10-30 22:00 | 620 | 620
2017-10-30 22:30 | 595 | 595
2017-10-30 23:00 | 552 | 552
2017-10-30 23:30 | 521 | 521
2017-10-31 | 501 | 501
2017-10-31 00:30 | 489 | 489
2017-10-31 01:00 | 476 | 476
2017-10-31 01:30 | 470 | 470
2017-10-31 02:00 | 476 | 476
2017-10-31 02:30 | 471 | 471
2017-10-31 03:00 | 463 | 462
2017-10-31 03:30 | 458 | 458
2017-10-31 04:00 | 455 | 455
2017-10-31 04:30 | 465 | 465
2017-10-31 05:00 | 471 | 471
2017-10-31 05:30 | 487 | 487
2017-10-31 06:00 | 499 | 498
2017-10-31 06:30 | 527 | 527
2017-10-31 07:00 | 555 | 555
2017-10-31 07:30 | 592 | 592
2017-10-31 08:00 | 597 | 597
2017-10-31 08:30 | 612 | 612
2017-10-31 09:00 | 618 | 618
2017-10-31 09:30 | 617 | 617
2017-10-31 10:00 | 615 | 615
2017-10-31 10:30 | 628 | 628
2017-10-31 11:00 | 629 | 629
2017-10-31 11:30 | 638 | 638
2017-10-31 12:00 | 650 | 650
2017-10-31 12:30 | 651 | 650
2017-10-31 13:00 | 649 | 649
2017-10-31 13:30 | 660 | 659
2017-10-31 14:00 | 673 | 672
2017-10-31 14:30 | 683 | 683
2017-10-31 15:00 | 688 | 687
2017-10-31 15:30 | 680 | 679
2017-10-31 16:00 | 678 | 677
2017-10-31 16:30 | 686 | 686
2017-10-31 17:00 | 689 | 689
2017-10-31 17:30 | 689 | 688
2017-10-31 18:00 | 679 | 679
2017-10-31 18:30 | 690 | 689
2017-10-31 19:00 | 703 | 702
2017-10-31 19:30 | 716 | 715
2017-10-31 20:00 | 708 | 707
2017-10-31 20:30 | 717 | 717
2017-10-31 21:00 | 705 | 704
2017-10-31 21:30 | 695 | 694
2017-10-31 22:00 | 667 | 667
2017-10-31 22:30 | 642 | 642
2017-10-31 23:00 | 610 | 610
2017-10-31 23:30 | 593 | 593
2017-11-01 | 572 | 572
2017-11-01 00:30 | 556 | 556
2017-11-01 01:00 | 537 | 537
2017-11-01 01:30 | 521 | 521
2017-11-01 02:00 | 510 | 510
2017-11-01 02:30 | 507 | 507
2017-11-01 03:00 | 499 | 499
2017-11-01 03:30 | 500 | 500
2017-11-01 04:00 | 501 | 501
2017-11-01 04:30 | 505 | 505
2017-11-01 05:00 | 507 | 507
2017-11-01 05:30 | 515 | 514
2017-11-01 06:00 | 531 | 531
2017-11-01 06:30 | 569 | 569
2017-11-01 07:00 | 594 | 594
2017-11-01 07:30 | 620 | 620
2017-11-01 08:00 | 636 | 636
2017-11-01 08:30 | 653 | 652
2017-11-01 09:00 | 649 | 648
2017-11-01 09:30 | 645 | 645
2017-11-01 10:00 | 640 | 639
2017-11-01 10:30 | 635 | 634
2017-11-01 11:00 | 619 | 619
2017-11-01 11:30 | 613 | 613
2017-11-01 12:00 | 610 | 610
2017-11-01 12:30 | 613 | 613
2017-11-01 13:00 | 625 | 625
2017-11-01 13:30 | 641 | 641
2017-11-01 14:00 | 663 | 662
2017-11-01 14:30 | 666 | 665
2017-11-01 15:00 | 663 | 663
2017-11-01 15:30 | 644 | 644
2017-11-01 16:00 | 650 | 650
2017-11-01 16:30 | 654 | 654
2017-11-01 17:00 | 665 | 665
2017-11-01 17:30 | 669 | 668
2017-11-01 18:00 | 664 | 663
2017-11-01 18:30 | 707 | 706
2017-11-01 19:00 | 726 | 725
2017-11-01 19:30 | 721 | 720
2017-11-01 20:00 | 702 | 701
2017-11-01 20:30 | 683 | 683
2017-11-01 21:00 | 658 | 658
2017-11-01 21:30 | 628 | 628
2017-11-01 22:00 | 605 | 605
2017-11-01 22:30 | 583 | 583
2017-11-01 23:00 | 560 | 560
2017-11-01 23:30 | 537 | 537
2017-11-02 | 514 | 514
2017-11-02 00:30 | 500 | 500
2017-11-02 01:00 | 483 | 483
2017-11-02 01:30 | 478 | 477
2017-11-02 02:00 | 479 | 478
2017-11-02 02:30 | 486 | 485
2017-11-02 03:00 | 482 | 482
2017-11-02 03:30 | 478 | 478
2017-11-02 04:00 | 472 | 472
2017-11-02 04:30 | 470 | 470
2017-11-02 05:00 | 471 | 470
2017-11-02 05:30 | 484 | 483
2017-11-02 06:00 | 500 | 500
2017-11-02 06:30 | 531 | 530
2017-11-02 07:00 | 560 | 560
2017-11-02 07:30 | 592 | 592
2017-11-02 08:00 | 609 | 609
2017-11-02 08:30 | 614 | 614
2017-11-02 09:00 | 628 | 628
2017-11-02 09:30 | 623 | 623
2017-11-02 10:00 | 619 | 619
2017-11-02 10:30 | 621 | 621
2017-11-02 11:00 | 623 | 623
2017-11-02 11:30 | 608 | 608
2017-11-02 12:00 | 617 | 617
2017-11-02 12:30 | 631 | 631
2017-11-02 13:00 | 632 | 632
2017-11-02 13:30 | 632 | 632
2017-11-02 14:00 | 640 | 640
2017-11-02 14:30 | 659 | 659
2017-11-02 15:00 | 662 | 662
2017-11-02 15:30 | 645 | 645
2017-11-02 16:00 | 652 | 652
2017-11-02 16:30 | 662 | 662
2017-11-02 17:00 | 663 | 662
2017-11-02 17:30 | 663 | 662
2017-11-02 18:00 | 699 | 699
2017-11-02 18:30 | 716 | 715
2017-11-02 19:00 | 737 | 737
2017-11-02 19:30 | 739 | 737
2017-11-02 20:00 | 713 | 712
2017-11-02 20:30 | 694 | 693
2017-11-02 21:00 | 673 | 672
2017-11-02 21:30 | 632 | 632
2017-11-02 22:00 | 600 | 600
2017-11-02 22:30 | 565 | 565
2017-11-02 23:00 | 540 | 540
2017-11-02 23:30 | 517 | 517
2017-11-03 | 498 | 498
2017-11-03 00:30 | 491 | 490
2017-11-03 01:00 | 471 | 471
2017-11-03 01:30 | 459 | 458
2017-11-03 02:00 | 453 | 452
2017-11-03 02:30 | 451 | 450
2017-11-03 03:00 | 453 | 453
2017-11-03 03:30 | 449 | 448
2017-11-03 04:00 | 446 | 445
2017-11-03 04:30 | 450 | 449
2017-11-03 05:00 | 456 | 455
2017-11-03 05:30 | 468 | 468
2017-11-03 06:00 | 485 | 484
2017-11-03 06:30 | 533 | 533
2017-11-03 07:00 | 568 | 568
2017-11-03 07:30 | 594 | 594
2017-11-03 08:00 | 608 | 608
2017-11-03 08:30 | 612 | 612
2017-11-03 09:00 | 614 | 614
2017-11-03 09:30 | 617 | 617
2017-11-03 10:00 | 605 | 605
2017-11-03 10:30 | 601 | 601
2017-11-03 11:00 | 601 | 601
2017-11-03 11:30 | 609 | 608
2017-11-03 12:00 | 612 | 612
2017-11-03 12:30 | 613 | 613
2017-11-03 13:00 | 612 | 612
2017-11-03 13:30 | 609 | 609
2017-11-03 14:00 | 619 | 619
2017-11-03 14:30 | 634 | 633
2017-11-03 15:00 | 639 | 639
2017-11-03 15:30 | 621 | 621
2017-11-03 16:00 | 629 | 629
2017-11-03 16:30 | 643 | 643
2017-11-03 17:00 | 651 | 650
2017-11-03 17:30 | 653 | 653
2017-11-03 18:00 | 675 | 675
2017-11-03 18:30 | 682 | 681
2017-11-03 19:00 | 702 | 702
2017-11-03 19:30 | 693 | 692
2017-11-03 20:00 | 688 | 687
2017-11-03 20:30 | 670 | 669
2017-11-03 21:00 | 642 | 641
2017-11-03 21:30 | 626 | 626
2017-11-03 22:00 | 610 | 610
2017-11-03 22:30 | 579 | 579
2017-11-03 23:00 | 556 | 556
2017-11-03 23:30 | 534 | 534
2017-11-04 | 512 | 512
2017-11-04 00:30 | 499 | 498
2017-11-04 01:00 | 478 | 478
2017-11-04 01:30 | 463 | 463
2017-11-04 02:00 | 455 | 455
2017-11-04 02:30 | 451 | 450
2017-11-04 03:00 | 448 | 447
2017-11-04 03:30 | 445 | 444
2017-11-04 04:00 | 442 | 441
2017-11-04 04:30 | 451 | 450
2017-11-04 05:00 | 460 | 459
2017-11-04 05:30 | 470 | 469
2017-11-04 06:00 | 466 | 466
2017-11-04 06:30 | 475 | 475
2017-11-04 07:00 | 483 | 482
2017-11-04 07:30 | 503 | 503
2017-11-04 08:00 | 518 | 518
2017-11-04 08:30 | 533 | 533
2017-11-04 09:00 | 546 | 546
2017-11-04 09:30 | 556 | 556
2017-11-04 10:00 | 553 | 553
2017-11-04 10:30 | 555 | 555
2017-11-04 11:00 | 555 | 555
2017-11-04 11:30 | 558 | 558
2017-11-04 12:00 | 560 | 560
2017-11-04 12:30 | 539 | 539
2017-11-04 13:00 | 419 | 419
2017-11-04 13:30 | 402 | 400
2017-11-04 14:00 | 497 | 496
2017-11-04 14:30 | 551 | 551
2017-11-04 15:00 | 568 | 567
2017-11-04 15:30 | 585 | 585
2017-11-04 16:00 | 605 | 605
2017-11-04 16:30 | 612 | 612
2017-11-04 17:00 | 631 | 631
2017-11-04 17:30 | 645 | 645
2017-11-04 18:00 | 648 | 647
2017-11-04 18:30 | 636 | 636
2017-11-04 19:00 | 653 | 653
2017-11-04 19:30 | 653 | 653
2017-11-04 20:00 | 640 | 640
2017-11-04 20:30 | 612 | 612
2017-11-04 21:00 | 596 | 595
2017-11-04 21:30 | 599 | 599
2017-11-04 22:00 | 580 | 580
2017-11-04 22:30 | 558 | 558
2017-11-04 23:00 | 536 | 536
2017-11-04 23:30 | 517 | 517
2017-11-05 | 496 | 495
2017-11-05 00:30 | 488 | 488
2017-11-05 01:00 | 469 | 469
2017-11-05 01:30 | 459 | 458
2017-11-05 02:00 | 454 | 453
2017-11-05 02:30 | 450 | 449
2017-11-05 03:00 | 439 | 437
2017-11-05 03:30 | 433 | 431
2017-11-05 04:00 | 429 | 427
2017-11-05 04:30 | 434 | 432
2017-11-05 05:00 | 436 | 434
2017-11-05 05:30 | 447 | 445
2017-11-05 06:00 | 452 | 450
2017-11-05 06:30 | 456 | 454
2017-11-05 07:00 | 457 | 455
2017-11-05 07:30 | 466 | 464
2017-11-05 08:00 | 479 | 478
2017-11-05 08:30 | 491 | 490
2017-11-05 09:00 | 499 | 498
2017-11-05 09:30 | 503 | 502
2017-11-05 10:00 | 512 | 510
2017-11-05 10:30 | 515 | 514
2017-11-05 11:00 | 507 | 507
2017-11-05 11:30 | 509 | 508
2017-11-05 12:00 | 515 | 514
2017-11-05 12:30 | 514 | 514
2017-11-05 13:00 | 515 | 514
2017-11-05 13:30 | 524 | 523
2017-11-05 14:00 | 535 | 534
2017-11-05 14:30 | 544 | 544
2017-11-05 15:00 | 548 | 547
2017-11-05 15:30 | 560 | 560
2017-11-05 16:00 | 586 | 586
2017-11-05 16:30 | 606 | 606
2017-11-05 17:00 | 632 | 632
2017-11-05 17:30 | 657 | 656
2017-11-05 18:00 | 644 | 644
2017-11-05 18:30 | 642 | 642
2017-11-05 19:00 | 667 | 667
2017-11-05 19:30 | 673 | 673
2017-11-05 20:00 | 649 | 649
2017-11-05 20:30 | 642 | 642
2017-11-05 21:00 | 627 | 627
2017-11-05 21:30 | 604 | 604
2017-11-05 22:00 | 579 | 579
2017-11-05 22:30 | 551 | 551
2017-11-05 23:00 | 520 | 520
2017-11-05 23:30 | 503 | 502
2017-11-06 | 483 | 482
2017-11-06 00:30 | 467 | 465
2017-11-06 01:00 | 452 | 451
2017-11-06 01:30 | 449 | 447
2017-11-06 02:00 | 443 | 441
2017-11-06 02:30 | 437 | 435
2017-11-06 03:00 | 436 | 434
2017-11-06 03:30 | 445 | 444
2017-11-06 04:00 | 441 | 439
2017-11-06 04:30 | 444 | 442
2017-11-06 05:00 | 448 | 446
2017-11-06 05:30 | 465 | 464
2017-11-06 06:00 | 478 | 476
2017-11-06 06:30 | 507 | 506
2017-11-06 07:00 | 538 | 537
2017-11-06 07:30 | 570 | 569
2017-11-06 08:00 | 580 | 580
2017-11-06 08:30 | 590 | 590
2017-11-06 09:00 | 585 | 585
2017-11-06 09:30 | 590 | 590
2017-11-06 10:00 | 580 | 580
2017-11-06 10:30 | 579 | 579
2017-11-06 11:00 | 573 | 573
2017-11-06 11:30 | 571 | 571
2017-11-06 12:00 | 572 | 572
2017-11-06 12:30 | 573 | 573
2017-11-06 13:00 | 579 | 579
2017-11-06 13:30 | 582 | 582
2017-11-06 14:00 | 595 | 595
2017-11-06 14:30 | 606 | 606
2017-11-06 15:00 | 617 | 617
2017-11-06 15:30 | 608 | 608
2017-11-06 16:00 | 617 | 617
2017-11-06 16:30 | 628 | 628
2017-11-06 17:00 | 647 | 647
2017-11-06 17:30 | 645 | 645
2017-11-06 18:00 | 680 | 680
2017-11-06 18:30 | 698 | 698
2017-11-06 19:00 | 724 | 724
2017-11-06 19:30 | 724 | 724
2017-11-06 20:00 | 703 | 703
2017-11-06 20:30 | 677 | 677
2017-11-06 21:00 | 650 | 650
2017-11-06 21:30 | 621 | 621
2017-11-06 22:00 | 588 | 587
2017-11-06 22:30 | 558 | 558
2017-11-06 23:00 | 533 | 532
2017-11-06 23:30 | 512 | 511
2017-11-07 | 492 | 491
2017-11-07 00:30 | 484 | 483
2017-11-07 01:00 | 468 | 467
2017-11-07 01:30 | 455 | 454
2017-11-07 02:00 | 447 | 445
2017-11-07 02:30 | 441 | 439
2017-11-07 03:00 | 435 | 433
2017-11-07 03:30 | 435 | 433
2017-11-07 04:00 | 437 | 435
2017-11-07 04:30 | 441 | 439
2017-11-07 05:00 | 443 | 441
2017-11-07 05:30 | 456 | 453
2017-11-07 06:00 | 468 | 466
2017-11-07 06:30 | 499 | 497
2017-11-07 07:00 | 531 | 529
2017-11-07 07:30 | 560 | 559
2017-11-07 08:00 | 570 | 570
2017-11-07 08:30 | 576 | 576
2017-11-07 09:00 | 576 | 576
2017-11-07 09:30 | 576 | 575
2017-11-07 10:00 | 572 | 571
2017-11-07 10:30 | 577 | 577
2017-11-07 11:00 | 576 | 575
2017-11-07 11:30 | 603 | 603
2017-11-07 12:00 | 622 | 622
2017-11-07 12:30 | 617 | 617
2017-11-07 13:00 | 615 | 615
2017-11-07 13:30 | 616 | 616
2017-11-07 14:00 | 629 | 629
2017-11-07 14:30 | 646 | 646
2017-11-07 15:00 | 653 | 653
2017-11-07 15:30 | 636 | 636
2017-11-07 16:00 | 651 | 651
2017-11-07 16:30 | 667 | 667
2017-11-07 17:00 | 688 | 688
2017-11-07 17:30 | 689 | 689
2017-11-07 18:00 | 701 | 701
2017-11-07 18:30 | 715 | 715
2017-11-07 19:00 | 742 | 742
2017-11-07 19:30 | 739 | 739
2017-11-07 20:00 | 712 | 711
2017-11-07 20:30 | 691 | 691
2017-11-07 21:00 | 669 | 669
2017-11-07 21:30 | 632 | 632
2017-11-07 22:00 | 594 | 594
2017-11-07 22:30 | 567 | 567
2017-11-07 23:00 | 545 | 545
2017-11-07 23:30 | 524 | 523
2017-11-08 | 500 | 499
2017-11-08 00:30 | 491 | 490
2017-11-08 01:00 | 478 | 477
2017-11-08 01:30 | 467 | 466
2017-11-08 02:00 | 463 | 462
2017-11-08 02:30 | 458 | 456
2017-11-08 03:00 | 460 | 458
2017-11-08 03:30 | 459 | 457
2017-11-08 04:00 | 461 | 459
2017-11-08 04:30 | 458 | 456
2017-11-08 05:00 | 457 | 456
2017-11-08 05:30 | 475 | 473
2017-11-08 06:00 | 491 | 490
2017-11-08 06:30 | 528 | 527
2017-11-08 07:00 | 546 | 545
2017-11-08 07:30 | 573 | 572
2017-11-08 08:00 | 596 | 596
2017-11-08 08:30 | 604 | 604
2017-11-08 09:00 | 603 | 603
2017-11-08 09:30 | 601 | 601
2017-11-08 10:00 | 614 | 614
2017-11-08 10:30 | 615 | 615
2017-11-08 11:00 | 615 | 615
2017-11-08 11:30 | 620 | 620
2017-11-08 12:00 | 632 | 632
2017-11-08 12:30 | 647 | 647
2017-11-08 13:00 | 646 | 646
2017-11-08 13:30 | 651 | 651
2017-11-08 14:00 | 656 | 656
2017-11-08 14:30 | 674 | 674
2017-11-08 15:00 | 689 | 689
2017-11-08 15:30 | 688 | 688
2017-11-08 16:00 | 706 | 705
2017-11-08 16:30 | 727 | 727
2017-11-08 17:00 | 734 | 734
2017-11-08 17:30 | 732 | 732
2017-11-08 18:00 | 731 | 731
2017-11-08 18:30 | 735 | 734
2017-11-08 19:00 | 752 | 751
2017-11-08 19:30 | 749 | 748
2017-11-08 20:00 | 737 | 737
2017-11-08 20:30 | 715 | 715
2017-11-08 21:00 | 695 | 695
2017-11-08 21:30 | 666 | 666
2017-11-08 22:00 | 626 | 626
2017-11-08 22:30 | 597 | 597
2017-11-08 23:00 | 567 | 567
2017-11-08 23:30 | 541 | 540
2017-11-09 | 524 | 523
2017-11-09 00:30 | 511 | 511
2017-11-09 01:00 | 495 | 494
2017-11-09 01:30 | 489 | 488
2017-11-09 02:00 | 486 | 484
2017-11-09 02:30 | 483 | 482
2017-11-09 03:00 | 479 | 477
2017-11-09 03:30 | 471 | 470
2017-11-09 04:00 | 476 | 474
2017-11-09 04:30 | 479 | 477
2017-11-09 05:00 | 481 | 479
2017-11-09 05:30 | 491 | 490
2017-11-09 06:00 | 504 | 503
2017-11-09 06:30 | 535 | 534
2017-11-09 07:00 | 566 | 565
2017-11-09 07:30 | 601 | 601
2017-11-09 08:00 | 624 | 624
2017-11-09 08:30 | 626 | 626
2017-11-09 09:00 | 628 | 628
2017-11-09 09:30 | 625 | 625
2017-11-09 10:00 | 620 | 620
2017-11-09 10:30 | 620 | 620
2017-11-09 11:00 | 597 | 597
2017-11-09 11:30 | 606 | 606
2017-11-09 12:00 | 629 | 629
2017-11-09 12:30 | 631 | 631
2017-11-09 13:00 | 623 | 623
2017-11-09 13:30 | 632 | 632
2017-11-09 14:00 | 642 | 642
2017-11-09 14:30 | 643 | 643
2017-11-09 15:00 | 643 | 643
2017-11-09 15:30 | 631 | 631
2017-11-09 16:00 | 630 | 630
2017-11-09 16:30 | 617 | 617
2017-11-09 17:00 | 555 | 555
2017-11-09 17:30 | 546 | 546
2017-11-09 18:00 | 555 | 554
2017-11-09 18:30 | 568 | 568
2017-11-09 19:00 | 529 | 529
2017-11-09 19:30 | 505 | 504
2017-11-09 20:00 | 485 | 484
2017-11-09 20:30 | 484 | 483
2017-11-09 21:00 | 470 | 468
2017-11-09 21:30 | 442 | 441
2017-11-09 22:00 | 414 | 412
2017-11-09 22:30 | 393 | 390
2017-11-09 23:00 | 379 | 375
2017-11-09 23:30 | 364 | 357
2017-11-10 | 408 | 402
2017-11-10 00:30 | 464 | 460
2017-11-10 01:00 | 461 | 458
2017-11-10 01:30 | 456 | 453
2017-11-10 02:00 | 452 | 449
2017-11-10 02:30 | 446 | 443
2017-11-10 03:00 | 441 | 437
2017-11-10 03:30 | 435 | 431
2017-11-10 04:00 | 434 | 430
2017-11-10 04:30 | 434 | 430
2017-11-10 05:00 | 433 | 429
2017-11-10 05:30 | 446 | 442
2017-11-10 06:00 | 459 | 456
2017-11-10 06:30 | 491 | 488
2017-11-10 07:00 | 518 | 516
2017-11-10 07:30 | 520 | 518
2017-11-10 08:00 | 460 | 459
2017-11-10 08:30 | 440 | 437
2017-11-10 09:00 | 434 | 430
2017-11-10 09:30 | 430 | 426
2017-11-10 10:00 | 395 | 391
2017-11-10 10:30 | 367 | 361
2017-11-10 11:00 | 353 | 346
2017-11-10 11:30 | 352 | 345
2017-11-10 12:00 | 381 | 374
2017-11-10 12:30 | 364 | 358
2017-11-10 13:00 | 320 | 313
2017-11-10 13:30 | 326 | 316
2017-11-10 14:00 | 355 | 346
2017-11-10 14:30 | 364 | 357
2017-11-10 15:00 | 352 | 346
2017-11-10 15:30 | 331 | 324
2017-11-10 16:00 | 341 | 333
2017-11-10 16:30 | 345 | 338
2017-11-10 17:00 | 349 | 342
2017-11-10 17:30 | 349 | 341
2017-11-10 18:00 | 375 | 368
2017-11-10 18:30 | 395 | 389
2017-11-10 19:00 | 411 | 406
2017-11-10 19:30 | 407 | 402
2017-11-10 20:00 | 390 | 385
2017-11-10 20:30 | 349 | 344
2017-11-10 21:00 | 314 | 306
2017-11-10 21:30 | 302 | 292
2017-11-10 22:00 | 303 | 291
2017-11-10 22:30 | 297 | 285
2017-11-10 23:00 | 278 | 266
2017-11-10 23:30 | 260 | 245
2017-11-11 | 242 | 225
2017-11-11 00:30 | 295 | 279
2017-11-11 01:00 | 300 | 288
2017-11-11 01:30 | 296 | 284
2017-11-11 02:00 | 292 | 280
2017-11-11 02:30 | 285 | 272
2017-11-11 03:00 | 281 | 267
2017-11-11 03:30 | 279 | 265
2017-11-11 04:00 | 272 | 257
2017-11-11 04:30 | 276 | 262
2017-11-11 05:00 | 279 | 264
2017-11-11 05:30 | 287 | 274
2017-11-11 06:00 | 288 | 274
2017-11-11 06:30 | 297 | 284
2017-11-11 07:00 | 298 | 286
2017-11-11 07:30 | 299 | 287
2017-11-11 08:00 | 308 | 296
2017-11-11 08:30 | 324 | 313
2017-11-11 09:00 | 328 | 319
2017-11-11 09:30 | 333 | 324
2017-11-11 10:00 | 322 | 313
2017-11-11 10:30 | 333 | 324
2017-11-11 11:00 | 332 | 323
2017-11-11 11:30 | 329 | 319
2017-11-11 12:00 | 338 | 329
2017-11-11 12:30 | 340 | 331
2017-11-11 13:00 | 341 | 333
2017-11-11 13:30 | 352 | 344
2017-11-11 14:00 | 343 | 335
2017-11-11 14:30 | 343 | 335
2017-11-11 15:00 | 367 | 359
2017-11-11 15:30 | 362 | 356
2017-11-11 16:00 | 335 | 327
2017-11-11 16:30 | 340 | 332
2017-11-11 17:00 | 357 | 349
2017-11-11 17:30 | 363 | 356
2017-11-11 18:00 | 363 | 357
2017-11-11 18:30 | 374 | 368
2017-11-11 19:00 | 394 | 388
2017-11-11 19:30 | 435 | 431
2017-11-11 20:00 | 499 | 496
2017-11-11 20:30 | 525 | 524
2017-11-11 21:00 | 515 | 514
2017-11-11 21:30 | 502 | 501
2017-11-11 22:00 | 497 | 496
2017-11-11 22:30 | 479 | 478
2017-11-11 23:00 | 484 | 482
2017-11-11 23:30 | 473 | 471
2017-11-12 | 452 | 450
2017-11-12 00:30 | 440 | 437
2017-11-12 01:00 | 437 | 433
2017-11-12 01:30 | 433 | 429
2017-11-12 02:00 | 419 | 415
2017-11-12 02:30 | 414 | 410
2017-11-12 03:00 | 404 | 400
2017-11-12 03:30 | 404 | 400
2017-11-12 04:00 | 405 | 400
2017-11-12 04:30 | 404 | 400
2017-11-12 05:00 | 403 | 398
2017-11-12 05:30 | 404 | 399
2017-11-12 06:00 | 396 | 390
2017-11-12 06:30 | 396 | 390
2017-11-12 07:00 | 393 | 387
2017-11-12 07:30 | 385 | 379
2017-11-12 08:00 | 396 | 389
2017-11-12 08:30 | 406 | 400
2017-11-12 09:00 | 419 | 413
2017-11-12 09:30 | 453 | 448
2017-11-12 10:00 | 438 | 434
2017-11-12 10:30 | 427 | 422
2017-11-12 11:00 | 431 | 427
2017-11-12 11:30 | 435 | 431
2017-11-12 12:00 | 433 | 429
2017-11-12 12:30 | 419 | 415
2017-11-12 13:00 | 439 | 435
2017-11-12 13:30 | 443 | 440
2017-11-12 14:00 | 437 | 434
2017-11-12 14:30 | 451 | 448
2017-11-12 15:00 | 460 | 457
2017-11-12 15:30 | 448 | 445
2017-11-12 16:00 | 450 | 447
2017-11-12 16:30 | 462 | 459
2017-11-12 17:00 | 475 | 473
2017-11-12 17:30 | 493 | 491
2017-11-12 18:00 | 538 | 537
2017-11-12 18:30 | 550 | 549
2017-11-12 19:00 | 581 | 581
2017-11-12 19:30 | 580 | 580
2017-11-12 20:00 | 561 | 561
2017-11-12 20:30 | 554 | 554
2017-11-12 21:00 | 539 | 538
2017-11-12 21:30 | 519 | 518
2017-11-12 22:00 | 502 | 501
2017-11-12 22:30 | 491 | 490
2017-11-12 23:00 | 489 | 487
2017-11-12 23:30 | 462 | 460
2017-11-13 | 447 | 444
2017-11-13 00:30 | 442 | 440
2017-11-13 01:00 | 416 | 413
2017-11-13 01:30 | 402 | 398
2017-11-13 02:00 | 397 | 393
2017-11-13 02:30 | 395 | 391
2017-11-13 03:00 | 389 | 384
2017-11-13 03:30 | 388 | 382
2017-11-13 04:00 | 385 | 379
2017-11-13 04:30 | 394 | 389
2017-11-13 05:00 | 394 | 389
2017-11-13 05:30 | 407 | 402
2017-11-13 06:00 | 427 | 423
2017-11-13 06:30 | 453 | 450
2017-11-13 07:00 | 471 | 468
2017-11-13 07:30 | 484 | 482
2017-11-13 08:00 | 490 | 488
2017-11-13 08:30 | 505 | 504
2017-11-13 09:00 | 506 | 504
2017-11-13 09:30 | 504 | 503
2017-11-13 10:00 | 504 | 503
2017-11-13 10:30 | 509 | 507
2017-11-13 11:00 | 503 | 501
2017-11-13 11:30 | 499 | 497
2017-11-13 12:00 | 509 | 507
2017-11-13 12:30 | 514 | 512
2017-11-13 13:00 | 510 | 508
2017-11-13 13:30 | 521 | 520
2017-11-13 14:00 | 538 | 537
2017-11-13 14:30 | 544 | 544
2017-11-13 15:00 | 490 | 489
2017-11-13 15:30 | 457 | 455
2017-11-13 16:00 | 394 | 392
2017-11-13 16:30 | 392 | 388
2017-11-13 17:00 | 396 | 392
2017-11-13 17:30 | 415 | 411
2017-11-13 18:00 | 443 | 439
2017-11-13 18:30 | 463 | 460
2017-11-13 19:00 | 479 | 477
2017-11-13 19:30 | 465 | 463
2017-11-13 20:00 | 439 | 436
2017-11-13 20:30 | 429 | 426
2017-11-13 21:00 | 415 | 411
2017-11-13 21:30 | 395 | 390
2017-11-13 22:00 | 383 | 378
2017-11-13 22:30 | 365 | 359
2017-11-13 23:00 | 359 | 353
2017-11-13 23:30 | 335 | 328
2017-11-14 | 318 | 310
2017-11-14 00:30 | 431 | 424
2017-11-14 01:00 | 468 | 464
2017-11-14 01:30 | 452 | 449
2017-11-14 02:00 | 431 | 428
2017-11-14 02:30 | 422 | 419
2017-11-14 03:00 | 416 | 413
2017-11-14 03:30 | 415 | 411
2017-11-14 04:00 | 416 | 412
2017-11-14 04:30 | 426 | 423
2017-11-14 05:00 | 423 | 419
2017-11-14 05:30 | 440 | 436
2017-11-14 06:00 | 402 | 398
2017-11-14 06:30 | 383 | 379
2017-11-14 07:00 | 400 | 396
2017-11-14 07:30 | 412 | 408
2017-11-14 08:00 | 434 | 431
2017-11-14 08:30 | 458 | 455
2017-11-14 09:00 | 450 | 447
2017-11-14 09:30 | 451 | 449
2017-11-14 10:00 | 437 | 435
2017-11-14 10:30 | 440 | 438
2017-11-14 11:00 | 440 | 438
2017-11-14 11:30 | 405 | 402
2017-11-14 12:00 | 374 | 370
2017-11-14 12:30 | 374 | 369
2017-11-14 13:00 | 367 | 362
2017-11-14 13:30 | 370 | 365
2017-11-14 14:00 | 385 | 381
2017-11-14 14:30 | 365 | 360
2017-11-14 15:00 | 343 | 337
2017-11-14 15:30 | 332 | 326
2017-11-14 16:00 | 329 | 322
2017-11-14 16:30 | 337 | 331
2017-11-14 17:00 | 329 | 323
2017-11-14 17:30 | 337 | 330
2017-11-14 18:00 | 356 | 349
2017-11-14 18:30 | 364 | 358
2017-11-14 19:00 | 390 | 385
2017-11-14 19:30 | 389 | 385
2017-11-14 20:00 | 409 | 405
2017-11-14 20:30 | 422 | 418
2017-11-14 21:00 | 413 | 410
2017-11-14 21:30 | 403 | 399
2017-11-14 22:00 | 391 | 386
2017-11-14 22:30 | 364 | 358
2017-11-14 23:00 | 363 | 357
2017-11-14 23:30 | 343 | 336
2017-11-15 | 331 | 324
2017-11-15 00:30 | 322 | 313
2017-11-15 01:00 | 272 | 261
2017-11-15 01:30 | 299 | 287
2017-11-15 02:00 | 292 | 282
2017-11-15 02:30 | 291 | 279
2017-11-15 03:00 | 288 | 277
2017-11-15 03:30 | 299 | 287
2017-11-15 04:00 | 302 | 292
2017-11-15 04:30 | 299 | 288
2017-11-15 05:00 | 313 | 303
2017-11-15 05:30 | 323 | 315
2017-11-15 06:00 | 335 | 326
2017-11-15 06:30 | 364 | 356
2017-11-15 07:00 | 382 | 376
2017-11-15 07:30 | 397 | 392
2017-11-15 08:00 | 402 | 398
2017-11-15 08:30 | 410 | 406
2017-11-15 09:00 | 337 | 333
2017-11-15 09:30 | 323 | 316
2017-11-15 10:00 | 321 | 312
2017-11-15 10:30 | 316 | 307
2017-11-15 11:00 | 320 | 311
2017-11-15 11:30 | 345 | 336
2017-11-15 12:00 | 443 | 437
2017-11-15 12:30 | 475 | 473
2017-11-15 13:00 | 495 | 493
2017-11-15 13:30 | 481 | 480
2017-11-15 14:00 | 489 | 487
2017-11-15 14:30 | 484 | 483
2017-11-15 15:00 | 447 | 446
2017-11-15 15:30 | 444 | 442
2017-11-15 16:00 | 462 | 460
2017-11-15 16:30 | 473 | 471
2017-11-15 17:00 | 418 | 415
2017-11-15 17:30 | 393 | 389
2017-11-15 18:00 | 396 | 392
2017-11-15 18:30 | 399 | 395
2017-11-15 19:00 | 484 | 480
2017-11-15 19:30 | 508 | 507
2017-11-15 20:00 | 497 | 496
2017-11-15 20:30 | 491 | 489
2017-11-15 21:00 | 472 | 470
2017-11-15 21:30 | 447 | 444
2017-11-15 22:00 | 438 | 435
2017-11-15 22:30 | 410 | 406
2017-11-15 23:00 | 401 | 397
2017-11-15 23:30 | 385 | 380
2017-11-16 | 365 | 359
2017-11-16 00:30 | 349 | 341
2017-11-16 01:00 | 337 | 328
2017-11-16 01:30 | 327 | 318
2017-11-16 02:00 | 321 | 311
2017-11-16 02:30 | 320 | 310
2017-11-16 03:00 | 313 | 302
2017-11-16 03:30 | 314 | 303
2017-11-16 04:00 | 315 | 305
2017-11-16 04:30 | 321 | 311
2017-11-16 05:00 | 334 | 324
2017-11-16 05:30 | 351 | 343
2017-11-16 06:00 | 357 | 350
2017-11-16 06:30 | 381 | 375
2017-11-16 07:00 | 407 | 402
2017-11-16 07:30 | 434 | 430
2017-11-16 08:00 | 447 | 443
2017-11-16 08:30 | 440 | 437
2017-11-16 09:00 | 439 | 436
2017-11-16 09:30 | 371 | 368
2017-11-16 10:00 | 354 | 346
2017-11-16 10:30 | 355 | 345
2017-11-16 11:00 | 355 | 345
2017-11-16 11:30 | 370 | 360
2017-11-16 12:00 | 368 | 359
2017-11-16 12:30 | 361 | 353
2017-11-16 13:00 | 365 | 357
2017-11-16 13:30 | 374 | 366
2017-11-16 14:00 | 387 | 380
2017-11-16 14:30 | 461 | 457
2017-11-16 15:00 | 477 | 475
2017-11-16 15:30 | 505 | 504
2017-11-16 16:00 | 580 | 580
2017-11-16 16:30 | 591 | 591
2017-11-16 17:00 | 597 | 597
2017-11-16 17:30 | 599 | 599
2017-11-16 18:00 | 608 | 608
2017-11-16 18:30 | 633 | 632
2017-11-16 19:00 | 645 | 645
2017-11-16 19:30 | 642 | 642
2017-11-16 20:00 | 624 | 624
2017-11-16 20:30 | 648 | 648
2017-11-16 21:00 | 636 | 636
2017-11-16 21:30 | 605 | 605
2017-11-16 22:00 | 594 | 594
2017-11-16 22:30 | 560 | 560
2017-11-16 23:00 | 542 | 541
2017-11-16 23:30 | 519 | 519
2017-11-17 | 497 | 496
2017-11-17 00:30 | 474 | 473
2017-11-17 01:00 | 466 | 465
2017-11-17 01:30 | 454 | 453
2017-11-17 02:00 | 444 | 443
2017-11-17 02:30 | 442 | 441
2017-11-17 03:00 | 439 | 437
2017-11-17 03:30 | 436 | 435
2017-11-17 04:00 | 439 | 437
2017-11-17 04:30 | 444 | 443
2017-11-17 05:00 | 447 | 446
2017-11-17 05:30 | 455 | 454
2017-11-17 06:00 | 468 | 467
2017-11-17 06:30 | 495 | 495
2017-11-17 07:00 | 511 | 510
2017-11-17 07:30 | 516 | 516
2017-11-17 08:00 | 544 | 544
2017-11-17 08:30 | 545 | 545
2017-11-17 09:00 | 550 | 550
2017-11-17 09:30 | 567 | 567
2017-11-17 10:00 | 566 | 566
2017-11-17 10:30 | 546 | 546
2017-11-17 11:00 | 544 | 544
2017-11-17 11:30 | 541 | 541
2017-11-17 12:00 | 541 | 541
2017-11-17 12:30 | 550 | 550
2017-11-17 13:00 | 562 | 562
2017-11-17 13:30 | 560 | 560
2017-11-17 14:00 | 562 | 562
2017-11-17 14:30 | 574 | 574
2017-11-17 15:00 | 589 | 589
2017-11-17 15:30 | 598 | 598
2017-11-17 16:00 | 591 | 591
2017-11-17 16:30 | 619 | 619
2017-11-17 17:00 | 633 | 633
2017-11-17 17:30 | 626 | 626
2017-11-17 18:00 | 628 | 627
2017-11-17 18:30 | 630 | 630
2017-11-17 19:00 | 642 | 641
2017-11-17 19:30 | 649 | 648
2017-11-17 20:00 | 641 | 641
2017-11-17 20:30 | 632 | 632
2017-11-17 21:00 | 619 | 619
2017-11-17 21:30 | 599 | 599
2017-11-17 22:00 | 591 | 591
2017-11-17 22:30 | 565 | 565
2017-11-17 23:00 | 558 | 558
2017-11-17 23:30 | 543 | 543
2017-11-18 | 523 | 523
2017-11-18 00:30 | 510 | 510
2017-11-18 01:00 | 493 | 493
2017-11-18 01:30 | 484 | 484
2017-11-18 02:00 | 478 | 478
2017-11-18 02:30 | 469 | 468
2017-11-18 03:00 | 447 | 446
2017-11-18 03:30 | 445 | 444
2017-11-18 04:00 | 439 | 438
2017-11-18 04:30 | 433 | 432
2017-11-18 05:00 | 457 | 456
2017-11-18 05:30 | 461 | 461
2017-11-18 06:00 | 465 | 464
2017-11-18 06:30 | 475 | 474
2017-11-18 07:00 | 453 | 453
2017-11-18 07:30 | 444 | 443
2017-11-18 08:00 | 460 | 459
2017-11-18 08:30 | 475 | 474
2017-11-18 09:00 | 474 | 474
2017-11-18 09:30 | 484 | 483
2017-11-18 10:00 | 487 | 486
2017-11-18 10:30 | 487 | 486
2017-11-18 11:00 | 484 | 483
2017-11-18 11:30 | 480 | 480
2017-11-18 12:00 | 494 | 494
2017-11-18 12:30 | 490 | 490
2017-11-18 13:00 | 484 | 483
2017-11-18 13:30 | 493 | 492
2017-11-18 14:00 | 505 | 504
2017-11-18 14:30 | 512 | 512
2017-11-18 15:00 | 515 | 514
2017-11-18 15:30 | 514 | 514
2017-11-18 16:00 | 513 | 513
2017-11-18 16:30 | 540 | 539
2017-11-18 17:00 | 563 | 563
2017-11-18 17:30 | 576 | 576
2017-11-18 18:00 | 591 | 591
2017-11-18 18:30 | 590 | 590
2017-11-18 19:00 | 609 | 609
2017-11-18 19:30 | 614 | 614
2017-11-18 20:00 | 593 | 593
2017-11-18 20:30 | 590 | 590
2017-11-18 21:00 | 580 | 580
2017-11-18 21:30 | 567 | 567
2017-11-18 22:00 | 568 | 567
2017-11-18 22:30 | 549 | 548
2017-11-18 23:00 | 547 | 546
2017-11-18 23:30 | 540 | 539
2017-11-19 | 521 | 521
2017-11-19 00:30 | 510 | 510
2017-11-19 01:00 | 491 | 491
2017-11-19 01:30 | 489 | 488
2017-11-19 02:00 | 476 | 476
2017-11-19 02:30 | 470 | 470
2017-11-19 03:00 | 466 | 465
2017-11-19 03:30 | 462 | 461
2017-11-19 04:00 | 455 | 454
2017-11-19 04:30 | 455 | 454
2017-11-19 05:00 | 457 | 456
2017-11-19 05:30 | 456 | 455
2017-11-19 06:00 | 447 | 445
2017-11-19 06:30 | 451 | 449
2017-11-19 07:00 | 446 | 445
2017-11-19 07:30 | 440 | 439
2017-11-19 08:00 | 450 | 449
2017-11-19 08:30 | 466 | 465
2017-11-19 09:00 | 475 | 474
2017-11-19 09:30 | 475 | 474
2017-11-19 10:00 | 486 | 485
2017-11-19 10:30 | 490 | 490
2017-11-19 11:00 | 480 | 479
2017-11-19 11:30 | 483 | 482
2017-11-19 12:00 | 482 | 482
2017-11-19 12:30 | 478 | 477
2017-11-19 13:00 | 474 | 473
2017-11-19 13:30 | 472 | 472
2017-11-19 14:00 | 479 | 479
2017-11-19 14:30 | 490 | 489
2017-11-19 15:00 | 498 | 497
2017-11-19 15:30 | 516 | 515
2017-11-19 16:00 | 516 | 515
2017-11-19 16:30 | 552 | 552
2017-11-19 17:00 | 569 | 569
2017-11-19 17:30 | 581 | 581
2017-11-19 18:00 | 599 | 599
2017-11-19 18:30 | 617 | 617
2017-11-19 19:00 | 633 | 633
2017-11-19 19:30 | 638 | 638
2017-11-19 20:00 | 621 | 621
2017-11-19 20:30 | 614 | 614
2017-11-19 21:00 | 593 | 593
2017-11-19 21:30 | 573 | 573
2017-11-19 22:00 | 565 | 565
2017-11-19 22:30 | 531 | 531
2017-11-19 23:00 | 524 | 524
2017-11-19 23:30 | 512 | 511
2017-11-20 | 503 | 503
2017-11-20 00:30 | 494 | 494
2017-11-20 01:00 | 480 | 480
2017-11-20 01:30 | 475 | 474
2017-11-20 02:00 | 466 | 465
2017-11-20 02:30 | 455 | 454
2017-11-20 03:00 | 448 | 447
2017-11-20 03:30 | 451 | 450
2017-11-20 04:00 | 454 | 453
2017-11-20 04:30 | 452 | 451
2017-11-20 05:00 | 461 | 460
2017-11-20 05:30 | 476 | 475
2017-11-20 06:00 | 488 | 488
2017-11-20 06:30 | 518 | 517
2017-11-20 07:00 | 533 | 533
2017-11-20 07:30 | 550 | 550
2017-11-20 08:00 | 573 | 573
2017-11-20 08:30 | 573 | 573
2017-11-20 09:00 | 581 | 581
2017-11-20 09:30 | 580 | 580
2017-11-20 10:00 | 580 | 580
2017-11-20 10:30 | 568 | 568
2017-11-20 11:00 | 559 | 559
2017-11-20 11:30 | 560 | 560
2017-11-20 12:00 | 563 | 563
2017-11-20 12:30 | 556 | 556
2017-11-20 13:00 | 564 | 564
2017-11-20 13:30 | 561 | 560
2017-11-20 14:00 | 561 | 561
2017-11-20 14:30 | 574 | 574
2017-11-20 15:00 | 579 | 578
2017-11-20 15:30 | 582 | 582
2017-11-20 16:00 | 582 | 582
2017-11-20 16:30 | 586 | 586
2017-11-20 17:00 | 591 | 591
2017-11-20 17:30 | 597 | 597
2017-11-20 18:00 | 630 | 630
2017-11-20 18:30 | 646 | 645
2017-11-20 19:00 | 665 | 665
2017-11-20 19:30 | 658 | 657
2017-11-20 20:00 | 648 | 648
2017-11-20 20:30 | 620 | 620
2017-11-20 21:00 | 600 | 600
2017-11-20 21:30 | 580 | 580
2017-11-20 22:00 | 564 | 563
2017-11-20 22:30 | 535 | 534
2017-11-20 23:00 | 535 | 534
2017-11-20 23:30 | 523 | 522
2017-11-21 | 499 | 498
2017-11-21 00:30 | 488 | 487
2017-11-21 01:00 | 480 | 479
2017-11-21 01:30 | 468 | 467
2017-11-21 02:00 | 460 | 458
2017-11-21 02:30 | 461 | 459
2017-11-21 03:00 | 455 | 453
2017-11-21 03:30 | 455 | 453
2017-11-21 04:00 | 454 | 452
2017-11-21 04:30 | 458 | 456
2017-11-21 05:00 | 461 | 459
2017-11-21 05:30 | 476 | 474
2017-11-21 06:00 | 487 | 486
2017-11-21 06:30 | 515 | 513
2017-11-21 07:00 | 527 | 526
2017-11-21 07:30 | 568 | 567
2017-11-21 08:00 | 577 | 577
2017-11-21 08:30 | 594 | 594
2017-11-21 09:00 | 595 | 595
2017-11-21 09:30 | 586 | 586
2017-11-21 10:00 | 581 | 581
2017-11-21 10:30 | 586 | 586
2017-11-21 11:00 | 593 | 593
2017-11-21 11:30 | 565 | 565
2017-11-21 12:00 | 558 | 557
2017-11-21 12:30 | 549 | 549
2017-11-21 13:00 | 554 | 553
2017-11-21 13:30 | 560 | 559
2017-11-21 14:00 | 560 | 559
2017-11-21 14:30 | 556 | 555
2017-11-21 15:00 | 553 | 553
2017-11-21 15:30 | 551 | 551
2017-11-21 16:00 | 557 | 556
2017-11-21 16:30 | 570 | 569
2017-11-21 17:00 | 581 | 581
2017-11-21 17:30 | 574 | 573
2017-11-21 18:00 | 600 | 600
2017-11-21 18:30 | 625 | 625
2017-11-21 19:00 | 643 | 643
2017-11-21 19:30 | 630 | 630
2017-11-21 20:00 | 617 | 617
2017-11-21 20:30 | 602 | 602
2017-11-21 21:00 | 577 | 577
2017-11-21 21:30 | 557 | 557
2017-11-21 22:00 | 542 | 542
2017-11-21 22:30 | 530 | 529
2017-11-21 23:00 | 531 | 530
2017-11-21 23:30 | 514 | 513
2017-11-22 | 493 | 492
2017-11-22 00:30 | 477 | 475
2017-11-22 01:00 | 467 | 465
2017-11-22 01:30 | 459 | 457
2017-11-22 02:00 | 458 | 455
2017-11-22 02:30 | 454 | 452
2017-11-22 03:00 | 439 | 437
2017-11-22 03:30 | 445 | 443
2017-11-22 04:00 | 446 | 444
2017-11-22 04:30 | 444 | 442
2017-11-22 05:00 | 451 | 449
2017-11-22 05:30 | 457 | 455
2017-11-22 06:00 | 472 | 470
2017-11-22 06:30 | 491 | 490
2017-11-22 07:00 | 503 | 501
2017-11-22 07:30 | 535 | 534
2017-11-22 08:00 | 537 | 536
2017-11-22 08:30 | 539 | 539
2017-11-22 09:00 | 544 | 544
2017-11-22 09:30 | 548 | 547
2017-11-22 10:00 | 552 | 551
2017-11-22 10:30 | 549 | 549
2017-11-22 11:00 | 545 | 544
2017-11-22 11:30 | 555 | 555
2017-11-22 12:00 | 548 | 547
2017-11-22 12:30 | 549 | 549
2017-11-22 13:00 | 571 | 570
2017-11-22 13:30 | 589 | 589
2017-11-22 14:00 | 599 | 599
2017-11-22 14:30 | 601 | 601
2017-11-22 15:00 | 610 | 610
2017-11-22 15:30 | 607 | 607
2017-11-22 16:00 | 602 | 601
2017-11-22 16:30 | 614 | 614
2017-11-22 17:00 | 626 | 626
2017-11-22 17:30 | 631 | 631
2017-11-22 18:00 | 640 | 640
2017-11-22 18:30 | 648 | 648
2017-11-22 19:00 | 657 | 657
2017-11-22 19:30 | 650 | 650
2017-11-22 20:00 | 635 | 635
2017-11-22 20:30 | 614 | 614
2017-11-22 21:00 | 594 | 594
2017-11-22 21:30 | 573 | 573
2017-11-22 22:00 | 546 | 545
2017-11-22 22:30 | 510 | 509
2017-11-22 23:00 | 491 | 490
2017-11-22 23:30 | 471 | 469
2017-11-23 | 460 | 458
2017-11-23 00:30 | 453 | 450
2017-11-23 01:00 | 461 | 459
2017-11-23 01:30 | 479 | 477
2017-11-23 02:00 | 475 | 473
2017-11-23 02:30 | 470 | 468
2017-11-23 03:00 | 467 | 465
2017-11-23 03:30 | 467 | 465
2017-11-23 04:00 | 465 | 463
2017-11-23 04:30 | 465 | 463
2017-11-23 05:00 | 477 | 475
2017-11-23 05:30 | 493 | 491
2017-11-23 06:00 | 504 | 502
2017-11-23 06:30 | 531 | 530
2017-11-23 07:00 | 537 | 536
2017-11-23 07:30 | 553 | 552
2017-11-23 08:00 | 566 | 565
2017-11-23 08:30 | 576 | 575
2017-11-23 09:00 | 573 | 573
2017-11-23 09:30 | 563 | 563
2017-11-23 10:00 | 542 | 542
2017-11-23 10:30 | 548 | 547
2017-11-23 11:00 | 551 | 550
2017-11-23 11:30 | 545 | 544
2017-11-23 12:00 | 549 | 548
2017-11-23 12:30 | 551 | 550
2017-11-23 13:00 | 561 | 560
2017-11-23 13:30 | 548 | 547
2017-11-23 14:00 | 550 | 549
2017-11-23 14:30 | 578 | 577
2017-11-23 15:00 | 578 | 577
2017-11-23 15:30 | 561 | 561
2017-11-23 16:00 | 582 | 582
2017-11-23 16:30 | 595 | 595
2017-11-23 17:00 | 601 | 601
2017-11-23 17:30 | 601 | 601
2017-11-23 18:00 | 632 | 632
2017-11-23 18:30 | 645 | 645
2017-11-23 19:00 | 664 | 664
2017-11-23 19:30 | 666 | 666
2017-11-23 20:00 | 657 | 657
2017-11-23 20:30 | 639 | 639
2017-11-23 21:00 | 617 | 617
2017-11-23 21:30 | 589 | 588
2017-11-23 22:00 | 560 | 560
2017-11-23 22:30 | 564 | 563
2017-11-23 23:00 | 556 | 555
2017-11-23 23:30 | 531 | 531
2017-11-24 | 517 | 516
2017-11-24 00:30 | 500 | 498
2017-11-24 01:00 | 488 | 487
2017-11-24 01:30 | 479 | 477
2017-11-24 02:00 | 476 | 474
2017-11-24 02:30 | 473 | 471
2017-11-24 03:00 | 469 | 467
2017-11-24 03:30 | 465 | 462
2017-11-24 04:00 | 473 | 471
2017-11-24 04:30 | 478 | 476
2017-11-24 05:00 | 476 | 474
2017-11-24 05:30 | 483 | 481
2017-11-24 06:00 | 502 | 500
2017-11-24 06:30 | 534 | 533
2017-11-24 07:00 | 548 | 547
2017-11-24 07:30 | 566 | 565
2017-11-24 08:00 | 577 | 577
2017-11-24 08:30 | 577 | 577
2017-11-24 09:00 | 567 | 567
2017-11-24 09:30 | 566 | 565
2017-11-24 10:00 | 570 | 570
2017-11-24 10:30 | 573 | 573
2017-11-24 11:00 | 562 | 562
2017-11-24 11:30 | 567 | 566
2017-11-24 12:00 | 587 | 587
2017-11-24 12:30 | 589 | 589
2017-11-24 13:00 | 601 | 601
2017-11-24 13:30 | 605 | 605
2017-11-24 14:00 | 544 | 544
2017-11-24 14:30 | 478 | 477
2017-11-24 15:00 | 489 | 487
2017-11-24 15:30 | 483 | 482
2017-11-24 16:00 | 462 | 461
2017-11-24 16:30 | 461 | 460
2017-11-24 17:00 | 465 | 464
2017-11-24 17:30 | 473 | 471
2017-11-24 18:00 | 471 | 470
2017-11-24 18:30 | 472 | 471
2017-11-24 19:00 | 482 | 481
2017-11-24 19:30 | 480 | 479
2017-11-24 20:00 | 465 | 464
2017-11-24 20:30 | 488 | 487
2017-11-24 21:00 | 483 | 482
2017-11-24 21:30 | 464 | 462
2017-11-24 22:00 | 463 | 461
2017-11-24 22:30 | 439 | 437
2017-11-24 23:00 | 429 | 427
2017-11-24 23:30 | 411 | 408
2017-11-25 | 514 | 511
2017-11-25 00:30 | 513 | 512
2017-11-25 01:00 | 501 | 500
2017-11-25 01:30 | 491 | 490
2017-11-25 02:00 | 488 | 487
2017-11-25 02:30 | 484 | 483
2017-11-25 03:00 | 478 | 476
2017-11-25 03:30 | 475 | 473
2017-11-25 04:00 | 469 | 468
2017-11-25 04:30 | 470 | 468
2017-11-25 05:00 | 471 | 469
2017-11-25 05:30 | 475 | 473
2017-11-25 06:00 | 478 | 476
2017-11-25 06:30 | 486 | 485
2017-11-25 07:00 | 491 | 490
2017-11-25 07:30 | 488 | 487
2017-11-25 08:00 | 491 | 490
2017-11-25 08:30 | 511 | 510
2017-11-25 09:00 | 526 | 525
2017-11-25 09:30 | 529 | 528
2017-11-25 10:00 | 528 | 527
2017-11-25 10:30 | 527 | 526
2017-11-25 11:00 | 528 | 527
2017-11-25 11:30 | 522 | 521
2017-11-25 12:00 | 521 | 520
2017-11-25 12:30 | 517 | 516
2017-11-25 13:00 | 528 | 527
2017-11-25 13:30 | 543 | 543
2017-11-25 14:00 | 552 | 551
2017-11-25 14:30 | 562 | 562
2017-11-25 15:00 | 570 | 569
2017-11-25 15:30 | 559 | 558
2017-11-25 16:00 | 570 | 570
2017-11-25 16:30 | 589 | 589
2017-11-25 17:00 | 593 | 593
2017-11-25 17:30 | 607 | 607
2017-11-25 18:00 | 610 | 610
2017-11-25 18:30 | 606 | 606
2017-11-25 19:00 | 614 | 614
2017-11-25 19:30 | 636 | 636
2017-11-25 20:00 | 622 | 622
2017-11-25 20:30 | 604 | 604
2017-11-25 21:00 | 592 | 592
2017-11-25 21:30 | 590 | 590
2017-11-25 22:00 | 586 | 586
2017-11-25 22:30 | 563 | 563
2017-11-25 23:00 | 558 | 558
2017-11-25 23:30 | 539 | 539
2017-11-26 | 521 | 520
2017-11-26 00:30 | 508 | 507
2017-11-26 01:00 | 499 | 498
2017-11-26 01:30 | 487 | 486
2017-11-26 02:00 | 475 | 473
2017-11-26 02:30 | 466 | 464
2017-11-26 03:00 | 465 | 464
2017-11-26 03:30 | 463 | 461
2017-11-26 04:00 | 460 | 458
2017-11-26 04:30 | 454 | 452
2017-11-26 05:00 | 457 | 455
2017-11-26 05:30 | 455 | 452
2017-11-26 06:00 | 448 | 446
2017-11-26 06:30 | 456 | 454
2017-11-26 07:00 | 451 | 449
2017-11-26 07:30 | 445 | 443
2017-11-26 08:00 | 452 | 450
2017-11-26 08:30 | 463 | 461
2017-11-26 09:00 | 477 | 475
2017-11-26 09:30 | 481 | 480
2017-11-26 10:00 | 484 | 482
2017-11-26 10:30 | 491 | 490
2017-11-26 11:00 | 488 | 486
2017-11-26 11:30 | 487 | 485
2017-11-26 12:00 | 491 | 489
2017-11-26 12:30 | 516 | 515
2017-11-26 13:00 | 530 | 529
2017-11-26 13:30 | 532 | 531
2017-11-26 14:00 | 534 | 533
2017-11-26 14:30 | 553 | 552
2017-11-26 15:00 | 558 | 557
2017-11-26 15:30 | 557 | 557
2017-11-26 16:00 | 549 | 548
2017-11-26 16:30 | 561 | 560
2017-11-26 17:00 | 586 | 586
2017-11-26 17:30 | 613 | 613
2017-11-26 18:00 | 646 | 646
2017-11-26 18:30 | 654 | 654
2017-11-26 19:00 | 671 | 671
2017-11-26 19:30 | 677 | 677
2017-11-26 20:00 | 659 | 659
2017-11-26 20:30 | 588 | 588
2017-11-26 21:00 | 536 | 536
2017-11-26 21:30 | 557 | 556
2017-11-26 22:00 | 574 | 573
2017-11-26 22:30 | 559 | 558
2017-11-26 23:00 | 555 | 554
2017-11-26 23:30 | 541 | 540
2017-11-27 | 521 | 520
2017-11-27 00:30 | 510 | 509
2017-11-27 01:00 | 495 | 493
2017-11-27 01:30 | 488 | 486
2017-11-27 02:00 | 481 | 479
2017-11-27 02:30 | 481 | 480
2017-11-27 03:00 | 483 | 482
2017-11-27 03:30 | 483 | 481
2017-11-27 04:00 | 479 | 477
2017-11-27 04:30 | 458 | 456
2017-11-27 05:00 | 414 | 411
2017-11-27 05:30 | 422 | 418
2017-11-27 06:00 | 432 | 428
2017-11-27 06:30 | 451 | 448
2017-11-27 07:00 | 468 | 465
2017-11-27 07:30 | 450 | 448
2017-11-27 08:00 | 427 | 424
2017-11-27 08:30 | 447 | 444
2017-11-27 09:00 | 453 | 450
2017-11-27 09:30 | 458 | 456
2017-11-27 10:00 | 459 | 457
2017-11-27 10:30 | 472 | 470
2017-11-27 11:00 | 491 | 490
2017-11-27 11:30 | 486 | 485
2017-11-27 12:00 | 478 | 476
2017-11-27 12:30 | 480 | 479
2017-11-27 13:00 | 497 | 495
2017-11-27 13:30 | 499 | 498
2017-11-27 14:00 | 501 | 500
2017-11-27 14:30 | 481 | 479
2017-11-27 15:00 | 465 | 464
2017-11-27 15:30 | 415 | 412
2017-11-27 16:00 | 401 | 398
2017-11-27 16:30 | 401 | 398
2017-11-27 17:00 | 418 | 414
2017-11-27 17:30 | 428 | 425
2017-11-27 18:00 | 432 | 429
2017-11-27 18:30 | 436 | 433
2017-11-27 19:00 | 447 | 444
2017-11-27 19:30 | 451 | 448
2017-11-27 20:00 | 436 | 434
2017-11-27 20:30 | 454 | 451
2017-11-27 21:00 | 505 | 503
2017-11-27 21:30 | 491 | 489
2017-11-27 22:00 | 479 | 477
2017-11-27 22:30 | 444 | 442
2017-11-27 23:00 | 436 | 433
2017-11-27 23:30 | 414 | 411
2017-11-28 | 445 | 441
2017-11-28 00:30 | 517 | 515
2017-11-28 01:00 | 510 | 508
2017-11-28 01:30 | 495 | 493
2017-11-28 02:00 | 489 | 488
2017-11-28 02:30 | 486 | 485
2017-11-28 03:00 | 483 | 482
2017-11-28 03:30 | 477 | 475
2017-11-28 04:00 | 475 | 474
2017-11-28 04:30 | 476 | 474
2017-11-28 05:00 | 482 | 480
2017-11-28 05:30 | 494 | 493
2017-11-28 06:00 | 505 | 503
2017-11-28 06:30 | 536 | 535
2017-11-28 07:00 | 548 | 547
2017-11-28 07:30 | 559 | 559
2017-11-28 08:00 | 556 | 555
2017-11-28 08:30 | 560 | 560
2017-11-28 09:00 | 573 | 573
2017-11-28 09:30 | 573 | 572
2017-11-28 10:00 | 564 | 564
2017-11-28 10:30 | 566 | 565
2017-11-28 11:00 | 581 | 581
2017-11-28 11:30 | 583 | 583
2017-11-28 12:00 | 582 | 582
2017-11-28 12:30 | 593 | 593
2017-11-28 13:00 | 597 | 597
2017-11-28 13:30 | 651 | 651
2017-11-28 14:00 | 662 | 662
2017-11-28 14:30 | 662 | 661
2017-11-28 15:00 | 662 | 662
2017-11-28 15:30 | 650 | 650
2017-11-28 16:00 | 642 | 642
2017-11-28 16:30 | 645 | 645
2017-11-28 17:00 | 648 | 648
2017-11-28 17:30 | 647 | 647
2017-11-28 18:00 | 674 | 674
2017-11-28 18:30 | 690 | 690
2017-11-28 19:00 | 713 | 713
2017-11-28 19:30 | 716 | 716
2017-11-28 20:00 | 703 | 703
2017-11-28 20:30 | 682 | 682
2017-11-28 21:00 | 633 | 633
2017-11-28 21:30 | 579 | 579
2017-11-28 22:00 | 562 | 562
2017-11-28 22:30 | 567 | 566
2017-11-28 23:00 | 554 | 554
2017-11-28 23:30 | 529 | 529
2017-11-29 | 501 | 500
2017-11-29 00:30 | 492 | 491
2017-11-29 01:00 | 482 | 480
2017-11-29 01:30 | 477 | 475
2017-11-29 02:00 | 468 | 467
2017-11-29 02:30 | 467 | 465
2017-11-29 03:00 | 463 | 461
2017-11-29 03:30 | 453 | 451
2017-11-29 04:00 | 453 | 451
2017-11-29 04:30 | 460 | 458
2017-11-29 05:00 | 467 | 465
2017-11-29 05:30 | 479 | 478
2017-11-29 06:00 | 493 | 491
2017-11-29 06:30 | 525 | 524
2017-11-29 07:00 | 553 | 552
2017-11-29 07:30 | 593 | 593
2017-11-29 08:00 | 605 | 604
2017-11-29 08:30 | 611 | 611
2017-11-29 09:00 | 615 | 615
2017-11-29 09:30 | 624 | 624
2017-11-29 10:00 | 600 | 600
2017-11-29 10:30 | 582 | 581
2017-11-29 11:00 | 603 | 602
2017-11-29 11:30 | 604 | 604
2017-11-29 12:00 | 609 | 609
2017-11-29 12:30 | 604 | 604
2017-11-29 13:00 | 629 | 629
2017-11-29 13:30 | 618 | 618
2017-11-29 14:00 | 619 | 619
2017-11-29 14:30 | 630 | 630
2017-11-29 15:00 | 649 | 649
2017-11-29 15:30 | 650 | 649
2017-11-29 16:00 | 654 | 654
2017-11-29 16:30 | 639 | 638
2017-11-29 17:00 | 644 | 644
2017-11-29 17:30 | 671 | 671
2017-11-29 18:00 | 674 | 674
2017-11-29 18:30 | 687 | 687
2017-11-29 19:00 | 719 | 719
2017-11-29 19:30 | 734 | 734
2017-11-29 20:00 | 719 | 719
2017-11-29 20:30 | 693 | 693
2017-11-29 21:00 | 673 | 672
2017-11-29 21:30 | 642 | 642
2017-11-29 22:00 | 620 | 620
2017-11-29 22:30 | 603 | 603
2017-11-29 23:00 | 608 | 607
2017-11-29 23:30 | 597 | 596
2017-11-30 | 573 | 572
2017-11-30 00:30 | 553 | 552
2017-11-30 01:00 | 542 | 541
2017-11-30 01:30 | 528 | 527
2017-11-30 02:00 | 520 | 519
2017-11-30 02:30 | 518 | 518
2017-11-30 03:00 | 523 | 522
2017-11-30 03:30 | 502 | 501
2017-11-30 04:00 | 498 | 497
2017-11-30 04:30 | 502 | 501
2017-11-30 05:00 | 501 | 500
2017-11-30 05:30 | 511 | 510
2017-11-30 06:00 | 522 | 521
2017-11-30 06:30 | 555 | 554
2017-11-30 07:00 | 569 | 568
2017-11-30 07:30 | 579 | 578
2017-11-30 08:00 | 606 | 605
2017-11-30 08:30 | 622 | 621
2017-11-30 09:00 | 623 | 623
2017-11-30 09:30 | 634 | 634
2017-11-30 10:00 | 630 | 629
2017-11-30 10:30 | 625 | 624
2017-11-30 11:00 | 627 | 627
2017-11-30 11:30 | 646 | 646
2017-11-30 12:00 | 647 | 647
2017-11-30 12:30 | 648 | 648
2017-11-30 13:00 | 565 | 564
2017-11-30 13:30 | 504 | 503
2017-11-30 14:00 | 495 | 494
2017-11-30 14:30 | 501 | 500
2017-11-30 15:00 | 507 | 506
2017-11-30 15:30 | 510 | 509
2017-11-30 16:00 | 484 | 483
2017-11-30 16:30 | 499 | 498
2017-11-30 17:00 | 515 | 514
2017-11-30 17:30 | 530 | 529
2017-11-30 18:00 | 537 | 536
2017-11-30 18:30 | 545 | 544
2017-11-30 19:00 | 560 | 559
2017-11-30 19:30 | 583 | 582
2017-11-30 20:00 | 573 | 573
2017-11-30 20:30 | 577 | 577
2017-11-30 21:00 | 554 | 553
2017-11-30 21:30 | 526 | 526
2017-11-30 22:00 | 510 | 510
2017-11-30 22:30 | 484 | 483
2017-11-30 23:00 | 591 | 590
2017-11-30 23:30 | 599 | 598
2017-12-01 | 579 | 578
2017-12-01 00:30 | 560 | 559
2017-12-01 01:00 | 535 | 535
2017-12-01 01:30 | 530 | 529
2017-12-01 02:00 | 524 | 523
2017-12-01 02:30 | 524 | 522
2017-12-01 03:00 | 518 | 517
2017-12-01 03:30 | 515 | 514
2017-12-01 04:00 | 509 | 508
2017-12-01 04:30 | 510 | 509
2017-12-01 05:00 | 517 | 516
2017-12-01 05:30 | 528 | 527
2017-12-01 06:00 | 542 | 541
2017-12-01 06:30 | 575 | 574
2017-12-01 07:00 | 585 | 584
2017-12-01 07:30 | 601 | 600
2017-12-01 08:00 | 618 | 617
2017-12-01 08:30 | 602 | 602
2017-12-01 09:00 | 602 | 602
2017-12-01 09:30 | 626 | 625
2017-12-01 10:00 | 632 | 632
2017-12-01 10:30 | 631 | 631
2017-12-01 11:00 | 632 | 632
2017-12-01 11:30 | 627 | 627
2017-12-01 12:00 | 644 | 644
2017-12-01 12:30 | 637 | 637
2017-12-01 13:00 | 553 | 553
2017-12-01 13:30 | 512 | 511
2017-12-01 14:00 | 519 | 518
2017-12-01 14:30 | 511 | 510
2017-12-01 15:00 | 515 | 514
2017-12-01 15:30 | 499 | 498
2017-12-01 16:00 | 493 | 492
2017-12-01 16:30 | 518 | 517
2017-12-01 17:00 | 528 | 527
2017-12-01 17:30 | 524 | 522
2017-12-01 18:00 | 530 | 529
2017-12-01 18:30 | 536 | 535
2017-12-01 19:00 | 549 | 548
2017-12-01 19:30 | 555 | 554
2017-12-01 20:00 | 549 | 548
2017-12-01 20:30 | 548 | 547
2017-12-01 21:00 | 647 | 646
2017-12-01 21:30 | 669 | 669
2017-12-01 22:00 | 660 | 660
2017-12-01 22:30 | 639 | 639
2017-12-01 23:00 | 626 | 626
2017-12-01 23:30 | 605 | 604
2017-12-02 | 586 | 586
2017-12-02 00:30 | 571 | 570
2017-12-02 01:00 | 542 | 541
2017-12-02 01:30 | 532 | 531
2017-12-02 02:00 | 521 | 520
2017-12-02 02:30 | 517 | 516
2017-12-02 03:00 | 516 | 515
2017-12-02 03:30 | 514 | 513
2017-12-02 04:00 | 514 | 513
2017-12-02 04:30 | 511 | 509
2017-12-02 05:00 | 518 | 517
2017-12-02 05:30 | 526 | 525
2017-12-02 06:00 | 525 | 524
2017-12-02 06:30 | 541 | 540
2017-12-02 07:00 | 538 | 537
2017-12-02 07:30 | 537 | 536
2017-12-02 08:00 | 551 | 550
2017-12-02 08:30 | 566 | 565
2017-12-02 09:00 | 583 | 582
2017-12-02 09:30 | 593 | 593
2017-12-02 10:00 | 591 | 590
2017-12-02 10:30 | 605 | 605
2017-12-02 11:00 | 605 | 604
2017-12-02 11:30 | 599 | 599
2017-12-02 12:00 | 610 | 610
2017-12-02 12:30 | 613 | 613
2017-12-02 13:00 | 621 | 621
2017-12-02 13:30 | 634 | 634
2017-12-02 14:00 | 643 | 643
2017-12-02 14:30 | 645 | 645
2017-12-02 15:00 | 666 | 666
2017-12-02 15:30 | 674 | 674
2017-12-02 16:00 | 674 | 674
2017-12-02 16:30 | 670 | 670
2017-12-02 17:00 | 677 | 677
2017-12-02 17:30 | 698 | 698
2017-12-02 18:00 | 702 | 702
2017-12-02 18:30 | 705 | 705
2017-12-02 19:00 | 719 | 719
2017-12-02 19:30 | 727 | 727
2017-12-02 20:00 | 712 | 711
2017-12-02 20:30 | 714 | 714
2017-12-02 21:00 | 691 | 690
2017-12-02 21:30 | 676 | 676
2017-12-02 22:00 | 655 | 655
2017-12-02 22:30 | 633 | 633
2017-12-02 23:00 | 645 | 645
2017-12-02 23:30 | 615 | 615
2017-12-03 | 599 | 599
2017-12-03 00:30 | 576 | 575
2017-12-03 01:00 | 563 | 562
2017-12-03 01:30 | 554 | 553
2017-12-03 02:00 | 548 | 546
2017-12-03 02:30 | 536 | 534
2017-12-03 03:00 | 534 | 533
2017-12-03 03:30 | 534 | 533
2017-12-03 04:00 | 531 | 530
2017-12-03 04:30 | 527 | 525
2017-12-03 05:00 | 528 | 527
2017-12-03 05:30 | 530 | 528
2017-12-03 06:00 | 524 | 523
2017-12-03 06:30 | 528 | 527
2017-12-03 07:00 | 532 | 531
2017-12-03 07:30 | 518 | 517
2017-12-03 08:00 | 525 | 523
2017-12-03 08:30 | 535 | 534
2017-12-03 09:00 | 555 | 554
2017-12-03 09:30 | 560 | 559
2017-12-03 10:00 | 574 | 574
2017-12-03 10:30 | 574 | 573
2017-12-03 11:00 | 586 | 585
2017-12-03 11:30 | 590 | 590
2017-12-03 12:00 | 601 | 600
2017-12-03 12:30 | 609 | 609
2017-12-03 13:00 | 635 | 635
2017-12-03 13:30 | 651 | 651
2017-12-03 14:00 | 661 | 661
2017-12-03 14:30 | 678 | 678
2017-12-03 15:00 | 676 | 676
2017-12-03 15:30 | 681 | 681
2017-12-03 16:00 | 666 | 666
2017-12-03 16:30 | 669 | 669
2017-12-03 17:00 | 684 | 684
2017-12-03 17:30 | 696 | 696
2017-12-03 18:00 | 721 | 721
2017-12-03 18:30 | 734 | 734
2017-12-03 19:00 | 730 | 730
2017-12-03 19:30 | 744 | 744
2017-12-03 20:00 | 729 | 729
2017-12-03 20:30 | 734 | 734
2017-12-03 21:00 | 705 | 705
2017-12-03 21:30 | 679 | 679
2017-12-03 22:00 | 646 | 646
2017-12-03 22:30 | 625 | 625
2017-12-03 23:00 | 622 | 622
2017-12-03 23:30 | 591 | 590
2017-12-04 | 567 | 566
2017-12-04 00:30 | 546 | 544
2017-12-04 01:00 | 526 | 524
2017-12-04 01:30 | 511 | 509
2017-12-04 02:00 | 500 | 498
2017-12-04 02:30 | 487 | 484
2017-12-04 03:00 | 484 | 481
2017-12-04 03:30 | 474 | 471
2017-12-04 04:00 | 473 | 470
2017-12-04 04:30 | 480 | 477
2017-12-04 05:00 | 484 | 481
2017-12-04 05:30 | 494 | 492
2017-12-04 06:00 | 505 | 502
2017-12-04 06:30 | 526 | 524
2017-12-04 07:00 | 555 | 553
2017-12-04 07:30 | 571 | 570
2017-12-04 08:00 | 597 | 597
2017-12-04 08:30 | 616 | 615
2017-12-04 09:00 | 619 | 619
2017-12-04 09:30 | 622 | 622
2017-12-04 10:00 | 615 | 615
2017-12-04 10:30 | 614 | 614
2017-12-04 11:00 | 590 | 590
2017-12-04 11:30 | 577 | 577
2017-12-04 12:00 | 569 | 569
2017-12-04 12:30 | 572 | 572
2017-12-04 13:00 | 586 | 586
2017-12-04 13:30 | 604 | 604
2017-12-04 14:00 | 616 | 616
2017-12-04 14:30 | 626 | 626
2017-12-04 15:00 | 637 | 637
2017-12-04 15:30 | 637 | 637
2017-12-04 16:00 | 636 | 636
2017-12-04 16:30 | 657 | 657
2017-12-04 17:00 | 661 | 661
2017-12-04 17:30 | 660 | 660
2017-12-04 18:00 | 699 | 699
2017-12-04 18:30 | 727 | 727
2017-12-04 19:00 | 761 | 760
2017-12-04 19:30 | 766 | 765
2017-12-04 20:00 | 748 | 747
2017-12-04 20:30 | 713 | 713
2017-12-04 21:00 | 675 | 675
2017-12-04 21:30 | 635 | 635
2017-12-04 22:00 | 632 | 632
2017-12-04 22:30 | 593 | 593
2017-12-04 23:00 | 600 | 600
2017-12-04 23:30 | 569 | 569
2017-12-05 | 561 | 561
2017-12-05 00:30 | 562 | 562
2017-12-05 01:00 | 543 | 543
2017-12-05 01:30 | 531 | 530
2017-12-05 02:00 | 523 | 522
2017-12-05 02:30 | 515 | 514
2017-12-05 03:00 | 500 | 499
2017-12-05 03:30 | 488 | 487
2017-12-05 04:00 | 469 | 467
2017-12-05 04:30 | 466 | 464
2017-12-05 05:00 | 466 | 463
2017-12-05 05:30 | 474 | 472
2017-12-05 06:00 | 483 | 481
2017-12-05 06:30 | 487 | 485
2017-12-05 07:00 | 506 | 504
2017-12-05 07:30 | 531 | 530
2017-12-05 08:00 | 542 | 541
2017-12-05 08:30 | 548 | 548
2017-12-05 09:00 | 556 | 555
2017-12-05 09:30 | 554 | 554
2017-12-05 10:00 | 550 | 550
2017-12-05 10:30 | 549 | 548
2017-12-05 11:00 | 563 | 563
2017-12-05 11:30 | 586 | 586
2017-12-05 12:00 | 585 | 585
2017-12-05 12:30 | 596 | 596
2017-12-05 13:00 | 606 | 606
2017-12-05 13:30 | 627 | 627
2017-12-05 14:00 | 635 | 635
2017-12-05 14:30 | 675 | 675
2017-12-05 15:00 | 688 | 688
2017-12-05 15:30 | 671 | 671
2017-12-05 16:00 | 665 | 665
2017-12-05 16:30 | 681 | 681
2017-12-05 17:00 | 618 | 618
2017-12-05 17:30 | 644 | 644
2017-12-05 18:00 | 656 | 656
2017-12-05 18:30 | 673 | 673
2017-12-05 19:00 | 679 | 679
2017-12-05 19:30 | 693 | 693
2017-12-05 20:00 | 683 | 683
2017-12-05 20:30 | 721 | 721
2017-12-05 21:00 | 703 | 703
2017-12-05 21:30 | 691 | 691
2017-12-05 22:00 | 670 | 670
2017-12-05 22:30 | 635 | 635
2017-12-05 23:00 | 640 | 640
2017-12-05 23:30 | 618 | 618
2017-12-06 | 598 | 598
2017-12-06 00:30 | 577 | 576
2017-12-06 01:00 | 566 | 565
2017-12-06 01:30 | 566 | 566
2017-12-06 02:00 | 557 | 556
2017-12-06 02:30 | 556 | 556
2017-12-06 03:00 | 551 | 550
2017-12-06 03:30 | 549 | 548
2017-12-06 04:00 | 547 | 546
2017-12-06 04:30 | 540 | 539
2017-12-06 05:00 | 539 | 538
2017-12-06 05:30 | 544 | 544
2017-12-06 06:00 | 550 | 549
2017-12-06 06:30 | 558 | 557
2017-12-06 07:00 | 570 | 570
2017-12-06 07:30 | 583 | 582
2017-12-06 08:00 | 589 | 589
2017-12-06 08:30 | 606 | 606
2017-12-06 09:00 | 620 | 619
2017-12-06 09:30 | 611 | 611
2017-12-06 10:00 | 609 | 609
2017-12-06 10:30 | 618 | 617
2017-12-06 11:00 | 623 | 623
2017-12-06 11:30 | 633 | 633
2017-12-06 12:00 | 639 | 639
2017-12-06 12:30 | 653 | 653
2017-12-06 13:00 | 657 | 657
2017-12-06 13:30 | 669 | 669
2017-12-06 14:00 | 688 | 688
2017-12-06 14:30 | 699 | 699
2017-12-06 15:00 | 708 | 707
2017-12-06 15:30 | 703 | 702
2017-12-06 16:00 | 698 | 697
2017-12-06 16:30 | 709 | 709
2017-12-06 17:00 | 724 | 723
2017-12-06 17:30 | 732 | 731
2017-12-06 18:00 | 727 | 726
2017-12-06 18:30 | 733 | 732
2017-12-06 19:00 | 743 | 742
2017-12-06 19:30 | 760 | 759
2017-12-06 20:00 | 747 | 746
2017-12-06 20:30 | 745 | 744
2017-12-06 21:00 | 725 | 725
2017-12-06 21:30 | 711 | 710
2017-12-06 22:00 | 683 | 682
2017-12-06 22:30 | 647 | 647
2017-12-06 23:00 | 662 | 662
2017-12-06 23:30 | 639 | 639
2017-12-07 | 607 | 607
2017-12-07 00:30 | 594 | 594
2017-12-07 01:00 | 574 | 574
2017-12-07 01:30 | 563 | 563
2017-12-07 02:00 | 557 | 557
2017-12-07 02:30 | 550 | 549
2017-12-07 03:00 | 544 | 543
2017-12-07 03:30 | 540 | 540
2017-12-07 04:00 | 535 | 534
2017-12-07 04:30 | 542 | 541
2017-12-07 05:00 | 548 | 547
2017-12-07 05:30 | 560 | 559
2017-12-07 06:00 | 567 | 566
2017-12-07 06:30 | 580 | 580
2017-12-07 07:00 | 577 | 576
2017-12-07 07:30 | 587 | 587
2017-12-07 08:00 | 595 | 595
2017-12-07 08:30 | 602 | 602
2017-12-07 09:00 | 612 | 612
2017-12-07 09:30 | 603 | 603
2017-12-07 10:00 | 554 | 554
2017-12-07 10:30 | 544 | 544
2017-12-07 11:00 | 558 | 557
2017-12-07 11:30 | 557 | 557
2017-12-07 12:00 | 553 | 552
2017-12-07 12:30 | 529 | 529
2017-12-07 13:00 | 510 | 509
2017-12-07 13:30 | 524 | 523
2017-12-07 14:00 | 551 | 550
2017-12-07 14:30 | 553 | 552
2017-12-07 15:00 | 549 | 548
2017-12-07 15:30 | 546 | 545
2017-12-07 16:00 | 554 | 553
2017-12-07 16:30 | 559 | 559
2017-12-07 17:00 | 565 | 564
2017-12-07 17:30 | 585 | 585
2017-12-07 18:00 | 591 | 591
2017-12-07 18:30 | 596 | 595
2017-12-07 19:00 | 610 | 609
2017-12-07 19:30 | 626 | 626
2017-12-07 20:00 | 623 | 622
2017-12-07 20:30 | 620 | 620
2017-12-07 21:00 | 599 | 599
2017-12-07 21:30 | 586 | 586
2017-12-07 22:00 | 572 | 572
2017-12-07 22:30 | 537 | 536
2017-12-07 23:00 | 551 | 550
2017-12-07 23:30 | 530 | 530
2017-12-08 | 505 | 504
2017-12-08 00:30 | 490 | 489
2017-12-08 01:00 | 471 | 469
2017-12-08 01:30 | 462 | 459
2017-12-08 02:00 | 450 | 447
2017-12-08 02:30 | 447 | 444
2017-12-08 03:00 | 442 | 438
2017-12-08 03:30 | 432 | 428
2017-12-08 04:00 | 432 | 428
2017-12-08 04:30 | 436 | 432
2017-12-08 05:00 | 436 | 432
2017-12-08 05:30 | 446 | 443
2017-12-08 06:00 | 457 | 454
2017-12-08 06:30 | 462 | 459
2017-12-08 07:00 | 464 | 461
2017-12-08 07:30 | 473 | 470
2017-12-08 08:00 | 490 | 488
2017-12-08 08:30 | 498 | 496
2017-12-08 09:00 | 513 | 511
2017-12-08 09:30 | 512 | 511
2017-12-08 10:00 | 508 | 507
2017-12-08 10:30 | 508 | 507
2017-12-08 11:00 | 510 | 509
2017-12-08 11:30 | 509 | 508
2017-12-08 12:00 | 507 | 506
2017-12-08 12:30 | 517 | 516
2017-12-08 13:00 | 551 | 550
2017-12-08 13:30 | 575 | 574
2017-12-08 14:00 | 585 | 584
2017-12-08 14:30 | 597 | 597
2017-12-08 15:00 | 602 | 602
2017-12-08 15:30 | 584 | 584
2017-12-08 16:00 | 569 | 569
2017-12-08 16:30 | 583 | 583
2017-12-08 17:00 | 569 | 569
2017-12-08 17:30 | 564 | 563
2017-12-08 18:00 | 568 | 567
2017-12-08 18:30 | 561 | 561
2017-12-08 19:00 | 568 | 567
2017-12-08 19:30 | 577 | 577
2017-12-08 20:00 | 566 | 565
2017-12-08 20:30 | 609 | 608
2017-12-08 21:00 | 697 | 696
2017-12-08 21:30 | 682 | 682
2017-12-08 22:00 | 675 | 675
2017-12-08 22:30 | 652 | 652
2017-12-08 23:00 | 665 | 665
2017-12-08 23:30 | 645 | 645
2017-12-09 | 623 | 623
2017-12-09 00:30 | 597 | 596
2017-12-09 01:00 | 579 | 578
2017-12-09 01:30 | 566 | 566
2017-12-09 02:00 | 561 | 561
2017-12-09 02:30 | 552 | 551
2017-12-09 03:00 | 544 | 543
2017-12-09 03:30 | 541 | 540
2017-12-09 04:00 | 536 | 535
2017-12-09 04:30 | 532 | 531
2017-12-09 05:00 | 537 | 536
2017-12-09 05:30 | 540 | 539
2017-12-09 06:00 | 535 | 535
2017-12-09 06:30 | 521 | 520
2017-12-09 07:00 | 511 | 510
2017-12-09 07:30 | 506 | 505
2017-12-09 08:00 | 522 | 521
2017-12-09 08:30 | 543 | 542
2017-12-09 09:00 | 558 | 557
2017-12-09 09:30 | 566 | 565
2017-12-09 10:00 | 563 | 562
2017-12-09 10:30 | 562 | 561
2017-12-09 11:00 | 561 | 561
2017-12-09 11:30 | 559 | 559
2017-12-09 12:00 | 573 | 572
2017-12-09 12:30 | 579 | 579
2017-12-09 13:00 | 587 | 586
2017-12-09 13:30 | 591 | 591
2017-12-09 14:00 | 603 | 603
2017-12-09 14:30 | 618 | 618
2017-12-09 15:00 | 629 | 629
2017-12-09 15:30 | 630 | 630
2017-12-09 16:00 | 621 | 621
2017-12-09 16:30 | 642 | 642
2017-12-09 17:00 | 658 | 658
2017-12-09 17:30 | 670 | 670
2017-12-09 18:00 | 674 | 674
2017-12-09 18:30 | 674 | 674
2017-12-09 19:00 | 681 | 681
2017-12-09 19:30 | 688 | 688
2017-12-09 20:00 | 672 | 672
2017-12-09 20:30 | 679 | 679
2017-12-09 21:00 | 662 | 662
2017-12-09 21:30 | 639 | 638
2017-12-09 22:00 | 629 | 628
2017-12-09 22:30 | 607 | 607
2017-12-09 23:00 | 618 | 618
2017-12-09 23:30 | 606 | 606
2017-12-10 | 588 | 587
2017-12-10 00:30 | 573 | 572
2017-12-10 01:00 | 558 | 557
2017-12-10 01:30 | 553 | 552
2017-12-10 02:00 | 546 | 545
2017-12-10 02:30 | 540 | 539
2017-12-10 03:00 | 532 | 531
2017-12-10 03:30 | 525 | 524
2017-12-10 04:00 | 518 | 517
2017-12-10 04:30 | 521 | 520
2017-12-10 05:00 | 520 | 519
2017-12-10 05:30 | 525 | 524
2017-12-10 06:00 | 516 | 515
2017-12-10 06:30 | 493 | 493
2017-12-10 07:00 | 481 | 479
2017-12-10 07:30 | 480 | 479
2017-12-10 08:00 | 492 | 491
2017-12-10 08:30 | 502 | 501
2017-12-10 09:00 | 510 | 509
2017-12-10 09:30 | 524 | 523
2017-12-10 10:00 | 529 | 529
2017-12-10 10:30 | 537 | 537
2017-12-10 11:00 | 540 | 540
2017-12-10 11:30 | 549 | 549
2017-12-10 12:00 | 557 | 557
2017-12-10 12:30 | 560 | 560
2017-12-10 13:00 | 566 | 566
2017-12-10 13:30 | 577 | 577
2017-12-10 14:00 | 587 | 587
2017-12-10 14:30 | 590 | 590
2017-12-10 15:00 | 588 | 588
2017-12-10 15:30 | 600 | 600
2017-12-10 16:00 | 605 | 605
2017-12-10 16:30 | 614 | 614
2017-12-10 17:00 | 638 | 638
2017-12-10 17:30 | 658 | 658
2017-12-10 18:00 | 676 | 675
2017-12-10 18:30 | 680 | 680
2017-12-10 19:00 | 685 | 685
2017-12-10 19:30 | 698 | 697
2017-12-10 20:00 | 691 | 690
2017-12-10 20:30 | 705 | 704
2017-12-10 21:00 | 691 | 690
2017-12-10 21:30 | 669 | 668
2017-12-10 22:00 | 655 | 655
2017-12-10 22:30 | 625 | 625
2017-12-10 23:00 | 629 | 629
2017-12-10 23:30 | 608 | 608
2017-12-11 | 589 | 589
2017-12-11 00:30 | 571 | 571
2017-12-11 01:00 | 555 | 555
2017-12-11 01:30 | 542 | 542
2017-12-11 02:00 | 534 | 534
2017-12-11 02:30 | 529 | 529
2017-12-11 03:00 | 521 | 521
2017-12-11 03:30 | 519 | 518
2017-12-11 04:00 | 518 | 517
2017-12-11 04:30 | 520 | 519
2017-12-11 05:00 | 529 | 529
2017-12-11 05:30 | 538 | 538
2017-12-11 06:00 | 545 | 545
2017-12-11 06:30 | 545 | 544
2017-12-11 07:00 | 554 | 554
2017-12-11 07:30 | 570 | 570
2017-12-11 08:00 | 595 | 595
2017-12-11 08:30 | 601 | 601
2017-12-11 09:00 | 605 | 605
2017-12-11 09:30 | 594 | 594
2017-12-11 10:00 | 588 | 588
2017-12-11 10:30 | 586 | 586
2017-12-11 11:00 | 589 | 589
2017-12-11 11:30 | 594 | 594
2017-12-11 12:00 | 606 | 606
2017-12-11 12:30 | 609 | 609
2017-12-11 13:00 | 614 | 614
2017-12-11 13:30 | 633 | 633
2017-12-11 14:00 | 654 | 654
2017-12-11 14:30 | 659 | 658
2017-12-11 15:00 | 662 | 662
2017-12-11 15:30 | 654 | 654
2017-12-11 16:00 | 659 | 659
2017-12-11 16:30 | 674 | 674
2017-12-11 17:00 | 695 | 695
2017-12-11 17:30 | 689 | 689
2017-12-11 18:00 | 713 | 713
2017-12-11 18:30 | 729 | 729
2017-12-11 19:00 | 740 | 739
2017-12-11 19:30 | 738 | 737
2017-12-11 20:00 | 718 | 717
2017-12-11 20:30 | 689 | 689
2017-12-11 21:00 | 669 | 668
2017-12-11 21:30 | 643 | 642
2017-12-11 22:00 | 640 | 640
2017-12-11 22:30 | 604 | 604
2017-12-11 23:00 | 579 | 579
2017-12-11 23:30 | 558 | 558
2017-12-12 | 536 | 535
2017-12-12 00:30 | 557 | 556
2017-12-12 01:00 | 543 | 543
2017-12-12 01:30 | 530 | 530
2017-12-12 02:00 | 520 | 520
2017-12-12 02:30 | 515 | 514
2017-12-12 03:00 | 510 | 510
2017-12-12 03:30 | 513 | 513
2017-12-12 04:00 | 507 | 506
2017-12-12 04:30 | 508 | 507
2017-12-12 05:00 | 511 | 510
2017-12-12 05:30 | 522 | 522
2017-12-12 06:00 | 527 | 526
2017-12-12 06:30 | 556 | 556
2017-12-12 07:00 | 538 | 538
2017-12-12 07:30 | 528 | 528
2017-12-12 08:00 | 545 | 544
2017-12-12 08:30 | 559 | 559
2017-12-12 09:00 | 567 | 567
2017-12-12 09:30 | 574 | 574
2017-12-12 10:00 | 574 | 574
2017-12-12 10:30 | 570 | 570
2017-12-12 11:00 | 567 | 567
2017-12-12 11:30 | 575 | 575
2017-12-12 12:00 | 585 | 585
2017-12-12 12:30 | 584 | 584
2017-12-12 13:00 | 589 | 589
2017-12-12 13:30 | 594 | 593
2017-12-12 14:00 | 608 | 608
2017-12-12 14:30 | 617 | 617
2017-12-12 15:00 | 626 | 626
2017-12-12 15:30 | 626 | 625
2017-12-12 16:00 | 641 | 641
2017-12-12 16:30 | 656 | 655
2017-12-12 17:00 | 657 | 657
2017-12-12 17:30 | 650 | 649
2017-12-12 18:00 | 678 | 677
2017-12-12 18:30 | 693 | 692
2017-12-12 19:00 | 701 | 700
2017-12-12 19:30 | 720 | 719
2017-12-12 20:00 | 710 | 709
2017-12-12 20:30 | 687 | 686
2017-12-12 21:00 | 669 | 668
2017-12-12 21:30 | 644 | 644
2017-12-12 22:00 | 640 | 640
2017-12-12 22:30 | 611 | 611
2017-12-12 23:00 | 582 | 582
2017-12-12 23:30 | 558 | 558
2017-12-13 | 535 | 535
2017-12-13 00:30 | 549 | 548
2017-12-13 01:00 | 537 | 537
2017-12-13 01:30 | 527 | 527
2017-12-13 02:00 | 518 | 518
2017-12-13 02:30 | 510 | 510
2017-12-13 03:00 | 509 | 508
2017-12-13 03:30 | 516 | 515
2017-12-13 04:00 | 523 | 523
2017-12-13 04:30 | 527 | 527
2017-12-13 05:00 | 531 | 531
2017-12-13 05:30 | 539 | 538
2017-12-13 06:00 | 548 | 547
2017-12-13 06:30 | 570 | 570
2017-12-13 07:00 | 556 | 556
2017-12-13 07:30 | 539 | 539
2017-12-13 08:00 | 547 | 546
2017-12-13 08:30 | 562 | 562
2017-12-13 09:00 | 572 | 572
2017-12-13 09:30 | 553 | 553
2017-12-13 10:00 | 547 | 547
2017-12-13 10:30 | 549 | 549
2017-12-13 11:00 | 554 | 554
2017-12-13 11:30 | 564 | 564
2017-12-13 12:00 | 576 | 576
2017-12-13 12:30 | 567 | 567
2017-12-13 13:00 | 576 | 576
2017-12-13 13:30 | 584 | 584
2017-12-13 14:00 | 594 | 594
2017-12-13 14:30 | 607 | 607
2017-12-13 15:00 | 615 | 615
2017-12-13 15:30 | 622 | 622
2017-12-13 16:00 | 630 | 630
2017-12-13 16:30 | 630 | 630
2017-12-13 17:00 | 623 | 623
2017-12-13 17:30 | 640 | 640
2017-12-13 18:00 | 655 | 655
2017-12-13 18:30 | 669 | 669
2017-12-13 19:00 | 699 | 699
2017-12-13 19:30 | 709 | 709
2017-12-13 20:00 | 692 | 692
2017-12-13 20:30 | 671 | 671
2017-12-13 21:00 | 654 | 654
2017-12-13 21:30 | 632 | 632
2017-12-13 22:00 | 635 | 635
2017-12-13 22:30 | 638 | 638
2017-12-13 23:00 | 613 | 613
2017-12-13 23:30 | 587 | 587
2017-12-14 | 561 | 561
2017-12-14 00:30 | 548 | 548
2017-12-14 01:00 | 526 | 526
2017-12-14 01:30 | 514 | 513
2017-12-14 02:00 | 510 | 509
2017-12-14 02:30 | 514 | 513
2017-12-14 03:00 | 516 | 515
2017-12-14 03:30 | 520 | 519
2017-12-14 04:00 | 515 | 514
2017-12-14 04:30 | 518 | 517
2017-12-14 05:00 | 521 | 520
2017-12-14 05:30 | 524 | 524
2017-12-14 06:00 | 526 | 526
2017-12-14 06:30 | 549 | 548
2017-12-14 07:00 | 547 | 546
2017-12-14 07:30 | 537 | 537
2017-12-14 08:00 | 553 | 553
2017-12-14 08:30 | 557 | 557
2017-12-14 09:00 | 555 | 554
2017-12-14 09:30 | 555 | 555
2017-12-14 10:00 | 558 | 558
2017-12-14 10:30 | 561 | 561
2017-12-14 11:00 | 579 | 579
2017-12-14 11:30 | 594 | 594
2017-12-14 12:00 | 585 | 585
2017-12-14 12:30 | 587 | 587
2017-12-14 13:00 | 602 | 602
2017-12-14 13:30 | 608 | 608
2017-12-14 14:00 | 621 | 621
2017-12-14 14:30 | 629 | 629
2017-12-14 15:00 | 640 | 640
2017-12-14 15:30 | 625 | 625
2017-12-14 16:00 | 633 | 633
2017-12-14 16:30 | 649 | 649
2017-12-14 17:00 | 677 | 677
2017-12-14 17:30 | 691 | 691
2017-12-14 18:00 | 721 | 721
2017-12-14 18:30 | 734 | 733
2017-12-14 19:00 | 747 | 746
2017-12-14 19:30 | 760 | 760
2017-12-14 20:00 | 736 | 735
2017-12-14 20:30 | 712 | 711
2017-12-14 21:00 | 694 | 694
2017-12-14 21:30 | 666 | 666
2017-12-14 22:00 | 637 | 637
2017-12-14 22:30 | 629 | 629
2017-12-14 23:00 | 627 | 626
2017-12-14 23:30 | 605 | 605
2017-12-15 | 584 | 584
2017-12-15 00:30 | 567 | 566
2017-12-15 01:00 | 551 | 550
2017-12-15 01:30 | 538 | 537
2017-12-15 02:00 | 533 | 532
2017-12-15 02:30 | 524 | 523
2017-12-15 03:00 | 517 | 516
2017-12-15 03:30 | 511 | 511
2017-12-15 04:00 | 513 | 512
2017-12-15 04:30 | 518 | 517
2017-12-15 05:00 | 522 | 521
2017-12-15 05:30 | 513 | 512
2017-12-15 06:00 | 519 | 518
2017-12-15 06:30 | 536 | 536
2017-12-15 07:00 | 560 | 560
2017-12-15 07:30 | 570 | 570
2017-12-15 08:00 | 579 | 579
2017-12-15 08:30 | 573 | 573
2017-12-15 09:00 | 579 | 579
2017-12-15 09:30 | 583 | 583
2017-12-15 10:00 | 580 | 580
2017-12-15 10:30 | 585 | 584
2017-12-15 11:00 | 586 | 586
2017-12-15 11:30 | 585 | 584
2017-12-15 12:00 | 584 | 584
2017-12-15 12:30 | 588 | 588
2017-12-15 13:00 | 603 | 603
2017-12-15 13:30 | 609 | 609
2017-12-15 14:00 | 608 | 608
2017-12-15 14:30 | 606 | 606
2017-12-15 15:00 | 621 | 621
2017-12-15 15:30 | 628 | 628
2017-12-15 16:00 | 635 | 635
2017-12-15 16:30 | 656 | 656
2017-12-15 17:00 | 672 | 672
2017-12-15 17:30 | 657 | 657
2017-12-15 18:00 | 694 | 694
2017-12-15 18:30 | 692 | 692
2017-12-15 19:00 | 697 | 697
2017-12-15 19:30 | 710 | 710
2017-12-15 20:00 | 704 | 704
2017-12-15 20:30 | 686 | 686
2017-12-15 21:00 | 672 | 672
2017-12-15 21:30 | 651 | 651
2017-12-15 22:00 | 642 | 642
2017-12-15 22:30 | 666 | 666
2017-12-15 23:00 | 644 | 644
2017-12-15 23:30 | 617 | 617
2017-12-16 | 593 | 593
2017-12-16 00:30 | 573 | 573
2017-12-16 01:00 | 559 | 558
2017-12-16 01:30 | 549 | 549
2017-12-16 02:00 | 539 | 538
2017-12-16 02:30 | 535 | 534
2017-12-16 03:00 | 527 | 526
2017-12-16 03:30 | 521 | 520
2017-12-16 04:00 | 517 | 516
2017-12-16 04:30 | 518 | 517
2017-12-16 05:00 | 518 | 517
2017-12-16 05:30 | 518 | 517
2017-12-16 06:00 | 513 | 512
2017-12-16 06:30 | 519 | 518
2017-12-16 07:00 | 512 | 511
2017-12-16 07:30 | 510 | 509
2017-12-16 08:00 | 524 | 523
2017-12-16 08:30 | 535 | 535
2017-12-16 09:00 | 555 | 554
2017-12-16 09:30 | 573 | 572
2017-12-16 10:00 | 577 | 577
2017-12-16 10:30 | 582 | 581
2017-12-16 11:00 | 595 | 595
2017-12-16 11:30 | 595 | 594
2017-12-16 12:00 | 593 | 593
2017-12-16 12:30 | 592 | 592
2017-12-16 13:00 | 590 | 590
2017-12-16 13:30 | 599 | 599
2017-12-16 14:00 | 610 | 610
2017-12-16 14:30 | 601 | 601
2017-12-16 15:00 | 624 | 624
2017-12-16 15:30 | 628 | 628
2017-12-16 16:00 | 628 | 628
2017-12-16 16:30 | 655 | 655
2017-12-16 17:00 | 666 | 666
2017-12-16 17:30 | 687 | 687
2017-12-16 18:00 | 704 | 703
2017-12-16 18:30 | 711 | 711
2017-12-16 19:00 | 707 | 707
2017-12-16 19:30 | 713 | 713
2017-12-16 20:00 | 714 | 714
2017-12-16 20:30 | 700 | 700
2017-12-16 21:00 | 696 | 696
2017-12-16 21:30 | 694 | 694
2017-12-16 22:00 | 676 | 676
2017-12-16 22:30 | 668 | 668
2017-12-16 23:00 | 647 | 647
2017-12-16 23:30 | 626 | 625
2017-12-17 | 609 | 609
2017-12-17 00:30 | 591 | 590
2017-12-17 01:00 | 573 | 573
2017-12-17 01:30 | 562 | 562
2017-12-17 02:00 | 555 | 555
2017-12-17 02:30 | 553 | 552
2017-12-17 03:00 | 544 | 543
2017-12-17 03:30 | 538 | 537
2017-12-17 04:00 | 529 | 528
2017-12-17 04:30 | 528 | 527
2017-12-17 05:00 | 527 | 526
2017-12-17 05:30 | 531 | 529
2017-12-17 06:00 | 522 | 521
2017-12-17 06:30 | 524 | 523
2017-12-17 07:00 | 518 | 517
2017-12-17 07:30 | 507 | 506
2017-12-17 08:00 | 517 | 515
2017-12-17 08:30 | 531 | 529
2017-12-17 09:00 | 536 | 535
2017-12-17 09:30 | 552 | 551
2017-12-17 10:00 | 553 | 552
2017-12-17 10:30 | 556 | 555
2017-12-17 11:00 | 551 | 550
2017-12-17 11:30 | 559 | 559
2017-12-17 12:00 | 567 | 566
2017-12-17 12:30 | 564 | 564
2017-12-17 13:00 | 575 | 574
2017-12-17 13:30 | 591 | 590
2017-12-17 14:00 | 599 | 599
2017-12-17 14:30 | 606 | 606
2017-12-17 15:00 | 617 | 617
2017-12-17 15:30 | 628 | 628
2017-12-17 16:00 | 636 | 636
2017-12-17 16:30 | 638 | 638
2017-12-17 17:00 | 650 | 650
2017-12-17 17:30 | 659 | 659
2017-12-17 18:00 | 668 | 668
2017-12-17 18:30 | 676 | 676
2017-12-17 19:00 | 692 | 692
2017-12-17 19:30 | 709 | 709
2017-12-17 20:00 | 708 | 708
2017-12-17 20:30 | 691 | 691
2017-12-17 21:00 | 685 | 685
2017-12-17 21:30 | 679 | 679
2017-12-17 22:00 | 663 | 663
2017-12-17 22:30 | 649 | 649
2017-12-17 23:00 | 621 | 621
2017-12-17 23:30 | 601 | 600
2017-12-18 | 585 | 585
2017-12-18 00:30 | 568 | 567
2017-12-18 01:00 | 554 | 553
2017-12-18 01:30 | 544 | 543
2017-12-18 02:00 | 536 | 534
2017-12-18 02:30 | 528 | 526
2017-12-18 03:00 | 524 | 523
2017-12-18 03:30 | 520 | 518
2017-12-18 04:00 | 519 | 517
2017-12-18 04:30 | 523 | 522
2017-12-18 05:00 | 529 | 528
2017-12-18 05:30 | 534 | 533
2017-12-18 06:00 | 533 | 532
2017-12-18 06:30 | 559 | 558
2017-12-18 07:00 | 569 | 568
2017-12-18 07:30 | 582 | 581
2017-12-18 08:00 | 599 | 599
2017-12-18 08:30 | 619 | 618
2017-12-18 09:00 | 629 | 628
2017-12-18 09:30 | 627 | 627
2017-12-18 10:00 | 625 | 625
2017-12-18 10:30 | 629 | 629
2017-12-18 11:00 | 622 | 622
2017-12-18 11:30 | 631 | 631
2017-12-18 12:00 | 638 | 638
2017-12-18 12:30 | 647 | 647
2017-12-18 13:00 | 643 | 642
2017-12-18 13:30 | 653 | 653
2017-12-18 14:00 | 647 | 647
2017-12-18 14:30 | 658 | 658
2017-12-18 15:00 | 682 | 682
2017-12-18 15:30 | 684 | 684
2017-12-18 16:00 | 674 | 674
2017-12-18 16:30 | 660 | 660
2017-12-18 17:00 | 660 | 660
2017-12-18 17:30 | 664 | 664
2017-12-18 18:00 | 662 | 662
2017-12-18 18:30 | 698 | 698
2017-12-18 19:00 | 733 | 733
2017-12-18 19:30 | 749 | 749
2017-12-18 20:00 | 743 | 742
2017-12-18 20:30 | 721 | 720
2017-12-18 21:00 | 725 | 725
2017-12-18 21:30 | 721 | 721
2017-12-18 22:00 | 703 | 703
2017-12-18 22:30 | 684 | 684
2017-12-18 23:00 | 659 | 659
2017-12-18 23:30 | 636 | 636
2017-12-19 | 617 | 617
2017-12-19 00:30 | 599 | 599
2017-12-19 01:00 | 583 | 583
2017-12-19 01:30 | 575 | 574
2017-12-19 02:00 | 558 | 558
2017-12-19 02:30 | 552 | 552
2017-12-19 03:00 | 547 | 546
2017-12-19 03:30 | 535 | 534
2017-12-19 04:00 | 533 | 532
2017-12-19 04:30 | 534 | 533
2017-12-19 05:00 | 536 | 535
2017-12-19 05:30 | 543 | 542
2017-12-19 06:00 | 552 | 551
2017-12-19 06:30 | 566 | 565
2017-12-19 07:00 | 571 | 571
2017-12-19 07:30 | 582 | 582
2017-12-19 08:00 | 603 | 603
2017-12-19 08:30 | 607 | 607
2017-12-19 09:00 | 565 | 565
2017-12-19 09:30 | 552 | 552
2017-12-19 10:00 | 546 | 546
2017-12-19 10:30 | 543 | 543
2017-12-19 11:00 | 549 | 548
2017-12-19 11:30 | 544 | 544
2017-12-19 12:00 | 519 | 519
2017-12-19 12:30 | 493 | 492
2017-12-19 13:00 | 518 | 517
2017-12-19 13:30 | 527 | 527
2017-12-19 14:00 | 530 | 529
2017-12-19 14:30 | 549 | 549
2017-12-19 15:00 | 555 | 554
2017-12-19 15:30 | 438 | 438
2017-12-19 16:00 | 429 | 427
2017-12-19 16:30 | 513 | 511
2017-12-19 17:00 | 534 | 533
2017-12-19 17:30 | 544 | 543
2017-12-19 18:00 | 583 | 583
2017-12-19 18:30 | 592 | 592
2017-12-19 19:00 | 606 | 606
2017-12-19 19:30 | 623 | 623
2017-12-19 20:00 | 616 | 616
2017-12-19 20:30 | 597 | 596
2017-12-19 21:00 | 595 | 595
2017-12-19 21:30 | 589 | 589
2017-12-19 22:00 | 567 | 567
2017-12-19 22:30 | 551 | 551
2017-12-19 23:00 | 530 | 530
2017-12-19 23:30 | 502 | 501
2017-12-20 | 484 | 482
2017-12-20 00:30 | 475 | 473
2017-12-20 01:00 | 461 | 459
2017-12-20 01:30 | 437 | 434
2017-12-20 02:00 | 427 | 424
2017-12-20 02:30 | 422 | 419
2017-12-20 03:00 | 418 | 415
2017-12-20 03:30 | 417 | 413
2017-12-20 04:00 | 414 | 410
2017-12-20 04:30 | 413 | 408
2017-12-20 05:00 | 414 | 410
2017-12-20 05:30 | 421 | 417
2017-12-20 06:00 | 424 | 420
2017-12-20 06:30 | 449 | 445
2017-12-20 07:00 | 453 | 450
2017-12-20 07:30 | 465 | 462
2017-12-20 08:00 | 493 | 491
2017-12-20 08:30 | 509 | 507
2017-12-20 09:00 | 513 | 512
2017-12-20 09:30 | 512 | 511
2017-12-20 10:00 | 518 | 517
2017-12-20 10:30 | 520 | 519
2017-12-20 11:00 | 521 | 520
2017-12-20 11:30 | 520 | 519
2017-12-20 12:00 | 520 | 520
2017-12-20 12:30 | 524 | 523
2017-12-20 13:00 | 529 | 528
2017-12-20 13:30 | 521 | 520
2017-12-20 14:00 | 551 | 550
2017-12-20 14:30 | 556 | 556
2017-12-20 15:00 | 568 | 568
2017-12-20 15:30 | 585 | 585
2017-12-20 16:00 | 595 | 595
2017-12-20 16:30 | 593 | 593
2017-12-20 17:00 | 602 | 602
2017-12-20 17:30 | 610 | 610
2017-12-20 18:00 | 614 | 614
2017-12-20 18:30 | 614 | 614
2017-12-20 19:00 | 623 | 623
2017-12-20 19:30 | 640 | 640
2017-12-20 20:00 | 634 | 634
2017-12-20 20:30 | 614 | 614
2017-12-20 21:00 | 593 | 593
2017-12-20 21:30 | 633 | 633
2017-12-20 22:00 | 709 | 709
2017-12-20 22:30 | 697 | 697
2017-12-20 23:00 | 688 | 687
2017-12-20 23:30 | 668 | 668
2017-12-21 | 646 | 646
2017-12-21 00:30 | 628 | 628
2017-12-21 01:00 | 608 | 608
2017-12-21 01:30 | 597 | 597
2017-12-21 02:00 | 584 | 584
2017-12-21 02:30 | 579 | 579
2017-12-21 03:00 | 580 | 579
2017-12-21 03:30 | 573 | 572
2017-12-21 04:00 | 569 | 569
2017-12-21 04:30 | 568 | 568
2017-12-21 05:00 | 572 | 571
2017-12-21 05:30 | 580 | 579
2017-12-21 06:00 | 586 | 585
2017-12-21 06:30 | 607 | 606
2017-12-21 07:00 | 620 | 620
2017-12-21 07:30 | 628 | 628
2017-12-21 08:00 | 640 | 640
2017-12-21 08:30 | 657 | 656
2017-12-21 09:00 | 660 | 660
2017-12-21 09:30 | 667 | 666
2017-12-21 10:00 | 671 | 671
2017-12-21 10:30 | 678 | 678
2017-12-21 11:00 | 666 | 666
2017-12-21 11:30 | 661 | 661
2017-12-21 12:00 | 670 | 670
2017-12-21 12:30 | 687 | 687
2017-12-21 13:00 | 692 | 692
2017-12-21 13:30 | 695 | 694
2017-12-21 14:00 | 709 | 709
2017-12-21 14:30 | 717 | 717
2017-12-21 15:00 | 699 | 698
2017-12-21 15:30 | 683 | 683
2017-12-21 16:00 | 688 | 688
2017-12-21 16:30 | 683 | 683
2017-12-21 17:00 | 656 | 655
2017-12-21 17:30 | 664 | 664
2017-12-21 18:00 | 718 | 718
2017-12-21 18:30 | 748 | 747
2017-12-21 19:00 | 758 | 757
2017-12-21 19:30 | 767 | 766
2017-12-21 20:00 | 778 | 777
2017-12-21 20:30 | 763 | 762
2017-12-21 21:00 | 745 | 744
2017-12-21 21:30 | 752 | 752
2017-12-21 22:00 | 742 | 741
2017-12-21 22:30 | 732 | 731
2017-12-21 23:00 | 704 | 704
2017-12-21 23:30 | 677 | 677
2017-12-22 | 649 | 649
2017-12-22 00:30 | 631 | 631
2017-12-22 01:00 | 617 | 617
2017-12-22 01:30 | 605 | 605
2017-12-22 02:00 | 596 | 596
2017-12-22 02:30 | 589 | 589
2017-12-22 03:00 | 585 | 585
2017-12-22 03:30 | 580 | 579
2017-12-22 04:00 | 576 | 575
2017-12-22 04:30 | 576 | 575
2017-12-22 05:00 | 575 | 574
2017-12-22 05:30 | 578 | 577
2017-12-22 06:00 | 583 | 582
2017-12-22 06:30 | 601 | 600
2017-12-22 07:00 | 601 | 601
2017-12-22 07:30 | 608 | 607
2017-12-22 08:00 | 623 | 623
2017-12-22 08:30 | 639 | 639
2017-12-22 09:00 | 645 | 645
2017-12-22 09:30 | 656 | 656
2017-12-22 10:00 | 656 | 656
2017-12-22 10:30 | 664 | 664
2017-12-22 11:00 | 660 | 660
2017-12-22 11:30 | 649 | 649
2017-12-22 12:00 | 657 | 657
2017-12-22 12:30 | 657 | 657
2017-12-22 13:00 | 660 | 660
2017-12-22 13:30 | 673 | 673
2017-12-22 14:00 | 682 | 682
2017-12-22 14:30 | 695 | 695
2017-12-22 15:00 | 701 | 701
2017-12-22 15:30 | 696 | 696
2017-12-22 16:00 | 709 | 709
2017-12-22 16:30 | 689 | 689
2017-12-22 17:00 | 699 | 698
2017-12-22 17:30 | 724 | 724
2017-12-22 18:00 | 761 | 760
2017-12-22 18:30 | 763 | 762
2017-12-22 19:00 | 772 | 772
2017-12-22 19:30 | 775 | 774
2017-12-22 20:00 | 785 | 785
2017-12-22 20:30 | 777 | 776
2017-12-22 21:00 | 763 | 763
2017-12-22 21:30 | 757 | 756
2017-12-22 22:00 | 744 | 743
2017-12-22 22:30 | 736 | 736
2017-12-22 23:00 | 718 | 718
2017-12-22 23:30 | 691 | 691
2017-12-23 | 670 | 670
2017-12-23 00:30 | 653 | 653
2017-12-23 01:00 | 634 | 634
2017-12-23 01:30 | 621 | 621
2017-12-23 02:00 | 610 | 610
2017-12-23 02:30 | 606 | 606
2017-12-23 03:00 | 598 | 598
2017-12-23 03:30 | 591 | 590
2017-12-23 04:00 | 592 | 591
2017-12-23 04:30 | 586 | 586
2017-12-23 05:00 | 582 | 581
2017-12-23 05:30 | 584 | 584
2017-12-23 06:00 | 578 | 578
2017-12-23 06:30 | 578 | 578
2017-12-23 07:00 | 589 | 589
2017-12-23 07:30 | 612 | 611
2017-12-23 08:00 | 620 | 620
2017-12-23 08:30 | 631 | 631
2017-12-23 09:00 | 637 | 637
2017-12-23 09:30 | 641 | 641
2017-12-23 10:00 | 629 | 629
2017-12-23 10:30 | 608 | 608
2017-12-23 11:00 | 610 | 610
2017-12-23 11:30 | 618 | 618
2017-12-23 12:00 | 622 | 622
2017-12-23 12:30 | 626 | 626
2017-12-23 13:00 | 631 | 631
2017-12-23 13:30 | 654 | 654
2017-12-23 14:00 | 657 | 657
2017-12-23 14:30 | 671 | 671
2017-12-23 15:00 | 686 | 686
2017-12-23 15:30 | 698 | 698
2017-12-23 16:00 | 712 | 712
2017-12-23 16:30 | 699 | 699
2017-12-23 17:00 | 708 | 708
2017-12-23 17:30 | 720 | 720
2017-12-23 18:00 | 729 | 729
2017-12-23 18:30 | 734 | 733
2017-12-23 19:00 | 744 | 743
2017-12-23 19:30 | 756 | 755
2017-12-23 20:00 | 753 | 752
2017-12-23 20:30 | 734 | 734
2017-12-23 21:00 | 751 | 751
2017-12-23 21:30 | 742 | 741
2017-12-23 22:00 | 726 | 726
2017-12-23 22:30 | 710 | 710
2017-12-23 23:00 | 685 | 685
2017-12-23 23:30 | 665 | 665
2017-12-24 | 644 | 644
2017-12-24 00:30 | 623 | 623
2017-12-24 01:00 | 611 | 611
2017-12-24 01:30 | 600 | 600
2017-12-24 02:00 | 586 | 585
2017-12-24 02:30 | 576 | 575
2017-12-24 03:00 | 573 | 573
2017-12-24 03:30 | 567 | 567
2017-12-24 04:00 | 562 | 562
2017-12-24 04:30 | 563 | 563
2017-12-24 05:00 | 558 | 557
2017-12-24 05:30 | 560 | 559
2017-12-24 06:00 | 554 | 554
2017-12-24 06:30 | 553 | 553
2017-12-24 07:00 | 562 | 562
2017-12-24 07:30 | 577 | 576
2017-12-24 08:00 | 590 | 589
2017-12-24 08:30 | 603 | 603
2017-12-24 09:00 | 609 | 608
2017-12-24 09:30 | 620 | 620
2017-12-24 10:00 | 609 | 609
2017-12-24 10:30 | 597 | 597
2017-12-24 11:00 | 591 | 591
2017-12-24 11:30 | 592 | 592
2017-12-24 12:00 | 594 | 594
2017-12-24 12:30 | 599 | 599
2017-12-24 13:00 | 596 | 596
2017-12-24 13:30 | 612 | 612
2017-12-24 14:00 | 603 | 603
2017-12-24 14:30 | 629 | 629
2017-12-24 15:00 | 650 | 650
2017-12-24 15:30 | 676 | 675
2017-12-24 16:00 | 695 | 694
2017-12-24 16:30 | 714 | 714
2017-12-24 17:00 | 709 | 709
2017-12-24 17:30 | 726 | 725
2017-12-24 18:00 | 752 | 752
2017-12-24 18:30 | 759 | 759
2017-12-24 19:00 | 765 | 765
2017-12-24 19:30 | 773 | 773
2017-12-24 20:00 | 769 | 769
2017-12-24 20:30 | 754 | 753
2017-12-24 21:00 | 738 | 737
2017-12-24 21:30 | 718 | 718
2017-12-24 22:00 | 699 | 699
2017-12-24 22:30 | 681 | 681
2017-12-24 23:00 | 659 | 659
2017-12-24 23:30 | 634 | 634
2017-12-25 | 607 | 607
2017-12-25 00:30 | 591 | 591
2017-12-25 01:00 | 574 | 574
2017-12-25 01:30 | 561 | 560
2017-12-25 02:00 | 551 | 550
2017-12-25 02:30 | 539 | 539
2017-12-25 03:00 | 533 | 532
2017-12-25 03:30 | 525 | 524
2017-12-25 04:00 | 520 | 519
2017-12-25 04:30 | 521 | 520
2017-12-25 05:00 | 519 | 518
2017-12-25 05:30 | 518 | 517
2017-12-25 06:00 | 514 | 513
2017-12-25 06:30 | 524 | 523
2017-12-25 07:00 | 530 | 529
2017-12-25 07:30 | 545 | 545
2017-12-25 08:00 | 556 | 555
2017-12-25 08:30 | 565 | 564
2017-12-25 09:00 | 567 | 566
2017-12-25 09:30 | 570 | 570
2017-12-25 10:00 | 564 | 563
2017-12-25 10:30 | 552 | 552
2017-12-25 11:00 | 547 | 547
2017-12-25 11:30 | 547 | 547
2017-12-25 12:00 | 548 | 547
2017-12-25 12:30 | 545 | 545
2017-12-25 13:00 | 543 | 542
2017-12-25 13:30 | 554 | 553
2017-12-25 14:00 | 558 | 557
2017-12-25 14:30 | 561 | 561
2017-12-25 15:00 | 563 | 563
2017-12-25 15:30 | 563 | 562
2017-12-25 16:00 | 579 | 579
2017-12-25 16:30 | 597 | 596
2017-12-25 17:00 | 619 | 619
2017-12-25 17:30 | 634 | 634
2017-12-25 18:00 | 672 | 672
2017-12-25 18:30 | 683 | 683
2017-12-25 19:00 | 689 | 689
2017-12-25 19:30 | 700 | 700
2017-12-25 20:00 | 705 | 705
2017-12-25 20:30 | 696 | 696
2017-12-25 21:00 | 685 | 685
2017-12-25 21:30 | 672 | 672
2017-12-25 22:00 | 654 | 654
2017-12-25 22:30 | 643 | 643
2017-12-25 23:00 | 624 | 624
2017-12-25 23:30 | 600 | 600
2017-12-26 | 582 | 582
2017-12-26 00:30 | 567 | 567
2017-12-26 01:00 | 550 | 550
2017-12-26 01:30 | 541 | 540
2017-12-26 02:00 | 534 | 533
2017-12-26 02:30 | 526 | 525
2017-12-26 03:00 | 520 | 519
2017-12-26 03:30 | 519 | 516
2017-12-26 04:00 | 518 | 515
2017-12-26 04:30 | 518 | 515
2017-12-26 05:00 | 516 | 513
2017-12-26 05:30 | 518 | 515
2017-12-26 06:00 | 513 | 510
2017-12-26 06:30 | 519 | 517
2017-12-26 07:00 | 526 | 524
2017-12-26 07:30 | 543 | 540
2017-12-26 08:00 | 554 | 552
2017-12-26 08:30 | 562 | 560
2017-12-26 09:00 | 568 | 566
2017-12-26 09:30 | 570 | 568
2017-12-26 10:00 | 560 | 558
2017-12-26 10:30 | 541 | 540
2017-12-26 11:00 | 538 | 536
2017-12-26 11:30 | 539 | 537
2017-12-26 12:00 | 538 | 536
2017-12-26 12:30 | 542 | 540
2017-12-26 13:00 | 550 | 548
2017-12-26 13:30 | 579 | 577
2017-12-26 14:00 | 595 | 594
2017-12-26 14:30 | 610 | 609
2017-12-26 15:00 | 622 | 622
2017-12-26 15:30 | 625 | 624
2017-12-26 16:00 | 643 | 642
2017-12-26 16:30 | 660 | 660
2017-12-26 17:00 | 678 | 678
2017-12-26 17:30 | 693 | 693
2017-12-26 18:00 | 724 | 724
2017-12-26 18:30 | 736 | 736
2017-12-26 19:00 | 752 | 752
2017-12-26 19:30 | 770 | 769
2017-12-26 20:00 | 772 | 771
2017-12-26 20:30 | 753 | 752
2017-12-26 21:00 | 738 | 737
2017-12-26 21:30 | 720 | 719
2017-12-26 22:00 | 695 | 695
2017-12-26 22:30 | 680 | 680
2017-12-26 23:00 | 655 | 655
2017-12-26 23:30 | 630 | 630
2017-12-27 | 611 | 611
2017-12-27 00:30 | 598 | 598
2017-12-27 01:00 | 584 | 584
2017-12-27 01:30 | 575 | 575
2017-12-27 02:00 | 565 | 565
2017-12-27 02:30 | 561 | 561
2017-12-27 03:00 | 555 | 554
2017-12-27 03:30 | 554 | 554
2017-12-27 04:00 | 552 | 551
2017-12-27 04:30 | 548 | 548
2017-12-27 05:00 | 550 | 549
2017-12-27 05:30 | 554 | 554
2017-12-27 06:00 | 553 | 553
2017-12-27 06:30 | 566 | 565
2017-12-27 07:00 | 577 | 576
2017-12-27 07:30 | 600 | 599
2017-12-27 08:00 | 622 | 621
2017-12-27 08:30 | 633 | 633
2017-12-27 09:00 | 636 | 636
2017-12-27 09:30 | 638 | 638
2017-12-27 10:00 | 626 | 626
2017-12-27 10:30 | 610 | 610
2017-12-27 11:00 | 611 | 611
2017-12-27 11:30 | 614 | 614
2017-12-27 12:00 | 627 | 627
2017-12-27 12:30 | 638 | 638
2017-12-27 13:00 | 643 | 643
2017-12-27 13:30 | 674 | 674
2017-12-27 14:00 | 685 | 685
2017-12-27 14:30 | 699 | 699
2017-12-27 15:00 | 709 | 709
2017-12-27 15:30 | 726 | 726
2017-12-27 16:00 | 750 | 750
2017-12-27 16:30 | 761 | 760
2017-12-27 17:00 | 758 | 757
2017-12-27 17:30 | 788 | 787
2017-12-27 18:00 | 801 | 800
2017-12-27 18:30 | 808 | 807
2017-12-27 19:00 | 822 | 821
2017-12-27 19:30 | 832 | 831
2017-12-27 20:00 | 828 | 827
2017-12-27 20:30 | 814 | 813
2017-12-27 21:00 | 793 | 792
2017-12-27 21:30 | 774 | 774
2017-12-27 22:00 | 745 | 745
2017-12-27 22:30 | 730 | 730
2017-12-27 23:00 | 701 | 701
2017-12-27 23:30 | 679 | 679
2017-12-28 | 660 | 660
2017-12-28 00:30 | 646 | 646
2017-12-28 01:00 | 634 | 634
2017-12-28 01:30 | 621 | 621
2017-12-28 02:00 | 610 | 610
2017-12-28 02:30 | 601 | 600
2017-12-28 03:00 | 592 | 591
2017-12-28 03:30 | 591 | 591
2017-12-28 04:00 | 584 | 584
2017-12-28 04:30 | 582 | 582
2017-12-28 05:00 | 588 | 587
2017-12-28 05:30 | 593 | 593
2017-12-28 06:00 | 589 | 589
2017-12-28 06:30 | 603 | 603
2017-12-28 07:00 | 608 | 608
2017-12-28 07:30 | 631 | 630
2017-12-28 08:00 | 644 | 643
2017-12-28 08:30 | 655 | 654
2017-12-28 09:00 | 665 | 664
2017-12-28 09:30 | 668 | 667
2017-12-28 10:00 | 656 | 655
2017-12-28 10:30 | 652 | 651
2017-12-28 11:00 | 640 | 639
2017-12-28 11:30 | 634 | 633
2017-12-28 12:00 | 645 | 644
2017-12-28 12:30 | 645 | 644
2017-12-28 13:00 | 545 | 544
2017-12-28 13:30 | 507 | 506
2017-12-28 14:00 | 515 | 515
2017-12-28 14:30 | 551 | 551
2017-12-28 15:00 | 571 | 571
2017-12-28 15:30 | 571 | 571
2017-12-28 16:00 | 596 | 596
2017-12-28 16:30 | 617 | 617
2017-12-28 17:00 | 615 | 614
2017-12-28 17:30 | 609 | 609
2017-12-28 18:00 | 637 | 637
2017-12-28 18:30 | 676 | 676
2017-12-28 19:00 | 682 | 681
2017-12-28 19:30 | 699 | 698
2017-12-28 20:00 | 696 | 694
2017-12-28 20:30 | 786 | 785
2017-12-28 21:00 | 796 | 793
2017-12-28 21:30 | 791 | 788
2017-12-28 22:00 | 764 | 761
2017-12-28 22:30 | 718 | 716
2017-12-28 23:00 | 700 | 698
2017-12-28 23:30 | 688 | 687
2017-12-29 | 666 | 665
2017-12-29 00:30 | 646 | 646
2017-12-29 01:00 | 630 | 629
2017-12-29 01:30 | 621 | 620
2017-12-29 02:00 | 611 | 610
2017-12-29 02:30 | 607 | 607
2017-12-29 03:00 | 603 | 603
2017-12-29 03:30 | 598 | 598
2017-12-29 04:00 | 595 | 595
2017-12-29 04:30 | 595 | 595
2017-12-29 05:00 | 595 | 595
2017-12-29 05:30 | 603 | 603
2017-12-29 06:00 | 598 | 598
2017-12-29 06:30 | 608 | 608
2017-12-29 07:00 | 620 | 619
2017-12-29 07:30 | 634 | 633
2017-12-29 08:00 | 655 | 655
2017-12-29 08:30 | 652 | 651
2017-12-29 09:00 | 683 | 683
2017-12-29 09:30 | 665 | 664
2017-12-29 10:00 | 660 | 659
2017-12-29 10:30 | 644 | 644
2017-12-29 11:00 | 620 | 619
2017-12-29 11:30 | 643 | 642
2017-12-29 12:00 | 591 | 590
2017-12-29 12:30 | 511 | 511
2017-12-29 13:00 | 520 | 520
2017-12-29 13:30 | 545 | 545
2017-12-29 14:00 | 561 | 561
2017-12-29 14:30 | 566 | 566
2017-12-29 15:00 | 575 | 575
2017-12-29 15:30 | 576 | 576
2017-12-29 16:00 | 597 | 597
2017-12-29 16:30 | 620 | 620
2017-12-29 17:00 | 641 | 641
2017-12-29 17:30 | 655 | 655
2017-12-29 18:00 | 680 | 679
2017-12-29 18:30 | 684 | 683
2017-12-29 19:00 | 665 | 664
2017-12-29 19:30 | 667 | 667
2017-12-29 20:00 | 688 | 687
2017-12-29 20:30 | 802 | 802
2017-12-29 21:00 | 821 | 818
2017-12-29 21:30 | 803 | 800
2017-12-29 22:00 | 778 | 775
2017-12-29 22:30 | 752 | 750
2017-12-29 23:00 | 726 | 725
2017-12-29 23:30 | 701 | 700
2017-12-30 | 677 | 677
2017-12-30 00:30 | 658 | 658
2017-12-30 01:00 | 641 | 641
2017-12-30 01:30 | 627 | 627
2017-12-30 02:00 | 621 | 621
2017-12-30 02:30 | 610 | 610
2017-12-30 03:00 | 606 | 606
2017-12-30 03:30 | 598 | 597
2017-12-30 04:00 | 594 | 594
2017-12-30 04:30 | 591 | 591
2017-12-30 05:00 | 594 | 593
2017-12-30 05:30 | 594 | 594
2017-12-30 06:00 | 585 | 585
2017-12-30 06:30 | 592 | 592
2017-12-30 07:00 | 599 | 598
2017-12-30 07:30 | 610 | 610
2017-12-30 08:00 | 617 | 616
2017-12-30 08:30 | 628 | 628
2017-12-30 09:00 | 639 | 638
2017-12-30 09:30 | 645 | 645
2017-12-30 10:00 | 643 | 643
2017-12-30 10:30 | 628 | 628
2017-12-30 11:00 | 629 | 629
2017-12-30 11:30 | 638 | 638
2017-12-30 12:00 | 649 | 649
2017-12-30 12:30 | 656 | 655
2017-12-30 13:00 | 668 | 668
2017-12-30 13:30 | 693 | 692
2017-12-30 14:00 | 708 | 707
2017-12-30 14:30 | 715 | 713
2017-12-30 15:00 | 726 | 725
2017-12-30 15:30 | 737 | 735
2017-12-30 16:00 | 755 | 753
2017-12-30 16:30 | 775 | 773
2017-12-30 17:00 | 776 | 773
2017-12-30 17:30 | 782 | 779
2017-12-30 18:00 | 790 | 787
2017-12-30 18:30 | 824 | 821
2017-12-30 19:00 | 840 | 837
2017-12-30 19:30 | 847 | 844
2017-12-30 20:00 | 845 | 842
2017-12-30 20:30 | 839 | 836
2017-12-30 21:00 | 821 | 818
2017-12-30 21:30 | 800 | 797
2017-12-30 22:00 | 776 | 774
2017-12-30 22:30 | 748 | 746
2017-12-30 23:00 | 721 | 720
2017-12-30 23:30 | 695 | 694
2017-12-31 | 676 | 675
2017-12-31 00:30 | 659 | 658
2017-12-31 01:00 | 644 | 643
2017-12-31 01:30 | 634 | 633
2017-12-31 02:00 | 623 | 622
2017-12-31 02:30 | 616 | 616
2017-12-31 03:00 | 608 | 607
2017-12-31 03:30 | 600 | 600
2017-12-31 04:00 | 594 | 594
2017-12-31 04:30 | 593 | 593
2017-12-31 05:00 | 591 | 591
2017-12-31 05:30 | 588 | 588
2017-12-31 06:00 | 582 | 581
2017-12-31 06:30 | 582 | 582
2017-12-31 07:00 | 581 | 581
2017-12-31 07:30 | 592 | 592
2017-12-31 08:00 | 598 | 597
2017-12-31 08:30 | 612 | 612
2017-12-31 09:00 | 620 | 620
2017-12-31 09:30 | 626 | 626
2017-12-31 10:00 | 627 | 627
2017-12-31 10:30 | 606 | 606
2017-12-31 11:00 | 612 | 612
2017-12-31 11:30 | 612 | 612
2017-12-31 12:00 | 624 | 623
2017-12-31 12:30 | 637 | 636
2017-12-31 13:00 | 644 | 643
2017-12-31 13:30 | 677 | 676
2017-12-31 14:00 | 675 | 674
2017-12-31 14:30 | 696 | 695
2017-12-31 15:00 | 720 | 719
2017-12-31 15:30 | 736 | 735
2017-12-31 16:00 | 760 | 758
2017-12-31 16:30 | 780 | 777
2017-12-31 17:00 | 774 | 770
2017-12-31 17:30 | 790 | 787
2017-12-31 18:00 | 799 | 796
2017-12-31 18:30 | 799 | 796
2017-12-31 19:00 | 795 | 792
2017-12-31 19:30 | 796 | 793
2017-12-31 20:00 | 798 | 795
2017-12-31 20:30 | 786 | 784
2017-12-31 21:00 | 769 | 766
2017-12-31 21:30 | 749 | 746
2017-12-31 22:00 | 737 | 736
2017-12-31 22:30 | 718 | 716
2017-12-31 23:00 | 703 | 702
2017-12-31 23:30 | 691 | 690
2018-01-01 | 670 | 669
2018-01-01 00:30 | 650 | 649
2018-01-01 01:00 | 645 | 644
2018-01-01 01:30 | 639 | 638
2018-01-01 02:00 | 631 | 631
2018-01-01 02:30 | 617 | 617
2018-01-01 03:00 | 614 | 613
2018-01-01 03:30 | 607 | 606
2018-01-01 04:00 | 597 | 597
2018-01-01 04:30 | 597 | 597
2018-01-01 05:00 | 593 | 593
2018-01-01 05:30 | 596 | 596
2018-01-01 06:00 | 589 | 589
2018-01-01 06:30 | 595 | 595
2018-01-01 07:00 | 596 | 596
2018-01-01 07:30 | 604 | 604
2018-01-01 08:00 | 614 | 614
2018-01-01 08:30 | 621 | 620
2018-01-01 09:00 | 628 | 628
2018-01-01 09:30 | 638 | 637
2018-01-01 10:00 | 634 | 633
2018-01-01 10:30 | 631 | 630
2018-01-01 11:00 | 638 | 637
2018-01-01 11:30 | 653 | 653
2018-01-01 12:00 | 670 | 669
2018-01-01 12:30 | 681 | 679
2018-01-01 13:00 | 690 | 689
2018-01-01 13:30 | 713 | 711
2018-01-01 14:00 | 738 | 736
2018-01-01 14:30 | 757 | 755
2018-01-01 15:00 | 700 | 698
2018-01-01 15:30 | 618 | 617
2018-01-01 16:00 | 632 | 632
2018-01-01 16:30 | 633 | 633
2018-01-01 17:00 | 653 | 653
2018-01-01 17:30 | 670 | 670
2018-01-01 18:00 | 700 | 699
2018-01-01 18:30 | 713 | 712
2018-01-01 19:00 | 717 | 715
2018-01-01 19:30 | 741 | 739
2018-01-01 20:00 | 736 | 734
2018-01-01 20:30 | 741 | 739
2018-01-01 21:00 | 727 | 725
2018-01-01 21:30 | 820 | 818
2018-01-01 22:00 | 815 | 812
2018-01-01 22:30 | 784 | 781
2018-01-01 23:00 | 755 | 753
2018-01-01 23:30 | 726 | 724
2018-01-02 | 695 | 694
2018-01-02 00:30 | 682 | 681
2018-01-02 01:00 | 668 | 668
2018-01-02 01:30 | 655 | 655
2018-01-02 02:00 | 647 | 647
2018-01-02 02:30 | 645 | 645
2018-01-02 03:00 | 644 | 644
2018-01-02 03:30 | 633 | 633
2018-01-02 04:00 | 630 | 630
2018-01-02 04:30 | 627 | 627
2018-01-02 05:00 | 628 | 628
2018-01-02 05:30 | 638 | 637
2018-01-02 06:00 | 643 | 643
2018-01-02 06:30 | 659 | 659
2018-01-02 07:00 | 676 | 675
2018-01-02 07:30 | 709 | 709
2018-01-02 08:00 | 734 | 734
2018-01-02 08:30 | 756 | 755
2018-01-02 09:00 | 766 | 764
2018-01-02 09:30 | 764 | 762
2018-01-02 10:00 | 734 | 731
2018-01-02 10:30 | 725 | 723
2018-01-02 11:00 | 746 | 743
2018-01-02 11:30 | 747 | 745
2018-01-02 12:00 | 752 | 749
2018-01-02 12:30 | 767 | 764
2018-01-02 13:00 | 781 | 778
2018-01-02 13:30 | 798 | 795
2018-01-02 14:00 | 844 | 841
2018-01-02 14:30 | 856 | 852
2018-01-02 15:00 | 863 | 859
2018-01-02 15:30 | 848 | 844
2018-01-02 16:00 | 884 | 880
2018-01-02 16:30 | 873 | 868
2018-01-02 17:00 | 862 | 857
2018-01-02 17:30 | 863 | 859
2018-01-02 18:00 | 884 | 881
2018-01-02 18:30 | 876 | 872
2018-01-02 19:00 | 861 | 857
2018-01-02 19:30 | 859 | 855
2018-01-02 20:00 | 844 | 840
2018-01-02 20:30 | 844 | 840
2018-01-02 21:00 | 827 | 823
2018-01-02 21:30 | 803 | 799
2018-01-02 22:00 | 766 | 763
2018-01-02 22:30 | 734 | 732
2018-01-02 23:00 | 710 | 708
2018-01-02 23:30 | 687 | 686
2018-01-03 | 668 | 667
2018-01-03 00:30 | 650 | 649
2018-01-03 01:00 | 636 | 635
2018-01-03 01:30 | 628 | 627
2018-01-03 02:00 | 620 | 620
2018-01-03 02:30 | 614 | 614
2018-01-03 03:00 | 601 | 601
2018-01-03 03:30 | 598 | 598
2018-01-03 04:00 | 595 | 595
2018-01-03 04:30 | 599 | 598
2018-01-03 05:00 | 601 | 600
2018-01-03 05:30 | 605 | 605
2018-01-03 06:00 | 603 | 603
2018-01-03 06:30 | 619 | 619
2018-01-03 07:00 | 639 | 638
2018-01-03 07:30 | 667 | 666
2018-01-03 08:00 | 689 | 688
2018-01-03 08:30 | 711 | 709
2018-01-03 09:00 | 723 | 721
2018-01-03 09:30 | 730 | 728
2018-01-03 10:00 | 713 | 711
2018-01-03 10:30 | 688 | 686
2018-01-03 11:00 | 652 | 650
2018-01-03 11:30 | 658 | 657
2018-01-03 12:00 | 670 | 668
2018-01-03 12:30 | 673 | 672
2018-01-03 13:00 | 683 | 681
2018-01-03 13:30 | 703 | 702
2018-01-03 14:00 | 701 | 699
2018-01-03 14:30 | 726 | 724
2018-01-03 15:00 | 757 | 755
2018-01-03 15:30 | 758 | 755
2018-01-03 16:00 | 751 | 749
2018-01-03 16:30 | 751 | 748
2018-01-03 17:00 | 767 | 764
2018-01-03 17:30 | 770 | 768
2018-01-03 18:00 | 776 | 773
2018-01-03 18:30 | 797 | 794
2018-01-03 19:00 | 807 | 804
2018-01-03 19:30 | 813 | 810
2018-01-03 20:00 | 822 | 819
2018-01-03 20:30 | 792 | 789
2018-01-03 21:00 | 770 | 768
2018-01-03 21:30 | 740 | 738
2018-01-03 22:00 | 701 | 699
2018-01-03 22:30 | 664 | 663
2018-01-03 23:00 | 628 | 627
2018-01-03 23:30 | 601 | 601
2018-01-04 | 582 | 582
2018-01-04 00:30 | 565 | 565
2018-01-04 01:00 | 549 | 549
2018-01-04 01:30 | 538 | 538
2018-01-04 02:00 | 527 | 527
2018-01-04 02:30 | 520 | 520
2018-01-04 03:00 | 515 | 515
2018-01-04 03:30 | 511 | 511
2018-01-04 04:00 | 507 | 507
2018-01-04 04:30 | 505 | 505
2018-01-04 05:00 | 506 | 505
2018-01-04 05:30 | 507 | 506
2018-01-04 06:00 | 505 | 504
2018-01-04 06:30 | 520 | 520
2018-01-04 07:00 | 529 | 529
2018-01-04 07:30 | 561 | 561
2018-01-04 08:00 | 581 | 581
2018-01-04 08:30 | 598 | 598
2018-01-04 09:00 | 618 | 618
2018-01-04 09:30 | 632 | 632
2018-01-04 10:00 | 622 | 622
2018-01-04 10:30 | 625 | 624
2018-01-04 11:00 | 628 | 627
2018-01-04 11:30 | 638 | 637
2018-01-04 12:00 | 643 | 642
2018-01-04 12:30 | 656 | 656
2018-01-04 13:00 | 659 | 658
2018-01-04 13:30 | 696 | 695
2018-01-04 14:00 | 711 | 710
2018-01-04 14:30 | 745 | 744
2018-01-04 15:00 | 741 | 739
2018-01-04 15:30 | 748 | 747
2018-01-04 16:00 | 765 | 763
2018-01-04 16:30 | 769 | 767
2018-01-04 17:00 | 761 | 759
2018-01-04 17:30 | 745 | 744
2018-01-04 18:00 | 793 | 792
2018-01-04 18:30 | 801 | 798
2018-01-04 19:00 | 811 | 808
2018-01-04 19:30 | 807 | 804
2018-01-04 20:00 | 793 | 790
2018-01-04 20:30 | 770 | 767
2018-01-04 21:00 | 745 | 742
2018-01-04 21:30 | 710 | 707
2018-01-04 22:00 | 668 | 666
2018-01-04 22:30 | 634 | 633
2018-01-04 23:00 | 653 | 653
2018-01-04 23:30 | 709 | 709
2018-01-05 | 682 | 682
2018-01-05 00:30 | 663 | 663
2018-01-05 01:00 | 654 | 654
2018-01-05 01:30 | 635 | 635
2018-01-05 02:00 | 628 | 628
2018-01-05 02:30 | 619 | 619
2018-01-05 03:00 | 615 | 614
2018-01-05 03:30 | 602 | 602
2018-01-05 04:00 | 599 | 599
2018-01-05 04:30 | 597 | 597
2018-01-05 05:00 | 596 | 596
2018-01-05 05:30 | 595 | 595
2018-01-05 06:00 | 606 | 606
2018-01-05 06:30 | 619 | 619
2018-01-05 07:00 | 632 | 632
2018-01-05 07:30 | 649 | 648
2018-01-05 08:00 | 671 | 671
2018-01-05 08:30 | 693 | 693
2018-01-05 09:00 | 706 | 706
2018-01-05 09:30 | 710 | 709
2018-01-05 10:00 | 686 | 685
2018-01-05 10:30 | 693 | 692
2018-01-05 11:00 | 717 | 716
2018-01-05 11:30 | 722 | 721
2018-01-05 12:00 | 722 | 721
2018-01-05 12:30 | 726 | 725
2018-01-05 13:00 | 710 | 708
2018-01-05 13:30 | 739 | 738
2018-01-05 14:00 | 729 | 727
2018-01-05 14:30 | 741 | 740
2018-01-05 15:00 | 741 | 740
2018-01-05 15:30 | 731 | 729
2018-01-05 16:00 | 728 | 726
2018-01-05 16:30 | 719 | 717
2018-01-05 17:00 | 716 | 714
2018-01-05 17:30 | 733 | 732
2018-01-05 18:00 | 752 | 750
2018-01-05 18:30 | 753 | 751
2018-01-05 19:00 | 763 | 762
2018-01-05 19:30 | 768 | 767
2018-01-05 20:00 | 762 | 761
2018-01-05 20:30 | 747 | 746
2018-01-05 21:00 | 725 | 724
2018-01-05 21:30 | 708 | 708
2018-01-05 22:00 | 693 | 692
2018-01-05 22:30 | 664 | 663
2018-01-05 23:00 | 643 | 642
2018-01-05 23:30 | 627 | 627
2018-01-06 | 607 | 607
2018-01-06 00:30 | 591 | 591
2018-01-06 01:00 | 579 | 579
2018-01-06 01:30 | 575 | 575
2018-01-06 02:00 | 564 | 564
2018-01-06 02:30 | 561 | 561
2018-01-06 03:00 | 554 | 554
2018-01-06 03:30 | 551 | 551
2018-01-06 04:00 | 544 | 544
2018-01-06 04:30 | 540 | 539
2018-01-06 05:00 | 544 | 544
2018-01-06 05:30 | 545 | 545
2018-01-06 06:00 | 541 | 541
2018-01-06 06:30 | 547 | 547
2018-01-06 07:00 | 551 | 551
2018-01-06 07:30 | 567 | 567
2018-01-06 08:00 | 577 | 577
2018-01-06 08:30 | 590 | 590
2018-01-06 09:00 | 593 | 593
2018-01-06 09:30 | 600 | 600
2018-01-06 10:00 | 583 | 583
2018-01-06 10:30 | 572 | 572
2018-01-06 11:00 | 576 | 576
2018-01-06 11:30 | 578 | 578
2018-01-06 12:00 | 591 | 591
2018-01-06 12:30 | 596 | 596
2018-01-06 13:00 | 605 | 605
2018-01-06 13:30 | 635 | 635
2018-01-06 14:00 | 648 | 648
2018-01-06 14:30 | 659 | 658
2018-01-06 15:00 | 668 | 668
2018-01-06 15:30 | 683 | 683
2018-01-06 16:00 | 697 | 697
2018-01-06 16:30 | 719 | 718
2018-01-06 17:00 | 741 | 740
2018-01-06 17:30 | 742 | 741
2018-01-06 18:00 | 759 | 758
2018-01-06 18:30 | 768 | 766
2018-01-06 19:00 | 784 | 782
2018-01-06 19:30 | 795 | 792
2018-01-06 20:00 | 795 | 792
2018-01-06 20:30 | 777 | 774
2018-01-06 21:00 | 760 | 757
2018-01-06 21:30 | 738 | 735
2018-01-06 22:00 | 719 | 717
2018-01-06 22:30 | 696 | 694
2018-01-06 23:00 | 669 | 668
2018-01-06 23:30 | 647 | 646
2018-01-07 | 631 | 631
2018-01-07 00:30 | 611 | 610
2018-01-07 01:00 | 599 | 599
2018-01-07 01:30 | 583 | 583
2018-01-07 02:00 | 574 | 574
2018-01-07 02:30 | 566 | 566
2018-01-07 03:00 | 562 | 562
2018-01-07 03:30 | 560 | 560
2018-01-07 04:00 | 557 | 557
2018-01-07 04:30 | 556 | 556
2018-01-07 05:00 | 554 | 554
2018-01-07 05:30 | 552 | 552
2018-01-07 06:00 | 550 | 550
2018-01-07 06:30 | 548 | 548
2018-01-07 07:00 | 558 | 558
2018-01-07 07:30 | 568 | 568
2018-01-07 08:00 | 565 | 565
2018-01-07 08:30 | 583 | 583
2018-01-07 09:00 | 595 | 595
2018-01-07 09:30 | 609 | 609
2018-01-07 10:00 | 586 | 586
2018-01-07 10:30 | 584 | 584
2018-01-07 11:00 | 584 | 583
2018-01-07 11:30 | 587 | 587
2018-01-07 12:00 | 588 | 587
2018-01-07 12:30 | 592 | 592
2018-01-07 13:00 | 596 | 595
2018-01-07 13:30 | 625 | 625
2018-01-07 14:00 | 628 | 628
2018-01-07 14:30 | 644 | 643
2018-01-07 15:00 | 651 | 650
2018-01-07 15:30 | 648 | 647
2018-01-07 16:00 | 645 | 644
2018-01-07 16:30 | 656 | 655
2018-01-07 17:00 | 673 | 672
2018-01-07 17:30 | 692 | 691
2018-01-07 18:00 | 720 | 719
2018-01-07 18:30 | 731 | 730
2018-01-07 19:00 | 749 | 747
2018-01-07 19:30 | 763 | 761
2018-01-07 20:00 | 785 | 783
2018-01-07 20:30 | 778 | 776
2018-01-07 21:00 | 761 | 760
2018-01-07 21:30 | 739 | 738
2018-01-07 22:00 | 716 | 715
2018-01-07 22:30 | 682 | 681
2018-01-07 23:00 | 660 | 660
2018-01-07 23:30 | 638 | 637
2018-01-08 | 623 | 623
2018-01-08 00:30 | 603 | 603
2018-01-08 01:00 | 588 | 588
2018-01-08 01:30 | 578 | 578
2018-01-08 02:00 | 571 | 571
2018-01-08 02:30 | 562 | 562
2018-01-08 03:00 | 554 | 554
2018-01-08 03:30 | 550 | 550
2018-01-08 04:00 | 548 | 548
2018-01-08 04:30 | 552 | 552
2018-01-08 05:00 | 555 | 555
2018-01-08 05:30 | 561 | 561
2018-01-08 06:00 | 566 | 566
2018-01-08 06:30 | 585 | 585
2018-01-08 07:00 | 610 | 610
2018-01-08 07:30 | 641 | 640
2018-01-08 08:00 | 654 | 654
2018-01-08 08:30 | 670 | 670
2018-01-08 09:00 | 680 | 679
2018-01-08 09:30 | 682 | 682
2018-01-08 10:00 | 662 | 662
2018-01-08 10:30 | 653 | 652
2018-01-08 11:00 | 653 | 652
2018-01-08 11:30 | 658 | 657
2018-01-08 12:00 | 668 | 668
2018-01-08 12:30 | 674 | 673
2018-01-08 13:00 | 634 | 633
2018-01-08 13:30 | 615 | 615
2018-01-08 14:00 | 571 | 571
2018-01-08 14:30 | 585 | 585
2018-01-08 15:00 | 555 | 555
2018-01-08 15:30 | 562 | 562
2018-01-08 16:00 | 538 | 538
2018-01-08 16:30 | 540 | 540
2018-01-08 17:00 | 557 | 557
2018-01-08 17:30 | 574 | 574
2018-01-08 18:00 | 598 | 597
2018-01-08 18:30 | 685 | 684
2018-01-08 19:00 | 714 | 713
2018-01-08 19:30 | 724 | 722
2018-01-08 20:00 | 720 | 719
2018-01-08 20:30 | 765 | 765
2018-01-08 21:00 | 754 | 753
2018-01-08 21:30 | 726 | 725
2018-01-08 22:00 | 697 | 697
2018-01-08 22:30 | 667 | 667
2018-01-08 23:00 | 640 | 640
2018-01-08 23:30 | 622 | 622
2018-01-09 | 604 | 604
2018-01-09 00:30 | 589 | 589
2018-01-09 01:00 | 575 | 575
2018-01-09 01:30 | 560 | 560
2018-01-09 02:00 | 549 | 549
2018-01-09 02:30 | 549 | 548
2018-01-09 03:00 | 546 | 546
2018-01-09 03:30 | 541 | 540
2018-01-09 04:00 | 535 | 535
2018-01-09 04:30 | 538 | 538
2018-01-09 05:00 | 539 | 538
2018-01-09 05:30 | 544 | 544
2018-01-09 06:00 | 547 | 547
2018-01-09 06:30 | 565 | 565
2018-01-09 07:00 | 590 | 590
2018-01-09 07:30 | 619 | 619
2018-01-09 08:00 | 635 | 635
2018-01-09 08:30 | 653 | 653
2018-01-09 09:00 | 656 | 656
2018-01-09 09:30 | 663 | 663
2018-01-09 10:00 | 637 | 636
2018-01-09 10:30 | 624 | 624
2018-01-09 11:00 | 619 | 619
2018-01-09 11:30 | 625 | 625
2018-01-09 12:00 | 632 | 632
2018-01-09 12:30 | 644 | 644
2018-01-09 13:00 | 673 | 672
2018-01-09 13:30 | 720 | 719
2018-01-09 14:00 | 728 | 726
2018-01-09 14:30 | 737 | 736
2018-01-09 15:00 | 733 | 732
2018-01-09 15:30 | 723 | 722
2018-01-09 16:00 | 730 | 729
2018-01-09 16:30 | 740 | 739
2018-01-09 17:00 | 711 | 710
2018-01-09 17:30 | 712 | 712
2018-01-09 18:00 | 740 | 739
2018-01-09 18:30 | 780 | 779
2018-01-09 19:00 | 802 | 800
2018-01-09 19:30 | 821 | 819
2018-01-09 20:00 | 829 | 827
2018-01-09 20:30 | 809 | 806
2018-01-09 21:00 | 778 | 775
2018-01-09 21:30 | 753 | 751
2018-01-09 22:00 | 723 | 722
2018-01-09 22:30 | 690 | 688
2018-01-09 23:00 | 657 | 656
2018-01-09 23:30 | 636 | 636
2018-01-10 | 611 | 611
2018-01-10 00:30 | 593 | 593
2018-01-10 01:00 | 582 | 582
2018-01-10 01:30 | 569 | 569
2018-01-10 02:00 | 562 | 562
2018-01-10 02:30 | 557 | 557
2018-01-10 03:00 | 547 | 547
2018-01-10 03:30 | 544 | 543
2018-01-10 04:00 | 543 | 543
2018-01-10 04:30 | 542 | 542
2018-01-10 05:00 | 549 | 549
2018-01-10 05:30 | 556 | 556
2018-01-10 06:00 | 560 | 560
2018-01-10 06:30 | 577 | 577
2018-01-10 07:00 | 591 | 591
2018-01-10 07:30 | 622 | 622
2018-01-10 08:00 | 652 | 652
2018-01-10 08:30 | 677 | 677
2018-01-10 09:00 | 687 | 686
2018-01-10 09:30 | 690 | 689
2018-01-10 10:00 | 673 | 671
2018-01-10 10:30 | 666 | 665
2018-01-10 11:00 | 670 | 670
2018-01-10 11:30 | 667 | 666
2018-01-10 12:00 | 676 | 675
2018-01-10 12:30 | 688 | 687
2018-01-10 13:00 | 699 | 698
2018-01-10 13:30 | 701 | 700
2018-01-10 14:00 | 709 | 708
2018-01-10 14:30 | 724 | 723
2018-01-10 15:00 | 738 | 737
2018-01-10 15:30 | 736 | 734
2018-01-10 16:00 | 737 | 736
2018-01-10 16:30 | 753 | 752
2018-01-10 17:00 | 757 | 756
2018-01-10 17:30 | 764 | 763
2018-01-10 18:00 | 774 | 772
2018-01-10 18:30 | 783 | 782
2018-01-10 19:00 | 803 | 802
2018-01-10 19:30 | 823 | 821
2018-01-10 20:00 | 821 | 819
2018-01-10 20:30 | 814 | 812
2018-01-10 21:00 | 791 | 788
2018-01-10 21:30 | 767 | 765
2018-01-10 22:00 | 736 | 734
2018-01-10 22:30 | 695 | 694
2018-01-10 23:00 | 665 | 665
2018-01-10 23:30 | 645 | 645
2018-01-11 | 625 | 625
2018-01-11 00:30 | 610 | 609
2018-01-11 01:00 | 600 | 600
2018-01-11 01:30 | 591 | 591
2018-01-11 02:00 | 585 | 585
2018-01-11 02:30 | 575 | 575
2018-01-11 03:00 | 574 | 574
2018-01-11 03:30 | 568 | 568
2018-01-11 04:00 | 542 | 542
2018-01-11 04:30 | 514 | 514
2018-01-11 05:00 | 501 | 501
2018-01-11 05:30 | 496 | 496
2018-01-11 06:00 | 478 | 478
2018-01-11 06:30 | 496 | 496
2018-01-11 07:00 | 516 | 516
2018-01-11 07:30 | 545 | 545
2018-01-11 08:00 | 554 | 554
2018-01-11 08:30 | 594 | 594
2018-01-11 09:00 | 597 | 596
2018-01-11 09:30 | 587 | 587
2018-01-11 10:00 | 571 | 570
2018-01-11 10:30 | 559 | 558
2018-01-11 11:00 | 577 | 577
2018-01-11 11:30 | 584 | 583
2018-01-11 12:00 | 575 | 574
2018-01-11 12:30 | 568 | 568
2018-01-11 13:00 | 568 | 568
2018-01-11 13:30 | 603 | 602
2018-01-11 14:00 | 570 | 570
2018-01-11 14:30 | 529 | 528
2018-01-11 15:00 | 531 | 531
2018-01-11 15:30 | 512 | 512
2018-01-11 16:00 | 486 | 486
2018-01-11 16:30 | 540 | 540
2018-01-11 17:00 | 546 | 546
2018-01-11 17:30 | 557 | 557
2018-01-11 18:00 | 599 | 599
2018-01-11 18:30 | 625 | 625
2018-01-11 19:00 | 633 | 633
2018-01-11 19:30 | 657 | 657
2018-01-11 20:00 | 644 | 644
2018-01-11 20:30 | 710 | 710
2018-01-11 21:00 | 695 | 693
2018-01-11 21:30 | 670 | 669
2018-01-11 22:00 | 680 | 680
2018-01-11 22:30 | 658 | 657
2018-01-11 23:00 | 624 | 624
2018-01-11 23:30 | 610 | 609
2018-01-12 | 599 | 599
2018-01-12 00:30 | 585 | 585
2018-01-12 01:00 | 575 | 575
2018-01-12 01:30 | 564 | 564
2018-01-12 02:00 | 554 | 554
2018-01-12 02:30 | 555 | 555
2018-01-12 03:00 | 557 | 557
2018-01-12 03:30 | 555 | 555
2018-01-12 04:00 | 553 | 553
2018-01-12 04:30 | 554 | 554
2018-01-12 05:00 | 561 | 561
2018-01-12 05:30 | 574 | 574
2018-01-12 06:00 | 577 | 577
2018-01-12 06:30 | 600 | 600
2018-01-12 07:00 | 622 | 622
2018-01-12 07:30 | 641 | 641
2018-01-12 08:00 | 663 | 662
2018-01-12 08:30 | 642 | 641
2018-01-12 09:00 | 579 | 578
2018-01-12 09:30 | 594 | 594
2018-01-12 10:00 | 579 | 579
2018-01-12 10:30 | 574 | 574
2018-01-12 11:00 | 571 | 571
2018-01-12 11:30 | 556 | 555
2018-01-12 12:00 | 524 | 524
2018-01-12 12:30 | 528 | 528
2018-01-12 13:00 | 508 | 508
2018-01-12 13:30 | 530 | 530
2018-01-12 14:00 | 527 | 527
2018-01-12 14:30 | 518 | 518
2018-01-12 15:00 | 521 | 521
2018-01-12 15:30 | 505 | 505
2018-01-12 16:00 | 438 | 437
2018-01-12 16:30 | 390 | 389
2018-01-12 17:00 | 400 | 398
2018-01-12 17:30 | 400 | 397
2018-01-12 18:00 | 450 | 447
2018-01-12 18:30 | 569 | 568
2018-01-12 19:00 | 600 | 600
2018-01-12 19:30 | 644 | 644
2018-01-12 20:00 | 648 | 648
2018-01-12 20:30 | 652 | 652
2018-01-12 21:00 | 635 | 635
2018-01-12 21:30 | 614 | 614
2018-01-12 22:00 | 587 | 587
2018-01-12 22:30 | 532 | 532
2018-01-12 23:00 | 525 | 524
2018-01-12 23:30 | 510 | 509
2018-01-13 | 493 | 491
2018-01-13 00:30 | 477 | 475
2018-01-13 01:00 | 462 | 460
2018-01-13 01:30 | 452 | 450
2018-01-13 02:00 | 445 | 441
2018-01-13 02:30 | 438 | 435
2018-01-13 03:00 | 427 | 423
2018-01-13 03:30 | 425 | 421
2018-01-13 04:00 | 423 | 418
2018-01-13 04:30 | 419 | 415
2018-01-13 05:00 | 415 | 411
2018-01-13 05:30 | 414 | 410
2018-01-13 06:00 | 409 | 405
2018-01-13 06:30 | 419 | 415
2018-01-13 07:00 | 421 | 417
2018-01-13 07:30 | 428 | 425
2018-01-13 08:00 | 444 | 441
2018-01-13 08:30 | 458 | 455
2018-01-13 09:00 | 468 | 466
2018-01-13 09:30 | 481 | 480
2018-01-13 10:00 | 467 | 465
2018-01-13 10:30 | 460 | 458
2018-01-13 11:00 | 462 | 460
2018-01-13 11:30 | 463 | 461
2018-01-13 12:00 | 441 | 439
2018-01-13 12:30 | 428 | 426
2018-01-13 13:00 | 436 | 433
2018-01-13 13:30 | 490 | 488
2018-01-13 14:00 | 492 | 491
2018-01-13 14:30 | 480 | 479
2018-01-13 15:00 | 503 | 501
2018-01-13 15:30 | 521 | 521
2018-01-13 16:00 | 535 | 534
2018-01-13 16:30 | 449 | 448
2018-01-13 17:00 | 487 | 485
2018-01-13 17:30 | 523 | 522
2018-01-13 18:00 | 544 | 544
2018-01-13 18:30 | 560 | 560
2018-01-13 19:00 | 568 | 567
2018-01-13 19:30 | 659 | 659
2018-01-13 20:00 | 751 | 751
2018-01-13 20:30 | 735 | 734
2018-01-13 21:00 | 745 | 745
2018-01-13 21:30 | 745 | 744
2018-01-13 22:00 | 721 | 721
2018-01-13 22:30 | 692 | 692
2018-01-13 23:00 | 670 | 670
2018-01-13 23:30 | 647 | 647
2018-01-14 | 630 | 630
2018-01-14 00:30 | 608 | 608
2018-01-14 01:00 | 599 | 599
2018-01-14 01:30 | 593 | 593
2018-01-14 02:00 | 580 | 579
2018-01-14 02:30 | 569 | 568
2018-01-14 03:00 | 567 | 566
2018-01-14 03:30 | 566 | 565
2018-01-14 04:00 | 563 | 562
2018-01-14 04:30 | 560 | 560
2018-01-14 05:00 | 560 | 559
2018-01-14 05:30 | 560 | 560
2018-01-14 06:00 | 549 | 548
2018-01-14 06:30 | 547 | 546
2018-01-14 07:00 | 550 | 549
2018-01-14 07:30 | 560 | 559
2018-01-14 08:00 | 570 | 569
2018-01-14 08:30 | 575 | 574
2018-01-14 09:00 | 587 | 586
2018-01-14 09:30 | 587 | 587
2018-01-14 10:00 | 577 | 577
2018-01-14 10:30 | 569 | 569
2018-01-14 11:00 | 575 | 574
2018-01-14 11:30 | 590 | 590
2018-01-14 12:00 | 598 | 597
2018-01-14 12:30 | 616 | 616
2018-01-14 13:00 | 614 | 614
2018-01-14 13:30 | 633 | 632
2018-01-14 14:00 | 655 | 655
2018-01-14 14:30 | 625 | 625
2018-01-14 15:00 | 599 | 599
2018-01-14 15:30 | 551 | 551
2018-01-14 16:00 | 565 | 565
2018-01-14 16:30 | 568 | 567
2018-01-14 17:00 | 589 | 589
2018-01-14 17:30 | 605 | 605
2018-01-14 18:00 | 616 | 616
2018-01-14 18:30 | 693 | 693
2018-01-14 19:00 | 724 | 724
2018-01-14 19:30 | 737 | 737
2018-01-14 20:00 | 801 | 800
2018-01-14 20:30 | 820 | 819
2018-01-14 21:00 | 804 | 803
2018-01-14 21:30 | 770 | 769
2018-01-14 22:00 | 736 | 736
2018-01-14 22:30 | 700 | 700
2018-01-14 23:00 | 673 | 673
2018-01-14 23:30 | 652 | 652
2018-01-15 | 630 | 630
2018-01-15 00:30 | 614 | 614
2018-01-15 01:00 | 600 | 599
2018-01-15 01:30 | 586 | 586
2018-01-15 02:00 | 580 | 580
2018-01-15 02:30 | 576 | 576
2018-01-15 03:00 | 576 | 576
2018-01-15 03:30 | 568 | 568
2018-01-15 04:00 | 567 | 567
2018-01-15 04:30 | 573 | 573
2018-01-15 05:00 | 578 | 578
2018-01-15 05:30 | 582 | 582
2018-01-15 06:00 | 590 | 590
2018-01-15 06:30 | 615 | 615
2018-01-15 07:00 | 644 | 644
2018-01-15 07:30 | 683 | 683
2018-01-15 08:00 | 704 | 704
2018-01-15 08:30 | 726 | 726
2018-01-15 09:00 | 744 | 744
2018-01-15 09:30 | 739 | 739
2018-01-15 10:00 | 725 | 725
2018-01-15 10:30 | 712 | 711
2018-01-15 11:00 | 718 | 717
2018-01-15 11:30 | 723 | 722
2018-01-15 12:00 | 745 | 745
2018-01-15 12:30 | 770 | 770
2018-01-15 13:00 | 786 | 784
2018-01-15 13:30 | 811 | 809
2018-01-15 14:00 | 822 | 820
2018-01-15 14:30 | 843 | 841
2018-01-15 15:00 | 864 | 862
2018-01-15 15:30 | 872 | 870
2018-01-15 16:00 | 834 | 831
2018-01-15 16:30 | 813 | 811
2018-01-15 17:00 | 792 | 791
2018-01-15 17:30 | 782 | 781
2018-01-15 18:00 | 802 | 801
2018-01-15 18:30 | 815 | 814
2018-01-15 19:00 | 823 | 822
2018-01-15 19:30 | 827 | 826
2018-01-15 20:00 | 820 | 818
2018-01-15 20:30 | 804 | 803
2018-01-15 21:00 | 782 | 781
2018-01-15 21:30 | 740 | 739
2018-01-15 22:00 | 680 | 680
2018-01-15 22:30 | 635 | 635
2018-01-15 23:00 | 610 | 610
2018-01-15 23:30 | 587 | 587
2018-01-16 | 567 | 567
2018-01-16 00:30 | 553 | 552
2018-01-16 01:00 | 540 | 538
2018-01-16 01:30 | 529 | 528
2018-01-16 02:00 | 528 | 527
2018-01-16 02:30 | 521 | 520
2018-01-16 03:00 | 502 | 500
2018-01-16 03:30 | 497 | 495
2018-01-16 04:00 | 544 | 542
2018-01-16 04:30 | 546 | 544
2018-01-16 05:00 | 553 | 552
2018-01-16 05:30 | 555 | 554
2018-01-16 06:00 | 568 | 567
2018-01-16 06:30 | 584 | 583
2018-01-16 07:00 | 600 | 600
2018-01-16 07:30 | 617 | 616
2018-01-16 08:00 | 644 | 643
2018-01-16 08:30 | 655 | 655
2018-01-16 09:00 | 655 | 655
2018-01-16 09:30 | 667 | 667
2018-01-16 10:00 | 657 | 657
2018-01-16 10:30 | 639 | 639
2018-01-16 11:00 | 630 | 630
2018-01-16 11:30 | 626 | 626
2018-01-16 12:00 | 640 | 640
2018-01-16 12:30 | 654 | 654
2018-01-16 13:00 | 639 | 639
2018-01-16 13:30 | 639 | 639
2018-01-16 14:00 | 626 | 626
2018-01-16 14:30 | 624 | 624
2018-01-16 15:00 | 628 | 628
2018-01-16 15:30 | 658 | 658
2018-01-16 16:00 | 673 | 673
2018-01-16 16:30 | 693 | 693
2018-01-16 17:00 | 697 | 697
2018-01-16 17:30 | 682 | 682
2018-01-16 18:00 | 728 | 728
2018-01-16 18:30 | 750 | 750
2018-01-16 19:00 | 763 | 763
2018-01-16 19:30 | 772 | 772
2018-01-16 20:00 | 774 | 774
2018-01-16 20:30 | 774 | 773
2018-01-16 21:00 | 754 | 754
2018-01-16 21:30 | 729 | 728
2018-01-16 22:00 | 707 | 706
2018-01-16 22:30 | 672 | 672
2018-01-16 23:00 | 644 | 644
2018-01-16 23:30 | 624 | 624
2018-01-17 | 608 | 608
2018-01-17 00:30 | 589 | 589
2018-01-17 01:00 | 571 | 571
2018-01-17 01:30 | 567 | 567
2018-01-17 02:00 | 559 | 559
2018-01-17 02:30 | 556 | 556
2018-01-17 03:00 | 556 | 555
2018-01-17 03:30 | 555 | 555
2018-01-17 04:00 | 551 | 551
2018-01-17 04:30 | 547 | 546
2018-01-17 05:00 | 551 | 550
2018-01-17 05:30 | 558 | 558
2018-01-17 06:00 | 566 | 566
2018-01-17 06:30 | 587 | 587
2018-01-17 07:00 | 609 | 608
2018-01-17 07:30 | 646 | 646
2018-01-17 08:00 | 665 | 665
2018-01-17 08:30 | 676 | 676
2018-01-17 09:00 | 666 | 666
2018-01-17 09:30 | 649 | 649
2018-01-17 10:00 | 578 | 578
2018-01-17 10:30 | 553 | 552
2018-01-17 11:00 | 540 | 539
2018-01-17 11:30 | 548 | 547
2018-01-17 12:00 | 558 | 558
2018-01-17 12:30 | 558 | 558
2018-01-17 13:00 | 558 | 558
2018-01-17 13:30 | 596 | 596
2018-01-17 14:00 | 574 | 574
2018-01-17 14:30 | 588 | 588
2018-01-17 15:00 | 592 | 592
2018-01-17 15:30 | 600 | 600
2018-01-17 16:00 | 609 | 609
2018-01-17 16:30 | 619 | 619
2018-01-17 17:00 | 615 | 615
2018-01-17 17:30 | 616 | 616
2018-01-17 18:00 | 624 | 624
2018-01-17 18:30 | 629 | 629
2018-01-17 19:00 | 647 | 647
2018-01-17 19:30 | 658 | 658
2018-01-17 20:00 | 657 | 657
2018-01-17 20:30 | 654 | 654
2018-01-17 21:00 | 652 | 652
2018-01-17 21:30 | 630 | 630
2018-01-17 22:00 | 598 | 598
2018-01-17 22:30 | 578 | 578
2018-01-17 23:00 | 577 | 577
2018-01-17 23:30 | 560 | 559
2018-01-18 | 545 | 544
2018-01-18 00:30 | 530 | 529
2018-01-18 01:00 | 515 | 514
2018-01-18 01:30 | 506 | 504
2018-01-18 02:00 | 502 | 501
2018-01-18 02:30 | 501 | 500
2018-01-18 03:00 | 498 | 497
2018-01-18 03:30 | 515 | 514
2018-01-18 04:00 | 519 | 519
2018-01-18 04:30 | 522 | 522
2018-01-18 05:00 | 529 | 528
2018-01-18 05:30 | 529 | 529
2018-01-18 06:00 | 526 | 525
2018-01-18 06:30 | 548 | 547
2018-01-18 07:00 | 567 | 567
2018-01-18 07:30 | 589 | 589
2018-01-18 08:00 | 609 | 609
2018-01-18 08:30 | 634 | 634
2018-01-18 09:00 | 631 | 631
2018-01-18 09:30 | 626 | 626
2018-01-18 10:00 | 613 | 613
2018-01-18 10:30 | 598 | 598
2018-01-18 11:00 | 590 | 590
2018-01-18 11:30 | 577 | 577
2018-01-18 12:00 | 588 | 588
2018-01-18 12:30 | 581 | 581
2018-01-18 13:00 | 594 | 594
2018-01-18 13:30 | 634 | 634
2018-01-18 14:00 | 616 | 616
2018-01-18 14:30 | 617 | 617
2018-01-18 15:00 | 606 | 606
2018-01-18 15:30 | 624 | 624
2018-01-18 16:00 | 594 | 594
2018-01-18 16:30 | 558 | 558
2018-01-18 17:00 | 554 | 554
2018-01-18 17:30 | 556 | 556
2018-01-18 18:00 | 607 | 607
2018-01-18 18:30 | 626 | 626
2018-01-18 19:00 | 635 | 635
2018-01-18 19:30 | 645 | 645
2018-01-18 20:00 | 635 | 635
2018-01-18 20:30 | 610 | 610
2018-01-18 21:00 | 589 | 589
2018-01-18 21:30 | 669 | 669
2018-01-18 22:00 | 652 | 652
2018-01-18 22:30 | 619 | 619
2018-01-18 23:00 | 581 | 581
2018-01-18 23:30 | 557 | 557
2018-01-19 | 542 | 542
2018-01-19 00:30 | 528 | 527
2018-01-19 01:00 | 519 | 518
2018-01-19 01:30 | 516 | 515
2018-01-19 02:00 | 509 | 508
2018-01-19 02:30 | 505 | 504
2018-01-19 03:00 | 521 | 519
2018-01-19 03:30 | 519 | 517
2018-01-19 04:00 | 515 | 513
2018-01-19 04:30 | 514 | 513
2018-01-19 05:00 | 518 | 517
2018-01-19 05:30 | 523 | 522
2018-01-19 06:00 | 532 | 530
2018-01-19 06:30 | 551 | 550
2018-01-19 07:00 | 528 | 527
2018-01-19 07:30 | 527 | 526
2018-01-19 08:00 | 542 | 541
2018-01-19 08:30 | 532 | 532
2018-01-19 09:00 | 494 | 493
2018-01-19 09:30 | 496 | 495
2018-01-19 10:00 | 463 | 462
2018-01-19 10:30 | 456 | 453
2018-01-19 11:00 | 448 | 446
2018-01-19 11:30 | 429 | 426
2018-01-19 12:00 | 389 | 386
2018-01-19 12:30 | 404 | 401
2018-01-19 13:00 | 403 | 401
2018-01-19 13:30 | 361 | 359
2018-01-19 14:00 | 347 | 343
2018-01-19 14:30 | 358 | 353
2018-01-19 15:00 | 354 | 349
2018-01-19 15:30 | 355 | 351
2018-01-19 16:00 | 344 | 340
2018-01-19 16:30 | 357 | 353
2018-01-19 17:00 | 374 | 370
2018-01-19 17:30 | 368 | 365
2018-01-19 18:00 | 376 | 372
2018-01-19 18:30 | 380 | 377
2018-01-19 19:00 | 401 | 399
2018-01-19 19:30 | 416 | 413
2018-01-19 20:00 | 416 | 414
2018-01-19 20:30 | 420 | 418
2018-01-19 21:00 | 405 | 402
2018-01-19 21:30 | 386 | 383
2018-01-19 22:00 | 366 | 362
2018-01-19 22:30 | 428 | 424
2018-01-19 23:00 | 509 | 507
2018-01-19 23:30 | 519 | 518
2018-01-20 | 500 | 499
2018-01-20 00:30 | 491 | 490
2018-01-20 01:00 | 477 | 475
2018-01-20 01:30 | 462 | 460
2018-01-20 02:00 | 450 | 448
2018-01-20 02:30 | 443 | 441
2018-01-20 03:00 | 438 | 436
2018-01-20 03:30 | 436 | 434
2018-01-20 04:00 | 433 | 431
2018-01-20 04:30 | 461 | 459
2018-01-20 05:00 | 472 | 470
2018-01-20 05:30 | 476 | 474
2018-01-20 06:00 | 477 | 475
2018-01-20 06:30 | 483 | 482
2018-01-20 07:00 | 482 | 481
2018-01-20 07:30 | 489 | 487
2018-01-20 08:00 | 502 | 501
2018-01-20 08:30 | 520 | 519
2018-01-20 09:00 | 528 | 528
2018-01-20 09:30 | 529 | 529
2018-01-20 10:00 | 526 | 525
2018-01-20 10:30 | 522 | 521
2018-01-20 11:00 | 521 | 520
2018-01-20 11:30 | 522 | 521
2018-01-20 12:00 | 525 | 525
2018-01-20 12:30 | 526 | 526
2018-01-20 13:00 | 514 | 514
2018-01-20 13:30 | 525 | 524
2018-01-20 14:00 | 522 | 522
2018-01-20 14:30 | 530 | 529
2018-01-20 15:00 | 538 | 538
2018-01-20 15:30 | 551 | 550
2018-01-20 16:00 | 558 | 557
2018-01-20 16:30 | 571 | 571
2018-01-20 17:00 | 595 | 595
2018-01-20 17:30 | 622 | 622
2018-01-20 18:00 | 634 | 634
2018-01-20 18:30 | 645 | 645
2018-01-20 19:00 | 655 | 655
2018-01-20 19:30 | 667 | 667
2018-01-20 20:00 | 656 | 656
2018-01-20 20:30 | 657 | 657
2018-01-20 21:00 | 647 | 647
2018-01-20 21:30 | 624 | 624
2018-01-20 22:00 | 612 | 612
2018-01-20 22:30 | 589 | 589
2018-01-20 23:00 | 565 | 565
2018-01-20 23:30 | 548 | 547
2018-01-21 | 533 | 533
2018-01-21 00:30 | 541 | 541
2018-01-21 01:00 | 538 | 537
2018-01-21 01:30 | 527 | 527
2018-01-21 02:00 | 521 | 520
2018-01-21 02:30 | 514 | 513
2018-01-21 03:00 | 512 | 511
2018-01-21 03:30 | 507 | 506
2018-01-21 04:00 | 501 | 500
2018-01-21 04:30 | 507 | 506
2018-01-21 05:00 | 505 | 504
2018-01-21 05:30 | 505 | 504
2018-01-21 06:00 | 492 | 490
2018-01-21 06:30 | 483 | 482
2018-01-21 07:00 | 495 | 493
2018-01-21 07:30 | 509 | 507
2018-01-21 08:00 | 517 | 516
2018-01-21 08:30 | 528 | 527
2018-01-21 09:00 | 531 | 531
2018-01-21 09:30 | 533 | 532
2018-01-21 10:00 | 522 | 521
2018-01-21 10:30 | 493 | 493
2018-01-21 11:00 | 504 | 503
2018-01-21 11:30 | 506 | 505
2018-01-21 12:00 | 507 | 507
2018-01-21 12:30 | 504 | 503
2018-01-21 13:00 | 510 | 510
2018-01-21 13:30 | 533 | 533
2018-01-21 14:00 | 543 | 542
2018-01-21 14:30 | 549 | 548
2018-01-21 15:00 | 556 | 556
2018-01-21 15:30 | 581 | 581
2018-01-21 16:00 | 590 | 590
2018-01-21 16:30 | 595 | 595
2018-01-21 17:00 | 602 | 602
2018-01-21 17:30 | 618 | 618
2018-01-21 18:00 | 638 | 638
2018-01-21 18:30 | 658 | 658
2018-01-21 19:00 | 670 | 670
2018-01-21 19:30 | 688 | 688
2018-01-21 20:00 | 695 | 695
2018-01-21 20:30 | 698 | 698
2018-01-21 21:00 | 691 | 691
2018-01-21 21:30 | 677 | 677
2018-01-21 22:00 | 657 | 657
2018-01-21 22:30 | 631 | 631
2018-01-21 23:00 | 605 | 605
2018-01-21 23:30 | 585 | 584
2018-01-22 | 573 | 573
2018-01-22 00:30 | 561 | 560
2018-01-22 01:00 | 553 | 553
2018-01-22 01:30 | 543 | 542
2018-01-22 02:00 | 531 | 531
2018-01-22 02:30 | 530 | 529
2018-01-22 03:00 | 529 | 528
2018-01-22 03:30 | 526 | 526
2018-01-22 04:00 | 530 | 529
2018-01-22 04:30 | 533 | 532
2018-01-22 05:00 | 535 | 534
2018-01-22 05:30 | 514 | 513
2018-01-22 06:00 | 482 | 481
2018-01-22 06:30 | 512 | 510
2018-01-22 07:00 | 549 | 548
2018-01-22 07:30 | 588 | 588
2018-01-22 08:00 | 593 | 593
2018-01-22 08:30 | 549 | 549
2018-01-22 09:00 | 518 | 517
2018-01-22 09:30 | 526 | 525
2018-01-22 10:00 | 502 | 501
2018-01-22 10:30 | 498 | 497
2018-01-22 11:00 | 507 | 506
2018-01-22 11:30 | 501 | 500
2018-01-22 12:00 | 505 | 504
2018-01-22 12:30 | 502 | 501
2018-01-22 13:00 | 490 | 489
2018-01-22 13:30 | 484 | 483
2018-01-22 14:00 | 481 | 480
2018-01-22 14:30 | 489 | 488
2018-01-22 15:00 | 499 | 498
2018-01-22 15:30 | 500 | 499
2018-01-22 16:00 | 470 | 469
2018-01-22 16:30 | 499 | 498
2018-01-22 17:00 | 521 | 521
2018-01-22 17:30 | 539 | 538
2018-01-22 18:00 | 548 | 548
2018-01-22 18:30 | 562 | 562
2018-01-22 19:00 | 579 | 579
2018-01-22 19:30 | 595 | 595
2018-01-22 20:00 | 603 | 603
2018-01-22 20:30 | 626 | 626
2018-01-22 21:00 | 618 | 618
2018-01-22 21:30 | 595 | 595
2018-01-22 22:00 | 569 | 569
2018-01-22 22:30 | 535 | 534
2018-01-22 23:00 | 503 | 503
2018-01-22 23:30 | 482 | 481
2018-01-23 | 461 | 460
2018-01-23 00:30 | 450 | 448
2018-01-23 01:00 | 439 | 437
2018-01-23 01:30 | 434 | 432
2018-01-23 02:00 | 424 | 421
2018-01-23 02:30 | 417 | 414
2018-01-23 03:00 | 417 | 413
2018-01-23 03:30 | 415 | 411
2018-01-23 04:00 | 415 | 411
2018-01-23 04:30 | 416 | 412
2018-01-23 05:00 | 418 | 415
2018-01-23 05:30 | 432 | 428
2018-01-23 06:00 | 447 | 444
2018-01-23 06:30 | 478 | 476
2018-01-23 07:00 | 499 | 497
2018-01-23 07:30 | 528 | 526
2018-01-23 08:00 | 535 | 534
2018-01-23 08:30 | 542 | 541
2018-01-23 09:00 | 549 | 548
2018-01-23 09:30 | 551 | 550
2018-01-23 10:00 | 524 | 523
2018-01-23 10:30 | 514 | 513
2018-01-23 11:00 | 527 | 526
2018-01-23 11:30 | 519 | 519
2018-01-23 12:00 | 511 | 510
2018-01-23 12:30 | 529 | 528
2018-01-23 13:00 | 533 | 533
2018-01-23 13:30 | 553 | 553
2018-01-23 14:00 | 570 | 570
2018-01-23 14:30 | 576 | 575
2018-01-23 15:00 | 577 | 576
2018-01-23 15:30 | 570 | 570
2018-01-23 16:00 | 487 | 487
2018-01-23 16:30 | 485 | 484
2018-01-23 17:00 | 497 | 496
2018-01-23 17:30 | 497 | 497
2018-01-23 18:00 | 500 | 500
2018-01-23 18:30 | 517 | 516
2018-01-23 19:00 | 544 | 544
2018-01-23 19:30 | 578 | 578
2018-01-23 20:00 | 641 | 641
2018-01-23 20:30 | 639 | 639
2018-01-23 21:00 | 616 | 616
2018-01-23 21:30 | 590 | 590
2018-01-23 22:00 | 566 | 566
2018-01-23 22:30 | 532 | 532
2018-01-23 23:00 | 507 | 507
2018-01-23 23:30 | 487 | 487
2018-01-24 | 469 | 469
2018-01-24 00:30 | 456 | 455
2018-01-24 01:00 | 445 | 443
2018-01-24 01:30 | 437 | 435
2018-01-24 02:00 | 429 | 427
2018-01-24 02:30 | 424 | 422
2018-01-24 03:00 | 426 | 424
2018-01-24 03:30 | 425 | 423
2018-01-24 04:00 | 426 | 423
2018-01-24 04:30 | 422 | 419
2018-01-24 05:00 | 425 | 423
2018-01-24 05:30 | 433 | 430
2018-01-24 06:00 | 450 | 447
2018-01-24 06:30 | 470 | 468
2018-01-24 07:00 | 501 | 500
2018-01-24 07:30 | 526 | 525
2018-01-24 08:00 | 530 | 529
2018-01-24 08:30 | 534 | 534
2018-01-24 09:00 | 543 | 542
2018-01-24 09:30 | 546 | 546
2018-01-24 10:00 | 533 | 532
2018-01-24 10:30 | 523 | 522
2018-01-24 11:00 | 525 | 524
2018-01-24 11:30 | 523 | 522
2018-01-24 12:00 | 536 | 536
2018-01-24 12:30 | 542 | 541
2018-01-24 13:00 | 518 | 517
2018-01-24 13:30 | 486 | 485
2018-01-24 14:00 | 487 | 486
2018-01-24 14:30 | 487 | 485
2018-01-24 15:00 | 487 | 486
2018-01-24 15:30 | 440 | 439
2018-01-24 16:00 | 443 | 441
2018-01-24 16:30 | 451 | 449
2018-01-24 17:00 | 468 | 466
2018-01-24 17:30 | 501 | 499
2018-01-24 18:00 | 508 | 506
2018-01-24 18:30 | 525 | 524
2018-01-24 19:00 | 545 | 544
2018-01-24 19:30 | 552 | 551
2018-01-24 20:00 | 609 | 609
2018-01-24 20:30 | 581 | 581
2018-01-24 21:00 | 557 | 557
2018-01-24 21:30 | 525 | 524
2018-01-24 22:00 | 500 | 500
2018-01-24 22:30 | 464 | 463
2018-01-24 23:00 | 443 | 441
2018-01-24 23:30 | 477 | 475
2018-01-25 | 539 | 538
2018-01-25 00:30 | 576 | 575
2018-01-25 01:00 | 576 | 576
2018-01-25 01:30 | 565 | 565
2018-01-25 02:00 | 560 | 560
2018-01-25 02:30 | 559 | 559
2018-01-25 03:00 | 554 | 554
2018-01-25 03:30 | 551 | 551
2018-01-25 04:00 | 549 | 548
2018-01-25 04:30 | 551 | 550
2018-01-25 05:00 | 555 | 555
2018-01-25 05:30 | 567 | 566
2018-01-25 06:00 | 550 | 550
2018-01-25 06:30 | 573 | 572
2018-01-25 07:00 | 576 | 575
2018-01-25 07:30 | 578 | 578
2018-01-25 08:00 | 589 | 589
2018-01-25 08:30 | 591 | 590
2018-01-25 09:00 | 593 | 593
2018-01-25 09:30 | 587 | 586
2018-01-25 10:00 | 586 | 585
2018-01-25 10:30 | 574 | 573
2018-01-25 11:00 | 587 | 587
2018-01-25 11:30 | 579 | 578
2018-01-25 12:00 | 564 | 563
2018-01-25 12:30 | 582 | 581
2018-01-25 13:00 | 605 | 604
2018-01-25 13:30 | 606 | 606
2018-01-25 14:00 | 613 | 613
2018-01-25 14:30 | 606 | 605
2018-01-25 15:00 | 588 | 588
2018-01-25 15:30 | 563 | 563
2018-01-25 16:00 | 559 | 559
2018-01-25 16:30 | 563 | 562
2018-01-25 17:00 | 592 | 592
2018-01-25 17:30 | 604 | 604
2018-01-25 18:00 | 622 | 622
2018-01-25 18:30 | 622 | 622
2018-01-25 19:00 | 635 | 635
2018-01-25 19:30 | 685 | 684
2018-01-25 20:00 | 682 | 682
2018-01-25 20:30 | 661 | 661
2018-01-25 21:00 | 636 | 636
2018-01-25 21:30 | 619 | 619
2018-01-25 22:00 | 597 | 596
2018-01-25 22:30 | 601 | 601
2018-01-25 23:00 | 580 | 579
2018-01-25 23:30 | 558 | 557
2018-01-26 | 537 | 536
2018-01-26 00:30 | 527 | 526
2018-01-26 01:00 | 515 | 514
2018-01-26 01:30 | 501 | 500
2018-01-26 02:00 | 490 | 488
2018-01-26 02:30 | 487 | 485
2018-01-26 03:00 | 483 | 481
2018-01-26 03:30 | 481 | 479
2018-01-26 04:00 | 476 | 474
2018-01-26 04:30 | 460 | 458
2018-01-26 05:00 | 473 | 471
2018-01-26 05:30 | 477 | 474
2018-01-26 06:00 | 479 | 477
2018-01-26 06:30 | 488 | 486
2018-01-26 07:00 | 497 | 495
2018-01-26 07:30 | 491 | 489
2018-01-26 08:00 | 492 | 490
2018-01-26 08:30 | 509 | 508
2018-01-26 09:00 | 517 | 516
2018-01-26 09:30 | 521 | 520
2018-01-26 10:00 | 520 | 519
2018-01-26 10:30 | 529 | 527
2018-01-26 11:00 | 506 | 505
2018-01-26 11:30 | 489 | 488
2018-01-26 12:00 | 471 | 470
2018-01-26 12:30 | 455 | 454
2018-01-26 13:00 | 477 | 476
2018-01-26 13:30 | 476 | 475
2018-01-26 14:00 | 463 | 462
2018-01-26 14:30 | 470 | 469
2018-01-26 15:00 | 494 | 493
2018-01-26 15:30 | 504 | 504
2018-01-26 16:00 | 512 | 511
2018-01-26 16:30 | 519 | 519
2018-01-26 17:00 | 536 | 535
2018-01-26 17:30 | 538 | 538
2018-01-26 18:00 | 553 | 553
2018-01-26 18:30 | 562 | 561
2018-01-26 19:00 | 579 | 579
2018-01-26 19:30 | 639 | 639
2018-01-26 20:00 | 638 | 638
2018-01-26 20:30 | 625 | 625
2018-01-26 21:00 | 608 | 608
2018-01-26 21:30 | 595 | 595
2018-01-26 22:00 | 582 | 582
2018-01-26 22:30 | 574 | 574
2018-01-26 23:00 | 555 | 555
2018-01-26 23:30 | 536 | 535
2018-01-27 | 519 | 518
2018-01-27 00:30 | 503 | 502
2018-01-27 01:00 | 493 | 492
2018-01-27 01:30 | 481 | 480
2018-01-27 02:00 | 473 | 472
2018-01-27 02:30 | 472 | 470
2018-01-27 03:00 | 466 | 464
2018-01-27 03:30 | 466 | 464
2018-01-27 04:00 | 459 | 457
2018-01-27 04:30 | 456 | 454
2018-01-27 05:00 | 454 | 452
2018-01-27 05:30 | 458 | 456
2018-01-27 06:00 | 458 | 456
2018-01-27 06:30 | 460 | 458
2018-01-27 07:00 | 462 | 460
2018-01-27 07:30 | 460 | 458
2018-01-27 08:00 | 469 | 468
2018-01-27 08:30 | 492 | 491
2018-01-27 09:00 | 501 | 500
2018-01-27 09:30 | 513 | 512
2018-01-27 10:00 | 509 | 508
2018-01-27 10:30 | 506 | 505
2018-01-27 11:00 | 501 | 500
2018-01-27 11:30 | 503 | 502
2018-01-27 12:00 | 502 | 501
2018-01-27 12:30 | 511 | 510
2018-01-27 13:00 | 512 | 512
2018-01-27 13:30 | 507 | 507
2018-01-27 14:00 | 509 | 508
2018-01-27 14:30 | 521 | 520
2018-01-27 15:00 | 529 | 528
2018-01-27 15:30 | 505 | 504
2018-01-27 16:00 | 522 | 521
2018-01-27 16:30 | 535 | 534
2018-01-27 17:00 | 549 | 548
2018-01-27 17:30 | 573 | 572
2018-01-27 18:00 | 590 | 590
2018-01-27 18:30 | 644 | 644
2018-01-27 19:00 | 655 | 655
2018-01-27 19:30 | 676 | 676
2018-01-27 20:00 | 677 | 677
2018-01-27 20:30 | 682 | 682
2018-01-27 21:00 | 674 | 674
2018-01-27 21:30 | 660 | 660
2018-01-27 22:00 | 639 | 638
2018-01-27 22:30 | 615 | 614
2018-01-27 23:00 | 594 | 593
2018-01-27 23:30 | 567 | 566
2018-01-28 | 543 | 542
2018-01-28 00:30 | 526 | 525
2018-01-28 01:00 | 512 | 511
2018-01-28 01:30 | 503 | 501
2018-01-28 02:00 | 491 | 489
2018-01-28 02:30 | 488 | 485
2018-01-28 03:00 | 487 | 484
2018-01-28 03:30 | 482 | 480
2018-01-28 04:00 | 474 | 471
2018-01-28 04:30 | 475 | 472
2018-01-28 05:00 | 476 | 473
2018-01-28 05:30 | 473 | 470
2018-01-28 06:00 | 470 | 467
2018-01-28 06:30 | 473 | 470
2018-01-28 07:00 | 471 | 467
2018-01-28 07:30 | 443 | 440
2018-01-28 08:00 | 455 | 451
2018-01-28 08:30 | 460 | 457
2018-01-28 09:00 | 471 | 468
2018-01-28 09:30 | 500 | 498
2018-01-28 10:00 | 521 | 519
2018-01-28 10:30 | 534 | 532
2018-01-28 11:00 | 533 | 532
2018-01-28 11:30 | 545 | 544
2018-01-28 12:00 | 549 | 549
2018-01-28 12:30 | 542 | 542
2018-01-28 13:00 | 546 | 545
2018-01-28 13:30 | 547 | 547
2018-01-28 14:00 | 555 | 555
2018-01-28 14:30 | 539 | 538
2018-01-28 15:00 | 555 | 554
2018-01-28 15:30 | 524 | 523
2018-01-28 16:00 | 516 | 516
2018-01-28 16:30 | 536 | 535
2018-01-28 17:00 | 568 | 567
2018-01-28 17:30 | 587 | 586
2018-01-28 18:00 | 634 | 634
2018-01-28 18:30 | 655 | 655
2018-01-28 19:00 | 672 | 672
2018-01-28 19:30 | 743 | 743
2018-01-28 20:00 | 744 | 744
2018-01-28 20:30 | 724 | 724
2018-01-28 21:00 | 703 | 702
2018-01-28 21:30 | 671 | 671
2018-01-28 22:00 | 643 | 643
2018-01-28 22:30 | 649 | 649
2018-01-28 23:00 | 623 | 623
2018-01-28 23:30 | 596 | 595
2018-01-29 | 573 | 573
2018-01-29 00:30 | 564 | 564
2018-01-29 01:00 | 555 | 554
2018-01-29 01:30 | 541 | 540
2018-01-29 02:00 | 528 | 527
2018-01-29 02:30 | 523 | 522
2018-01-29 03:00 | 518 | 517
2018-01-29 03:30 | 515 | 514
2018-01-29 04:00 | 517 | 516
2018-01-29 04:30 | 523 | 522
2018-01-29 05:00 | 522 | 521
2018-01-29 05:30 | 536 | 535
2018-01-29 06:00 | 550 | 550
2018-01-29 06:30 | 577 | 577
2018-01-29 07:00 | 599 | 599
2018-01-29 07:30 | 597 | 596
2018-01-29 08:00 | 613 | 613
2018-01-29 08:30 | 576 | 576
2018-01-29 09:00 | 549 | 549
2018-01-29 09:30 | 545 | 545
2018-01-29 10:00 | 554 | 554
2018-01-29 10:30 | 548 | 548
2018-01-29 11:00 | 550 | 550
2018-01-29 11:30 | 524 | 524
2018-01-29 12:00 | 495 | 495
2018-01-29 12:30 | 517 | 517
2018-01-29 13:00 | 521 | 521
2018-01-29 13:30 | 514 | 514
2018-01-29 14:00 | 526 | 526
2018-01-29 14:30 | 544 | 544
2018-01-29 15:00 | 546 | 546
2018-01-29 15:30 | 518 | 518
2018-01-29 16:00 | 536 | 536
2018-01-29 16:30 | 561 | 561
2018-01-29 17:00 | 578 | 578
2018-01-29 17:30 | 587 | 587
2018-01-29 18:00 | 593 | 593
2018-01-29 18:30 | 609 | 609
2018-01-29 19:00 | 632 | 632
2018-01-29 19:30 | 678 | 678
2018-01-29 20:00 | 675 | 675
2018-01-29 20:30 | 650 | 649
2018-01-29 21:00 | 625 | 625
2018-01-29 21:30 | 591 | 591
2018-01-29 22:00 | 562 | 562
2018-01-29 22:30 | 550 | 550
2018-01-29 23:00 | 522 | 522
2018-01-29 23:30 | 493 | 493
2018-01-30 | 472 | 471
2018-01-30 00:30 | 457 | 456
2018-01-30 01:00 | 438 | 437
2018-01-30 01:30 | 430 | 429
2018-01-30 02:00 | 423 | 421
2018-01-30 02:30 | 413 | 411
2018-01-30 03:00 | 407 | 405
2018-01-30 03:30 | 404 | 401
2018-01-30 04:00 | 400 | 397
2018-01-30 04:30 | 403 | 400
2018-01-30 05:00 | 411 | 408
2018-01-30 05:30 | 419 | 417
2018-01-30 06:00 | 435 | 432
2018-01-30 06:30 | 458 | 456
2018-01-30 07:00 | 482 | 480
2018-01-30 07:30 | 476 | 475
2018-01-30 08:00 | 488 | 487
2018-01-30 08:30 | 478 | 476
2018-01-30 09:00 | 484 | 482
2018-01-30 09:30 | 480 | 478
2018-01-30 10:00 | 475 | 473
2018-01-30 10:30 | 480 | 478
2018-01-30 11:00 | 471 | 469
2018-01-30 11:30 | 472 | 470
2018-01-30 12:00 | 483 | 482
2018-01-30 12:30 | 509 | 508
2018-01-30 13:00 | 520 | 519
2018-01-30 13:30 | 520 | 519
2018-01-30 14:00 | 508 | 507
2018-01-30 14:30 | 524 | 523
2018-01-30 15:00 | 493 | 492
2018-01-30 15:30 | 455 | 454
2018-01-30 16:00 | 465 | 464
2018-01-30 16:30 | 497 | 496
2018-01-30 17:00 | 553 | 552
2018-01-30 17:30 | 581 | 580
2018-01-30 18:00 | 586 | 585
2018-01-30 18:30 | 595 | 595
2018-01-30 19:00 | 592 | 592
2018-01-30 19:30 | 624 | 624
2018-01-30 20:00 | 619 | 619
2018-01-30 20:30 | 621 | 621
2018-01-30 21:00 | 602 | 602
2018-01-30 21:30 | 565 | 565
2018-01-30 22:00 | 534 | 534
2018-01-30 22:30 | 529 | 528
2018-01-30 23:00 | 505 | 504
2018-01-30 23:30 | 490 | 489
2018-01-31 | 471 | 469
2018-01-31 00:30 | 475 | 473
2018-01-31 01:00 | 463 | 461
2018-01-31 01:30 | 454 | 451
2018-01-31 02:00 | 450 | 447
2018-01-31 02:30 | 442 | 438
2018-01-31 03:00 | 439 | 436
2018-01-31 03:30 | 435 | 431
2018-01-31 04:00 | 429 | 425
2018-01-31 04:30 | 431 | 427
2018-01-31 05:00 | 434 | 430
2018-01-31 05:30 | 446 | 442
2018-01-31 06:00 | 459 | 456
2018-01-31 06:30 | 484 | 481
2018-01-31 07:00 | 508 | 506
2018-01-31 07:30 | 488 | 486
2018-01-31 08:00 | 488 | 486
2018-01-31 08:30 | 460 | 458
2018-01-31 09:00 | 452 | 450
2018-01-31 09:30 | 454 | 452
2018-01-31 10:00 | 459 | 457
2018-01-31 10:30 | 466 | 463
2018-01-31 11:00 | 468 | 466
2018-01-31 11:30 | 473 | 471
2018-01-31 12:00 | 459 | 457
2018-01-31 12:30 | 465 | 463
2018-01-31 13:00 | 471 | 469
2018-01-31 13:30 | 487 | 485
2018-01-31 14:00 | 497 | 496
2018-01-31 14:30 | 543 | 542
2018-01-31 15:00 | 553 | 553
2018-01-31 15:30 | 522 | 521
2018-01-31 16:00 | 539 | 538
2018-01-31 16:30 | 560 | 560
2018-01-31 17:00 | 572 | 572
2018-01-31 17:30 | 592 | 592
2018-01-31 18:00 | 607 | 607
2018-01-31 18:30 | 611 | 611
2018-01-31 19:00 | 633 | 633
2018-01-31 19:30 | 641 | 641
2018-01-31 20:00 | 638 | 638
2018-01-31 20:30 | 626 | 626
2018-01-31 21:00 | 600 | 600
2018-01-31 21:30 | 568 | 568
2018-01-31 22:00 | 530 | 530
2018-01-31 22:30 | 547 | 546
2018-01-31 23:00 | 575 | 575
2018-01-31 23:30 | 662 | 662
2018-02-01 | 641 | 641
2018-02-01 00:30 | 635 | 635
2018-02-01 01:00 | 609 | 609
2018-02-01 01:30 | 593 | 593
2018-02-01 02:00 | 584 | 584
2018-02-01 02:30 | 576 | 576
2018-02-01 03:00 | 570 | 569
2018-02-01 03:30 | 565 | 564
2018-02-01 04:00 | 563 | 563
2018-02-01 04:30 | 562 | 561
2018-02-01 05:00 | 566 | 565
2018-02-01 05:30 | 577 | 576
2018-02-01 06:00 | 588 | 588
2018-02-01 06:30 | 610 | 609
2018-02-01 07:00 | 630 | 630
2018-02-01 07:30 | 600 | 600
2018-02-01 08:00 | 606 | 606
2018-02-01 08:30 | 592 | 592
2018-02-01 09:00 | 590 | 590
2018-02-01 09:30 | 601 | 600
2018-02-01 10:00 | 597 | 596
2018-02-01 10:30 | 600 | 599
2018-02-01 11:00 | 601 | 600
2018-02-01 11:30 | 609 | 608
2018-02-01 12:00 | 619 | 619
2018-02-01 12:30 | 609 | 608
2018-02-01 13:00 | 603 | 602
2018-02-01 13:30 | 589 | 588
2018-02-01 14:00 | 597 | 596
2018-02-01 14:30 | 593 | 593
2018-02-01 15:00 | 610 | 609
2018-02-01 15:30 | 624 | 624
2018-02-01 16:00 | 660 | 659
2018-02-01 16:30 | 667 | 667
2018-02-01 17:00 | 683 | 683
2018-02-01 17:30 | 689 | 688
2018-02-01 18:00 | 720 | 719
2018-02-01 18:30 | 733 | 733
2018-02-01 19:00 | 754 | 754
2018-02-01 19:30 | 791 | 791
2018-02-01 20:00 | 788 | 788
2018-02-01 20:30 | 774 | 774
2018-02-01 21:00 | 748 | 748
2018-02-01 21:30 | 707 | 707
2018-02-01 22:00 | 677 | 677
2018-02-01 22:30 | 706 | 706
2018-02-01 23:00 | 688 | 688
2018-02-01 23:30 | 655 | 654
2018-02-02 | 634 | 633
2018-02-02 00:30 | 620 | 619
2018-02-02 01:00 | 610 | 609
2018-02-02 01:30 | 599 | 598
2018-02-02 02:00 | 590 | 588
2018-02-02 02:30 | 585 | 583
2018-02-02 03:00 | 580 | 578
2018-02-02 03:30 | 575 | 573
2018-02-02 04:00 | 577 | 575
2018-02-02 04:30 | 576 | 574
2018-02-02 05:00 | 576 | 574
2018-02-02 05:30 | 585 | 583
2018-02-02 06:00 | 601 | 599
2018-02-02 06:30 | 625 | 624
2018-02-02 07:00 | 630 | 629
2018-02-02 07:30 | 597 | 596
2018-02-02 08:00 | 605 | 603
2018-02-02 08:30 | 605 | 603
2018-02-02 09:00 | 592 | 590
2018-02-02 09:30 | 589 | 588
2018-02-02 10:00 | 584 | 582
2018-02-02 10:30 | 590 | 588
2018-02-02 11:00 | 616 | 615
2018-02-02 11:30 | 638 | 637
2018-02-02 12:00 | 639 | 638
2018-02-02 12:30 | 654 | 653
2018-02-02 13:00 | 663 | 663
2018-02-02 13:30 | 672 | 672
2018-02-02 14:00 | 679 | 679
2018-02-02 14:30 | 663 | 663
2018-02-02 15:00 | 656 | 656
2018-02-02 15:30 | 660 | 660
2018-02-02 16:00 | 683 | 683
2018-02-02 16:30 | 685 | 685
2018-02-02 17:00 | 676 | 676
2018-02-02 17:30 | 680 | 680
2018-02-02 18:00 | 683 | 683
2018-02-02 18:30 | 698 | 698
2018-02-02 19:00 | 712 | 712
2018-02-02 19:30 | 727 | 727
2018-02-02 20:00 | 725 | 725
2018-02-02 20:30 | 711 | 711
2018-02-02 21:00 | 712 | 712
2018-02-02 21:30 | 713 | 713
2018-02-02 22:00 | 696 | 696
2018-02-02 22:30 | 715 | 715
2018-02-02 23:00 | 688 | 688
2018-02-02 23:30 | 659 | 659
2018-02-03 | 641 | 641
2018-02-03 00:30 | 632 | 632
2018-02-03 01:00 | 613 | 612
2018-02-03 01:30 | 598 | 597
2018-02-03 02:00 | 590 | 589
2018-02-03 02:30 | 581 | 580
2018-02-03 03:00 | 576 | 575
2018-02-03 03:30 | 576 | 575
2018-02-03 04:00 | 573 | 572
2018-02-03 04:30 | 569 | 567
2018-02-03 05:00 | 569 | 567
2018-02-03 05:30 | 569 | 567
2018-02-03 06:00 | 573 | 571
2018-02-03 06:30 | 575 | 573
2018-02-03 07:00 | 570 | 569
2018-02-03 07:30 | 540 | 538
2018-02-03 08:00 | 586 | 584
2018-02-03 08:30 | 600 | 599
2018-02-03 09:00 | 607 | 606
2018-02-03 09:30 | 608 | 607
2018-02-03 10:00 | 586 | 585
2018-02-03 10:30 | 588 | 586
2018-02-03 11:00 | 589 | 588
2018-02-03 11:30 | 586 | 585
2018-02-03 12:00 | 568 | 567
2018-02-03 12:30 | 575 | 574
2018-02-03 13:00 | 580 | 579
2018-02-03 13:30 | 588 | 587
2018-02-03 14:00 | 604 | 603
2018-02-03 14:30 | 635 | 634
2018-02-03 15:00 | 654 | 653
2018-02-03 15:30 | 664 | 663
2018-02-03 16:00 | 693 | 693
2018-02-03 16:30 | 694 | 694
2018-02-03 17:00 | 702 | 702
2018-02-03 17:30 | 724 | 724
2018-02-03 18:00 | 731 | 731
2018-02-03 18:30 | 736 | 736
2018-02-03 19:00 | 738 | 738
2018-02-03 19:30 | 741 | 741
2018-02-03 20:00 | 738 | 738
2018-02-03 20:30 | 751 | 751
2018-02-03 21:00 | 734 | 734
2018-02-03 21:30 | 710 | 710
2018-02-03 22:00 | 704 | 704
2018-02-03 22:30 | 720 | 720
2018-02-03 23:00 | 705 | 705
2018-02-03 23:30 | 683 | 683
2018-02-04 | 662 | 662
2018-02-04 00:30 | 647 | 647
2018-02-04 01:00 | 629 | 628
2018-02-04 01:30 | 618 | 617
2018-02-04 02:00 | 610 | 610
2018-02-04 02:30 | 602 | 601
2018-02-04 03:00 | 594 | 593
2018-02-04 03:30 | 588 | 587
2018-02-04 04:00 | 584 | 583
2018-02-04 04:30 | 583 | 581
2018-02-04 05:00 | 577 | 576
2018-02-04 05:30 | 574 | 573
2018-02-04 06:00 | 574 | 573
2018-02-04 06:30 | 574 | 572
2018-02-04 07:00 | 556 | 554
2018-02-04 07:30 | 536 | 535
2018-02-04 08:00 | 534 | 532
2018-02-04 08:30 | 523 | 521
2018-02-04 09:00 | 523 | 520
2018-02-04 09:30 | 529 | 527
2018-02-04 10:00 | 527 | 525
2018-02-04 10:30 | 536 | 533
2018-02-04 11:00 | 527 | 525
2018-02-04 11:30 | 519 | 516
2018-02-04 12:00 | 523 | 520
2018-02-04 12:30 | 518 | 515
2018-02-04 13:00 | 531 | 528
2018-02-04 13:30 | 537 | 534
2018-02-04 14:00 | 553 | 551
2018-02-04 14:30 | 564 | 562
2018-02-04 15:00 | 559 | 558
2018-02-04 15:30 | 579 | 578
2018-02-04 16:00 | 628 | 626
2018-02-04 16:30 | 663 | 663
2018-02-04 17:00 | 671 | 671
2018-02-04 17:30 | 684 | 683
2018-02-04 18:00 | 703 | 703
2018-02-04 18:30 | 706 | 706
2018-02-04 19:00 | 710 | 710
2018-02-04 19:30 | 704 | 704
2018-02-04 20:00 | 687 | 687
2018-02-04 20:30 | 672 | 671
2018-02-04 21:00 | 650 | 650
2018-02-04 21:30 | 625 | 624
2018-02-04 22:00 | 605 | 604
2018-02-04 22:30 | 619 | 618
2018-02-04 23:00 | 597 | 596
2018-02-04 23:30 | 575 | 574
2018-02-05 | 554 | 552
2018-02-05 00:30 | 552 | 550
2018-02-05 01:00 | 541 | 539
2018-02-05 01:30 | 534 | 532
2018-02-05 02:00 | 531 | 528
2018-02-05 02:30 | 524 | 522
2018-02-05 03:00 | 520 | 517
2018-02-05 03:30 | 512 | 509
2018-02-05 04:00 | 511 | 508
2018-02-05 04:30 | 514 | 511
2018-02-05 05:00 | 517 | 514
2018-02-05 05:30 | 529 | 526
2018-02-05 06:00 | 551 | 548
2018-02-05 06:30 | 581 | 580
2018-02-05 07:00 | 593 | 592
2018-02-05 07:30 | 583 | 582
2018-02-05 08:00 | 595 | 594
2018-02-05 08:30 | 596 | 596
2018-02-05 09:00 | 589 | 588
2018-02-05 09:30 | 579 | 579
2018-02-05 10:00 | 577 | 576
2018-02-05 10:30 | 572 | 571
2018-02-05 11:00 | 558 | 557
2018-02-05 11:30 | 552 | 550
2018-02-05 12:00 | 548 | 546
2018-02-05 12:30 | 556 | 555
2018-02-05 13:00 | 556 | 555
2018-02-05 13:30 | 540 | 539
2018-02-05 14:00 | 559 | 558
2018-02-05 14:30 | 528 | 527
2018-02-05 15:00 | 523 | 522
2018-02-05 15:30 | 522 | 521
2018-02-05 16:00 | 529 | 527
2018-02-05 16:30 | 551 | 549
2018-02-05 17:00 | 556 | 555
2018-02-05 17:30 | 575 | 574
2018-02-05 18:00 | 588 | 588
2018-02-05 18:30 | 596 | 596
2018-02-05 19:00 | 610 | 609
2018-02-05 19:30 | 609 | 609
2018-02-05 20:00 | 602 | 602
2018-02-05 20:30 | 587 | 587
2018-02-05 21:00 | 565 | 565
2018-02-05 21:30 | 542 | 541
2018-02-05 22:00 | 523 | 522
2018-02-05 22:30 | 507 | 505
2018-02-05 23:00 | 502 | 500
2018-02-05 23:30 | 484 | 483
2018-02-06 | 470 | 468
2018-02-06 00:30 | 459 | 456
2018-02-06 01:00 | 449 | 447
2018-02-06 01:30 | 449 | 446
2018-02-06 02:00 | 446 | 444
2018-02-06 02:30 | 440 | 437
2018-02-06 03:00 | 440 | 437
2018-02-06 03:30 | 435 | 432
2018-02-06 04:00 | 432 | 428
2018-02-06 04:30 | 429 | 426
2018-02-06 05:00 | 436 | 433
2018-02-06 05:30 | 453 | 450
2018-02-06 06:00 | 465 | 462
2018-02-06 06:30 | 495 | 493
2018-02-06 07:00 | 514 | 512
2018-02-06 07:30 | 514 | 513
2018-02-06 08:00 | 522 | 521
2018-02-06 08:30 | 519 | 518
2018-02-06 09:00 | 506 | 505
2018-02-06 09:30 | 502 | 501
2018-02-06 10:00 | 489 | 488
2018-02-06 10:30 | 494 | 493
2018-02-06 11:00 | 486 | 484
2018-02-06 11:30 | 469 | 467
2018-02-06 12:00 | 471 | 469
2018-02-06 12:30 | 482 | 480
2018-02-06 13:00 | 478 | 476
2018-02-06 13:30 | 477 | 475
2018-02-06 14:00 | 483 | 481
2018-02-06 14:30 | 476 | 475
2018-02-06 15:00 | 469 | 467
2018-02-06 15:30 | 472 | 470
2018-02-06 16:00 | 486 | 484
2018-02-06 16:30 | 498 | 496
2018-02-06 17:00 | 508 | 506
2018-02-06 17:30 | 526 | 525
2018-02-06 18:00 | 538 | 537
2018-02-06 18:30 | 553 | 552
2018-02-06 19:00 | 567 | 566
2018-02-06 19:30 | 576 | 575
2018-02-06 20:00 | 567 | 567
2018-02-06 20:30 | 559 | 558
2018-02-06 21:00 | 539 | 539
2018-02-06 21:30 | 518 | 517
2018-02-06 22:00 | 493 | 491
2018-02-06 22:30 | 459 | 457
2018-02-06 23:00 | 441 | 439
2018-02-06 23:30 | 418 | 415
2018-02-07 | 399 | 394
2018-02-07 00:30 | 393 | 388
2018-02-07 01:00 | 380 | 375
2018-02-07 01:30 | 384 | 378
2018-02-07 02:00 | 383 | 378
2018-02-07 02:30 | 378 | 373
2018-02-07 03:00 | 372 | 366
2018-02-07 03:30 | 377 | 372
2018-02-07 04:00 | 370 | 364
2018-02-07 04:30 | 370 | 364
2018-02-07 05:00 | 372 | 366
2018-02-07 05:30 | 388 | 383
2018-02-07 06:00 | 401 | 396
2018-02-07 06:30 | 433 | 429
2018-02-07 07:00 | 458 | 454
2018-02-07 07:30 | 459 | 456
2018-02-07 08:00 | 456 | 453
2018-02-07 08:30 | 465 | 462
2018-02-07 09:00 | 465 | 462
2018-02-07 09:30 | 461 | 458
2018-02-07 10:00 | 456 | 453
2018-02-07 10:30 | 449 | 446
2018-02-07 11:00 | 445 | 442
2018-02-07 11:30 | 446 | 442
2018-02-07 12:00 | 444 | 441
2018-02-07 12:30 | 462 | 459
2018-02-07 13:00 | 466 | 464
2018-02-07 13:30 | 457 | 454
2018-02-07 14:00 | 468 | 466
2018-02-07 14:30 | 467 | 464
2018-02-07 15:00 | 478 | 475
2018-02-07 15:30 | 481 | 479
2018-02-07 16:00 | 501 | 499
2018-02-07 16:30 | 503 | 501
2018-02-07 17:00 | 519 | 518
2018-02-07 17:30 | 535 | 534
2018-02-07 18:00 | 549 | 548
2018-02-07 18:30 | 550 | 549
2018-02-07 19:00 | 569 | 568
2018-02-07 19:30 | 590 | 589
2018-02-07 20:00 | 591 | 590
2018-02-07 20:30 | 580 | 580
2018-02-07 21:00 | 557 | 556
2018-02-07 21:30 | 538 | 537
2018-02-07 22:00 | 513 | 511
2018-02-07 22:30 | 484 | 482
2018-02-07 23:00 | 459 | 456
2018-02-07 23:30 | 439 | 435
2018-02-08 | 422 | 418
2018-02-08 00:30 | 413 | 408
2018-02-08 01:00 | 398 | 393
2018-02-08 01:30 | 392 | 386
2018-02-08 02:00 | 386 | 379
2018-02-08 02:30 | 377 | 370
2018-02-08 03:00 | 377 | 369
2018-02-08 03:30 | 384 | 376
2018-02-08 04:00 | 383 | 376
2018-02-08 04:30 | 379 | 372
2018-02-08 05:00 | 383 | 376
2018-02-08 05:30 | 396 | 389
2018-02-08 06:00 | 404 | 397
2018-02-08 06:30 | 433 | 427
2018-02-08 07:00 | 453 | 448
2018-02-08 07:30 | 455 | 451
2018-02-08 08:00 | 467 | 463
2018-02-08 08:30 | 443 | 440
2018-02-08 09:00 | 391 | 386
2018-02-08 09:30 | 376 | 370
2018-02-08 10:00 | 364 | 356
2018-02-08 10:30 | 370 | 362
2018-02-08 11:00 | 377 | 369
2018-02-08 11:30 | 366 | 359
2018-02-08 12:00 | 345 | 337
2018-02-08 12:30 | 311 | 301
2018-02-08 13:00 | 329 | 318
2018-02-08 13:30 | 351 | 341
2018-02-08 14:00 | 355 | 346
2018-02-08 14:30 | 351 | 343
2018-02-08 15:00 | 343 | 335
2018-02-08 15:30 | 310 | 302
2018-02-08 16:00 | 271 | 260
2018-02-08 16:30 | 303 | 292
2018-02-08 17:00 | 333 | 325
2018-02-08 17:30 | 346 | 340
2018-02-08 18:00 | 358 | 352
2018-02-08 18:30 | 382 | 377
2018-02-08 19:00 | 406 | 402
2018-02-08 19:30 | 433 | 430
2018-02-08 20:00 | 425 | 423
2018-02-08 20:30 | 405 | 403
2018-02-08 21:00 | 386 | 383
2018-02-08 21:30 | 403 | 399
2018-02-08 22:00 | 464 | 461
2018-02-08 22:30 | 449 | 447
2018-02-08 23:00 | 425 | 423
2018-02-08 23:30 | 405 | 403
2018-02-09 | 386 | 383
2018-02-09 00:30 | 421 | 417
2018-02-09 01:00 | 409 | 405
2018-02-09 01:30 | 399 | 395
2018-02-09 02:00 | 391 | 387
2018-02-09 02:30 | 384 | 379
2018-02-09 03:00 | 386 | 381
2018-02-09 03:30 | 386 | 382
2018-02-09 04:00 | 385 | 380
2018-02-09 04:30 | 384 | 380
2018-02-09 05:00 | 392 | 387
2018-02-09 05:30 | 401 | 397
2018-02-09 06:00 | 407 | 403
2018-02-09 06:30 | 426 | 422
2018-02-09 07:00 | 420 | 417
2018-02-09 07:30 | 403 | 399
2018-02-09 08:00 | 411 | 407
2018-02-09 08:30 | 409 | 405
2018-02-09 09:00 | 405 | 401
2018-02-09 09:30 | 396 | 391
2018-02-09 10:00 | 399 | 395
2018-02-09 10:30 | 391 | 387
2018-02-09 11:00 | 399 | 394
2018-02-09 11:30 | 439 | 434
2018-02-09 12:00 | 449 | 446
2018-02-09 12:30 | 459 | 456
2018-02-09 13:00 | 457 | 455
2018-02-09 13:30 | 454 | 452
2018-02-09 14:00 | 468 | 466
2018-02-09 14:30 | 462 | 460
2018-02-09 15:00 | 451 | 448
2018-02-09 15:30 | 472 | 469
2018-02-09 16:00 | 476 | 475
2018-02-09 16:30 | 486 | 485
2018-02-09 17:00 | 484 | 482
2018-02-09 17:30 | 498 | 497
2018-02-09 18:00 | 506 | 505
2018-02-09 18:30 | 514 | 513
2018-02-09 19:00 | 531 | 530
2018-02-09 19:30 | 562 | 562
2018-02-09 20:00 | 565 | 564
2018-02-09 20:30 | 585 | 584
2018-02-09 21:00 | 579 | 579
2018-02-09 21:30 | 560 | 559
2018-02-09 22:00 | 536 | 535
2018-02-09 22:30 | 508 | 507
2018-02-09 23:00 | 491 | 489
2018-02-09 23:30 | 472 | 470
2018-02-10 | 459 | 456
2018-02-10 00:30 | 443 | 440
2018-02-10 01:00 | 433 | 430
2018-02-10 01:30 | 428 | 424
2018-02-10 02:00 | 419 | 415
2018-02-10 02:30 | 411 | 405
2018-02-10 03:00 | 410 | 404
2018-02-10 03:30 | 409 | 403
2018-02-10 04:00 | 404 | 398
2018-02-10 04:30 | 399 | 393
2018-02-10 05:00 | 384 | 378
2018-02-10 05:30 | 387 | 380
2018-02-10 06:00 | 384 | 377
2018-02-10 06:30 | 387 | 380
2018-02-10 07:00 | 398 | 391
2018-02-10 07:30 | 401 | 394
2018-02-10 08:00 | 409 | 402
2018-02-10 08:30 | 417 | 411
2018-02-10 09:00 | 426 | 421
2018-02-10 09:30 | 427 | 421
2018-02-10 10:00 | 430 | 425
2018-02-10 10:30 | 432 | 427
2018-02-10 11:00 | 430 | 425
2018-02-10 11:30 | 432 | 427
2018-02-10 12:00 | 433 | 428
2018-02-10 12:30 | 428 | 423
2018-02-10 13:00 | 431 | 427
2018-02-10 13:30 | 437 | 433
2018-02-10 14:00 | 442 | 438
2018-02-10 14:30 | 438 | 434
2018-02-10 15:00 | 443 | 439
2018-02-10 15:30 | 467 | 464
2018-02-10 16:00 | 494 | 491
2018-02-10 16:30 | 497 | 495
2018-02-10 17:00 | 516 | 514
2018-02-10 17:30 | 534 | 532
2018-02-10 18:00 | 561 | 560
2018-02-10 18:30 | 581 | 580
2018-02-10 19:00 | 598 | 597
2018-02-10 19:30 | 613 | 612
2018-02-10 20:00 | 607 | 607
2018-02-10 20:30 | 608 | 608
2018-02-10 21:00 | 586 | 585
2018-02-10 21:30 | 570 | 569
2018-02-10 22:00 | 552 | 551
2018-02-10 22:30 | 527 | 525
2018-02-10 23:00 | 507 | 504
2018-02-10 23:30 | 487 | 484
2018-02-11 | 471 | 468
2018-02-11 00:30 | 464 | 460
2018-02-11 01:00 | 450 | 445
2018-02-11 01:30 | 439 | 434
2018-02-11 02:00 | 433 | 427
2018-02-11 02:30 | 447 | 442
2018-02-11 03:00 | 443 | 438
2018-02-11 03:30 | 446 | 441
2018-02-11 04:00 | 441 | 436
2018-02-11 04:30 | 439 | 433
2018-02-11 05:00 | 436 | 431
2018-02-11 05:30 | 439 | 434
2018-02-11 06:00 | 435 | 430
2018-02-11 06:30 | 436 | 430
2018-02-11 07:00 | 433 | 428
2018-02-11 07:30 | 429 | 423
2018-02-11 08:00 | 416 | 411
2018-02-11 08:30 | 412 | 406
2018-02-11 09:00 | 400 | 393
2018-02-11 09:30 | 401 | 395
2018-02-11 10:00 | 405 | 398
2018-02-11 10:30 | 411 | 405
2018-02-11 11:00 | 415 | 409
2018-02-11 11:30 | 417 | 411
2018-02-11 12:00 | 423 | 417
2018-02-11 12:30 | 427 | 422
2018-02-11 13:00 | 437 | 433
2018-02-11 13:30 | 443 | 440
2018-02-11 14:00 | 448 | 444
2018-02-11 14:30 | 460 | 456
2018-02-11 15:00 | 471 | 468
2018-02-11 15:30 | 484 | 482
2018-02-11 16:00 | 500 | 498
2018-02-11 16:30 | 511 | 510
2018-02-11 17:00 | 469 | 467
2018-02-11 17:30 | 420 | 417
2018-02-11 18:00 | 448 | 443
2018-02-11 18:30 | 519 | 516
2018-02-11 19:00 | 563 | 561
2018-02-11 19:30 | 589 | 588
2018-02-11 20:00 | 582 | 581
2018-02-11 20:30 | 588 | 587
2018-02-11 21:00 | 582 | 581
2018-02-11 21:30 | 575 | 574
2018-02-11 22:00 | 541 | 540
2018-02-11 22:30 | 531 | 530
2018-02-11 23:00 | 543 | 541
2018-02-11 23:30 | 520 | 518
2018-02-12 | 505 | 502
2018-02-12 00:30 | 459 | 455
2018-02-12 01:00 | 406 | 400
2018-02-12 01:30 | 398 | 390
2018-02-12 02:00 | 389 | 381
2018-02-12 02:30 | 388 | 378
2018-02-12 03:00 | 381 | 371
2018-02-12 03:30 | 359 | 349
2018-02-12 04:00 | 319 | 306
2018-02-12 04:30 | 331 | 316
2018-02-12 05:00 | 334 | 320
2018-02-12 05:30 | 344 | 330
2018-02-12 06:00 | 351 | 338
2018-02-12 06:30 | 378 | 367
2018-02-12 07:00 | 402 | 392
2018-02-12 07:30 | 422 | 414
2018-02-12 08:00 | 422 | 415
2018-02-12 08:30 | 421 | 415
2018-02-12 09:00 | 416 | 410
2018-02-12 09:30 | 413 | 407
2018-02-12 10:00 | 408 | 403
2018-02-12 10:30 | 410 | 403
2018-02-12 11:00 | 421 | 416
2018-02-12 11:30 | 427 | 422
2018-02-12 12:00 | 438 | 434
2018-02-12 12:30 | 451 | 448
2018-02-12 13:00 | 453 | 450
2018-02-12 13:30 | 455 | 453
2018-02-12 14:00 | 462 | 459
2018-02-12 14:30 | 453 | 450
2018-02-12 15:00 | 391 | 388
2018-02-12 15:30 | 393 | 389
2018-02-12 16:00 | 459 | 455
2018-02-12 16:30 | 469 | 467
2018-02-12 17:00 | 397 | 395
2018-02-12 17:30 | 395 | 391
2018-02-12 18:00 | 419 | 415
2018-02-12 18:30 | 460 | 457
2018-02-12 19:00 | 463 | 461
2018-02-12 19:30 | 500 | 498
2018-02-12 20:00 | 592 | 591
2018-02-12 20:30 | 621 | 621
2018-02-12 21:00 | 595 | 595
2018-02-12 21:30 | 577 | 577
2018-02-12 22:00 | 546 | 545
2018-02-12 22:30 | 587 | 586
2018-02-12 23:00 | 562 | 561
2018-02-12 23:30 | 563 | 561
2018-02-13 | 549 | 548
2018-02-13 00:30 | 534 | 533
2018-02-13 01:00 | 520 | 518
2018-02-13 01:30 | 513 | 510
2018-02-13 02:00 | 502 | 501
2018-02-13 02:30 | 499 | 497
2018-02-13 03:00 | 493 | 492
2018-02-13 03:30 | 490 | 488
2018-02-13 04:00 | 487 | 485
2018-02-13 04:30 | 484 | 482
2018-02-13 05:00 | 487 | 485
2018-02-13 05:30 | 499 | 498
2018-02-13 06:00 | 507 | 505
2018-02-13 06:30 | 534 | 533
2018-02-13 07:00 | 550 | 549
2018-02-13 07:30 | 561 | 560
2018-02-13 08:00 | 571 | 570
2018-02-13 08:30 | 539 | 539
2018-02-13 09:00 | 518 | 517
2018-02-13 09:30 | 496 | 495
2018-02-13 10:00 | 474 | 473
2018-02-13 10:30 | 499 | 498
2018-02-13 11:00 | 479 | 477
2018-02-13 11:30 | 455 | 453
2018-02-13 12:00 | 468 | 465
2018-02-13 12:30 | 483 | 481
2018-02-13 13:00 | 492 | 490
2018-02-13 13:30 | 501 | 500
2018-02-13 14:00 | 514 | 513
2018-02-13 14:30 | 561 | 560
2018-02-13 15:00 | 604 | 604
2018-02-13 15:30 | 545 | 545
2018-02-13 16:00 | 500 | 500
2018-02-13 16:30 | 385 | 384
2018-02-13 17:00 | 377 | 373
2018-02-13 17:30 | 319 | 314
2018-02-13 18:00 | 331 | 324
2018-02-13 18:30 | 368 | 361
2018-02-13 19:00 | 389 | 384
2018-02-13 19:30 | 374 | 369
2018-02-13 20:00 | 462 | 457
2018-02-13 20:30 | 562 | 560
2018-02-13 21:00 | 604 | 603
2018-02-13 21:30 | 598 | 597
2018-02-13 22:00 | 558 | 558
2018-02-13 22:30 | 624 | 624
2018-02-13 23:00 | 623 | 622
2018-02-13 23:30 | 594 | 594
2018-02-14 | 578 | 577
2018-02-14 00:30 | 556 | 555
2018-02-14 01:00 | 545 | 544
2018-02-14 01:30 | 533 | 532
2018-02-14 02:00 | 522 | 521
2018-02-14 02:30 | 512 | 510
2018-02-14 03:00 | 506 | 504
2018-02-14 03:30 | 505 | 503
2018-02-14 04:00 | 500 | 498
2018-02-14 04:30 | 507 | 505
2018-02-14 05:00 | 506 | 504
2018-02-14 05:30 | 523 | 521
2018-02-14 06:00 | 535 | 533
2018-02-14 06:30 | 563 | 562
2018-02-14 07:00 | 578 | 577
2018-02-14 07:30 | 505 | 504
2018-02-14 08:00 | 474 | 472
2018-02-14 08:30 | 478 | 475
2018-02-14 09:00 | 494 | 491
2018-02-14 09:30 | 490 | 488
2018-02-14 10:00 | 446 | 444
2018-02-14 10:30 | 419 | 415
2018-02-14 11:00 | 439 | 434
2018-02-14 11:30 | 453 | 450
2018-02-14 12:00 | 474 | 471
2018-02-14 12:30 | 468 | 466
2018-02-14 13:00 | 466 | 464
2018-02-14 13:30 | 480 | 478
2018-02-14 14:00 | 500 | 498
2018-02-14 14:30 | 513 | 512
2018-02-14 15:00 | 505 | 504
2018-02-14 15:30 | 406 | 405
2018-02-14 16:00 | 322 | 317
2018-02-14 16:30 | 247 | 236
2018-02-14 17:00 | 221 | 204
2018-02-14 17:30 | 212 | 191
2018-02-14 18:00 | 222 | 200
2018-02-14 18:30 | 261 | 243
2018-02-14 19:00 | 280 | 265
2018-02-14 19:30 | 235 | 219
2018-02-14 20:00 | 331 | 318
2018-02-14 20:30 | 410 | 403
2018-02-14 21:00 | 519 | 515
2018-02-14 21:30 | 544 | 543
2018-02-14 22:00 | 513 | 511
2018-02-14 22:30 | 490 | 488
2018-02-14 23:00 | 454 | 452
2018-02-14 23:30 | 425 | 422
2018-02-15 | 405 | 401
2018-02-15 00:30 | 405 | 400
2018-02-15 01:00 | 390 | 385
2018-02-15 01:30 | 376 | 371
2018-02-15 02:00 | 363 | 356
2018-02-15 02:30 | 354 | 347
2018-02-15 03:00 | 351 | 344
2018-02-15 03:30 | 348 | 341
2018-02-15 04:00 | 349 | 342
2018-02-15 04:30 | 372 | 365
2018-02-15 05:00 | 396 | 391
2018-02-15 05:30 | 407 | 402
2018-02-15 06:00 | 419 | 414
2018-02-15 06:30 | 440 | 436
2018-02-15 07:00 | 462 | 459
2018-02-15 07:30 | 451 | 448
2018-02-15 08:00 | 462 | 459
2018-02-15 08:30 | 468 | 466
2018-02-15 09:00 | 465 | 463
2018-02-15 09:30 | 475 | 473
2018-02-15 10:00 | 473 | 472
2018-02-15 10:30 | 474 | 472
2018-02-15 11:00 | 450 | 448
2018-02-15 11:30 | 477 | 475
2018-02-15 12:00 | 481 | 479
2018-02-15 12:30 | 468 | 466
2018-02-15 13:00 | 454 | 452
2018-02-15 13:30 | 474 | 472
2018-02-15 14:00 | 517 | 516
2018-02-15 14:30 | 488 | 487
2018-02-15 15:00 | 469 | 468
2018-02-15 15:30 | 397 | 396
2018-02-15 16:00 | 291 | 287
2018-02-15 16:30 | 289 | 279
2018-02-15 17:00 | 261 | 251
2018-02-15 17:30 | 255 | 242
2018-02-15 18:00 | 410 | 402
2018-02-15 18:30 | 423 | 420
2018-02-15 19:00 | 453 | 450
2018-02-15 19:30 | 497 | 495
2018-02-15 20:00 | 549 | 548
2018-02-15 20:30 | 607 | 606
2018-02-15 21:00 | 690 | 690
2018-02-15 21:30 | 673 | 673
2018-02-15 22:00 | 640 | 640
2018-02-15 22:30 | 597 | 597
2018-02-15 23:00 | 613 | 612
2018-02-15 23:30 | 652 | 651
2018-02-16 | 622 | 622
2018-02-16 00:30 | 603 | 603
2018-02-16 01:00 | 581 | 581
2018-02-16 01:30 | 574 | 573
2018-02-16 02:00 | 563 | 562
2018-02-16 02:30 | 560 | 560
2018-02-16 03:00 | 555 | 554
2018-02-16 03:30 | 547 | 546
2018-02-16 04:00 | 540 | 539
2018-02-16 04:30 | 539 | 538
2018-02-16 05:00 | 541 | 540
2018-02-16 05:30 | 546 | 545
2018-02-16 06:00 | 558 | 557
2018-02-16 06:30 | 583 | 582
2018-02-16 07:00 | 609 | 609
2018-02-16 07:30 | 614 | 614
2018-02-16 08:00 | 628 | 628
2018-02-16 08:30 | 637 | 637
2018-02-16 09:00 | 632 | 631
2018-02-16 09:30 | 631 | 631
2018-02-16 10:00 | 630 | 629
2018-02-16 10:30 | 641 | 640
2018-02-16 11:00 | 639 | 639
2018-02-16 11:30 | 641 | 641
2018-02-16 12:00 | 664 | 664
2018-02-16 12:30 | 671 | 671
2018-02-16 13:00 | 684 | 684
2018-02-16 13:30 | 688 | 688
2018-02-16 14:00 | 682 | 682
2018-02-16 14:30 | 632 | 632
2018-02-16 15:00 | 594 | 594
2018-02-16 15:30 | 530 | 530
2018-02-16 16:00 | 545 | 544
2018-02-16 16:30 | 548 | 548
2018-02-16 17:00 | 557 | 556
2018-02-16 17:30 | 592 | 591
2018-02-16 18:00 | 637 | 636
2018-02-16 18:30 | 710 | 710
2018-02-16 19:00 | 735 | 735
2018-02-16 19:30 | 742 | 742
2018-02-16 20:00 | 731 | 731
2018-02-16 20:30 | 732 | 732
2018-02-16 21:00 | 784 | 784
2018-02-16 21:30 | 754 | 754
2018-02-16 22:00 | 721 | 721
2018-02-16 22:30 | 690 | 690
2018-02-16 23:00 | 662 | 662
2018-02-16 23:30 | 633 | 633
2018-02-17 | 604 | 603
2018-02-17 00:30 | 587 | 587
2018-02-17 01:00 | 596 | 595
2018-02-17 01:30 | 564 | 563
2018-02-17 02:00 | 541 | 540
2018-02-17 02:30 | 525 | 524
2018-02-17 03:00 | 521 | 520
2018-02-17 03:30 | 512 | 510
2018-02-17 04:00 | 506 | 505
2018-02-17 04:30 | 503 | 502
2018-02-17 05:00 | 506 | 504
2018-02-17 05:30 | 509 | 507
2018-02-17 06:00 | 510 | 508
2018-02-17 06:30 | 512 | 511
2018-02-17 07:00 | 513 | 512
2018-02-17 07:30 | 493 | 492
2018-02-17 08:00 | 498 | 497
2018-02-17 08:30 | 533 | 532
2018-02-17 09:00 | 548 | 547
2018-02-17 09:30 | 542 | 542
2018-02-17 10:00 | 525 | 525
2018-02-17 10:30 | 508 | 507
2018-02-17 11:00 | 508 | 507
2018-02-17 11:30 | 505 | 504
2018-02-17 12:00 | 513 | 512
2018-02-17 12:30 | 527 | 525
2018-02-17 13:00 | 534 | 533
2018-02-17 13:30 | 546 | 545
2018-02-17 14:00 | 570 | 569
2018-02-17 14:30 | 588 | 588
2018-02-17 15:00 | 585 | 585
2018-02-17 15:30 | 596 | 596
2018-02-17 16:00 | 629 | 629
2018-02-17 16:30 | 643 | 643
2018-02-17 17:00 | 661 | 661
2018-02-17 17:30 | 667 | 667
2018-02-17 18:00 | 682 | 682
2018-02-17 18:30 | 719 | 719
2018-02-17 19:00 | 741 | 741
2018-02-17 19:30 | 733 | 733
2018-02-17 20:00 | 600 | 600
2018-02-17 20:30 | 701 | 701
2018-02-17 21:00 | 706 | 706
2018-02-17 21:30 | 702 | 702
2018-02-17 22:00 | 684 | 684
2018-02-17 22:30 | 649 | 649
2018-02-17 23:00 | 619 | 619
2018-02-17 23:30 | 588 | 587
2018-02-18 | 563 | 563
2018-02-18 00:30 | 546 | 545
2018-02-18 01:00 | 528 | 527
2018-02-18 01:30 | 512 | 511
2018-02-18 02:00 | 502 | 500
2018-02-18 02:30 | 495 | 493
2018-02-18 03:00 | 490 | 487
2018-02-18 03:30 | 483 | 481
2018-02-18 04:00 | 481 | 479
2018-02-18 04:30 | 473 | 471
2018-02-18 05:00 | 443 | 441
2018-02-18 05:30 | 424 | 420
2018-02-18 06:00 | 418 | 414
2018-02-18 06:30 | 416 | 411
2018-02-18 07:00 | 414 | 409
2018-02-18 07:30 | 399 | 394
2018-02-18 08:00 | 401 | 396
2018-02-18 08:30 | 416 | 412
2018-02-18 09:00 | 406 | 402
2018-02-18 09:30 | 410 | 406
2018-02-18 10:00 | 422 | 418
2018-02-18 10:30 | 464 | 461
2018-02-18 11:00 | 473 | 471
2018-02-18 11:30 | 486 | 485
2018-02-18 12:00 | 499 | 498
2018-02-18 12:30 | 516 | 515
2018-02-18 13:00 | 532 | 531
2018-02-18 13:30 | 543 | 543
2018-02-18 14:00 | 557 | 557
2018-02-18 14:30 | 573 | 572
2018-02-18 15:00 | 588 | 588
2018-02-18 15:30 | 607 | 607
2018-02-18 16:00 | 630 | 630
2018-02-18 16:30 | 648 | 648
2018-02-18 17:00 | 676 | 676
2018-02-18 17:30 | 696 | 695
2018-02-18 18:00 | 705 | 705
2018-02-18 18:30 | 750 | 750
2018-02-18 19:00 | 775 | 774
2018-02-18 19:30 | 787 | 787
2018-02-18 20:00 | 777 | 776
2018-02-18 20:30 | 746 | 746
2018-02-18 21:00 | 719 | 719
2018-02-18 21:30 | 660 | 659
2018-02-18 22:00 | 625 | 625
2018-02-18 22:30 | 580 | 580
2018-02-18 23:00 | 552 | 552
2018-02-18 23:30 | 531 | 530
2018-02-19 | 510 | 509
2018-02-19 00:30 | 494 | 492
2018-02-19 01:00 | 475 | 474
2018-02-19 01:30 | 466 | 464
2018-02-19 02:00 | 459 | 458
2018-02-19 02:30 | 459 | 457
2018-02-19 03:00 | 449 | 447
2018-02-19 03:30 | 443 | 441
2018-02-19 04:00 | 444 | 441
2018-02-19 04:30 | 469 | 467
2018-02-19 05:00 | 480 | 479
2018-02-19 05:30 | 489 | 487
2018-02-19 06:00 | 505 | 503
2018-02-19 06:30 | 532 | 531
2018-02-19 07:00 | 549 | 549
2018-02-19 07:30 | 547 | 546
2018-02-19 08:00 | 558 | 557
2018-02-19 08:30 | 536 | 536
2018-02-19 09:00 | 483 | 483
2018-02-19 09:30 | 484 | 483
2018-02-19 10:00 | 478 | 477
2018-02-19 10:30 | 482 | 481
2018-02-19 11:00 | 477 | 476
2018-02-19 11:30 | 469 | 468
2018-02-19 12:00 | 439 | 438
2018-02-19 12:30 | 460 | 458
2018-02-19 13:00 | 472 | 471
2018-02-19 13:30 | 488 | 487
2018-02-19 14:00 | 496 | 495
2018-02-19 14:30 | 520 | 519
2018-02-19 15:00 | 534 | 533
2018-02-19 15:30 | 536 | 535
2018-02-19 16:00 | 491 | 491
2018-02-19 16:30 | 501 | 500
2018-02-19 17:00 | 515 | 515
2018-02-19 17:30 | 529 | 529
2018-02-19 18:00 | 546 | 546
2018-02-19 18:30 | 611 | 611
2018-02-19 19:00 | 576 | 576
2018-02-19 19:30 | 581 | 581
2018-02-19 20:00 | 587 | 587
2018-02-19 20:30 | 601 | 601
2018-02-19 21:00 | 573 | 573
2018-02-19 21:30 | 543 | 543
2018-02-19 22:00 | 503 | 503
2018-02-19 22:30 | 492 | 490
2018-02-19 23:00 | 468 | 466
2018-02-19 23:30 | 442 | 440
2018-02-20 | 421 | 418
2018-02-20 00:30 | 409 | 406
2018-02-20 01:00 | 392 | 388
2018-02-20 01:30 | 380 | 375
2018-02-20 02:00 | 377 | 372
2018-02-20 02:30 | 367 | 361
2018-02-20 03:00 | 360 | 352
2018-02-20 03:30 | 354 | 346
2018-02-20 04:00 | 352 | 344
2018-02-20 04:30 | 353 | 345
2018-02-20 05:00 | 362 | 354
2018-02-20 05:30 | 373 | 365
2018-02-20 06:00 | 389 | 383
2018-02-20 06:30 | 405 | 399
2018-02-20 07:00 | 435 | 430
2018-02-20 07:30 | 488 | 485
2018-02-20 08:00 | 512 | 510
2018-02-20 08:30 | 521 | 519
2018-02-20 09:00 | 487 | 485
2018-02-20 09:30 | 461 | 460
2018-02-20 10:00 | 474 | 472
2018-02-20 10:30 | 496 | 495
2018-02-20 11:00 | 492 | 491
2018-02-20 11:30 | 483 | 481
2018-02-20 12:00 | 479 | 478
2018-02-20 12:30 | 468 | 467
2018-02-20 13:00 | 471 | 470
2018-02-20 13:30 | 496 | 494
2018-02-20 14:00 | 488 | 487
2018-02-20 14:30 | 485 | 484
2018-02-20 15:00 | 487 | 485
2018-02-20 15:30 | 507 | 506
2018-02-20 16:00 | 526 | 525
2018-02-20 16:30 | 516 | 516
2018-02-20 17:00 | 480 | 479
2018-02-20 17:30 | 526 | 525
2018-02-20 18:00 | 551 | 550
2018-02-20 18:30 | 566 | 565
2018-02-20 19:00 | 578 | 578
2018-02-20 19:30 | 581 | 581
2018-02-20 20:00 | 583 | 582
2018-02-20 20:30 | 549 | 548
2018-02-20 21:00 | 516 | 515
2018-02-20 21:30 | 521 | 519
2018-02-20 22:00 | 504 | 502
2018-02-20 22:30 | 411 | 409
2018-02-20 23:00 | 422 | 419
2018-02-20 23:30 | 492 | 490
2018-02-21 | 476 | 474
2018-02-21 00:30 | 473 | 471
2018-02-21 01:00 | 470 | 468
2018-02-21 01:30 | 460 | 458
2018-02-21 02:00 | 456 | 454
2018-02-21 02:30 | 451 | 448
2018-02-21 03:00 | 449 | 446
2018-02-21 03:30 | 451 | 448
2018-02-21 04:00 | 449 | 446
2018-02-21 04:30 | 452 | 449
2018-02-21 05:00 | 459 | 456
2018-02-21 05:30 | 469 | 466
2018-02-21 06:00 | 480 | 478
2018-02-21 06:30 | 507 | 504
2018-02-21 07:00 | 533 | 532
2018-02-21 07:30 | 562 | 561
2018-02-21 08:00 | 575 | 574
2018-02-21 08:30 | 572 | 572
2018-02-21 09:00 | 559 | 558
2018-02-21 09:30 | 557 | 557
2018-02-21 10:00 | 555 | 554
2018-02-21 10:30 | 539 | 538
2018-02-21 11:00 | 542 | 541
2018-02-21 11:30 | 549 | 548
2018-02-21 12:00 | 525 | 524
2018-02-21 12:30 | 522 | 521
2018-02-21 13:00 | 532 | 531
2018-02-21 13:30 | 522 | 521
2018-02-21 14:00 | 554 | 553
2018-02-21 14:30 | 542 | 541
2018-02-21 15:00 | 523 | 522
2018-02-21 15:30 | 519 | 519
2018-02-21 16:00 | 552 | 551
2018-02-21 16:30 | 572 | 571
2018-02-21 17:00 | 575 | 575
2018-02-21 17:30 | 566 | 566
2018-02-21 18:00 | 581 | 581
2018-02-21 18:30 | 536 | 536
2018-02-21 19:00 | 527 | 527
2018-02-21 19:30 | 608 | 607
2018-02-21 20:00 | 626 | 626
2018-02-21 20:30 | 606 | 606
2018-02-21 21:00 | 590 | 590
2018-02-21 21:30 | 590 | 590
2018-02-21 22:00 | 573 | 572
2018-02-21 22:30 | 539 | 539
2018-02-21 23:00 | 528 | 527
2018-02-21 23:30 | 509 | 508
2018-02-22 | 488 | 487
2018-02-22 00:30 | 486 | 485
2018-02-22 01:00 | 473 | 471
2018-02-22 01:30 | 462 | 460
2018-02-22 02:00 | 455 | 453
2018-02-22 02:30 | 454 | 452
2018-02-22 03:00 | 448 | 445
2018-02-22 03:30 | 447 | 444
2018-02-22 04:00 | 444 | 441
2018-02-22 04:30 | 448 | 444
2018-02-22 05:00 | 456 | 453
2018-02-22 05:30 | 460 | 457
2018-02-22 06:00 | 476 | 474
2018-02-22 06:30 | 506 | 504
2018-02-22 07:00 | 529 | 527
2018-02-22 07:30 | 547 | 546
2018-02-22 08:00 | 561 | 560
2018-02-22 08:30 | 558 | 557
2018-02-22 09:00 | 558 | 558
2018-02-22 09:30 | 549 | 548
2018-02-22 10:00 | 546 | 545
2018-02-22 10:30 | 548 | 548
2018-02-22 11:00 | 536 | 536
2018-02-22 11:30 | 538 | 537
2018-02-22 12:00 | 520 | 519
2018-02-22 12:30 | 519 | 518
2018-02-22 13:00 | 535 | 534
2018-02-22 13:30 | 550 | 549
2018-02-22 14:00 | 549 | 548
2018-02-22 14:30 | 556 | 555
2018-02-22 15:00 | 540 | 540
2018-02-22 15:30 | 550 | 550
2018-02-22 16:00 | 565 | 565
2018-02-22 16:30 | 556 | 555
2018-02-22 17:00 | 570 | 570
2018-02-22 17:30 | 576 | 576
2018-02-22 18:00 | 584 | 584
2018-02-22 18:30 | 599 | 599
2018-02-22 19:00 | 618 | 618
2018-02-22 19:30 | 651 | 651
2018-02-22 20:00 | 640 | 640
2018-02-22 20:30 | 645 | 645
2018-02-22 21:00 | 628 | 628
2018-02-22 21:30 | 634 | 634
2018-02-22 22:00 | 610 | 610
2018-02-22 22:30 | 557 | 557
2018-02-22 23:00 | 520 | 519
2018-02-22 23:30 | 463 | 461
2018-02-23 | 446 | 443
2018-02-23 00:30 | 434 | 431
2018-02-23 01:00 | 417 | 413
2018-02-23 01:30 | 406 | 402
2018-02-23 02:00 | 393 | 388
2018-02-23 02:30 | 393 | 388
2018-02-23 03:00 | 387 | 381
2018-02-23 03:30 | 389 | 383
2018-02-23 04:00 | 389 | 382
2018-02-23 04:30 | 387 | 380
2018-02-23 05:00 | 394 | 388
2018-02-23 05:30 | 409 | 404
2018-02-23 06:00 | 424 | 419
2018-02-23 06:30 | 457 | 453
2018-02-23 07:00 | 483 | 479
2018-02-23 07:30 | 515 | 513
2018-02-23 08:00 | 530 | 529
2018-02-23 08:30 | 536 | 535
2018-02-23 09:00 | 528 | 527
2018-02-23 09:30 | 553 | 552
2018-02-23 10:00 | 565 | 565
2018-02-23 10:30 | 563 | 563
2018-02-23 11:00 | 559 | 559
2018-02-23 11:30 | 523 | 523
2018-02-23 12:00 | 509 | 508
2018-02-23 12:30 | 517 | 517
2018-02-23 13:00 | 510 | 510
2018-02-23 13:30 | 507 | 507
2018-02-23 14:00 | 506 | 505
2018-02-23 14:30 | 510 | 509
2018-02-23 15:00 | 525 | 525
2018-02-23 15:30 | 532 | 531
2018-02-23 16:00 | 546 | 546
2018-02-23 16:30 | 577 | 577
2018-02-23 17:00 | 584 | 584
2018-02-23 17:30 | 599 | 599
2018-02-23 18:00 | 587 | 587
2018-02-23 18:30 | 603 | 603
2018-02-23 19:00 | 622 | 622
2018-02-23 19:30 | 618 | 618
2018-02-23 20:00 | 600 | 600
2018-02-23 20:30 | 569 | 569
2018-02-23 21:00 | 552 | 552
2018-02-23 21:30 | 533 | 533
2018-02-23 22:00 | 509 | 509
2018-02-23 22:30 | 484 | 484
2018-02-23 23:00 | 473 | 472
2018-02-23 23:30 | 453 | 452
2018-02-24 | 435 | 433
2018-02-24 00:30 | 421 | 419
2018-02-24 01:00 | 407 | 405
2018-02-24 01:30 | 400 | 396
2018-02-24 02:00 | 389 | 384
2018-02-24 02:30 | 386 | 381
2018-02-24 03:00 | 390 | 385
2018-02-24 03:30 | 389 | 385
2018-02-24 04:00 | 385 | 380
2018-02-24 04:30 | 381 | 376
2018-02-24 05:00 | 386 | 381
2018-02-24 05:30 | 394 | 389
2018-02-24 06:00 | 423 | 419
2018-02-24 06:30 | 437 | 434
2018-02-24 07:00 | 444 | 441
2018-02-24 07:30 | 465 | 462
2018-02-24 08:00 | 486 | 484
2018-02-24 08:30 | 497 | 496
2018-02-24 09:00 | 505 | 504
2018-02-24 09:30 | 534 | 533
2018-02-24 10:00 | 530 | 529
2018-02-24 10:30 | 538 | 537
2018-02-24 11:00 | 540 | 539
2018-02-24 11:30 | 533 | 532
2018-02-24 12:00 | 521 | 520
2018-02-24 12:30 | 509 | 509
2018-02-24 13:00 | 515 | 514
2018-02-24 13:30 | 526 | 526
2018-02-24 14:00 | 539 | 538
2018-02-24 14:30 | 544 | 544
2018-02-24 15:00 | 549 | 548
2018-02-24 15:30 | 562 | 561
2018-02-24 16:00 | 575 | 574
2018-02-24 16:30 | 574 | 574
2018-02-24 17:00 | 569 | 568
2018-02-24 17:30 | 570 | 570
2018-02-24 18:00 | 602 | 601
2018-02-24 18:30 | 604 | 604
2018-02-24 19:00 | 595 | 595
2018-02-24 19:30 | 599 | 599
2018-02-24 20:00 | 598 | 598
2018-02-24 20:30 | 576 | 576
2018-02-24 21:00 | 569 | 569
2018-02-24 21:30 | 554 | 553
2018-02-24 22:00 | 542 | 541
2018-02-24 22:30 | 549 | 548
2018-02-24 23:00 | 545 | 545
2018-02-24 23:30 | 526 | 526
2018-02-25 | 510 | 509
2018-02-25 00:30 | 499 | 498
2018-02-25 01:00 | 489 | 488
2018-02-25 01:30 | 482 | 481
2018-02-25 02:00 | 475 | 473
2018-02-25 02:30 | 464 | 462
2018-02-25 03:00 | 459 | 456
2018-02-25 03:30 | 459 | 457
2018-02-25 04:00 | 456 | 453
2018-02-25 04:30 | 457 | 454
2018-02-25 05:00 | 459 | 456
2018-02-25 05:30 | 471 | 468
2018-02-25 06:00 | 490 | 488
2018-02-25 06:30 | 494 | 492
2018-02-25 07:00 | 498 | 496
2018-02-25 07:30 | 477 | 475
2018-02-25 08:00 | 461 | 458
2018-02-25 08:30 | 470 | 468
2018-02-25 09:00 | 477 | 474
2018-02-25 09:30 | 481 | 479
2018-02-25 10:00 | 469 | 468
2018-02-25 10:30 | 465 | 463
2018-02-25 11:00 | 466 | 463
2018-02-25 11:30 | 482 | 480
2018-02-25 12:00 | 497 | 495
2018-02-25 12:30 | 498 | 497
2018-02-25 13:00 | 535 | 534
2018-02-25 13:30 | 570 | 570
2018-02-25 14:00 | 572 | 572
2018-02-25 14:30 | 558 | 558
2018-02-25 15:00 | 563 | 563
2018-02-25 15:30 | 568 | 568
2018-02-25 16:00 | 562 | 562
2018-02-25 16:30 | 550 | 550
2018-02-25 17:00 | 559 | 559
2018-02-25 17:30 | 569 | 569
2018-02-25 18:00 | 592 | 592
2018-02-25 18:30 | 593 | 593
2018-02-25 19:00 | 599 | 599
2018-02-25 19:30 | 602 | 602
2018-02-25 20:00 | 589 | 589
2018-02-25 20:30 | 569 | 568
2018-02-25 21:00 | 556 | 556
2018-02-25 21:30 | 536 | 536
2018-02-25 22:00 | 512 | 512
2018-02-25 22:30 | 485 | 484
2018-02-25 23:00 | 465 | 464
2018-02-25 23:30 | 449 | 448
2018-02-26 | 437 | 434
2018-02-26 00:30 | 430 | 427
2018-02-26 01:00 | 418 | 415
2018-02-26 01:30 | 411 | 408
2018-02-26 02:00 | 405 | 401
2018-02-26 02:30 | 401 | 397
2018-02-26 03:00 | 397 | 392
2018-02-26 03:30 | 399 | 395
2018-02-26 04:00 | 397 | 393
2018-02-26 04:30 | 395 | 390
2018-02-26 05:00 | 400 | 395
2018-02-26 05:30 | 417 | 413
2018-02-26 06:00 | 432 | 429
2018-02-26 06:30 | 462 | 459
2018-02-26 07:00 | 488 | 486
2018-02-26 07:30 | 525 | 523
2018-02-26 08:00 | 545 | 544
2018-02-26 08:30 | 548 | 547
2018-02-26 09:00 | 547 | 546
2018-02-26 09:30 | 544 | 543
2018-02-26 10:00 | 541 | 540
2018-02-26 10:30 | 541 | 540
2018-02-26 11:00 | 548 | 548
2018-02-26 11:30 | 558 | 557
2018-02-26 12:00 | 578 | 577
2018-02-26 12:30 | 601 | 601
2018-02-26 13:00 | 597 | 597
2018-02-26 13:30 | 610 | 609
2018-02-26 14:00 | 640 | 640
2018-02-26 14:30 | 583 | 583
2018-02-26 15:00 | 584 | 583
2018-02-26 15:30 | 612 | 612
2018-02-26 16:00 | 616 | 616
2018-02-26 16:30 | 607 | 607
2018-02-26 17:00 | 609 | 609
2018-02-26 17:30 | 602 | 601
2018-02-26 18:00 | 643 | 643
2018-02-26 18:30 | 664 | 663
2018-02-26 19:00 | 686 | 686
2018-02-26 19:30 | 690 | 690
2018-02-26 20:00 | 674 | 674
2018-02-26 20:30 | 655 | 655
2018-02-26 21:00 | 626 | 626
2018-02-26 21:30 | 592 | 592
2018-02-26 22:00 | 563 | 563
2018-02-26 22:30 | 530 | 529
2018-02-26 23:00 | 502 | 501
2018-02-26 23:30 | 479 | 478
2018-02-27 | 459 | 457
2018-02-27 00:30 | 449 | 447
2018-02-27 01:00 | 439 | 436
2018-02-27 01:30 | 446 | 443
2018-02-27 02:00 | 436 | 434
2018-02-27 02:30 | 428 | 425
2018-02-27 03:00 | 423 | 420
2018-02-27 03:30 | 417 | 413
2018-02-27 04:00 | 414 | 410
2018-02-27 04:30 | 419 | 415
2018-02-27 05:00 | 425 | 421
2018-02-27 05:30 | 444 | 441
2018-02-27 06:00 | 457 | 454
2018-02-27 06:30 | 485 | 482
2018-02-27 07:00 | 513 | 512
2018-02-27 07:30 | 525 | 524
2018-02-27 08:00 | 540 | 539
2018-02-27 08:30 | 543 | 542
2018-02-27 09:00 | 536 | 535
2018-02-27 09:30 | 546 | 545
2018-02-27 10:00 | 534 | 533
2018-02-27 10:30 | 534 | 534
2018-02-27 11:00 | 536 | 535
2018-02-27 11:30 | 533 | 532
2018-02-27 12:00 | 544 | 543
2018-02-27 12:30 | 547 | 546
2018-02-27 13:00 | 561 | 560
2018-02-27 13:30 | 588 | 587
2018-02-27 14:00 | 610 | 610
2018-02-27 14:30 | 626 | 625
2018-02-27 15:00 | 620 | 620
2018-02-27 15:30 | 603 | 603
2018-02-27 16:00 | 597 | 597
2018-02-27 16:30 | 610 | 610
2018-02-27 17:00 | 633 | 633
2018-02-27 17:30 | 652 | 652
2018-02-27 18:00 | 657 | 657
2018-02-27 18:30 | 672 | 672
2018-02-27 19:00 | 686 | 686
2018-02-27 19:30 | 689 | 689
2018-02-27 20:00 | 674 | 674
2018-02-27 20:30 | 652 | 651
2018-02-27 21:00 | 630 | 630
2018-02-27 21:30 | 591 | 591
2018-02-27 22:00 | 550 | 550
2018-02-27 22:30 | 529 | 529
2018-02-27 23:00 | 514 | 513
2018-02-27 23:30 | 502 | 501
2018-02-28 | 480 | 479
2018-02-28 00:30 | 476 | 474
2018-02-28 01:00 | 461 | 459
2018-02-28 01:30 | 444 | 441
2018-02-28 02:00 | 444 | 440
2018-02-28 02:30 | 439 | 436
2018-02-28 03:00 | 436 | 432
2018-02-28 03:30 | 436 | 432
2018-02-28 04:00 | 431 | 427
2018-02-28 04:30 | 454 | 450
2018-02-28 05:00 | 462 | 460
2018-02-28 05:30 | 476 | 474
2018-02-28 06:00 | 491 | 489
2018-02-28 06:30 | 527 | 525
2018-02-28 07:00 | 560 | 558
2018-02-28 07:30 | 596 | 595
2018-02-28 08:00 | 611 | 611
2018-02-28 08:30 | 613 | 613
2018-02-28 09:00 | 602 | 602
2018-02-28 09:30 | 604 | 603
2018-02-28 10:00 | 610 | 610
2018-02-28 10:30 | 608 | 607
2018-02-28 11:00 | 593 | 593
2018-02-28 11:30 | 570 | 570
2018-02-28 12:00 | 573 | 572
2018-02-28 12:30 | 585 | 584
2018-02-28 13:00 | 588 | 588
2018-02-28 13:30 | 560 | 560
2018-02-28 14:00 | 599 | 598
2018-02-28 14:30 | 618 | 618
2018-02-28 15:00 | 623 | 623
2018-02-28 15:30 | 610 | 609
2018-02-28 16:00 | 605 | 605
2018-02-28 16:30 | 590 | 590
2018-02-28 17:00 | 592 | 592
2018-02-28 17:30 | 591 | 590
2018-02-28 18:00 | 607 | 606
2018-02-28 18:30 | 620 | 620
2018-02-28 19:00 | 638 | 638
2018-02-28 19:30 | 635 | 634
2018-02-28 20:00 | 624 | 624
2018-02-28 20:30 | 594 | 594
2018-02-28 21:00 | 568 | 567
2018-02-28 21:30 | 568 | 567
2018-02-28 22:00 | 544 | 543
2018-02-28 22:30 | 515 | 513
2018-02-28 23:00 | 495 | 492
2018-02-28 23:30 | 473 | 470
2018-03-01 | 458 | 455
2018-03-01 00:30 | 454 | 451
2018-03-01 01:00 | 442 | 438
2018-03-01 01:30 | 439 | 436
2018-03-01 02:00 | 429 | 426
2018-03-01 02:30 | 429 | 425
2018-03-01 03:00 | 422 | 418
2018-03-01 03:30 | 424 | 420
2018-03-01 04:00 | 422 | 417
2018-03-01 04:30 | 419 | 415
2018-03-01 05:00 | 427 | 423
2018-03-01 05:30 | 438 | 434
2018-03-01 06:00 | 454 | 451
2018-03-01 06:30 | 487 | 484
2018-03-01 07:00 | 518 | 516
2018-03-01 07:30 | 560 | 559
2018-03-01 08:00 | 578 | 577
2018-03-01 08:30 | 580 | 579
2018-03-01 09:00 | 553 | 553
2018-03-01 09:30 | 515 | 514
2018-03-01 10:00 | 491 | 489
2018-03-01 10:30 | 487 | 486
2018-03-01 11:00 | 485 | 483
2018-03-01 11:30 | 455 | 453
2018-03-01 12:00 | 428 | 425
2018-03-01 12:30 | 422 | 419
2018-03-01 13:00 | 350 | 346
2018-03-01 13:30 | 342 | 336
2018-03-01 14:00 | 346 | 338
2018-03-01 14:30 | 377 | 371
2018-03-01 15:00 | 373 | 367
2018-03-01 15:30 | 375 | 370
2018-03-01 16:00 | 393 | 388
2018-03-01 16:30 | 400 | 396
2018-03-01 17:00 | 409 | 405
2018-03-01 17:30 | 414 | 410
2018-03-01 18:00 | 429 | 426
2018-03-01 18:30 | 447 | 444
2018-03-01 19:00 | 470 | 468
2018-03-01 19:30 | 473 | 471
2018-03-01 20:00 | 451 | 449
2018-03-01 20:30 | 430 | 428
2018-03-01 21:00 | 470 | 467
2018-03-01 21:30 | 506 | 504
2018-03-01 22:00 | 560 | 559
2018-03-01 22:30 | 532 | 531
2018-03-01 23:00 | 503 | 502
2018-03-01 23:30 | 480 | 479
2018-03-02 | 461 | 459
2018-03-02 00:30 | 450 | 447
2018-03-02 01:00 | 443 | 440
2018-03-02 01:30 | 433 | 430
2018-03-02 02:00 | 426 | 423
2018-03-02 02:30 | 413 | 409
2018-03-02 03:00 | 407 | 403
2018-03-02 03:30 | 408 | 403
2018-03-02 04:00 | 407 | 403
2018-03-02 04:30 | 406 | 402
2018-03-02 05:00 | 405 | 401
2018-03-02 05:30 | 421 | 417
2018-03-02 06:00 | 436 | 432
2018-03-02 06:30 | 471 | 468
2018-03-02 07:00 | 496 | 493
2018-03-02 07:30 | 525 | 524
2018-03-02 08:00 | 536 | 535
2018-03-02 08:30 | 518 | 517
2018-03-02 09:00 | 536 | 535
2018-03-02 09:30 | 558 | 557
2018-03-02 10:00 | 559 | 558
2018-03-02 10:30 | 555 | 555
2018-03-02 11:00 | 566 | 565
2018-03-02 11:30 | 563 | 563
2018-03-02 12:00 | 555 | 555
2018-03-02 12:30 | 555 | 555
2018-03-02 13:00 | 560 | 560
2018-03-02 13:30 | 572 | 572
2018-03-02 14:00 | 583 | 583
2018-03-02 14:30 | 583 | 583
2018-03-02 15:00 | 570 | 569
2018-03-02 15:30 | 583 | 583
2018-03-02 16:00 | 601 | 601
2018-03-02 16:30 | 633 | 633
2018-03-02 17:00 | 645 | 645
2018-03-02 17:30 | 643 | 643
2018-03-02 18:00 | 647 | 647
2018-03-02 18:30 | 652 | 652
2018-03-02 19:00 | 663 | 663
2018-03-02 19:30 | 670 | 670
2018-03-02 20:00 | 659 | 659
2018-03-02 20:30 | 658 | 658
2018-03-02 21:00 | 641 | 641
2018-03-02 21:30 | 620 | 619
2018-03-02 22:00 | 600 | 600
2018-03-02 22:30 | 566 | 565
2018-03-02 23:00 | 542 | 541
2018-03-02 23:30 | 518 | 516
2018-03-03 | 498 | 496
2018-03-03 00:30 | 488 | 485
2018-03-03 01:00 | 474 | 471
2018-03-03 01:30 | 465 | 461
2018-03-03 02:00 | 459 | 456
2018-03-03 02:30 | 454 | 451
2018-03-03 03:00 | 452 | 449
2018-03-03 03:30 | 450 | 447
2018-03-03 04:00 | 443 | 440
2018-03-03 04:30 | 439 | 435
2018-03-03 05:00 | 441 | 437
2018-03-03 05:30 | 446 | 443
2018-03-03 06:00 | 452 | 449
2018-03-03 06:30 | 459 | 456
2018-03-03 07:00 | 470 | 468
2018-03-03 07:30 | 482 | 480
2018-03-03 08:00 | 491 | 489
2018-03-03 08:30 | 502 | 500
2018-03-03 09:00 | 508 | 507
2018-03-03 09:30 | 516 | 515
2018-03-03 10:00 | 508 | 506
2018-03-03 10:30 | 461 | 459
2018-03-03 11:00 | 464 | 461
2018-03-03 11:30 | 449 | 446
2018-03-03 12:00 | 478 | 476
2018-03-03 12:30 | 508 | 506
2018-03-03 13:00 | 512 | 511
2018-03-03 13:30 | 516 | 515
2018-03-03 14:00 | 511 | 510
2018-03-03 14:30 | 521 | 520
2018-03-03 15:00 | 519 | 519
2018-03-03 15:30 | 535 | 534
2018-03-03 16:00 | 554 | 553
2018-03-03 16:30 | 566 | 565
2018-03-03 17:00 | 578 | 578
2018-03-03 17:30 | 608 | 607
2018-03-03 18:00 | 626 | 626
2018-03-03 18:30 | 638 | 638
2018-03-03 19:00 | 653 | 653
2018-03-03 19:30 | 655 | 655
2018-03-03 20:00 | 639 | 639
2018-03-03 20:30 | 620 | 620
2018-03-03 21:00 | 600 | 600
2018-03-03 21:30 | 578 | 578
2018-03-03 22:00 | 560 | 559
2018-03-03 22:30 | 533 | 532
2018-03-03 23:00 | 511 | 509
2018-03-03 23:30 | 491 | 489
2018-03-04 | 471 | 468
2018-03-04 00:30 | 460 | 457
2018-03-04 01:00 | 450 | 447
2018-03-04 01:30 | 444 | 440
2018-03-04 02:00 | 434 | 431
2018-03-04 02:30 | 432 | 428
2018-03-04 03:00 | 424 | 420
2018-03-04 03:30 | 418 | 414
2018-03-04 04:00 | 412 | 408
2018-03-04 04:30 | 416 | 411
2018-03-04 05:00 | 417 | 412
2018-03-04 05:30 | 421 | 417
2018-03-04 06:00 | 420 | 416
2018-03-04 06:30 | 423 | 418
2018-03-04 07:00 | 430 | 426
2018-03-04 07:30 | 457 | 454
2018-03-04 08:00 | 468 | 465
2018-03-04 08:30 | 470 | 467
2018-03-04 09:00 | 462 | 460
2018-03-04 09:30 | 469 | 466
2018-03-04 10:00 | 496 | 494
2018-03-04 10:30 | 519 | 517
2018-03-04 11:00 | 516 | 514
2018-03-04 11:30 | 512 | 511
2018-03-04 12:00 | 526 | 525
2018-03-04 12:30 | 526 | 525
2018-03-04 13:00 | 518 | 517
2018-03-04 13:30 | 528 | 526
2018-03-04 14:00 | 543 | 542
2018-03-04 14:30 | 544 | 543
2018-03-04 15:00 | 539 | 539
2018-03-04 15:30 | 531 | 531
2018-03-04 16:00 | 559 | 558
2018-03-04 16:30 | 564 | 564
2018-03-04 17:00 | 583 | 583
2018-03-04 17:30 | 615 | 615
2018-03-04 18:00 | 621 | 621
2018-03-04 18:30 | 646 | 646
2018-03-04 19:00 | 653 | 653
2018-03-04 19:30 | 658 | 658
2018-03-04 20:00 | 642 | 642
2018-03-04 20:30 | 637 | 637
2018-03-04 21:00 | 620 | 620
2018-03-04 21:30 | 591 | 590
2018-03-04 22:00 | 563 | 562
2018-03-04 22:30 | 534 | 533
2018-03-04 23:00 | 510 | 509
2018-03-04 23:30 | 491 | 488
2018-03-05 | 477 | 475
2018-03-05 00:30 | 465 | 462
2018-03-05 01:00 | 451 | 448
2018-03-05 01:30 | 470 | 467
2018-03-05 02:00 | 470 | 468
2018-03-05 02:30 | 468 | 466
2018-03-05 03:00 | 460 | 457
2018-03-05 03:30 | 459 | 457
2018-03-05 04:00 | 456 | 453
2018-03-05 04:30 | 460 | 458
2018-03-05 05:00 | 463 | 460
2018-03-05 05:30 | 478 | 475
2018-03-05 06:00 | 495 | 493
2018-03-05 06:30 | 506 | 504
2018-03-05 07:00 | 531 | 530
2018-03-05 07:30 | 567 | 566
2018-03-05 08:00 | 578 | 578
2018-03-05 08:30 | 571 | 571
2018-03-05 09:00 | 542 | 542
2018-03-05 09:30 | 488 | 488
2018-03-05 10:00 | 482 | 481
2018-03-05 10:30 | 496 | 494
2018-03-05 11:00 | 486 | 484
2018-03-05 11:30 | 506 | 504
2018-03-05 12:00 | 506 | 505
2018-03-05 12:30 | 492 | 492
2018-03-05 13:00 | 499 | 498
2018-03-05 13:30 | 517 | 516
2018-03-05 14:00 | 567 | 567
2018-03-05 14:30 | 535 | 535
2018-03-05 15:00 | 538 | 537
2018-03-05 15:30 | 517 | 516
2018-03-05 16:00 | 467 | 466
2018-03-05 16:30 | 465 | 463
2018-03-05 17:00 | 467 | 466
2018-03-05 17:30 | 466 | 464
2018-03-05 18:00 | 470 | 468
2018-03-05 18:30 | 485 | 484
2018-03-05 19:00 | 506 | 505
2018-03-05 19:30 | 503 | 502
2018-03-05 20:00 | 486 | 485
2018-03-05 20:30 | 453 | 451
2018-03-05 21:00 | 424 | 421
2018-03-05 21:30 | 409 | 406
2018-03-05 22:00 | 381 | 377
2018-03-05 22:30 | 370 | 365
2018-03-05 23:00 | 414 | 409
2018-03-05 23:30 | 451 | 448
2018-03-06 | 512 | 510
2018-03-06 00:30 | 503 | 502
2018-03-06 01:00 | 494 | 492
2018-03-06 01:30 | 484 | 482
2018-03-06 02:00 | 472 | 470
2018-03-06 02:30 | 473 | 471
2018-03-06 03:00 | 470 | 468
2018-03-06 03:30 | 468 | 466
2018-03-06 04:00 | 468 | 466
2018-03-06 04:30 | 472 | 470
2018-03-06 05:00 | 482 | 480
2018-03-06 05:30 | 490 | 488
2018-03-06 06:00 | 504 | 503
2018-03-06 06:30 | 480 | 479
2018-03-06 07:00 | 464 | 462
2018-03-06 07:30 | 488 | 486
2018-03-06 08:00 | 477 | 475
2018-03-06 08:30 | 405 | 404
2018-03-06 09:00 | 407 | 404
2018-03-06 09:30 | 410 | 407
2018-03-06 10:00 | 412 | 409
2018-03-06 10:30 | 403 | 401
2018-03-06 11:00 | 392 | 389
2018-03-06 11:30 | 395 | 391
2018-03-06 12:00 | 402 | 398
2018-03-06 12:30 | 449 | 446
2018-03-06 13:00 | 459 | 457
2018-03-06 13:30 | 460 | 459
2018-03-06 14:00 | 454 | 452
2018-03-06 14:30 | 462 | 460
2018-03-06 15:00 | 399 | 397
2018-03-06 15:30 | 393 | 389
2018-03-06 16:00 | 412 | 409
2018-03-06 16:30 | 432 | 430
2018-03-06 17:00 | 449 | 447
2018-03-06 17:30 | 454 | 453
2018-03-06 18:00 | 484 | 483
2018-03-06 18:30 | 500 | 499
2018-03-06 19:00 | 523 | 522
2018-03-06 19:30 | 522 | 521
2018-03-06 20:00 | 507 | 506
2018-03-06 20:30 | 484 | 483
2018-03-06 21:00 | 461 | 460
2018-03-06 21:30 | 499 | 497
2018-03-06 22:00 | 528 | 527
2018-03-06 22:30 | 589 | 588
2018-03-06 23:00 | 569 | 569
2018-03-06 23:30 | 546 | 545
2018-03-07 | 524 | 524
2018-03-07 00:30 | 514 | 514
2018-03-07 01:00 | 501 | 500
2018-03-07 01:30 | 492 | 490
2018-03-07 02:00 | 487 | 485
2018-03-07 02:30 | 485 | 484
2018-03-07 03:00 | 480 | 478
2018-03-07 03:30 | 473 | 471
2018-03-07 04:00 | 453 | 451
2018-03-07 04:30 | 438 | 435
2018-03-07 05:00 | 441 | 438
2018-03-07 05:30 | 450 | 447
2018-03-07 06:00 | 410 | 407
2018-03-07 06:30 | 419 | 415
2018-03-07 07:00 | 440 | 437
2018-03-07 07:30 | 494 | 491
2018-03-07 08:00 | 501 | 499
2018-03-07 08:30 | 461 | 459
2018-03-07 09:00 | 448 | 446
2018-03-07 09:30 | 440 | 438
2018-03-07 10:00 | 432 | 429
2018-03-07 10:30 | 446 | 443
2018-03-07 11:00 | 430 | 427
2018-03-07 11:30 | 426 | 423
2018-03-07 12:00 | 432 | 429
2018-03-07 12:30 | 438 | 436
2018-03-07 13:00 | 427 | 424
2018-03-07 13:30 | 425 | 422
2018-03-07 14:00 | 441 | 438
2018-03-07 14:30 | 483 | 481
2018-03-07 15:00 | 480 | 479
2018-03-07 15:30 | 480 | 479
2018-03-07 16:00 | 479 | 477
2018-03-07 16:30 | 479 | 478
2018-03-07 17:00 | 488 | 487
2018-03-07 17:30 | 497 | 496
2018-03-07 18:00 | 505 | 505
2018-03-07 18:30 | 523 | 522
2018-03-07 19:00 | 551 | 550
2018-03-07 19:30 | 555 | 555
2018-03-07 20:00 | 538 | 538
2018-03-07 20:30 | 542 | 542
2018-03-07 21:00 | 538 | 537
2018-03-07 21:30 | 557 | 557
2018-03-07 22:00 | 556 | 555
2018-03-07 22:30 | 527 | 527
2018-03-07 23:00 | 507 | 507
2018-03-07 23:30 | 481 | 480
2018-03-08 | 468 | 467
2018-03-08 00:30 | 466 | 464
2018-03-08 01:00 | 458 | 456
2018-03-08 01:30 | 459 | 457
2018-03-08 02:00 | 451 | 449
2018-03-08 02:30 | 450 | 448
2018-03-08 03:00 | 443 | 441
2018-03-08 03:30 | 436 | 434
2018-03-08 04:00 | 442 | 439
2018-03-08 04:30 | 449 | 446
2018-03-08 05:00 | 391 | 388
2018-03-08 05:30 | 376 | 372
2018-03-08 06:00 | 427 | 423
2018-03-08 06:30 | 485 | 482
2018-03-08 07:00 | 518 | 516
2018-03-08 07:30 | 564 | 563
2018-03-08 08:00 | 596 | 596
2018-03-08 08:30 | 605 | 605
2018-03-08 09:00 | 610 | 610
2018-03-08 09:30 | 626 | 626
2018-03-08 10:00 | 607 | 606
2018-03-08 10:30 | 570 | 570
2018-03-08 11:00 | 562 | 561
2018-03-08 11:30 | 548 | 547
2018-03-08 12:00 | 553 | 552
2018-03-08 12:30 | 526 | 525
2018-03-08 13:00 | 467 | 466
2018-03-08 13:30 | 413 | 410
2018-03-08 14:00 | 415 | 411
2018-03-08 14:30 | 404 | 400
2018-03-08 15:00 | 410 | 406
2018-03-08 15:30 | 419 | 415
2018-03-08 16:00 | 417 | 414
2018-03-08 16:30 | 438 | 434
2018-03-08 17:00 | 445 | 442
2018-03-08 17:30 | 457 | 454
2018-03-08 18:00 | 462 | 459
2018-03-08 18:30 | 473 | 471
2018-03-08 19:00 | 489 | 487
2018-03-08 19:30 | 476 | 475
2018-03-08 20:00 | 461 | 459
2018-03-08 20:30 | 444 | 442
2018-03-08 21:00 | 433 | 430
2018-03-08 21:30 | 403 | 399
2018-03-08 22:00 | 383 | 378
2018-03-08 22:30 | 356 | 351
2018-03-08 23:00 | 403 | 397
2018-03-08 23:30 | 402 | 398
2018-03-09 | 385 | 380
2018-03-09 00:30 | 373 | 368
2018-03-09 01:00 | 357 | 351
2018-03-09 01:30 | 351 | 344
2018-03-09 02:00 | 346 | 338
2018-03-09 02:30 | 344 | 336
2018-03-09 03:00 | 341 | 333
2018-03-09 03:30 | 340 | 332
2018-03-09 04:00 | 344 | 336
2018-03-09 04:30 | 342 | 334
2018-03-09 05:00 | 349 | 341
2018-03-09 05:30 | 363 | 356
2018-03-09 06:00 | 386 | 379
2018-03-09 06:30 | 417 | 412
2018-03-09 07:00 | 437 | 433
2018-03-09 07:30 | 474 | 470
2018-03-09 08:00 | 495 | 493
2018-03-09 08:30 | 492 | 490
2018-03-09 09:00 | 418 | 416
2018-03-09 09:30 | 402 | 398
2018-03-09 10:00 | 396 | 391
2018-03-09 10:30 | 387 | 382
2018-03-09 11:00 | 369 | 363
2018-03-09 11:30 | 360 | 353
2018-03-09 12:00 | 370 | 363
2018-03-09 12:30 | 376 | 370
2018-03-09 13:00 | 376 | 370
2018-03-09 13:30 | 379 | 373
2018-03-09 14:00 | 382 | 376
2018-03-09 14:30 | 385 | 379
2018-03-09 15:00 | 381 | 376
2018-03-09 15:30 | 380 | 375
2018-03-09 16:00 | 394 | 388
2018-03-09 16:30 | 405 | 400
2018-03-09 17:00 | 418 | 414
2018-03-09 17:30 | 428 | 424
2018-03-09 18:00 | 424 | 420
2018-03-09 18:30 | 427 | 423
2018-03-09 19:00 | 440 | 437
2018-03-09 19:30 | 432 | 429
2018-03-09 20:00 | 413 | 410
2018-03-09 20:30 | 396 | 392
2018-03-09 21:00 | 450 | 446
2018-03-09 21:30 | 496 | 494
2018-03-09 22:00 | 563 | 561
2018-03-09 22:30 | 543 | 543
2018-03-09 23:00 | 523 | 522
2018-03-09 23:30 | 499 | 497
2018-03-10 | 490 | 488
2018-03-10 00:30 | 476 | 474
2018-03-10 01:00 | 466 | 464
2018-03-10 01:30 | 453 | 451
2018-03-10 02:00 | 449 | 446
2018-03-10 02:30 | 442 | 439
2018-03-10 03:00 | 441 | 438
2018-03-10 03:30 | 440 | 437
2018-03-10 04:00 | 443 | 440
2018-03-10 04:30 | 447 | 444
2018-03-10 05:00 | 447 | 444
2018-03-10 05:30 | 454 | 451
2018-03-10 06:00 | 457 | 455
2018-03-10 06:30 | 468 | 465
2018-03-10 07:00 | 472 | 470
2018-03-10 07:30 | 489 | 487
2018-03-10 08:00 | 494 | 492
2018-03-10 08:30 | 498 | 496
2018-03-10 09:00 | 499 | 498
2018-03-10 09:30 | 503 | 502
2018-03-10 10:00 | 503 | 502
2018-03-10 10:30 | 504 | 502
2018-03-10 11:00 | 492 | 491
2018-03-10 11:30 | 489 | 488
2018-03-10 12:00 | 489 | 488
2018-03-10 12:30 | 486 | 484
2018-03-10 13:00 | 485 | 483
2018-03-10 13:30 | 490 | 488
2018-03-10 14:00 | 496 | 495
2018-03-10 14:30 | 514 | 513
2018-03-10 15:00 | 529 | 528
2018-03-10 15:30 | 546 | 545
2018-03-10 16:00 | 559 | 558
2018-03-10 16:30 | 569 | 569
2018-03-10 17:00 | 587 | 587
2018-03-10 17:30 | 603 | 603
2018-03-10 18:00 | 625 | 625
2018-03-10 18:30 | 636 | 636
2018-03-10 19:00 | 644 | 644
2018-03-10 19:30 | 648 | 648
2018-03-10 20:00 | 630 | 630
2018-03-10 20:30 | 611 | 611
2018-03-10 21:00 | 595 | 595
2018-03-10 21:30 | 585 | 584
2018-03-10 22:00 | 569 | 568
2018-03-10 22:30 | 553 | 552
2018-03-10 23:00 | 534 | 533
2018-03-10 23:30 | 515 | 514
2018-03-11 | 504 | 503
2018-03-11 00:30 | 492 | 490
2018-03-11 01:00 | 481 | 479
2018-03-11 01:30 | 469 | 467
2018-03-11 02:00 | 460 | 458
2018-03-11 02:30 | 453 | 450
2018-03-11 03:00 | 453 | 451
2018-03-11 03:30 | 455 | 452
2018-03-11 04:00 | 452 | 449
2018-03-11 04:30 | 453 | 450
2018-03-11 05:00 | 449 | 446
2018-03-11 05:30 | 456 | 452
2018-03-11 06:00 | 460 | 457
2018-03-11 06:30 | 459 | 456
2018-03-11 07:00 | 466 | 463
2018-03-11 07:30 | 474 | 471
2018-03-11 08:00 | 475 | 472
2018-03-11 08:30 | 474 | 472
2018-03-11 09:00 | 471 | 469
2018-03-11 09:30 | 480 | 478
2018-03-11 10:00 | 481 | 478
2018-03-11 10:30 | 485 | 484
2018-03-11 11:00 | 466 | 465
2018-03-11 11:30 | 462 | 460
2018-03-11 12:00 | 472 | 470
2018-03-11 12:30 | 468 | 466
2018-03-11 13:00 | 453 | 450
2018-03-11 13:30 | 460 | 458
2018-03-11 14:00 | 458 | 456
2018-03-11 14:30 | 467 | 465
2018-03-11 15:00 | 484 | 483
2018-03-11 15:30 | 493 | 491
2018-03-11 16:00 | 516 | 514
2018-03-11 16:30 | 526 | 525
2018-03-11 17:00 | 544 | 543
2018-03-11 17:30 | 566 | 565
2018-03-11 18:00 | 588 | 588
2018-03-11 18:30 | 608 | 608
2018-03-11 19:00 | 629 | 629
2018-03-11 19:30 | 634 | 634
2018-03-11 20:00 | 617 | 617
2018-03-11 20:30 | 593 | 593
2018-03-11 21:00 | 578 | 578
2018-03-11 21:30 | 562 | 562
2018-03-11 22:00 | 537 | 536
2018-03-11 22:30 | 506 | 505
2018-03-11 23:00 | 489 | 487
2018-03-11 23:30 | 469 | 467
2018-03-12 | 456 | 454
2018-03-12 00:30 | 439 | 437
2018-03-12 01:00 | 430 | 428
2018-03-12 01:30 | 420 | 417
2018-03-12 02:00 | 418 | 415
2018-03-12 02:30 | 409 | 406
2018-03-12 03:00 | 405 | 401
2018-03-12 03:30 | 403 | 399
2018-03-12 04:00 | 402 | 398
2018-03-12 04:30 | 401 | 398
2018-03-12 05:00 | 410 | 406
2018-03-12 05:30 | 425 | 422
2018-03-12 06:00 | 440 | 437
2018-03-12 06:30 | 468 | 465
2018-03-12 07:00 | 499 | 497
2018-03-12 07:30 | 516 | 515
2018-03-12 08:00 | 500 | 499
2018-03-12 08:30 | 495 | 494
2018-03-12 09:00 | 497 | 495
2018-03-12 09:30 | 490 | 489
2018-03-12 10:00 | 484 | 483
2018-03-12 10:30 | 478 | 476
2018-03-12 11:00 | 482 | 480
2018-03-12 11:30 | 493 | 492
2018-03-12 12:00 | 490 | 488
2018-03-12 12:30 | 499 | 498
2018-03-12 13:00 | 497 | 496
2018-03-12 13:30 | 499 | 498
2018-03-12 14:00 | 522 | 521
2018-03-12 14:30 | 531 | 530
2018-03-12 15:00 | 503 | 502
2018-03-12 15:30 | 520 | 519
2018-03-12 16:00 | 531 | 530
2018-03-12 16:30 | 540 | 539
2018-03-12 17:00 | 556 | 555
2018-03-12 17:30 | 580 | 579
2018-03-12 18:00 | 600 | 600
2018-03-12 18:30 | 614 | 614
2018-03-12 19:00 | 616 | 616
2018-03-12 19:30 | 623 | 623
2018-03-12 20:00 | 603 | 603
2018-03-12 20:30 | 579 | 578
2018-03-12 21:00 | 554 | 554
2018-03-12 21:30 | 529 | 528
2018-03-12 22:00 | 504 | 503
2018-03-12 22:30 | 475 | 474
2018-03-12 23:00 | 451 | 449
2018-03-12 23:30 | 428 | 425
2018-03-13 | 412 | 408
2018-03-13 00:30 | 405 | 401
2018-03-13 01:00 | 393 | 389
2018-03-13 01:30 | 385 | 380
2018-03-13 02:00 | 376 | 372
2018-03-13 02:30 | 370 | 365
2018-03-13 03:00 | 361 | 355
2018-03-13 03:30 | 360 | 354
2018-03-13 04:00 | 353 | 347
2018-03-13 04:30 | 360 | 353
2018-03-13 05:00 | 366 | 359
2018-03-13 05:30 | 378 | 372
2018-03-13 06:00 | 393 | 387
2018-03-13 06:30 | 420 | 415
2018-03-13 07:00 | 443 | 439
2018-03-13 07:30 | 462 | 458
2018-03-13 08:00 | 454 | 451
2018-03-13 08:30 | 444 | 442
2018-03-13 09:00 | 436 | 434
2018-03-13 09:30 | 437 | 434
2018-03-13 10:00 | 431 | 428
2018-03-13 10:30 | 423 | 420
2018-03-13 11:00 | 423 | 421
2018-03-13 11:30 | 428 | 425
2018-03-13 12:00 | 441 | 439
2018-03-13 12:30 | 451 | 449
2018-03-13 13:00 | 447 | 445
2018-03-13 13:30 | 448 | 446
2018-03-13 14:00 | 464 | 462
2018-03-13 14:30 | 467 | 465
2018-03-13 15:00 | 472 | 471
2018-03-13 15:30 | 476 | 475
2018-03-13 16:00 | 483 | 482
2018-03-13 16:30 | 490 | 488
2018-03-13 17:00 | 519 | 518
2018-03-13 17:30 | 534 | 533
2018-03-13 18:00 | 559 | 559
2018-03-13 18:30 | 594 | 594
2018-03-13 19:00 | 624 | 623
2018-03-13 19:30 | 635 | 635
2018-03-13 20:00 | 618 | 618
2018-03-13 20:30 | 595 | 595
2018-03-13 21:00 | 573 | 573
2018-03-13 21:30 | 547 | 547
2018-03-13 22:00 | 518 | 517
2018-03-13 22:30 | 488 | 487
2018-03-13 23:00 | 464 | 462
2018-03-13 23:30 | 441 | 438
2018-03-14 | 418 | 415
2018-03-14 00:30 | 403 | 400
2018-03-14 01:00 | 396 | 392
2018-03-14 01:30 | 387 | 383
2018-03-14 02:00 | 378 | 374
2018-03-14 02:30 | 376 | 371
2018-03-14 03:00 | 371 | 365
2018-03-14 03:30 | 370 | 364
2018-03-14 04:00 | 368 | 363
2018-03-14 04:30 | 373 | 367
2018-03-14 05:00 | 379 | 373
2018-03-14 05:30 | 391 | 386
2018-03-14 06:00 | 411 | 407
2018-03-14 06:30 | 439 | 435
2018-03-14 07:00 | 462 | 459
2018-03-14 07:30 | 477 | 475
2018-03-14 08:00 | 467 | 466
2018-03-14 08:30 | 460 | 458
2018-03-14 09:00 | 458 | 455
2018-03-14 09:30 | 446 | 444
2018-03-14 10:00 | 435 | 433
2018-03-14 10:30 | 443 | 440
2018-03-14 11:00 | 441 | 438
2018-03-14 11:30 | 443 | 441
2018-03-14 12:00 | 433 | 431
2018-03-14 12:30 | 447 | 444
2018-03-14 13:00 | 454 | 452
2018-03-14 13:30 | 456 | 454
2018-03-14 14:00 | 461 | 459
2018-03-14 14:30 | 466 | 465
2018-03-14 15:00 | 480 | 478
2018-03-14 15:30 | 494 | 492
2018-03-14 16:00 | 513 | 512
2018-03-14 16:30 | 536 | 535
2018-03-14 17:00 | 554 | 553
2018-03-14 17:30 | 595 | 594
2018-03-14 18:00 | 607 | 607
2018-03-14 18:30 | 617 | 617
2018-03-14 19:00 | 645 | 645
2018-03-14 19:30 | 651 | 651
2018-03-14 20:00 | 639 | 639
2018-03-14 20:30 | 612 | 612
2018-03-14 21:00 | 584 | 584
2018-03-14 21:30 | 562 | 562
2018-03-14 22:00 | 533 | 532
2018-03-14 22:30 | 498 | 497
2018-03-14 23:00 | 474 | 472
2018-03-14 23:30 | 451 | 449
2018-03-15 | 433 | 431
2018-03-15 00:30 | 418 | 415
2018-03-15 01:00 | 408 | 404
2018-03-15 01:30 | 401 | 397
2018-03-15 02:00 | 393 | 389
2018-03-15 02:30 | 389 | 385
2018-03-15 03:00 | 387 | 383
2018-03-15 03:30 | 390 | 386
2018-03-15 04:00 | 387 | 382
2018-03-15 04:30 | 364 | 360
2018-03-15 05:00 | 323 | 316
2018-03-15 05:30 | 338 | 330
2018-03-15 06:00 | 348 | 341
2018-03-15 06:30 | 383 | 377
2018-03-15 07:00 | 397 | 392
2018-03-15 07:30 | 372 | 367
2018-03-15 08:00 | 322 | 316
2018-03-15 08:30 | 325 | 317
2018-03-15 09:00 | 353 | 346
2018-03-15 09:30 | 362 | 356
2018-03-15 10:00 | 351 | 345
2018-03-15 10:30 | 348 | 342
2018-03-15 11:00 | 332 | 325
2018-03-15 11:30 | 330 | 322
2018-03-15 12:00 | 335 | 327
2018-03-15 12:30 | 343 | 336
2018-03-15 13:00 | 290 | 282
2018-03-15 13:30 | 277 | 266
2018-03-15 14:00 | 296 | 284
2018-03-15 14:30 | 302 | 292
2018-03-15 15:00 | 302 | 295
2018-03-15 15:30 | 302 | 295
2018-03-15 16:00 | 322 | 315
2018-03-15 16:30 | 348 | 343
2018-03-15 17:00 | 425 | 422
2018-03-15 17:30 | 471 | 470
2018-03-15 18:00 | 464 | 463
2018-03-15 18:30 | 408 | 406
2018-03-15 19:00 | 428 | 426
2018-03-15 19:30 | 440 | 438
2018-03-15 20:00 | 422 | 420
2018-03-15 20:30 | 398 | 396
2018-03-15 21:00 | 398 | 395
2018-03-15 21:30 | 476 | 473
2018-03-15 22:00 | 524 | 522
2018-03-15 22:30 | 490 | 490
2018-03-15 23:00 | 471 | 470
2018-03-15 23:30 | 452 | 450
2018-03-16 | 432 | 429
2018-03-16 00:30 | 415 | 412
2018-03-16 01:00 | 404 | 401
2018-03-16 01:30 | 394 | 390
2018-03-16 02:00 | 386 | 382
2018-03-16 02:30 | 371 | 366
2018-03-16 03:00 | 369 | 363
2018-03-16 03:30 | 367 | 361
2018-03-16 04:00 | 369 | 363
2018-03-16 04:30 | 372 | 367
2018-03-16 05:00 | 378 | 373
2018-03-16 05:30 | 399 | 395
2018-03-16 06:00 | 397 | 393
2018-03-16 06:30 | 421 | 417
2018-03-16 07:00 | 444 | 440
2018-03-16 07:30 | 456 | 453
2018-03-16 08:00 | 454 | 452
2018-03-16 08:30 | 447 | 446
2018-03-16 09:00 | 441 | 439
2018-03-16 09:30 | 438 | 435
2018-03-16 10:00 | 433 | 431
2018-03-16 10:30 | 440 | 438
2018-03-16 11:00 | 438 | 436
2018-03-16 11:30 | 444 | 442
2018-03-16 12:00 | 454 | 452
2018-03-16 12:30 | 460 | 458
2018-03-16 13:00 | 465 | 463
2018-03-16 13:30 | 471 | 470
2018-03-16 14:00 | 482 | 481
2018-03-16 14:30 | 501 | 500
2018-03-16 15:00 | 504 | 504
2018-03-16 15:30 | 511 | 510
2018-03-16 16:00 | 530 | 530
2018-03-16 16:30 | 551 | 551
2018-03-16 17:00 | 572 | 572
2018-03-16 17:30 | 580 | 580
2018-03-16 18:00 | 602 | 602
2018-03-16 18:30 | 624 | 624
2018-03-16 19:00 | 645 | 645
2018-03-16 19:30 | 649 | 649
2018-03-16 20:00 | 626 | 626
2018-03-16 20:30 | 606 | 606
2018-03-16 21:00 | 585 | 585
2018-03-16 21:30 | 568 | 568
2018-03-16 22:00 | 546 | 546
2018-03-16 22:30 | 512 | 511
2018-03-16 23:00 | 491 | 490
2018-03-16 23:30 | 468 | 467
2018-03-17 | 448 | 447
2018-03-17 00:30 | 458 | 457
2018-03-17 01:00 | 450 | 449
2018-03-17 01:30 | 443 | 441
2018-03-17 02:00 | 431 | 429
2018-03-17 02:30 | 428 | 426
2018-03-17 03:00 | 427 | 424
2018-03-17 03:30 | 423 | 421
2018-03-17 04:00 | 423 | 421
2018-03-17 04:30 | 419 | 417
2018-03-17 05:00 | 424 | 422
2018-03-17 05:30 | 427 | 425
2018-03-17 06:00 | 433 | 430
2018-03-17 06:30 | 439 | 437
2018-03-17 07:00 | 445 | 443
2018-03-17 07:30 | 448 | 447
2018-03-17 08:00 | 445 | 443
2018-03-17 08:30 | 444 | 443
2018-03-17 09:00 | 446 | 444
2018-03-17 09:30 | 444 | 442
2018-03-17 10:00 | 437 | 435
2018-03-17 10:30 | 427 | 426
2018-03-17 11:00 | 424 | 422
2018-03-17 11:30 | 426 | 423
2018-03-17 12:00 | 435 | 433
2018-03-17 12:30 | 440 | 438
2018-03-17 13:00 | 431 | 429
2018-03-17 13:30 | 424 | 422
2018-03-17 14:00 | 436 | 434
2018-03-17 14:30 | 449 | 447
2018-03-17 15:00 | 457 | 455
2018-03-17 15:30 | 473 | 471
2018-03-17 16:00 | 498 | 496
2018-03-17 16:30 | 515 | 514
2018-03-17 17:00 | 541 | 540
2018-03-17 17:30 | 570 | 569
2018-03-17 18:00 | 584 | 584
2018-03-17 18:30 | 615 | 615
2018-03-17 19:00 | 632 | 632
2018-03-17 19:30 | 634 | 634
2018-03-17 20:00 | 616 | 616
2018-03-17 20:30 | 598 | 597
2018-03-17 21:00 | 578 | 578
2018-03-17 21:30 | 560 | 559
2018-03-17 22:00 | 544 | 543
2018-03-17 22:30 | 543 | 542
2018-03-17 23:00 | 529 | 528
2018-03-17 23:30 | 508 | 507
2018-03-18 | 491 | 490
2018-03-18 00:30 | 476 | 475
2018-03-18 01:00 | 469 | 467
2018-03-18 01:30 | 456 | 454
2018-03-18 02:00 | 451 | 448
2018-03-18 02:30 | 447 | 444
2018-03-18 03:00 | 440 | 438
2018-03-18 03:30 | 441 | 439
2018-03-18 04:00 | 441 | 438
2018-03-18 04:30 | 433 | 430
2018-03-18 05:00 | 427 | 425
2018-03-18 05:30 | 433 | 431
2018-03-18 06:00 | 434 | 432
2018-03-18 06:30 | 438 | 435
2018-03-18 07:00 | 436 | 433
2018-03-18 07:30 | 435 | 432
2018-03-18 08:00 | 434 | 431
2018-03-18 08:30 | 444 | 441
2018-03-18 09:00 | 458 | 456
2018-03-18 09:30 | 471 | 468
2018-03-18 10:00 | 477 | 475
2018-03-18 10:30 | 478 | 477
2018-03-18 11:00 | 472 | 470
2018-03-18 11:30 | 476 | 475
2018-03-18 12:00 | 486 | 484
2018-03-18 12:30 | 489 | 488
2018-03-18 13:00 | 496 | 495
2018-03-18 13:30 | 484 | 483
2018-03-18 14:00 | 496 | 495
2018-03-18 14:30 | 502 | 501
2018-03-18 15:00 | 507 | 506
2018-03-18 15:30 | 524 | 523
2018-03-18 16:00 | 527 | 526
2018-03-18 16:30 | 547 | 547
2018-03-18 17:00 | 559 | 559
2018-03-18 17:30 | 588 | 587
2018-03-18 18:00 | 615 | 614
2018-03-18 18:30 | 648 | 647
2018-03-18 19:00 | 674 | 674
2018-03-18 19:30 | 696 | 696
2018-03-18 20:00 | 676 | 676
2018-03-18 20:30 | 648 | 648
2018-03-18 21:00 | 628 | 628
2018-03-18 21:30 | 607 | 607
2018-03-18 22:00 | 574 | 574
2018-03-18 22:30 | 546 | 545
2018-03-18 23:00 | 520 | 519
2018-03-18 23:30 | 500 | 499
2018-03-19 | 486 | 484
2018-03-19 00:30 | 472 | 470
2018-03-19 01:00 | 456 | 454
2018-03-19 01:30 | 444 | 442
2018-03-19 02:00 | 444 | 441
2018-03-19 02:30 | 435 | 432
2018-03-19 03:00 | 432 | 428
2018-03-19 03:30 | 427 | 423
2018-03-19 04:00 | 427 | 423
2018-03-19 04:30 | 433 | 430
2018-03-19 05:00 | 437 | 433
2018-03-19 05:30 | 453 | 450
2018-03-19 06:00 | 470 | 467
2018-03-19 06:30 | 499 | 497
2018-03-19 07:00 | 531 | 529
2018-03-19 07:30 | 555 | 554
2018-03-19 08:00 | 550 | 550
2018-03-19 08:30 | 527 | 526
2018-03-19 09:00 | 465 | 463
2018-03-19 09:30 | 464 | 462
2018-03-19 10:00 | 467 | 464
2018-03-19 10:30 | 468 | 466
2018-03-19 11:00 | 462 | 459
2018-03-19 11:30 | 444 | 442
2018-03-19 12:00 | 409 | 406
2018-03-19 12:30 | 357 | 352
2018-03-19 13:00 | 361 | 355
2018-03-19 13:30 | 372 | 366
2018-03-19 14:00 | 372 | 366
2018-03-19 14:30 | 376 | 371
2018-03-19 15:00 | 383 | 379
2018-03-19 15:30 | 382 | 378
2018-03-19 16:00 | 381 | 377
2018-03-19 16:30 | 380 | 376
2018-03-19 17:00 | 400 | 396
2018-03-19 17:30 | 404 | 400
2018-03-19 18:00 | 417 | 414
2018-03-19 18:30 | 446 | 444
2018-03-19 19:00 | 475 | 473
2018-03-19 19:30 | 477 | 476
2018-03-19 20:00 | 458 | 456
2018-03-19 20:30 | 434 | 432
2018-03-19 21:00 | 410 | 407
2018-03-19 21:30 | 384 | 380
2018-03-19 22:00 | 361 | 356
2018-03-19 22:30 | 351 | 346
2018-03-19 23:00 | 398 | 393
2018-03-19 23:30 | 394 | 390
2018-03-20 | 374 | 369
2018-03-20 00:30 | 358 | 352
2018-03-20 01:00 | 345 | 339
2018-03-20 01:30 | 342 | 334
2018-03-20 02:00 | 332 | 324
2018-03-20 02:30 | 327 | 318
2018-03-20 03:00 | 321 | 312
2018-03-20 03:30 | 320 | 311
2018-03-20 04:00 | 315 | 306
2018-03-20 04:30 | 319 | 310
2018-03-20 05:00 | 319 | 310
2018-03-20 05:30 | 332 | 324
2018-03-20 06:00 | 344 | 336
2018-03-20 06:30 | 306 | 298
2018-03-20 07:00 | 323 | 313
2018-03-20 07:30 | 342 | 333
2018-03-20 08:00 | 351 | 345
2018-03-20 08:30 | 345 | 338
2018-03-20 09:00 | 338 | 331
2018-03-20 09:30 | 324 | 317
2018-03-20 10:00 | 330 | 323
2018-03-20 10:30 | 330 | 323
2018-03-20 11:00 | 330 | 323
2018-03-20 11:30 | 335 | 328
2018-03-20 12:00 | 335 | 328
2018-03-20 12:30 | 339 | 332
2018-03-20 13:00 | 340 | 334
2018-03-20 13:30 | 345 | 338
2018-03-20 14:00 | 361 | 355
2018-03-20 14:30 | 373 | 368
2018-03-20 15:00 | 384 | 380
2018-03-20 15:30 | 396 | 392
2018-03-20 16:00 | 409 | 406
2018-03-20 16:30 | 424 | 421
2018-03-20 17:00 | 449 | 446
2018-03-20 17:30 | 449 | 447
2018-03-20 18:00 | 460 | 458
2018-03-20 18:30 | 491 | 490
2018-03-20 19:00 | 526 | 524
2018-03-20 19:30 | 529 | 528
2018-03-20 20:00 | 518 | 517
2018-03-20 20:30 | 487 | 486
2018-03-20 21:00 | 462 | 460
2018-03-20 21:30 | 433 | 430
2018-03-20 22:00 | 411 | 407
2018-03-20 22:30 | 438 | 434
2018-03-20 23:00 | 466 | 463
2018-03-20 23:30 | 529 | 527
2018-03-21 | 507 | 506
2018-03-21 00:30 | 495 | 493
2018-03-21 01:00 | 482 | 480
2018-03-21 01:30 | 469 | 467
2018-03-21 02:00 | 462 | 460
2018-03-21 02:30 | 455 | 454
2018-03-21 03:00 | 451 | 450
2018-03-21 03:30 | 450 | 448
2018-03-21 04:00 | 451 | 449
2018-03-21 04:30 | 451 | 450
2018-03-21 05:00 | 451 | 449
2018-03-21 05:30 | 467 | 466
2018-03-21 06:00 | 483 | 482
2018-03-21 06:30 | 516 | 515
2018-03-21 07:00 | 542 | 542
2018-03-21 07:30 | 557 | 557
2018-03-21 08:00 | 559 | 559
2018-03-21 08:30 | 556 | 556
2018-03-21 09:00 | 556 | 556
2018-03-21 09:30 | 572 | 572
2018-03-21 10:00 | 563 | 563
2018-03-21 10:30 | 553 | 553
2018-03-21 11:00 | 566 | 565
2018-03-21 11:30 | 560 | 559
2018-03-21 12:00 | 557 | 557
2018-03-21 12:30 | 566 | 566
2018-03-21 13:00 | 571 | 570
2018-03-21 13:30 | 561 | 560
2018-03-21 14:00 | 572 | 572
2018-03-21 14:30 | 583 | 582
2018-03-21 15:00 | 600 | 600
2018-03-21 15:30 | 605 | 605
2018-03-21 16:00 | 635 | 635
2018-03-21 16:30 | 614 | 614
2018-03-21 17:00 | 604 | 604
2018-03-21 17:30 | 617 | 617
2018-03-21 18:00 | 632 | 631
2018-03-21 18:30 | 657 | 657
2018-03-21 19:00 | 681 | 681
2018-03-21 19:30 | 668 | 668
2018-03-21 20:00 | 646 | 646
2018-03-21 20:30 | 612 | 612
2018-03-21 21:00 | 593 | 593
2018-03-21 21:30 | 602 | 601
2018-03-21 22:00 | 590 | 590
2018-03-21 22:30 | 555 | 555
2018-03-21 23:00 | 527 | 527
2018-03-21 23:30 | 503 | 502
2018-03-22 | 486 | 485
2018-03-22 00:30 | 471 | 470
2018-03-22 01:00 | 462 | 460
2018-03-22 01:30 | 448 | 447
2018-03-22 02:00 | 440 | 438
2018-03-22 02:30 | 436 | 434
2018-03-22 03:00 | 435 | 433
2018-03-22 03:30 | 431 | 429
2018-03-22 04:00 | 431 | 428
2018-03-22 04:30 | 433 | 430
2018-03-22 05:00 | 440 | 438
2018-03-22 05:30 | 449 | 447
2018-03-22 06:00 | 466 | 464
2018-03-22 06:30 | 501 | 499
2018-03-22 07:00 | 527 | 526
2018-03-22 07:30 | 551 | 550
2018-03-22 08:00 | 569 | 569
2018-03-22 08:30 | 570 | 570
2018-03-22 09:00 | 550 | 550
2018-03-22 09:30 | 527 | 527
2018-03-22 10:00 | 519 | 519
2018-03-22 10:30 | 518 | 517
2018-03-22 11:00 | 521 | 520
2018-03-22 11:30 | 517 | 516
2018-03-22 12:00 | 527 | 526
2018-03-22 12:30 | 529 | 528
2018-03-22 13:00 | 541 | 541
2018-03-22 13:30 | 552 | 552
2018-03-22 14:00 | 552 | 552
2018-03-22 14:30 | 555 | 554
2018-03-22 15:00 | 572 | 572
2018-03-22 15:30 | 566 | 566
2018-03-22 16:00 | 581 | 581
2018-03-22 16:30 | 590 | 590
2018-03-22 17:00 | 576 | 576
2018-03-22 17:30 | 578 | 578
2018-03-22 18:00 | 630 | 630
2018-03-22 18:30 | 657 | 657
2018-03-22 19:00 | 677 | 677
2018-03-22 19:30 | 670 | 670
2018-03-22 20:00 | 649 | 649
2018-03-22 20:30 | 638 | 638
2018-03-22 21:00 | 608 | 608
2018-03-22 21:30 | 584 | 584
2018-03-22 22:00 | 562 | 562
2018-03-22 22:30 | 537 | 536
2018-03-22 23:00 | 508 | 508
2018-03-22 23:30 | 489 | 488
2018-03-23 | 466 | 465
2018-03-23 00:30 | 454 | 452
2018-03-23 01:00 | 449 | 448
2018-03-23 01:30 | 438 | 437
2018-03-23 02:00 | 432 | 430
2018-03-23 02:30 | 425 | 423
2018-03-23 03:00 | 426 | 423
2018-03-23 03:30 | 425 | 423
2018-03-23 04:00 | 420 | 418
2018-03-23 04:30 | 428 | 426
2018-03-23 05:00 | 432 | 430
2018-03-23 05:30 | 445 | 443
2018-03-23 06:00 | 461 | 460
2018-03-23 06:30 | 493 | 492
2018-03-23 07:00 | 520 | 519
2018-03-23 07:30 | 553 | 552
2018-03-23 08:00 | 577 | 576
2018-03-23 08:30 | 594 | 594
2018-03-23 09:00 | 595 | 595
2018-03-23 09:30 | 593 | 593
2018-03-23 10:00 | 580 | 580
2018-03-23 10:30 | 569 | 568
2018-03-23 11:00 | 595 | 592
2018-03-23 11:30 | 590 | 589
2018-03-23 12:00 | 562 | 562
2018-03-23 12:30 | 525 | 524
2018-03-23 13:00 | 524 | 524
2018-03-23 13:30 | 521 | 521
2018-03-23 14:00 | 522 | 522
2018-03-23 14:30 | 516 | 516
2018-03-23 15:00 | 520 | 520
2018-03-23 15:30 | 544 | 543
2018-03-23 16:00 | 556 | 555
2018-03-23 16:30 | 566 | 566
2018-03-23 17:00 | 571 | 571
2018-03-23 17:30 | 569 | 569
2018-03-23 18:00 | 569 | 569
2018-03-23 18:30 | 582 | 582
2018-03-23 19:00 | 600 | 600
2018-03-23 19:30 | 593 | 593
2018-03-23 20:00 | 576 | 576
2018-03-23 20:30 | 555 | 555
2018-03-23 21:00 | 539 | 539
2018-03-23 21:30 | 526 | 526
2018-03-23 22:00 | 508 | 508
2018-03-23 22:30 | 509 | 509
2018-03-23 23:00 | 495 | 495
2018-03-23 23:30 | 480 | 479
2018-03-24 | 462 | 461
2018-03-24 00:30 | 448 | 447
2018-03-24 01:00 | 442 | 441
2018-03-24 01:30 | 432 | 430
2018-03-24 02:00 | 427 | 425
2018-03-24 02:30 | 421 | 419
2018-03-24 03:00 | 414 | 412
2018-03-24 03:30 | 414 | 411
2018-03-24 04:00 | 410 | 407
2018-03-24 04:30 | 414 | 412
2018-03-24 05:00 | 414 | 412
2018-03-24 05:30 | 423 | 420
2018-03-24 06:00 | 425 | 423
2018-03-24 06:30 | 440 | 438
2018-03-24 07:00 | 451 | 449
2018-03-24 07:30 | 471 | 470
2018-03-24 08:00 | 487 | 486
2018-03-24 08:30 | 500 | 499
2018-03-24 09:00 | 507 | 507
2018-03-24 09:30 | 502 | 501
2018-03-24 10:00 | 506 | 505
2018-03-24 10:30 | 513 | 512
2018-03-24 11:00 | 511 | 510
2018-03-24 11:30 | 510 | 510
2018-03-24 12:00 | 525 | 524
2018-03-24 12:30 | 521 | 520
2018-03-24 13:00 | 523 | 523
2018-03-24 13:30 | 528 | 527
2018-03-24 14:00 | 520 | 520
2018-03-24 14:30 | 505 | 505
2018-03-24 15:00 | 514 | 514
2018-03-24 15:30 | 518 | 517
2018-03-24 16:00 | 508 | 508
2018-03-24 16:30 | 523 | 522
2018-03-24 17:00 | 535 | 535
2018-03-24 17:30 | 548 | 548
2018-03-24 18:00 | 562 | 561
2018-03-24 18:30 | 572 | 572
2018-03-24 19:00 | 574 | 574
2018-03-24 19:30 | 566 | 566
2018-03-24 20:00 | 540 | 540
2018-03-24 20:30 | 519 | 519
2018-03-24 21:00 | 507 | 506
2018-03-24 21:30 | 486 | 485
2018-03-24 22:00 | 470 | 470
2018-03-24 22:30 | 449 | 448
2018-03-24 23:00 | 432 | 431
2018-03-24 23:30 | 417 | 415
2018-03-25 | 406 | 404
2018-03-25 00:30 | 393 | 390
2018-03-25 01:00 | 382 | 380
2018-03-25 01:30 | 375 | 372
2018-03-25 02:00 | 372 | 369
2018-03-25 02:30 | 370 | 367
2018-03-25 03:00 | 375 | 371
2018-03-25 03:30 | 374 | 370
2018-03-25 04:00 | 367 | 363
2018-03-25 04:30 | 366 | 362
2018-03-25 05:00 | 365 | 361
2018-03-25 05:30 | 372 | 368
2018-03-25 06:00 | 374 | 370
2018-03-25 06:30 | 378 | 374
2018-03-25 07:00 | 387 | 383
2018-03-25 07:30 | 405 | 401
2018-03-25 08:00 | 423 | 420
2018-03-25 08:30 | 445 | 442
2018-03-25 09:00 | 453 | 451
2018-03-25 09:30 | 458 | 457
2018-03-25 10:00 | 457 | 456
2018-03-25 10:30 | 466 | 464
2018-03-25 11:00 | 472 | 471
2018-03-25 11:30 | 462 | 461
2018-03-25 12:00 | 472 | 470
2018-03-25 12:30 | 478 | 477
2018-03-25 13:00 | 482 | 481
2018-03-25 13:30 | 461 | 460
2018-03-25 14:00 | 472 | 470
2018-03-25 14:30 | 473 | 472
2018-03-25 15:00 | 483 | 482
2018-03-25 15:30 | 483 | 483
2018-03-25 16:00 | 480 | 480
2018-03-25 16:30 | 498 | 497
2018-03-25 17:00 | 513 | 512
2018-03-25 17:30 | 524 | 524
2018-03-25 18:00 | 548 | 548
2018-03-25 18:30 | 568 | 567
2018-03-25 19:00 | 585 | 585
2018-03-25 19:30 | 572 | 572
2018-03-25 20:00 | 553 | 553
2018-03-25 20:30 | 534 | 534
2018-03-25 21:00 | 516 | 516
2018-03-25 21:30 | 519 | 518
2018-03-25 22:00 | 505 | 505
2018-03-25 22:30 | 479 | 478
2018-03-25 23:00 | 453 | 451
2018-03-25 23:30 | 438 | 436
2018-03-26 | 424 | 422
2018-03-26 00:30 | 419 | 417
2018-03-26 01:00 | 407 | 405
2018-03-26 01:30 | 399 | 397
2018-03-26 02:00 | 397 | 394
2018-03-26 02:30 | 397 | 394
2018-03-26 03:00 | 395 | 392
2018-03-26 03:30 | 398 | 395
2018-03-26 04:00 | 397 | 394
2018-03-26 04:30 | 396 | 393
2018-03-26 05:00 | 404 | 401
2018-03-26 05:30 | 418 | 416
2018-03-26 06:00 | 435 | 433
2018-03-26 06:30 | 475 | 473
2018-03-26 07:00 | 507 | 506
2018-03-26 07:30 | 550 | 550
2018-03-26 08:00 | 569 | 569
2018-03-26 08:30 | 570 | 570
2018-03-26 09:00 | 564 | 564
2018-03-26 09:30 | 572 | 572
2018-03-26 10:00 | 572 | 572
2018-03-26 10:30 | 569 | 569
2018-03-26 11:00 | 564 | 564
2018-03-26 11:30 | 562 | 562
2018-03-26 12:00 | 563 | 563
2018-03-26 12:30 | 574 | 573
2018-03-26 13:00 | 577 | 577
2018-03-26 13:30 | 574 | 574
2018-03-26 14:00 | 573 | 573
2018-03-26 14:30 | 577 | 577
2018-03-26 15:00 | 576 | 576
2018-03-26 15:30 | 584 | 584
2018-03-26 16:00 | 590 | 590
2018-03-26 16:30 | 588 | 588
2018-03-26 17:00 | 596 | 596
2018-03-26 17:30 | 591 | 591
2018-03-26 18:00 | 605 | 605
2018-03-26 18:30 | 627 | 627
2018-03-26 19:00 | 635 | 635
2018-03-26 19:30 | 619 | 619
2018-03-26 20:00 | 600 | 600
2018-03-26 20:30 | 578 | 578
2018-03-26 21:00 | 554 | 554
2018-03-26 21:30 | 527 | 527
2018-03-26 22:00 | 509 | 509
2018-03-26 22:30 | 484 | 483
2018-03-26 23:00 | 461 | 460
2018-03-26 23:30 | 449 | 447
2018-03-27 | 444 | 442
2018-03-27 00:30 | 438 | 436
2018-03-27 01:00 | 431 | 430
2018-03-27 01:30 | 423 | 421
2018-03-27 02:00 | 417 | 415
2018-03-27 02:30 | 412 | 409
2018-03-27 03:00 | 410 | 407
2018-03-27 03:30 | 418 | 415
2018-03-27 04:00 | 421 | 418
2018-03-27 04:30 | 422 | 418
2018-03-27 05:00 | 427 | 425
2018-03-27 05:30 | 446 | 443
2018-03-27 06:00 | 457 | 455
2018-03-27 06:30 | 490 | 489
2018-03-27 07:00 | 520 | 519
2018-03-27 07:30 | 562 | 561
2018-03-27 08:00 | 582 | 581
2018-03-27 08:30 | 591 | 590
2018-03-27 09:00 | 597 | 596
2018-03-27 09:30 | 600 | 599
2018-03-27 10:00 | 585 | 585
2018-03-27 10:30 | 567 | 567
2018-03-27 11:00 | 560 | 559
2018-03-27 11:30 | 560 | 559
2018-03-27 12:00 | 527 | 527
2018-03-27 12:30 | 451 | 450
2018-03-27 13:00 | 444 | 442
2018-03-27 13:30 | 443 | 441
2018-03-27 14:00 | 542 | 541
2018-03-27 14:30 | 574 | 573
2018-03-27 15:00 | 566 | 566
2018-03-27 15:30 | 587 | 587
2018-03-27 16:00 | 608 | 608
2018-03-27 16:30 | 612 | 612
2018-03-27 17:00 | 603 | 603
2018-03-27 17:30 | 607 | 607
2018-03-27 18:00 | 621 | 621
2018-03-27 18:30 | 639 | 639
2018-03-27 19:00 | 658 | 658
2018-03-27 19:30 | 655 | 655
2018-03-27 20:00 | 638 | 638
2018-03-27 20:30 | 619 | 619
2018-03-27 21:00 | 604 | 604
2018-03-27 21:30 | 578 | 578
2018-03-27 22:00 | 548 | 548
2018-03-27 22:30 | 513 | 513
2018-03-27 23:00 | 491 | 490
2018-03-27 23:30 | 475 | 473
2018-03-28 | 460 | 458
2018-03-28 00:30 | 452 | 449
2018-03-28 01:00 | 441 | 438
2018-03-28 01:30 | 436 | 433
2018-03-28 02:00 | 430 | 426
2018-03-28 02:30 | 424 | 421
2018-03-28 03:00 | 419 | 415
2018-03-28 03:30 | 420 | 416
2018-03-28 04:00 | 421 | 417
2018-03-28 04:30 | 422 | 418
2018-03-28 05:00 | 424 | 420
2018-03-28 05:30 | 441 | 437
2018-03-28 06:00 | 457 | 453
2018-03-28 06:30 | 493 | 490
2018-03-28 07:00 | 517 | 515
2018-03-28 07:30 | 546 | 545
2018-03-28 08:00 | 554 | 553
2018-03-28 08:30 | 558 | 558
2018-03-28 09:00 | 502 | 501
2018-03-28 09:30 | 424 | 421
2018-03-28 10:00 | 423 | 419
2018-03-28 10:30 | 444 | 440
2018-03-28 11:00 | 417 | 413
2018-03-28 11:30 | 412 | 408
2018-03-28 12:00 | 431 | 427
2018-03-28 12:30 | 443 | 440
2018-03-28 13:00 | 460 | 457
2018-03-28 13:30 | 485 | 483
2018-03-28 14:00 | 454 | 452
2018-03-28 14:30 | 433 | 431
2018-03-28 15:00 | 383 | 380
2018-03-28 15:30 | 388 | 383
2018-03-28 16:00 | 397 | 392
2018-03-28 16:30 | 401 | 397
2018-03-28 17:00 | 410 | 406
2018-03-28 17:30 | 410 | 407
2018-03-28 18:00 | 415 | 412
2018-03-28 18:30 | 437 | 434
2018-03-28 19:00 | 473 | 471
2018-03-28 19:30 | 469 | 467
2018-03-28 20:00 | 449 | 448
2018-03-28 20:30 | 427 | 425
2018-03-28 21:00 | 408 | 405
2018-03-28 21:30 | 389 | 385
2018-03-28 22:00 | 360 | 355
2018-03-28 22:30 | 325 | 319
2018-03-28 23:00 | 368 | 362
2018-03-28 23:30 | 366 | 361
2018-03-29 | 345 | 340
2018-03-29 00:30 | 330 | 323
2018-03-29 01:00 | 316 | 307
2018-03-29 01:30 | 309 | 299
2018-03-29 02:00 | 301 | 290
2018-03-29 02:30 | 297 | 286
2018-03-29 03:00 | 286 | 274
2018-03-29 03:30 | 288 | 276
2018-03-29 04:00 | 293 | 279
2018-03-29 04:30 | 295 | 281
2018-03-29 05:00 | 299 | 285
2018-03-29 05:30 | 312 | 299
2018-03-29 06:00 | 350 | 339
2018-03-29 06:30 | 378 | 370
2018-03-29 07:00 | 399 | 393
2018-03-29 07:30 | 405 | 400
2018-03-29 08:00 | 401 | 396
2018-03-29 08:30 | 398 | 393
2018-03-29 09:00 | 381 | 375
2018-03-29 09:30 | 288 | 280
2018-03-29 10:00 | 286 | 273
2018-03-29 10:30 | 263 | 248
2018-03-29 11:00 | 318 | 305
2018-03-29 11:30 | 333 | 323
2018-03-29 12:00 | 340 | 332
2018-03-29 12:30 | 326 | 317
2018-03-29 13:00 | 273 | 262
2018-03-29 13:30 | 260 | 245
2018-03-29 14:00 | 260 | 243
2018-03-29 14:30 | 214 | 193
2018-03-29 15:00 | 237 | 214
2018-03-29 15:30 | 271 | 253
2018-03-29 16:00 | 300 | 286
2018-03-29 16:30 | 363 | 353
2018-03-29 17:00 | 371 | 364
2018-03-29 17:30 | 384 | 378
2018-03-29 18:00 | 409 | 404
2018-03-29 18:30 | 413 | 409
2018-03-29 19:00 | 438 | 434
2018-03-29 19:30 | 433 | 430
2018-03-29 20:00 | 417 | 414
2018-03-29 20:30 | 461 | 458
2018-03-29 21:00 | 455 | 453
2018-03-29 21:30 | 430 | 428
2018-03-29 22:00 | 406 | 402
2018-03-29 22:30 | 376 | 371
2018-03-29 23:00 | 401 | 397
2018-03-29 23:30 | 455 | 452
2018-03-30 | 436 | 433
2018-03-30 00:30 | 422 | 419
2018-03-30 01:00 | 406 | 403
2018-03-30 01:30 | 395 | 391
2018-03-30 02:00 | 387 | 382
2018-03-30 02:30 | 375 | 370
2018-03-30 03:00 | 373 | 367
2018-03-30 03:30 | 368 | 361
2018-03-30 04:00 | 367 | 361
2018-03-30 04:30 | 363 | 356
2018-03-30 05:00 | 366 | 359
2018-03-30 05:30 | 370 | 363
2018-03-30 06:00 | 371 | 364
2018-03-30 06:30 | 380 | 373
2018-03-30 07:00 | 379 | 373
2018-03-30 07:30 | 376 | 369
2018-03-30 08:00 | 362 | 355
2018-03-30 08:30 | 362 | 354
2018-03-30 09:00 | 389 | 383
2018-03-30 09:30 | 391 | 386
2018-03-30 10:00 | 391 | 385
2018-03-30 10:30 | 382 | 376
2018-03-30 11:00 | 358 | 352
2018-03-30 11:30 | 363 | 357
2018-03-30 12:00 | 380 | 374
2018-03-30 12:30 | 388 | 382
2018-03-30 13:00 | 396 | 391
2018-03-30 13:30 | 407 | 401
2018-03-30 14:00 | 418 | 414
2018-03-30 14:30 | 435 | 430
2018-03-30 15:00 | 452 | 449
2018-03-30 15:30 | 475 | 473
2018-03-30 16:00 | 495 | 493
2018-03-30 16:30 | 518 | 516
2018-03-30 17:00 | 531 | 530
2018-03-30 17:30 | 564 | 563
2018-03-30 18:00 | 591 | 590
2018-03-30 18:30 | 611 | 611
2018-03-30 19:00 | 635 | 635
2018-03-30 19:30 | 633 | 633
2018-03-30 20:00 | 612 | 611
2018-03-30 20:30 | 585 | 585
2018-03-30 21:00 | 567 | 566
2018-03-30 21:30 | 548 | 548
2018-03-30 22:00 | 529 | 528
2018-03-30 22:30 | 505 | 504
2018-03-30 23:00 | 486 | 484
2018-03-30 23:30 | 464 | 462
2018-03-31 | 444 | 441
2018-03-31 00:30 | 431 | 427
2018-03-31 01:00 | 418 | 414
2018-03-31 01:30 | 407 | 401
2018-03-31 02:00 | 404 | 399
2018-03-31 02:30 | 399 | 393
2018-03-31 03:00 | 391 | 385
2018-03-31 03:30 | 388 | 382
2018-03-31 04:00 | 390 | 383
2018-03-31 04:30 | 388 | 382
2018-03-31 05:00 | 394 | 387
2018-03-31 05:30 | 395 | 388
2018-03-31 06:00 | 394 | 387
2018-03-31 06:30 | 400 | 393
2018-03-31 07:00 | 409 | 402
2018-03-31 07:30 | 402 | 395
2018-03-31 08:00 | 402 | 395
2018-03-31 08:30 | 404 | 397
2018-03-31 09:00 | 406 | 399
2018-03-31 09:30 | 409 | 403
2018-03-31 10:00 | 414 | 408
2018-03-31 10:30 | 415 | 410
2018-03-31 11:00 | 417 | 412
2018-03-31 11:30 | 420 | 415
2018-03-31 12:00 | 426 | 420
2018-03-31 12:30 | 427 | 422
2018-03-31 13:00 | 438 | 433
2018-03-31 13:30 | 441 | 437
2018-03-31 14:00 | 463 | 459
2018-03-31 14:30 | 472 | 468
2018-03-31 15:00 | 476 | 472
2018-03-31 15:30 | 470 | 467
2018-03-31 16:00 | 488 | 485
2018-03-31 16:30 | 499 | 496
2018-03-31 17:00 | 520 | 518
2018-03-31 17:30 | 548 | 547
2018-03-31 18:00 | 572 | 571
2018-03-31 18:30 | 591 | 590
2018-03-31 19:00 | 605 | 605
2018-03-31 19:30 | 598 | 598
2018-03-31 20:00 | 581 | 581
2018-03-31 20:30 | 561 | 561
2018-03-31 21:00 | 549 | 548
2018-03-31 21:30 | 530 | 529
2018-03-31 22:00 | 517 | 515
2018-03-31 22:30 | 490 | 489
2018-03-31 23:00 | 472 | 470
2018-03-31 23:30 | 454 | 451
2018-04-01 | 440 | 437
2018-04-01 00:30 | 429 | 426
2018-04-01 01:00 | 413 | 409
2018-04-01 01:30 | 406 | 401
2018-04-01 02:00 | 398 | 394
2018-04-01 02:30 | 390 | 386
2018-04-01 03:00 | 388 | 384
2018-04-01 03:30 | 383 | 379
2018-04-01 04:00 | 375 | 370
2018-04-01 04:30 | 376 | 371
2018-04-01 05:00 | 377 | 371
2018-04-01 05:30 | 385 | 380
2018-04-01 06:00 | 381 | 375
2018-04-01 06:30 | 388 | 383
2018-04-01 07:00 | 390 | 385
2018-04-01 07:30 | 397 | 392
2018-04-01 08:00 | 391 | 387
2018-04-01 08:30 | 421 | 416
2018-04-01 09:00 | 434 | 430
2018-04-01 09:30 | 413 | 410
2018-04-01 10:00 | 432 | 428
2018-04-01 10:30 | 427 | 423
2018-04-01 11:00 | 410 | 406
2018-04-01 11:30 | 401 | 397
2018-04-01 12:00 | 418 | 414
2018-04-01 12:30 | 417 | 413
2018-04-01 13:00 | 431 | 427
2018-04-01 13:30 | 436 | 433
2018-04-01 14:00 | 424 | 421
2018-04-01 14:30 | 424 | 421
2018-04-01 15:00 | 453 | 450
2018-04-01 15:30 | 462 | 460
2018-04-01 16:00 | 468 | 466
2018-04-01 16:30 | 469 | 467
2018-04-01 17:00 | 491 | 490
2018-04-01 17:30 | 497 | 496
2018-04-01 18:00 | 528 | 527
2018-04-01 18:30 | 559 | 558
2018-04-01 19:00 | 574 | 574
2018-04-01 19:30 | 571 | 571
2018-04-01 20:00 | 553 | 552
2018-04-01 20:30 | 534 | 533
2018-04-01 21:00 | 518 | 517
2018-04-01 21:30 | 505 | 504
2018-04-01 22:00 | 491 | 490
2018-04-01 22:30 | 473 | 470
2018-04-01 23:00 | 457 | 455
2018-04-01 23:30 | 435 | 432
2018-04-02 | 416 | 412
2018-04-02 00:30 | 407 | 403
2018-04-02 01:00 | 402 | 397
2018-04-02 01:30 | 393 | 388
2018-04-02 02:00 | 384 | 378
2018-04-02 02:30 | 380 | 374
2018-04-02 03:00 | 372 | 366
2018-04-02 03:30 | 368 | 361
2018-04-02 04:00 | 368 | 361
2018-04-02 04:30 | 369 | 362
2018-04-02 05:00 | 372 | 365
2018-04-02 05:30 | 375 | 368
2018-04-02 06:00 | 381 | 374
2018-04-02 06:30 | 389 | 383
2018-04-02 07:00 | 388 | 383
2018-04-02 07:30 | 397 | 392
2018-04-02 08:00 | 405 | 400
2018-04-02 08:30 | 400 | 394
2018-04-02 09:00 | 407 | 402
2018-04-02 09:30 | 424 | 419
2018-04-02 10:00 | 428 | 424
2018-04-02 10:30 | 413 | 409
2018-04-02 11:00 | 404 | 400
2018-04-02 11:30 | 437 | 433
2018-04-02 12:00 | 446 | 442
2018-04-02 12:30 | 444 | 440
2018-04-02 13:00 | 436 | 433
2018-04-02 13:30 | 435 | 432
2018-04-02 14:00 | 426 | 422
2018-04-02 14:30 | 438 | 434
2018-04-02 15:00 | 446 | 443
2018-04-02 15:30 | 464 | 461
2018-04-02 16:00 | 481 | 478
2018-04-02 16:30 | 503 | 501
2018-04-02 17:00 | 505 | 503
2018-04-02 17:30 | 539 | 537
2018-04-02 18:00 | 563 | 563
2018-04-02 18:30 | 586 | 586
2018-04-02 19:00 | 605 | 605
2018-04-02 19:30 | 589 | 589
2018-04-02 20:00 | 566 | 566
2018-04-02 20:30 | 545 | 545
2018-04-02 21:00 | 530 | 529
2018-04-02 21:30 | 505 | 505
2018-04-02 22:00 | 484 | 483
2018-04-02 22:30 | 459 | 458
2018-04-02 23:00 | 443 | 441
2018-04-02 23:30 | 426 | 424
2018-04-03 | 413 | 411
2018-04-03 00:30 | 401 | 398
2018-04-03 01:00 | 386 | 383
2018-04-03 01:30 | 379 | 375
2018-04-03 02:00 | 379 | 375
2018-04-03 02:30 | 375 | 370
2018-04-03 03:00 | 373 | 369
2018-04-03 03:30 | 369 | 364
2018-04-03 04:00 | 368 | 363
2018-04-03 04:30 | 368 | 363
2018-04-03 05:00 | 370 | 365
2018-04-03 05:30 | 385 | 380
2018-04-03 06:00 | 400 | 395
2018-04-03 06:30 | 430 | 426
2018-04-03 07:00 | 450 | 447
2018-04-03 07:30 | 470 | 468
2018-04-03 08:00 | 472 | 470
2018-04-03 08:30 | 464 | 463
2018-04-03 09:00 | 458 | 456
2018-04-03 09:30 | 453 | 452
2018-04-03 10:00 | 450 | 448
2018-04-03 10:30 | 453 | 451
2018-04-03 11:00 | 458 | 457
2018-04-03 11:30 | 452 | 451
2018-04-03 12:00 | 456 | 454
2018-04-03 12:30 | 454 | 453
2018-04-03 13:00 | 458 | 456
2018-04-03 13:30 | 479 | 477
2018-04-03 14:00 | 487 | 486
2018-04-03 14:30 | 494 | 492
2018-04-03 15:00 | 499 | 498
2018-04-03 15:30 | 499 | 498
2018-04-03 16:00 | 508 | 506
2018-04-03 16:30 | 515 | 514
2018-04-03 17:00 | 540 | 539
2018-04-03 17:30 | 557 | 556
2018-04-03 18:00 | 576 | 576
2018-04-03 18:30 | 600 | 599
2018-04-03 19:00 | 622 | 622
2018-04-03 19:30 | 610 | 610
2018-04-03 20:00 | 582 | 582
2018-04-03 20:30 | 560 | 560
2018-04-03 21:00 | 539 | 539
2018-04-03 21:30 | 522 | 521
2018-04-03 22:00 | 498 | 497
2018-04-03 22:30 | 471 | 470
2018-04-03 23:00 | 447 | 446
2018-04-03 23:30 | 426 | 423
2018-04-04 | 409 | 406
2018-04-04 00:30 | 397 | 393
2018-04-04 01:00 | 387 | 382
2018-04-04 01:30 | 376 | 371
2018-04-04 02:00 | 370 | 364
2018-04-04 02:30 | 362 | 356
2018-04-04 03:00 | 360 | 354
2018-04-04 03:30 | 356 | 349
2018-04-04 04:00 | 350 | 344
2018-04-04 04:30 | 352 | 346
2018-04-04 05:00 | 353 | 347
2018-04-04 05:30 | 366 | 360
2018-04-04 06:00 | 378 | 373
2018-04-04 06:30 | 406 | 401
2018-04-04 07:00 | 426 | 422
2018-04-04 07:30 | 452 | 449
2018-04-04 08:00 | 450 | 448
2018-04-04 08:30 | 442 | 440
2018-04-04 09:00 | 445 | 443
2018-04-04 09:30 | 438 | 435
2018-04-04 10:00 | 425 | 422
2018-04-04 10:30 | 392 | 389
2018-04-04 11:00 | 342 | 337
2018-04-04 11:30 | 336 | 330
2018-04-04 12:00 | 336 | 329
2018-04-04 12:30 | 338 | 331
2018-04-04 13:00 | 345 | 339
2018-04-04 13:30 | 345 | 339
2018-04-04 14:00 | 324 | 317
2018-04-04 14:30 | 336 | 329
2018-04-04 15:00 | 354 | 348
2018-04-04 15:30 | 358 | 352
2018-04-04 16:00 | 370 | 364
2018-04-04 16:30 | 392 | 387
2018-04-04 17:00 | 313 | 308
2018-04-04 17:30 | 317 | 310
2018-04-04 18:00 | 340 | 333
2018-04-04 18:30 | 367 | 361
2018-04-04 19:00 | 386 | 381
2018-04-04 19:30 | 374 | 370
2018-04-04 20:00 | 355 | 350
2018-04-04 20:30 | 333 | 327
2018-04-04 21:00 | 312 | 306
2018-04-04 21:30 | 298 | 290
2018-04-04 22:00 | 279 | 270
2018-04-04 22:30 | 255 | 244
2018-04-04 23:00 | 295 | 284
2018-04-04 23:30 | 297 | 287
2018-04-05 | 281 | 271
2018-04-05 00:30 | 268 | 256
2018-04-05 01:00 | 253 | 241
2018-04-05 01:30 | 246 | 232
2018-04-05 02:00 | 239 | 224
2018-04-05 02:30 | 232 | 215
2018-04-05 03:00 | 229 | 212
2018-04-05 03:30 | 229 | 212
2018-04-05 04:00 | 231 | 214
2018-04-05 04:30 | 232 | 216
2018-04-05 05:00 | 236 | 220
2018-04-05 05:30 | 243 | 228
2018-04-05 06:00 | 251 | 236
2018-04-05 06:30 | 281 | 268
2018-04-05 07:00 | 298 | 288
2018-04-05 07:30 | 313 | 304
2018-04-05 08:00 | 316 | 307
2018-04-05 08:30 | 334 | 327
2018-04-05 09:00 | 329 | 322
2018-04-05 09:30 | 315 | 308
2018-04-05 10:00 | 304 | 296
2018-04-05 10:30 | 304 | 294
2018-04-05 11:00 | 302 | 293
2018-04-05 11:30 | 298 | 289
2018-04-05 12:00 | 306 | 296
2018-04-05 12:30 | 313 | 304
2018-04-05 13:00 | 324 | 316
2018-04-05 13:30 | 326 | 319
2018-04-05 14:00 | 337 | 330
2018-04-05 14:30 | 344 | 338
2018-04-05 15:00 | 350 | 344
2018-04-05 15:30 | 364 | 359
2018-04-05 16:00 | 370 | 365
2018-04-05 16:30 | 384 | 380
2018-04-05 17:00 | 325 | 320
2018-04-05 17:30 | 335 | 328
2018-04-05 18:00 | 362 | 356
2018-04-05 18:30 | 395 | 391
2018-04-05 19:00 | 415 | 412
2018-04-05 19:30 | 405 | 403
2018-04-05 20:00 | 386 | 383
2018-04-05 20:30 | 367 | 363
2018-04-05 21:00 | 346 | 341
2018-04-05 21:30 | 321 | 315
2018-04-05 22:00 | 299 | 291
2018-04-05 22:30 | 273 | 263
2018-04-05 23:00 | 251 | 239
2018-04-05 23:30 | 298 | 286
2018-04-06 | 295 | 286
2018-04-06 00:30 | 330 | 322
2018-04-06 01:00 | 398 | 393
2018-04-06 01:30 | 391 | 387
2018-04-06 02:00 | 379 | 375
2018-04-06 02:30 | 377 | 372
2018-04-06 03:00 | 379 | 374
2018-04-06 03:30 | 379 | 375
2018-04-06 04:00 | 379 | 375
2018-04-06 04:30 | 380 | 376
2018-04-06 05:00 | 382 | 378
2018-04-06 05:30 | 396 | 392
2018-04-06 06:00 | 413 | 409
2018-04-06 06:30 | 437 | 434
2018-04-06 07:00 | 452 | 449
2018-04-06 07:30 | 468 | 466
2018-04-06 08:00 | 472 | 470
2018-04-06 08:30 | 455 | 453
2018-04-06 09:00 | 463 | 460
2018-04-06 09:30 | 461 | 459
2018-04-06 10:00 | 447 | 446
2018-04-06 10:30 | 450 | 448
2018-04-06 11:00 | 447 | 446
2018-04-06 11:30 | 466 | 464
2018-04-06 12:00 | 481 | 479
2018-04-06 12:30 | 478 | 477
2018-04-06 13:00 | 489 | 488
2018-04-06 13:30 | 501 | 500
2018-04-06 14:00 | 490 | 489
2018-04-06 14:30 | 480 | 479
2018-04-06 15:00 | 501 | 500
2018-04-06 15:30 | 518 | 517
2018-04-06 16:00 | 500 | 500
2018-04-06 16:30 | 550 | 549
2018-04-06 17:00 | 565 | 565
2018-04-06 17:30 | 574 | 574
2018-04-06 18:00 | 576 | 576
2018-04-06 18:30 | 595 | 595
2018-04-06 19:00 | 612 | 612
2018-04-06 19:30 | 605 | 605
2018-04-06 20:00 | 581 | 581
2018-04-06 20:30 | 565 | 565
2018-04-06 21:00 | 545 | 545
2018-04-06 21:30 | 534 | 534
2018-04-06 22:00 | 521 | 521
2018-04-06 22:30 | 491 | 491
2018-04-06 23:00 | 477 | 476
2018-04-06 23:30 | 454 | 453
2018-04-07 | 436 | 434
2018-04-07 00:30 | 428 | 425
2018-04-07 01:00 | 415 | 412
2018-04-07 01:30 | 401 | 399
2018-04-07 02:00 | 394 | 391
2018-04-07 02:30 | 388 | 386
2018-04-07 03:00 | 384 | 381
2018-04-07 03:30 | 382 | 379
2018-04-07 04:00 | 382 | 379
2018-04-07 04:30 | 403 | 399
2018-04-07 05:00 | 404 | 401
2018-04-07 05:30 | 411 | 409
2018-04-07 06:00 | 417 | 415
2018-04-07 06:30 | 425 | 423
2018-04-07 07:00 | 437 | 435
2018-04-07 07:30 | 453 | 451
2018-04-07 08:00 | 451 | 449
2018-04-07 08:30 | 458 | 457
2018-04-07 09:00 | 458 | 457
2018-04-07 09:30 | 442 | 441
2018-04-07 10:00 | 439 | 438
2018-04-07 10:30 | 413 | 411
2018-04-07 11:00 | 422 | 420
2018-04-07 11:30 | 412 | 410
2018-04-07 12:00 | 416 | 413
2018-04-07 12:30 | 422 | 419
2018-04-07 13:00 | 430 | 428
2018-04-07 13:30 | 440 | 439
2018-04-07 14:00 | 434 | 432
2018-04-07 14:30 | 443 | 442
2018-04-07 15:00 | 455 | 454
2018-04-07 15:30 | 471 | 469
2018-04-07 16:00 | 480 | 479
2018-04-07 16:30 | 489 | 488
2018-04-07 17:00 | 511 | 510
2018-04-07 17:30 | 533 | 532
2018-04-07 18:00 | 560 | 559
2018-04-07 18:30 | 592 | 591
2018-04-07 19:00 | 603 | 603
2018-04-07 19:30 | 589 | 589
2018-04-07 20:00 | 573 | 573
2018-04-07 20:30 | 554 | 553
2018-04-07 21:00 | 537 | 536
2018-04-07 21:30 | 523 | 522
2018-04-07 22:00 | 507 | 506
2018-04-07 22:30 | 486 | 485
2018-04-07 23:00 | 470 | 468
2018-04-07 23:30 | 457 | 454
2018-04-08 | 446 | 443
2018-04-08 00:30 | 431 | 427
2018-04-08 01:00 | 415 | 411
2018-04-08 01:30 | 401 | 396
2018-04-08 02:00 | 391 | 386
2018-04-08 02:30 | 386 | 379
2018-04-08 03:00 | 381 | 374
2018-04-08 03:30 | 381 | 374
2018-04-08 04:00 | 386 | 379
2018-04-08 04:30 | 384 | 378
2018-04-08 05:00 | 384 | 377
2018-04-08 05:30 | 387 | 380
2018-04-08 06:00 | 389 | 382
2018-04-08 06:30 | 394 | 387
2018-04-08 07:00 | 400 | 394
2018-04-08 07:30 | 398 | 392
2018-04-08 08:00 | 400 | 394
2018-04-08 08:30 | 416 | 410
2018-04-08 09:00 | 411 | 406
2018-04-08 09:30 | 421 | 416
2018-04-08 10:00 | 417 | 412
2018-04-08 10:30 | 419 | 414
2018-04-08 11:00 | 412 | 406
2018-04-08 11:30 | 412 | 407
2018-04-08 12:00 | 425 | 420
2018-04-08 12:30 | 412 | 407
2018-04-08 13:00 | 419 | 413
2018-04-08 13:30 | 429 | 424
2018-04-08 14:00 | 445 | 440
2018-04-08 14:30 | 463 | 459
2018-04-08 15:00 | 471 | 468
2018-04-08 15:30 | 493 | 490
2018-04-08 16:00 | 499 | 497
2018-04-08 16:30 | 503 | 501
2018-04-08 17:00 | 544 | 543
2018-04-08 17:30 | 564 | 563
2018-04-08 18:00 | 597 | 596
2018-04-08 18:30 | 627 | 626
2018-04-08 19:00 | 647 | 646
2018-04-08 19:30 | 634 | 633
2018-04-08 20:00 | 605 | 605
2018-04-08 20:30 | 589 | 589
2018-04-08 21:00 | 571 | 570
2018-04-08 21:30 | 552 | 552
2018-04-08 22:00 | 527 | 526
2018-04-08 22:30 | 521 | 520
2018-04-08 23:00 | 504 | 503
2018-04-08 23:30 | 486 | 484
2018-04-09 | 470 | 468
2018-04-09 00:30 | 456 | 453
2018-04-09 01:00 | 447 | 444
2018-04-09 01:30 | 436 | 432
2018-04-09 02:00 | 433 | 429
2018-04-09 02:30 | 432 | 428
2018-04-09 03:00 | 427 | 423
2018-04-09 03:30 | 423 | 419
2018-04-09 04:00 | 420 | 416
2018-04-09 04:30 | 421 | 416
2018-04-09 05:00 | 429 | 425
2018-04-09 05:30 | 440 | 436
2018-04-09 06:00 | 453 | 450
2018-04-09 06:30 | 484 | 481
2018-04-09 07:00 | 512 | 509
2018-04-09 07:30 | 542 | 540
2018-04-09 08:00 | 555 | 553
2018-04-09 08:30 | 553 | 552
2018-04-09 09:00 | 543 | 541
2018-04-09 09:30 | 518 | 517
2018-04-09 10:00 | 493 | 491
2018-04-09 10:30 | 487 | 484
2018-04-09 11:00 | 489 | 486
2018-04-09 11:30 | 488 | 486
2018-04-09 12:00 | 490 | 487
2018-04-09 12:30 | 489 | 487
2018-04-09 13:00 | 499 | 496
2018-04-09 13:30 | 499 | 497
2018-04-09 14:00 | 520 | 518
2018-04-09 14:30 | 531 | 529
2018-04-09 15:00 | 535 | 533
2018-04-09 15:30 | 546 | 544
2018-04-09 16:00 | 555 | 554
2018-04-09 16:30 | 570 | 569
2018-04-09 17:00 | 576 | 575
2018-04-09 17:30 | 582 | 581
2018-04-09 18:00 | 609 | 608
2018-04-09 18:30 | 633 | 633
2018-04-09 19:00 | 657 | 657
2018-04-09 19:30 | 637 | 636
2018-04-09 20:00 | 612 | 611
2018-04-09 20:30 | 595 | 594
2018-04-09 21:00 | 580 | 579
2018-04-09 21:30 | 557 | 557
2018-04-09 22:00 | 537 | 536
2018-04-09 22:30 | 524 | 523
2018-04-09 23:00 | 508 | 506
2018-04-09 23:30 | 486 | 483
2018-04-10 | 468 | 464
2018-04-10 00:30 | 453 | 449
2018-04-10 01:00 | 444 | 440
2018-04-10 01:30 | 434 | 430
2018-04-10 02:00 | 427 | 422
2018-04-10 02:30 | 419 | 414
2018-04-10 03:00 | 412 | 408
2018-04-10 03:30 | 407 | 402
2018-04-10 04:00 | 409 | 404
2018-04-10 04:30 | 411 | 406
2018-04-10 05:00 | 414 | 409
2018-04-10 05:30 | 425 | 420
2018-04-10 06:00 | 440 | 435
2018-04-10 06:30 | 466 | 462
2018-04-10 07:00 | 483 | 480
2018-04-10 07:30 | 498 | 495
2018-04-10 08:00 | 495 | 492
2018-04-10 08:30 | 488 | 486
2018-04-10 09:00 | 484 | 481
2018-04-10 09:30 | 495 | 492
2018-04-10 10:00 | 502 | 499
2018-04-10 10:30 | 496 | 494
2018-04-10 11:00 | 500 | 498
2018-04-10 11:30 | 499 | 497
2018-04-10 12:00 | 499 | 497
2018-04-10 12:30 | 497 | 495
2018-04-10 13:00 | 501 | 499
2018-04-10 13:30 | 512 | 510
2018-04-10 14:00 | 529 | 527
2018-04-10 14:30 | 535 | 534
2018-04-10 15:00 | 526 | 525
2018-04-10 15:30 | 532 | 531
2018-04-10 16:00 | 547 | 546
2018-04-10 16:30 | 561 | 560
2018-04-10 17:00 | 582 | 581
2018-04-10 17:30 | 589 | 589
2018-04-10 18:00 | 599 | 599
2018-04-10 18:30 | 614 | 613
2018-04-10 19:00 | 639 | 639
2018-04-10 19:30 | 623 | 623
2018-04-10 20:00 | 595 | 595
2018-04-10 20:30 | 581 | 581
2018-04-10 21:00 | 561 | 560
2018-04-10 21:30 | 536 | 535
2018-04-10 22:00 | 514 | 513
2018-04-10 22:30 | 508 | 506
2018-04-10 23:00 | 496 | 494
2018-04-10 23:30 | 471 | 468
2018-04-11 | 450 | 447
2018-04-11 00:30 | 437 | 433
2018-04-11 01:00 | 414 | 411
2018-04-11 01:30 | 413 | 408
2018-04-11 02:00 | 405 | 400
2018-04-11 02:30 | 405 | 399
2018-04-11 03:00 | 394 | 388
2018-04-11 03:30 | 388 | 382
2018-04-11 04:00 | 391 | 385
2018-04-11 04:30 | 395 | 389
2018-04-11 05:00 | 401 | 395
2018-04-11 05:30 | 412 | 406
2018-04-11 06:00 | 425 | 420
2018-04-11 06:30 | 449 | 445
2018-04-11 07:00 | 467 | 463
2018-04-11 07:30 | 491 | 488
2018-04-11 08:00 | 471 | 468
2018-04-11 08:30 | 431 | 429
2018-04-11 09:00 | 428 | 424
2018-04-11 09:30 | 421 | 418
2018-04-11 10:00 | 423 | 419
2018-04-11 10:30 | 403 | 399
2018-04-11 11:00 | 392 | 388
2018-04-11 11:30 | 352 | 347
2018-04-11 12:00 | 326 | 319
2018-04-11 12:30 | 339 | 331
2018-04-11 13:00 | 340 | 333
2018-04-11 13:30 | 337 | 329
2018-04-11 14:00 | 339 | 332
2018-04-11 14:30 | 348 | 341
2018-04-11 15:00 | 337 | 331
2018-04-11 15:30 | 354 | 347
2018-04-11 16:00 | 362 | 355
2018-04-11 16:30 | 312 | 304
2018-04-11 17:00 | 301 | 292
2018-04-11 17:30 | 317 | 308
2018-04-11 18:00 | 339 | 331
2018-04-11 18:30 | 359 | 352
2018-04-11 19:00 | 380 | 374
2018-04-11 19:30 | 370 | 365
2018-04-11 20:00 | 348 | 342
2018-04-11 20:30 | 332 | 325
2018-04-11 21:00 | 317 | 308
2018-04-11 21:30 | 305 | 295
2018-04-11 22:00 | 357 | 348
2018-04-11 22:30 | 368 | 361
2018-04-11 23:00 | 347 | 341
2018-04-11 23:30 | 327 | 319
2018-04-12 | 311 | 301
2018-04-12 00:30 | 296 | 286
2018-04-12 01:00 | 286 | 275
2018-04-12 01:30 | 280 | 267
2018-04-12 02:00 | 275 | 261
2018-04-12 02:30 | 272 | 259
2018-04-12 03:00 | 269 | 255
2018-04-12 03:30 | 273 | 258
2018-04-12 04:00 | 274 | 259
2018-04-12 04:30 | 278 | 264
2018-04-12 05:00 | 282 | 268
2018-04-12 05:30 | 295 | 282
2018-04-12 06:00 | 311 | 300
2018-04-12 06:30 | 331 | 321
2018-04-12 07:00 | 353 | 345
2018-04-12 07:30 | 364 | 356
2018-04-12 08:00 | 352 | 345
2018-04-12 08:30 | 375 | 368
2018-04-12 09:00 | 380 | 374
2018-04-12 09:30 | 365 | 359
2018-04-12 10:00 | 355 | 348
2018-04-12 10:30 | 363 | 355
2018-04-12 11:00 | 368 | 360
2018-04-12 11:30 | 354 | 347
2018-04-12 12:00 | 343 | 335
2018-04-12 12:30 | 357 | 348
2018-04-12 13:00 | 354 | 345
2018-04-12 13:30 | 349 | 341
2018-04-12 14:00 | 358 | 349
2018-04-12 14:30 | 352 | 344
2018-04-12 15:00 | 351 | 342
2018-04-12 15:30 | 328 | 319
2018-04-12 16:00 | 376 | 367
2018-04-12 16:30 | 315 | 307
2018-04-12 17:00 | 332 | 322
2018-04-12 17:30 | 359 | 350
2018-04-12 18:00 | 382 | 375
2018-04-12 18:30 | 402 | 396
2018-04-12 19:00 | 425 | 420
2018-04-12 19:30 | 406 | 401
2018-04-12 20:00 | 404 | 399
2018-04-12 20:30 | 393 | 388
2018-04-12 21:00 | 379 | 373
2018-04-12 21:30 | 361 | 354
2018-04-12 22:00 | 402 | 395
2018-04-12 22:30 | 387 | 381
2018-04-12 23:00 | 370 | 364
2018-04-12 23:30 | 402 | 395
2018-04-13 | 463 | 458
2018-04-13 00:30 | 447 | 444
2018-04-13 01:00 | 423 | 419
2018-04-13 01:30 | 390 | 386
2018-04-13 02:00 | 385 | 380
2018-04-13 02:30 | 377 | 371
2018-04-13 03:00 | 375 | 368
2018-04-13 03:30 | 374 | 368
2018-04-13 04:00 | 367 | 360
2018-04-13 04:30 | 353 | 345
2018-04-13 05:00 | 353 | 345
2018-04-13 05:30 | 365 | 357
2018-04-13 06:00 | 372 | 365
2018-04-13 06:30 | 399 | 393
2018-04-13 07:00 | 422 | 417
2018-04-13 07:30 | 449 | 445
2018-04-13 08:00 | 472 | 469
2018-04-13 08:30 | 502 | 499
2018-04-13 09:00 | 496 | 494
2018-04-13 09:30 | 500 | 498
2018-04-13 10:00 | 500 | 498
2018-04-13 10:30 | 491 | 489
2018-04-13 11:00 | 485 | 482
2018-04-13 11:30 | 472 | 469
2018-04-13 12:00 | 483 | 480
2018-04-13 12:30 | 479 | 476
2018-04-13 13:00 | 490 | 487
2018-04-13 13:30 | 484 | 482
2018-04-13 14:00 | 498 | 496
2018-04-13 14:30 | 512 | 510
2018-04-13 15:00 | 525 | 523
2018-04-13 15:30 | 469 | 467
2018-04-13 16:00 | 402 | 399
2018-04-13 16:30 | 403 | 398
2018-04-13 17:00 | 420 | 415
2018-04-13 17:30 | 439 | 435
2018-04-13 18:00 | 455 | 452
2018-04-13 18:30 | 473 | 470
2018-04-13 19:00 | 484 | 482
2018-04-13 19:30 | 475 | 473
2018-04-13 20:00 | 458 | 455
2018-04-13 20:30 | 438 | 436
2018-04-13 21:00 | 426 | 423
2018-04-13 21:30 | 407 | 403
2018-04-13 22:00 | 388 | 383
2018-04-13 22:30 | 369 | 363
2018-04-13 23:00 | 407 | 401
2018-04-13 23:30 | 463 | 459
2018-04-14 | 454 | 451
2018-04-14 00:30 | 442 | 439
2018-04-14 01:00 | 433 | 429
2018-04-14 01:30 | 424 | 420
2018-04-14 02:00 | 418 | 414
2018-04-14 02:30 | 411 | 406
2018-04-14 03:00 | 406 | 400
2018-04-14 03:30 | 403 | 397
2018-04-14 04:00 | 401 | 395
2018-04-14 04:30 | 404 | 398
2018-04-14 05:00 | 402 | 396
2018-04-14 05:30 | 409 | 404
2018-04-14 06:00 | 413 | 408
2018-04-14 06:30 | 429 | 424
2018-04-14 07:00 | 437 | 433
2018-04-14 07:30 | 452 | 448
2018-04-14 08:00 | 454 | 451
2018-04-14 08:30 | 467 | 463
2018-04-14 09:00 | 469 | 466
2018-04-14 09:30 | 465 | 462
2018-04-14 10:00 | 456 | 453
2018-04-14 10:30 | 468 | 465
2018-04-14 11:00 | 466 | 463
2018-04-14 11:30 | 461 | 458
2018-04-14 12:00 | 457 | 454
2018-04-14 12:30 | 464 | 462
2018-04-14 13:00 | 456 | 453
2018-04-14 13:30 | 451 | 449
2018-04-14 14:00 | 460 | 457
2018-04-14 14:30 | 447 | 444
2018-04-14 15:00 | 433 | 429
2018-04-14 15:30 | 439 | 436
2018-04-14 16:00 | 455 | 451
2018-04-14 16:30 | 471 | 468
2018-04-14 17:00 | 488 | 486
2018-04-14 17:30 | 522 | 520
2018-04-14 18:00 | 546 | 545
2018-04-14 18:30 | 565 | 564
2018-04-14 19:00 | 579 | 578
2018-04-14 19:30 | 562 | 561
2018-04-14 20:00 | 540 | 539
2018-04-14 20:30 | 521 | 520
2018-04-14 21:00 | 513 | 511
2018-04-14 21:30 | 497 | 495
2018-04-14 22:00 | 474 | 471
2018-04-14 22:30 | 455 | 452
2018-04-14 23:00 | 445 | 441
2018-04-14 23:30 | 430 | 426
2018-04-15 | 437 | 433
2018-04-15 00:30 | 453 | 449
2018-04-15 01:00 | 447 | 444
2018-04-15 01:30 | 441 | 437
2018-04-15 02:00 | 437 | 433
2018-04-15 02:30 | 427 | 423
2018-04-15 03:00 | 423 | 418
2018-04-15 03:30 | 414 | 409
2018-04-15 04:00 | 416 | 410
2018-04-15 04:30 | 416 | 411
2018-04-15 05:00 | 415 | 410
2018-04-15 05:30 | 421 | 415
2018-04-15 06:00 | 423 | 418
2018-04-15 06:30 | 434 | 429
2018-04-15 07:00 | 434 | 430
2018-04-15 07:30 | 417 | 413
2018-04-15 08:00 | 397 | 392
2018-04-15 08:30 | 394 | 388
2018-04-15 09:00 | 388 | 382
2018-04-15 09:30 | 389 | 383
2018-04-15 10:00 | 389 | 383
2018-04-15 10:30 | 391 | 385
2018-04-15 11:00 | 397 | 392
2018-04-15 11:30 | 396 | 390
2018-04-15 12:00 | 406 | 401
2018-04-15 12:30 | 412 | 407
2018-04-15 13:00 | 421 | 416
2018-04-15 13:30 | 425 | 420
2018-04-15 14:00 | 429 | 425
2018-04-15 14:30 | 452 | 449
2018-04-15 15:00 | 460 | 458
2018-04-15 15:30 | 476 | 474
2018-04-15 16:00 | 489 | 487
2018-04-15 16:30 | 504 | 502
2018-04-15 17:00 | 527 | 525
2018-04-15 17:30 | 560 | 559
2018-04-15 18:00 | 594 | 594
2018-04-15 18:30 | 629 | 629
2018-04-15 19:00 | 649 | 649
2018-04-15 19:30 | 636 | 636
2018-04-15 20:00 | 614 | 614
2018-04-15 20:30 | 591 | 590
2018-04-15 21:00 | 574 | 573
2018-04-15 21:30 | 555 | 554
2018-04-15 22:00 | 535 | 533
2018-04-15 22:30 | 505 | 503
2018-04-15 23:00 | 486 | 483
2018-04-15 23:30 | 467 | 464
2018-04-16 | 456 | 452
2018-04-16 00:30 | 440 | 436
2018-04-16 01:00 | 433 | 429
2018-04-16 01:30 | 419 | 414
2018-04-16 02:00 | 416 | 411
2018-04-16 02:30 | 413 | 408
2018-04-16 03:00 | 403 | 398
2018-04-16 03:30 | 409 | 403
2018-04-16 04:00 | 406 | 400
2018-04-16 04:30 | 378 | 372
2018-04-16 05:00 | 341 | 333
2018-04-16 05:30 | 351 | 341
2018-04-16 06:00 | 370 | 361
2018-04-16 06:30 | 400 | 393
2018-04-16 07:00 | 432 | 426
2018-04-16 07:30 | 432 | 427
2018-04-16 08:00 | 387 | 381
2018-04-16 08:30 | 399 | 393
2018-04-16 09:00 | 414 | 408
2018-04-16 09:30 | 402 | 396
2018-04-16 10:00 | 388 | 382
2018-04-16 10:30 | 324 | 316
2018-04-16 11:00 | 310 | 299
2018-04-16 11:30 | 317 | 306
2018-04-16 12:00 | 310 | 299
2018-04-16 12:30 | 310 | 298
2018-04-16 13:00 | 307 | 295
2018-04-16 13:30 | 312 | 298
2018-04-16 14:00 | 319 | 306
2018-04-16 14:30 | 323 | 311
2018-04-16 15:00 | 339 | 327
2018-04-16 15:30 | 359 | 349
2018-04-16 16:00 | 369 | 360
2018-04-16 16:30 | 394 | 387
2018-04-16 17:00 | 389 | 383
2018-04-16 17:30 | 403 | 396
2018-04-16 18:00 | 427 | 422
2018-04-16 18:30 | 451 | 447
2018-04-16 19:00 | 464 | 460
2018-04-16 19:30 | 448 | 445
2018-04-16 20:00 | 424 | 420
2018-04-16 20:30 | 407 | 402
2018-04-16 21:00 | 377 | 371
2018-04-16 21:30 | 421 | 414
2018-04-16 22:00 | 413 | 407
2018-04-16 22:30 | 389 | 382
2018-04-16 23:00 | 364 | 356
2018-04-16 23:30 | 340 | 330
2018-04-17 | 376 | 366
2018-04-17 00:30 | 443 | 436
2018-04-17 01:00 | 432 | 427
2018-04-17 01:30 | 427 | 421
2018-04-17 02:00 | 420 | 415
2018-04-17 02:30 | 417 | 411
2018-04-17 03:00 | 411 | 405
2018-04-17 03:30 | 408 | 401
2018-04-17 04:00 | 404 | 397
2018-04-17 04:30 | 412 | 404
2018-04-17 05:00 | 416 | 409
2018-04-17 05:30 | 428 | 421
2018-04-17 06:00 | 446 | 440
2018-04-17 06:30 | 478 | 473
2018-04-17 07:00 | 508 | 504
2018-04-17 07:30 | 528 | 525
2018-04-17 08:00 | 537 | 534
2018-04-17 08:30 | 527 | 525
2018-04-17 09:00 | 519 | 517
2018-04-17 09:30 | 517 | 514
2018-04-17 10:00 | 519 | 517
2018-04-17 10:30 | 506 | 504
2018-04-17 11:00 | 506 | 503
2018-04-17 11:30 | 499 | 497
2018-04-17 12:00 | 507 | 504
2018-04-17 12:30 | 513 | 510
2018-04-17 13:00 | 510 | 507
2018-04-17 13:30 | 506 | 504
2018-04-17 14:00 | 418 | 416
2018-04-17 14:30 | 381 | 376
2018-04-17 15:00 | 400 | 394
2018-04-17 15:30 | 411 | 406
2018-04-17 16:00 | 433 | 428
2018-04-17 16:30 | 463 | 459
2018-04-17 17:00 | 465 | 462
2018-04-17 17:30 | 486 | 484
2018-04-17 18:00 | 507 | 505
2018-04-17 18:30 | 540 | 539
2018-04-17 19:00 | 560 | 558
2018-04-17 19:30 | 541 | 540
2018-04-17 20:00 | 520 | 519
2018-04-17 20:30 | 492 | 491
2018-04-17 21:00 | 462 | 460
2018-04-17 21:30 | 440 | 437
2018-04-17 22:00 | 420 | 416
2018-04-17 22:30 | 388 | 383
2018-04-17 23:00 | 421 | 416
2018-04-17 23:30 | 477 | 472
2018-04-18 | 465 | 461
2018-04-18 00:30 | 451 | 447
2018-04-18 01:00 | 442 | 438
2018-04-18 01:30 | 435 | 430
2018-04-18 02:00 | 428 | 423
2018-04-18 02:30 | 420 | 415
2018-04-18 03:00 | 415 | 409
2018-04-18 03:30 | 414 | 408
2018-04-18 04:00 | 413 | 407
2018-04-18 04:30 | 417 | 411
2018-04-18 05:00 | 420 | 415
2018-04-18 05:30 | 429 | 424
2018-04-18 06:00 | 441 | 436
2018-04-18 06:30 | 470 | 466
2018-04-18 07:00 | 499 | 495
2018-04-18 07:30 | 533 | 530
2018-04-18 08:00 | 539 | 538
2018-04-18 08:30 | 537 | 536
2018-04-18 09:00 | 531 | 530
2018-04-18 09:30 | 513 | 512
2018-04-18 10:00 | 507 | 505
2018-04-18 10:30 | 504 | 502
2018-04-18 11:00 | 486 | 484
2018-04-18 11:30 | 477 | 475
2018-04-18 12:00 | 474 | 472
2018-04-18 12:30 | 479 | 477
2018-04-18 13:00 | 489 | 486
2018-04-18 13:30 | 493 | 491
2018-04-18 14:00 | 492 | 489
2018-04-18 14:30 | 501 | 499
2018-04-18 15:00 | 511 | 509
2018-04-18 15:30 | 525 | 523
2018-04-18 16:00 | 544 | 542
2018-04-18 16:30 | 477 | 476
2018-04-18 17:00 | 448 | 446
2018-04-18 17:30 | 455 | 452
2018-04-18 18:00 | 478 | 476
2018-04-18 18:30 | 506 | 504
2018-04-18 19:00 | 527 | 525
2018-04-18 19:30 | 507 | 506
2018-04-18 20:00 | 486 | 485
2018-04-18 20:30 | 458 | 456
2018-04-18 21:00 | 440 | 437
2018-04-18 21:30 | 419 | 416
2018-04-18 22:00 | 394 | 389
2018-04-18 22:30 | 366 | 361
2018-04-18 23:00 | 400 | 393
2018-04-18 23:30 | 455 | 451
2018-04-19 | 443 | 440
2018-04-19 00:30 | 430 | 426
2018-04-19 01:00 | 418 | 413
2018-04-19 01:30 | 410 | 405
2018-04-19 02:00 | 404 | 398
2018-04-19 02:30 | 398 | 392
2018-04-19 03:00 | 396 | 390
2018-04-19 03:30 | 392 | 386
2018-04-19 04:00 | 395 | 388
2018-04-19 04:30 | 396 | 389
2018-04-19 05:00 | 393 | 386
2018-04-19 05:30 | 408 | 402
2018-04-19 06:00 | 420 | 414
2018-04-19 06:30 | 455 | 450
2018-04-19 07:00 | 481 | 477
2018-04-19 07:30 | 505 | 502
2018-04-19 08:00 | 499 | 496
2018-04-19 08:30 | 493 | 490
2018-04-19 09:00 | 510 | 507
2018-04-19 09:30 | 494 | 492
2018-04-19 10:00 | 471 | 469
2018-04-19 10:30 | 473 | 469
2018-04-19 11:00 | 463 | 459
2018-04-19 11:30 | 466 | 462
2018-04-19 12:00 | 470 | 466
2018-04-19 12:30 | 476 | 473
2018-04-19 13:00 | 477 | 475
2018-04-19 13:30 | 484 | 481
2018-04-19 14:00 | 434 | 431
2018-04-19 14:30 | 363 | 357
2018-04-19 15:00 | 366 | 363
2018-04-19 15:30 | 381 | 370
2018-04-19 16:00 | 393 | 385
2018-04-19 16:30 | 408 | 403
2018-04-19 17:00 | 427 | 423
2018-04-19 17:30 | 426 | 423
2018-04-19 18:00 | 454 | 451
2018-04-19 18:30 | 488 | 486
2018-04-19 19:00 | 511 | 509
2018-04-19 19:30 | 493 | 492
2018-04-19 20:00 | 473 | 472
2018-04-19 20:30 | 448 | 446
2018-04-19 21:00 | 429 | 427
2018-04-19 21:30 | 407 | 404
2018-04-19 22:00 | 379 | 375
2018-04-19 22:30 | 366 | 360
2018-04-19 23:00 | 415 | 410
2018-04-19 23:30 | 473 | 469
2018-04-20 | 467 | 464
2018-04-20 00:30 | 451 | 449
2018-04-20 01:00 | 440 | 437
2018-04-20 01:30 | 430 | 426
2018-04-20 02:00 | 425 | 422
2018-04-20 02:30 | 426 | 422
2018-04-20 03:00 | 422 | 418
2018-04-20 03:30 | 422 | 418
2018-04-20 04:00 | 418 | 414
2018-04-20 04:30 | 430 | 426
2018-04-20 05:00 | 434 | 430
2018-04-20 05:30 | 452 | 448
2018-04-20 06:00 | 468 | 465
2018-04-20 06:30 | 496 | 493
2018-04-20 07:00 | 522 | 521
2018-04-20 07:30 | 533 | 532
2018-04-20 08:00 | 519 | 518
2018-04-20 08:30 | 510 | 509
2018-04-20 09:00 | 497 | 496
2018-04-20 09:30 | 487 | 486
2018-04-20 10:00 | 478 | 477
2018-04-20 10:30 | 473 | 471
2018-04-20 11:00 | 472 | 470
2018-04-20 11:30 | 472 | 470
2018-04-20 12:00 | 481 | 479
2018-04-20 12:30 | 486 | 484
2018-04-20 13:00 | 488 | 487
2018-04-20 13:30 | 495 | 494
2018-04-20 14:00 | 498 | 497
2018-04-20 14:30 | 436 | 435
2018-04-20 15:00 | 381 | 378
2018-04-20 15:30 | 392 | 387
2018-04-20 16:00 | 396 | 392
2018-04-20 16:30 | 398 | 393
2018-04-20 17:00 | 417 | 413
2018-04-20 17:30 | 438 | 435
2018-04-20 18:00 | 458 | 456
2018-04-20 18:30 | 482 | 480
2018-04-20 19:00 | 500 | 498
2018-04-20 19:30 | 488 | 487
2018-04-20 20:00 | 469 | 468
2018-04-20 20:30 | 450 | 448
2018-04-20 21:00 | 429 | 427
2018-04-20 21:30 | 411 | 407
2018-04-20 22:00 | 385 | 381
2018-04-20 22:30 | 363 | 358
2018-04-20 23:00 | 408 | 403
2018-04-20 23:30 | 458 | 455
2018-04-21 | 449 | 447
2018-04-21 00:30 | 437 | 435
2018-04-21 01:00 | 428 | 425
2018-04-21 01:30 | 418 | 415
2018-04-21 02:00 | 412 | 409
2018-04-21 02:30 | 410 | 406
2018-04-21 03:00 | 402 | 398
2018-04-21 03:30 | 400 | 396
2018-04-21 04:00 | 394 | 389
2018-04-21 04:30 | 398 | 393
2018-04-21 05:00 | 399 | 395
2018-04-21 05:30 | 404 | 399
2018-04-21 06:00 | 413 | 409
2018-04-21 06:30 | 422 | 418
2018-04-21 07:00 | 428 | 425
2018-04-21 07:30 | 432 | 428
2018-04-21 08:00 | 440 | 437
2018-04-21 08:30 | 430 | 427
2018-04-21 09:00 | 428 | 425
2018-04-21 09:30 | 410 | 407
2018-04-21 10:00 | 399 | 396
2018-04-21 10:30 | 397 | 394
2018-04-21 11:00 | 388 | 384
2018-04-21 11:30 | 388 | 384
2018-04-21 12:00 | 390 | 387
2018-04-21 12:30 | 390 | 387
2018-04-21 13:00 | 389 | 386
2018-04-21 13:30 | 396 | 393
2018-04-21 14:00 | 406 | 403
2018-04-21 14:30 | 413 | 410
2018-04-21 15:00 | 431 | 429
2018-04-21 15:30 | 445 | 443
2018-04-21 16:00 | 469 | 467
2018-04-21 16:30 | 487 | 486
2018-04-21 17:00 | 509 | 509
2018-04-21 17:30 | 546 | 545
2018-04-21 18:00 | 573 | 573
2018-04-21 18:30 | 601 | 601
2018-04-21 19:00 | 610 | 610
2018-04-21 19:30 | 594 | 594
2018-04-21 20:00 | 575 | 575
2018-04-21 20:30 | 557 | 557
2018-04-21 21:00 | 538 | 538
2018-04-21 21:30 | 519 | 519
2018-04-21 22:00 | 499 | 499
2018-04-21 22:30 | 508 | 507
2018-04-21 23:00 | 496 | 495
2018-04-21 23:30 | 477 | 476
2018-04-22 | 462 | 461
2018-04-22 00:30 | 451 | 449
2018-04-22 01:00 | 437 | 435
2018-04-22 01:30 | 428 | 425
2018-04-22 02:00 | 420 | 417
2018-04-22 02:30 | 414 | 411
2018-04-22 03:00 | 410 | 407
2018-04-22 03:30 | 409 | 406
2018-04-22 04:00 | 409 | 406
2018-04-22 04:30 | 402 | 398
2018-04-22 05:00 | 405 | 402
2018-04-22 05:30 | 412 | 409
2018-04-22 06:00 | 416 | 413
2018-04-22 06:30 | 426 | 424
2018-04-22 07:00 | 424 | 421
2018-04-22 07:30 | 417 | 414
2018-04-22 08:00 | 390 | 387
2018-04-22 08:30 | 379 | 376
2018-04-22 09:00 | 380 | 376
2018-04-22 09:30 | 384 | 380
2018-04-22 10:00 | 379 | 374
2018-04-22 10:30 | 377 | 373
2018-04-22 11:00 | 380 | 376
2018-04-22 11:30 | 383 | 379
2018-04-22 12:00 | 377 | 373
2018-04-22 12:30 | 376 | 372
2018-04-22 13:00 | 381 | 377
2018-04-22 13:30 | 384 | 380
2018-04-22 14:00 | 399 | 395
2018-04-22 14:30 | 402 | 399
2018-04-22 15:00 | 422 | 419
2018-04-22 15:30 | 451 | 449
2018-04-22 16:00 | 459 | 457
2018-04-22 16:30 | 471 | 470
2018-04-22 17:00 | 511 | 511
2018-04-22 17:30 | 551 | 551
2018-04-22 18:00 | 590 | 590
2018-04-22 18:30 | 622 | 622
2018-04-22 19:00 | 635 | 635
2018-04-22 19:30 | 617 | 617
2018-04-22 20:00 | 589 | 589
2018-04-22 20:30 | 567 | 567
2018-04-22 21:00 | 545 | 545
2018-04-22 21:30 | 529 | 528
2018-04-22 22:00 | 505 | 504
2018-04-22 22:30 | 479 | 478
2018-04-22 23:00 | 454 | 453
2018-04-22 23:30 | 435 | 433
2018-04-23 | 423 | 421
2018-04-23 00:30 | 437 | 435
2018-04-23 01:00 | 435 | 433
2018-04-23 01:30 | 424 | 421
2018-04-23 02:00 | 424 | 422
2018-04-23 02:30 | 414 | 411
2018-04-23 03:00 | 413 | 410
2018-04-23 03:30 | 416 | 413
2018-04-23 04:00 | 414 | 411
2018-04-23 04:30 | 419 | 416
2018-04-23 05:00 | 424 | 421
2018-04-23 05:30 | 438 | 435
2018-04-23 06:00 | 456 | 454
2018-04-23 06:30 | 488 | 486
2018-04-23 07:00 | 518 | 517
2018-04-23 07:30 | 555 | 554
2018-04-23 08:00 | 527 | 527
2018-04-23 08:30 | 503 | 503
2018-04-23 09:00 | 493 | 492
2018-04-23 09:30 | 487 | 486
2018-04-23 10:00 | 481 | 480
2018-04-23 10:30 | 477 | 476
2018-04-23 11:00 | 477 | 476
2018-04-23 11:30 | 479 | 478
2018-04-23 12:00 | 490 | 489
2018-04-23 12:30 | 488 | 486
2018-04-23 13:00 | 491 | 489
2018-04-23 13:30 | 504 | 502
2018-04-23 14:00 | 501 | 500
2018-04-23 14:30 | 511 | 510
2018-04-23 15:00 | 514 | 513
2018-04-23 15:30 | 514 | 514
2018-04-23 16:00 | 540 | 539
2018-04-23 16:30 | 545 | 545
2018-04-23 17:00 | 580 | 580
2018-04-23 17:30 | 601 | 601
2018-04-23 18:00 | 629 | 629
2018-04-23 18:30 | 664 | 664
2018-04-23 19:00 | 679 | 679
2018-04-23 19:30 | 656 | 656
2018-04-23 20:00 | 640 | 640
2018-04-23 20:30 | 608 | 608
2018-04-23 21:00 | 585 | 585
2018-04-23 21:30 | 573 | 573
2018-04-23 22:00 | 555 | 555
2018-04-23 22:30 | 545 | 545
2018-04-23 23:00 | 521 | 521
2018-04-23 23:30 | 499 | 498
2018-04-24 | 483 | 482
2018-04-24 00:30 | 470 | 469
2018-04-24 01:00 | 461 | 459
2018-04-24 01:30 | 448 | 446
2018-04-24 02:00 | 437 | 434
2018-04-24 02:30 | 438 | 435
2018-04-24 03:00 | 440 | 437
2018-04-24 03:30 | 432 | 429
2018-04-24 04:00 | 434 | 431
2018-04-24 04:30 | 442 | 439
2018-04-24 05:00 | 447 | 444
2018-04-24 05:30 | 460 | 457
2018-04-24 06:00 | 475 | 473
2018-04-24 06:30 | 505 | 503
2018-04-24 07:00 | 512 | 511
2018-04-24 07:30 | 541 | 539
2018-04-24 08:00 | 539 | 538
2018-04-24 08:30 | 529 | 528
2018-04-24 09:00 | 509 | 508
2018-04-24 09:30 | 491 | 490
2018-04-24 10:00 | 478 | 476
2018-04-24 10:30 | 470 | 467
2018-04-24 11:00 | 461 | 458
2018-04-24 11:30 | 462 | 459
2018-04-24 12:00 | 475 | 472
2018-04-24 12:30 | 473 | 470
2018-04-24 13:00 | 469 | 466
2018-04-24 13:30 | 464 | 462
2018-04-24 14:00 | 473 | 471
2018-04-24 14:30 | 493 | 491
2018-04-24 15:00 | 496 | 495
2018-04-24 15:30 | 503 | 502
2018-04-24 16:00 | 514 | 514
2018-04-24 16:30 | 514 | 513
2018-04-24 17:00 | 534 | 534
2018-04-24 17:30 | 561 | 560
2018-04-24 18:00 | 587 | 587
2018-04-24 18:30 | 613 | 613
2018-04-24 19:00 | 632 | 632
2018-04-24 19:30 | 619 | 619
2018-04-24 20:00 | 598 | 598
2018-04-24 20:30 | 575 | 575
2018-04-24 21:00 | 553 | 553
2018-04-24 21:30 | 534 | 534
2018-04-24 22:00 | 517 | 517
2018-04-24 22:30 | 517 | 516
2018-04-24 23:00 | 497 | 496
2018-04-24 23:30 | 475 | 474
2018-04-25 | 456 | 454
2018-04-25 00:30 | 446 | 444
2018-04-25 01:00 | 437 | 434
2018-04-25 01:30 | 439 | 436
2018-04-25 02:00 | 424 | 422
2018-04-25 02:30 | 414 | 410
2018-04-25 03:00 | 404 | 400
2018-04-25 03:30 | 399 | 395
2018-04-25 04:00 | 320 | 315
2018-04-25 04:30 | 320 | 313
2018-04-25 05:00 | 345 | 337
2018-04-25 05:30 | 365 | 359
2018-04-25 06:00 | 373 | 368
2018-04-25 06:30 | 385 | 380
2018-04-25 07:00 | 383 | 378
2018-04-25 07:30 | 374 | 370
2018-04-25 08:00 | 347 | 341
2018-04-25 08:30 | 345 | 339
2018-04-25 09:00 | 328 | 322
2018-04-25 09:30 | 321 | 314
2018-04-25 10:00 | 279 | 270
2018-04-25 10:30 | 242 | 227
2018-04-25 11:00 | 259 | 243
2018-04-25 11:30 | 290 | 276
2018-04-25 12:00 | 317 | 305
2018-04-25 12:30 | 340 | 331
2018-04-25 13:00 | 359 | 351
2018-04-25 13:30 | 360 | 353
2018-04-25 14:00 | 368 | 361
2018-04-25 14:30 | 378 | 371
2018-04-25 15:00 | 387 | 381
2018-04-25 15:30 | 407 | 402
2018-04-25 16:00 | 426 | 422
2018-04-25 16:30 | 447 | 443
2018-04-25 17:00 | 480 | 477
2018-04-25 17:30 | 525 | 523
2018-04-25 18:00 | 565 | 564
2018-04-25 18:30 | 595 | 595
2018-04-25 19:00 | 615 | 614
2018-04-25 19:30 | 595 | 595
2018-04-25 20:00 | 572 | 572
2018-04-25 20:30 | 552 | 551
2018-04-25 21:00 | 519 | 517
2018-04-25 21:30 | 470 | 467
2018-04-25 22:00 | 448 | 445
2018-04-25 22:30 | 445 | 441
2018-04-25 23:00 | 421 | 418
2018-04-25 23:30 | 376 | 371
2018-04-26 | 362 | 356
2018-04-26 00:30 | 360 | 353
2018-04-26 01:00 | 346 | 339
2018-04-26 01:30 | 332 | 325
2018-04-26 02:00 | 327 | 319
2018-04-26 02:30 | 328 | 319
2018-04-26 03:00 | 323 | 314
2018-04-26 03:30 | 322 | 313
2018-04-26 04:00 | 325 | 317
2018-04-26 04:30 | 326 | 317
2018-04-26 05:00 | 336 | 328
2018-04-26 05:30 | 346 | 339
2018-04-26 06:00 | 362 | 355
2018-04-26 06:30 | 395 | 389
2018-04-26 07:00 | 418 | 414
2018-04-26 07:30 | 422 | 419
2018-04-26 08:00 | 391 | 389
2018-04-26 08:30 | 348 | 345
2018-04-26 09:00 | 287 | 281
2018-04-26 09:30 | 271 | 261
2018-04-26 10:00 | 263 | 252
2018-04-26 10:30 | 261 | 249
2018-04-26 11:00 | 259 | 246
2018-04-26 11:30 | 228 | 214
2018-04-26 12:00 | 195 | 177
2018-04-26 12:30 | 159 | 132
2018-04-26 13:00 | 158 | 126
2018-04-26 13:30 | 164 | 133
2018-04-26 14:00 | 170 | 142
2018-04-26 14:30 | 179 | 153
2018-04-26 15:00 | 188 | 164
2018-04-26 15:30 | 200 | 180
2018-04-26 16:00 | 215 | 197
2018-04-26 16:30 | 236 | 219
2018-04-26 17:00 | 256 | 241
2018-04-26 17:30 | 279 | 267
2018-04-26 18:00 | 310 | 300
2018-04-26 18:30 | 338 | 331
2018-04-26 19:00 | 354 | 349
2018-04-26 19:30 | 341 | 337
2018-04-26 20:00 | 321 | 315
2018-04-26 20:30 | 294 | 287
2018-04-26 21:00 | 265 | 255
2018-04-26 21:30 | 245 | 232
2018-04-26 22:00 | 219 | 203
2018-04-26 22:30 | 228 | 210
2018-04-26 23:00 | 271 | 256
2018-04-26 23:30 | 265 | 253
2018-04-27 | 246 | 233
2018-04-27 00:30 | 236 | 221
2018-04-27 01:00 | 227 | 210
2018-04-27 01:30 | 219 | 199
2018-04-27 02:00 | 214 | 193
2018-04-27 02:30 | 212 | 190
2018-04-27 03:00 | 213 | 191
2018-04-27 03:30 | 204 | 181
2018-04-27 04:00 | 208 | 185
2018-04-27 04:30 | 212 | 189
2018-04-27 05:00 | 216 | 193
2018-04-27 05:30 | 227 | 206
2018-04-27 06:00 | 243 | 224
2018-04-27 06:30 | 272 | 257
2018-04-27 07:00 | 295 | 282
2018-04-27 07:30 | 300 | 289
2018-04-27 08:00 | 276 | 265
2018-04-27 08:30 | 248 | 234
2018-04-27 09:00 | 224 | 206
2018-04-27 09:30 | 221 | 201
2018-04-27 10:00 | 217 | 196
2018-04-27 10:30 | 215 | 193
2018-04-27 11:00 | 216 | 193
2018-04-27 11:30 | 213 | 190
2018-04-27 12:00 | 216 | 194
2018-04-27 12:30 | 216 | 193
2018-04-27 13:00 | 218 | 195
2018-04-27 13:30 | 225 | 204
2018-04-27 14:00 | 232 | 212
2018-04-27 14:30 | 244 | 227
2018-04-27 15:00 | 259 | 244
2018-04-27 15:30 | 270 | 257
2018-04-27 16:00 | 223 | 207
2018-04-27 16:30 | 235 | 216
2018-04-27 17:00 | 256 | 240
2018-04-27 17:30 | 279 | 265
2018-04-27 18:00 | 299 | 289
2018-04-27 18:30 | 320 | 311
2018-04-27 19:00 | 325 | 317
2018-04-27 19:30 | 311 | 303
2018-04-27 20:00 | 299 | 289
2018-04-27 20:30 | 286 | 276
2018-04-27 21:00 | 284 | 272
2018-04-27 21:30 | 278 | 265
2018-04-27 22:00 | 257 | 243
2018-04-27 22:30 | 258 | 243
2018-04-27 23:00 | 305 | 292
2018-04-27 23:30 | 344 | 335
2018-04-28 | 406 | 399
2018-04-28 00:30 | 397 | 393
2018-04-28 01:00 | 383 | 379
2018-04-28 01:30 | 371 | 366
2018-04-28 02:00 | 365 | 359
2018-04-28 02:30 | 363 | 357
2018-04-28 03:00 | 357 | 350
2018-04-28 03:30 | 359 | 353
2018-04-28 04:00 | 357 | 351
2018-04-28 04:30 | 359 | 353
2018-04-28 05:00 | 361 | 355
2018-04-28 05:30 | 365 | 358
2018-04-28 06:00 | 373 | 367
2018-04-28 06:30 | 386 | 381
2018-04-28 07:00 | 391 | 386
2018-04-28 07:30 | 390 | 385
2018-04-28 08:00 | 369 | 364
2018-04-28 08:30 | 361 | 355
2018-04-28 09:00 | 356 | 350
2018-04-28 09:30 | 351 | 344
2018-04-28 10:00 | 337 | 329
2018-04-28 10:30 | 321 | 313
2018-04-28 11:00 | 301 | 291
2018-04-28 11:30 | 301 | 290
2018-04-28 12:00 | 295 | 283
2018-04-28 12:30 | 286 | 273
2018-04-28 13:00 | 291 | 278
2018-04-28 13:30 | 319 | 307
2018-04-28 14:00 | 313 | 303
2018-04-28 14:30 | 328 | 318
2018-04-28 15:00 | 330 | 322
2018-04-28 15:30 | 354 | 346
2018-04-28 16:00 | 400 | 393
2018-04-28 16:30 | 414 | 410
2018-04-28 17:00 | 449 | 445
2018-04-28 17:30 | 496 | 494
2018-04-28 18:00 | 528 | 526
2018-04-28 18:30 | 560 | 558
2018-04-28 19:00 | 558 | 558
2018-04-28 19:30 | 540 | 539
2018-04-28 20:00 | 522 | 521
2018-04-28 20:30 | 505 | 504
2018-04-28 21:00 | 492 | 491
2018-04-28 21:30 | 478 | 476
2018-04-28 22:00 | 465 | 462
2018-04-28 22:30 | 468 | 465
2018-04-28 23:00 | 456 | 453
2018-04-28 23:30 | 442 | 439
2018-04-29 | 424 | 421
2018-04-29 00:30 | 416 | 411
2018-04-29 01:00 | 402 | 397
2018-04-29 01:30 | 394 | 388
2018-04-29 02:00 | 389 | 383
2018-04-29 02:30 | 384 | 378
2018-04-29 03:00 | 379 | 373
2018-04-29 03:30 | 373 | 367
2018-04-29 04:00 | 375 | 369
2018-04-29 04:30 | 378 | 372
2018-04-29 05:00 | 380 | 374
2018-04-29 05:30 | 384 | 378
2018-04-29 06:00 | 388 | 382
2018-04-29 06:30 | 392 | 387
2018-04-29 07:00 | 391 | 385
2018-04-29 07:30 | 383 | 378
2018-04-29 08:00 | 354 | 348
2018-04-29 08:30 | 352 | 346
2018-04-29 09:00 | 345 | 338
2018-04-29 09:30 | 363 | 355
2018-04-29 10:00 | 347 | 340
2018-04-29 10:30 | 340 | 332
2018-04-29 11:00 | 328 | 320
2018-04-29 11:30 | 329 | 320
2018-04-29 12:00 | 337 | 329
2018-04-29 12:30 | 342 | 334
2018-04-29 13:00 | 354 | 346
2018-04-29 13:30 | 363 | 356
2018-04-29 14:00 | 339 | 333
2018-04-29 14:30 | 353 | 346
2018-04-29 15:00 | 369 | 363
2018-04-29 15:30 | 390 | 385
2018-04-29 16:00 | 412 | 408
2018-04-29 16:30 | 444 | 441
2018-04-29 17:00 | 485 | 482
2018-04-29 17:30 | 533 | 532
2018-04-29 18:00 | 570 | 570
2018-04-29 18:30 | 608 | 608
2018-04-29 19:00 | 607 | 607
2018-04-29 19:30 | 585 | 585
2018-04-29 20:00 | 557 | 556
2018-04-29 20:30 | 534 | 534
2018-04-29 21:00 | 522 | 521
2018-04-29 21:30 | 508 | 507
2018-04-29 22:00 | 478 | 476
2018-04-29 22:30 | 473 | 471
2018-04-29 23:00 | 463 | 460
2018-04-29 23:30 | 445 | 442
2018-04-30 | 432 | 429
2018-04-30 00:30 | 425 | 422
2018-04-30 01:00 | 415 | 411
2018-04-30 01:30 | 408 | 404
2018-04-30 02:00 | 400 | 395
2018-04-30 02:30 | 394 | 390
2018-04-30 03:00 | 396 | 392
2018-04-30 03:30 | 397 | 392
2018-04-30 04:00 | 395 | 391
2018-04-30 04:30 | 395 | 391
2018-04-30 05:00 | 404 | 400
2018-04-30 05:30 | 422 | 418
2018-04-30 06:00 | 433 | 430
2018-04-30 06:30 | 471 | 468
2018-04-30 07:00 | 498 | 496
2018-04-30 07:30 | 515 | 514
2018-04-30 08:00 | 480 | 480
2018-04-30 08:30 | 442 | 441
2018-04-30 09:00 | 428 | 427
2018-04-30 09:30 | 418 | 416
2018-04-30 10:00 | 351 | 349
2018-04-30 10:30 | 337 | 332
2018-04-30 11:00 | 344 | 339
2018-04-30 11:30 | 330 | 325
2018-04-30 12:00 | 327 | 321
2018-04-30 12:30 | 335 | 329
2018-04-30 13:00 | 337 | 331
2018-04-30 13:30 | 349 | 343
2018-04-30 14:00 | 338 | 333
2018-04-30 14:30 | 369 | 365
2018-04-30 15:00 | 420 | 417
2018-04-30 15:30 | 439 | 437
2018-04-30 16:00 | 453 | 452
2018-04-30 16:30 | 493 | 492
2018-04-30 17:00 | 511 | 510
2018-04-30 17:30 | 536 | 535
2018-04-30 18:00 | 555 | 555
2018-04-30 18:30 | 599 | 599
2018-04-30 19:00 | 603 | 603
2018-04-30 19:30 | 581 | 581
2018-04-30 20:00 | 573 | 573
2018-04-30 20:30 | 557 | 557
2018-04-30 21:00 | 541 | 541
2018-04-30 21:30 | 521 | 521
2018-04-30 22:00 | 500 | 499
2018-04-30 22:30 | 496 | 495
2018-04-30 23:00 | 478 | 476
2018-04-30 23:30 | 458 | 456
2018-05-01 | 446 | 443
2018-05-01 00:30 | 436 | 433
2018-05-01 01:00 | 426 | 422
2018-05-01 01:30 | 423 | 419
2018-05-01 02:00 | 414 | 410
2018-05-01 02:30 | 406 | 402
2018-05-01 03:00 | 405 | 401
2018-05-01 03:30 | 402 | 398
2018-05-01 04:00 | 399 | 394
2018-05-01 04:30 | 407 | 402
2018-05-01 05:00 | 407 | 403
2018-05-01 05:30 | 424 | 420
2018-05-01 06:00 | 446 | 443
2018-05-01 06:30 | 481 | 478
2018-05-01 07:00 | 487 | 486
2018-05-01 07:30 | 498 | 497
2018-05-01 08:00 | 487 | 486
2018-05-01 08:30 | 451 | 450
2018-05-01 09:00 | 421 | 419
2018-05-01 09:30 | 429 | 426
2018-05-01 10:00 | 426 | 422
2018-05-01 10:30 | 413 | 408
2018-05-01 11:00 | 395 | 390
2018-05-01 11:30 | 410 | 406
2018-05-01 12:00 | 418 | 415
2018-05-01 12:30 | 416 | 413
2018-05-01 13:00 | 418 | 415
2018-05-01 13:30 | 404 | 400
2018-05-01 14:00 | 431 | 427
2018-05-01 14:30 | 479 | 475
2018-05-01 15:00 | 488 | 486
2018-05-01 15:30 | 464 | 463
2018-05-01 16:00 | 464 | 462
2018-05-01 16:30 | 473 | 471
2018-05-01 17:00 | 502 | 501
2018-05-01 17:30 | 536 | 535
2018-05-01 18:00 | 564 | 564
2018-05-01 18:30 | 599 | 599
2018-05-01 19:00 | 605 | 605
2018-05-01 19:30 | 585 | 585
2018-05-01 20:00 | 565 | 565
2018-05-01 20:30 | 543 | 543
2018-05-01 21:00 | 516 | 515
2018-05-01 21:30 | 515 | 514
2018-05-01 22:00 | 494 | 494
2018-05-01 22:30 | 492 | 491
2018-05-01 23:00 | 473 | 472
2018-05-01 23:30 | 455 | 453
2018-05-02 | 439 | 437
2018-05-02 00:30 | 428 | 425
2018-05-02 01:00 | 418 | 415
2018-05-02 01:30 | 414 | 411
2018-05-02 02:00 | 406 | 402
2018-05-02 02:30 | 405 | 401
2018-05-02 03:00 | 401 | 398
2018-05-02 03:30 | 402 | 398
2018-05-02 04:00 | 399 | 395
2018-05-02 04:30 | 406 | 402
2018-05-02 05:00 | 402 | 398
2018-05-02 05:30 | 399 | 395
2018-05-02 06:00 | 419 | 415
2018-05-02 06:30 | 456 | 453
2018-05-02 07:00 | 478 | 475
2018-05-02 07:30 | 505 | 503
2018-05-02 08:00 | 528 | 527
2018-05-02 08:30 | 514 | 513
2018-05-02 09:00 | 490 | 490
2018-05-02 09:30 | 461 | 460
2018-05-02 10:00 | 446 | 444
2018-05-02 10:30 | 421 | 419
2018-05-02 11:00 | 424 | 422
2018-05-02 11:30 | 411 | 409
2018-05-02 12:00 | 429 | 427
2018-05-02 12:30 | 448 | 446
2018-05-02 13:00 | 441 | 440
2018-05-02 13:30 | 448 | 447
2018-05-02 14:00 | 475 | 473
2018-05-02 14:30 | 485 | 484
2018-05-02 15:00 | 475 | 474
2018-05-02 15:30 | 468 | 467
2018-05-02 16:00 | 474 | 473
2018-05-02 16:30 | 499 | 498
2018-05-02 17:00 | 512 | 512
2018-05-02 17:30 | 535 | 535
2018-05-02 18:00 | 563 | 563
2018-05-02 18:30 | 589 | 589
2018-05-02 19:00 | 598 | 598
2018-05-02 19:30 | 587 | 587
2018-05-02 20:00 | 566 | 566
2018-05-02 20:30 | 543 | 543
2018-05-02 21:00 | 517 | 516
2018-05-02 21:30 | 493 | 492
2018-05-02 22:00 | 473 | 471
2018-05-02 22:30 | 445 | 443
2018-05-02 23:00 | 420 | 419
2018-05-02 23:30 | 405 | 403
2018-05-03 | 392 | 389
2018-05-03 00:30 | 391 | 388
2018-05-03 01:00 | 410 | 407
2018-05-03 01:30 | 405 | 402
2018-05-03 02:00 | 364 | 361
2018-05-03 02:30 | 366 | 361
2018-05-03 03:00 | 357 | 352
2018-05-03 03:30 | 366 | 360
2018-05-03 04:00 | 378 | 373
2018-05-03 04:30 | 336 | 331
2018-05-03 05:00 | 299 | 292
2018-05-03 05:30 | 311 | 302
2018-05-03 06:00 | 337 | 329
2018-05-03 06:30 | 384 | 378
2018-05-03 07:00 | 417 | 412
2018-05-03 07:30 | 442 | 439
2018-05-03 08:00 | 413 | 411
2018-05-03 08:30 | 334 | 330
2018-05-03 09:00 | 328 | 320
2018-05-03 09:30 | 296 | 287
2018-05-03 10:00 | 287 | 276
2018-05-03 10:30 | 283 | 270
2018-05-03 11:00 | 312 | 300
2018-05-03 11:30 | 294 | 282
2018-05-03 12:00 | 264 | 250
2018-05-03 12:30 | 257 | 241
2018-05-03 13:00 | 250 | 232
2018-05-03 13:30 | 253 | 235
2018-05-03 14:00 | 259 | 243
2018-05-03 14:30 | 261 | 245
2018-05-03 15:00 | 273 | 258
2018-05-03 15:30 | 303 | 291
2018-05-03 16:00 | 323 | 314
2018-05-03 16:30 | 348 | 341
2018-05-03 17:00 | 368 | 362
2018-05-03 17:30 | 378 | 373
2018-05-03 18:00 | 397 | 393
2018-05-03 18:30 | 427 | 423
2018-05-03 19:00 | 438 | 435
2018-05-03 19:30 | 422 | 420
2018-05-03 20:00 | 406 | 404
2018-05-03 20:30 | 384 | 381
2018-05-03 21:00 | 435 | 431
2018-05-03 21:30 | 479 | 476
2018-05-03 22:00 | 537 | 536
2018-05-03 22:30 | 504 | 504
2018-05-03 23:00 | 487 | 485
2018-05-03 23:30 | 459 | 457
2018-05-04 | 444 | 441
2018-05-04 00:30 | 433 | 430
2018-05-04 01:00 | 422 | 419
2018-05-04 01:30 | 419 | 415
2018-05-04 02:00 | 414 | 410
2018-05-04 02:30 | 406 | 402
2018-05-04 03:00 | 404 | 399
2018-05-04 03:30 | 401 | 397
2018-05-04 04:00 | 399 | 395
2018-05-04 04:30 | 408 | 404
2018-05-04 05:00 | 419 | 415
2018-05-04 05:30 | 429 | 426
2018-05-04 06:00 | 448 | 445
2018-05-04 06:30 | 470 | 467
2018-05-04 07:00 | 506 | 504
2018-05-04 07:30 | 525 | 524
2018-05-04 08:00 | 513 | 512
2018-05-04 08:30 | 487 | 486
2018-05-04 09:00 | 458 | 456
2018-05-04 09:30 | 438 | 434
2018-05-04 10:00 | 436 | 432
2018-05-04 10:30 | 423 | 418
2018-05-04 11:00 | 415 | 410
2018-05-04 11:30 | 420 | 414
2018-05-04 12:00 | 424 | 419
2018-05-04 12:30 | 419 | 414
2018-05-04 13:00 | 440 | 435
2018-05-04 13:30 | 448 | 444
2018-05-04 14:00 | 449 | 445
2018-05-04 14:30 | 453 | 449
2018-05-04 15:00 | 456 | 453
2018-05-04 15:30 | 449 | 445
2018-05-04 16:00 | 476 | 472
2018-05-04 16:30 | 500 | 497
2018-05-04 17:00 | 531 | 529
2018-05-04 17:30 | 556 | 554
2018-05-04 18:00 | 579 | 579
2018-05-04 18:30 | 597 | 597
2018-05-04 19:00 | 607 | 606
2018-05-04 19:30 | 596 | 595
2018-05-04 20:00 | 575 | 574
2018-05-04 20:30 | 557 | 556
2018-05-04 21:00 | 538 | 537
2018-05-04 21:30 | 553 | 551
2018-05-04 22:00 | 535 | 533
2018-05-04 22:30 | 514 | 512
2018-05-04 23:00 | 493 | 490
2018-05-04 23:30 | 468 | 465
2018-05-05 | 445 | 441
2018-05-05 00:30 | 439 | 435
2018-05-05 01:00 | 432 | 428
2018-05-05 01:30 | 422 | 418
2018-05-05 02:00 | 410 | 404
2018-05-05 02:30 | 409 | 403
2018-05-05 03:00 | 408 | 402
2018-05-05 03:30 | 402 | 396
2018-05-05 04:00 | 407 | 401
2018-05-05 04:30 | 405 | 399
2018-05-05 05:00 | 405 | 399
2018-05-05 05:30 | 418 | 412
2018-05-05 06:00 | 423 | 418
2018-05-05 06:30 | 427 | 422
2018-05-05 07:00 | 436 | 431
2018-05-05 07:30 | 437 | 433
2018-05-05 08:00 | 427 | 422
2018-05-05 08:30 | 419 | 415
2018-05-05 09:00 | 392 | 386
2018-05-05 09:30 | 376 | 369
2018-05-05 10:00 | 367 | 360
2018-05-05 10:30 | 363 | 355
2018-05-05 11:00 | 349 | 342
2018-05-05 11:30 | 353 | 346
2018-05-05 12:00 | 351 | 344
2018-05-05 12:30 | 350 | 342
2018-05-05 13:00 | 350 | 342
2018-05-05 13:30 | 358 | 350
2018-05-05 14:00 | 362 | 355
2018-05-05 14:30 | 367 | 360
2018-05-05 15:00 | 379 | 373
2018-05-05 15:30 | 396 | 390
2018-05-05 16:00 | 427 | 423
2018-05-05 16:30 | 459 | 456
2018-05-05 17:00 | 471 | 469
2018-05-05 17:30 | 493 | 491
2018-05-05 18:00 | 522 | 521
2018-05-05 18:30 | 548 | 547
2018-05-05 19:00 | 550 | 549
2018-05-05 19:30 | 536 | 535
2018-05-05 20:00 | 513 | 512
2018-05-05 20:30 | 498 | 496
2018-05-05 21:00 | 498 | 496
2018-05-05 21:30 | 487 | 485
2018-05-05 22:00 | 475 | 473
2018-05-05 22:30 | 476 | 474
2018-05-05 23:00 | 464 | 461
2018-05-05 23:30 | 447 | 444
2018-05-06 | 438 | 435
2018-05-06 00:30 | 433 | 430
2018-05-06 01:00 | 420 | 416
2018-05-06 01:30 | 414 | 410
2018-05-06 02:00 | 407 | 404
2018-05-06 02:30 | 404 | 400
2018-05-06 03:00 | 398 | 394
2018-05-06 03:30 | 395 | 391
2018-05-06 04:00 | 395 | 390
2018-05-06 04:30 | 397 | 393
2018-05-06 05:00 | 399 | 394
2018-05-06 05:30 | 403 | 398
2018-05-06 06:00 | 404 | 400
2018-05-06 06:30 | 406 | 402
2018-05-06 07:00 | 413 | 408
2018-05-06 07:30 | 420 | 415
2018-05-06 08:00 | 404 | 400
2018-05-06 08:30 | 402 | 398
2018-05-06 09:00 | 399 | 395
2018-05-06 09:30 | 387 | 382
2018-05-06 10:00 | 360 | 354
2018-05-06 10:30 | 352 | 346
2018-05-06 11:00 | 349 | 342
2018-05-06 11:30 | 345 | 337
2018-05-06 12:00 | 350 | 343
2018-05-06 12:30 | 343 | 336
2018-05-06 13:00 | 350 | 343
2018-05-06 13:30 | 361 | 354
2018-05-06 14:00 | 367 | 361
2018-05-06 14:30 | 379 | 373
2018-05-06 15:00 | 378 | 373
2018-05-06 15:30 | 404 | 399
2018-05-06 16:00 | 418 | 414
2018-05-06 16:30 | 441 | 438
2018-05-06 17:00 | 467 | 464
2018-05-06 17:30 | 506 | 504
2018-05-06 18:00 | 532 | 530
2018-05-06 18:30 | 564 | 563
2018-05-06 19:00 | 566 | 566
2018-05-06 19:30 | 552 | 552
2018-05-06 20:00 | 535 | 534
2018-05-06 20:30 | 517 | 516
2018-05-06 21:00 | 501 | 500
2018-05-06 21:30 | 518 | 516
2018-05-06 22:00 | 504 | 503
2018-05-06 22:30 | 489 | 488
2018-05-06 23:00 | 470 | 467
2018-05-06 23:30 | 452 | 450
2018-05-07 | 435 | 432
2018-05-07 00:30 | 432 | 428
2018-05-07 01:00 | 427 | 423
2018-05-07 01:30 | 414 | 410
2018-05-07 02:00 | 408 | 404
2018-05-07 02:30 | 404 | 400
2018-05-07 03:00 | 405 | 400
2018-05-07 03:30 | 403 | 399
2018-05-07 04:00 | 405 | 401
2018-05-07 04:30 | 407 | 403
2018-05-07 05:00 | 407 | 403
2018-05-07 05:30 | 411 | 407
2018-05-07 06:00 | 413 | 409
2018-05-07 06:30 | 420 | 416
2018-05-07 07:00 | 427 | 423
2018-05-07 07:30 | 430 | 426
2018-05-07 08:00 | 416 | 412
2018-05-07 08:30 | 403 | 399
2018-05-07 09:00 | 393 | 388
2018-05-07 09:30 | 387 | 382
2018-05-07 10:00 | 374 | 368
2018-05-07 10:30 | 363 | 357
2018-05-07 11:00 | 354 | 347
2018-05-07 11:30 | 356 | 348
2018-05-07 12:00 | 365 | 358
2018-05-07 12:30 | 365 | 358
2018-05-07 13:00 | 369 | 362
2018-05-07 13:30 | 382 | 375
2018-05-07 14:00 | 390 | 384
2018-05-07 14:30 | 380 | 374
2018-05-07 15:00 | 401 | 395
2018-05-07 15:30 | 413 | 408
2018-05-07 16:00 | 430 | 426
2018-05-07 16:30 | 455 | 452
2018-05-07 17:00 | 471 | 469
2018-05-07 17:30 | 510 | 508
2018-05-07 18:00 | 550 | 548
2018-05-07 18:30 | 586 | 585
2018-05-07 19:00 | 589 | 589
2018-05-07 19:30 | 589 | 589
2018-05-07 20:00 | 571 | 571
2018-05-07 20:30 | 549 | 548
2018-05-07 21:00 | 528 | 526
2018-05-07 21:30 | 508 | 506
2018-05-07 22:00 | 487 | 485
2018-05-07 22:30 | 466 | 462
2018-05-07 23:00 | 444 | 440
2018-05-07 23:30 | 454 | 450
2018-05-08 | 442 | 438
2018-05-08 00:30 | 433 | 429
2018-05-08 01:00 | 422 | 418
2018-05-08 01:30 | 415 | 409
2018-05-08 02:00 | 415 | 409
2018-05-08 02:30 | 411 | 406
2018-05-08 03:00 | 406 | 400
2018-05-08 03:30 | 401 | 395
2018-05-08 04:00 | 404 | 398
2018-05-08 04:30 | 410 | 404
2018-05-08 05:00 | 412 | 407
2018-05-08 05:30 | 430 | 424
2018-05-08 06:00 | 449 | 444
2018-05-08 06:30 | 479 | 475
2018-05-08 07:00 | 510 | 507
2018-05-08 07:30 | 537 | 535
2018-05-08 08:00 | 542 | 540
2018-05-08 08:30 | 524 | 523
2018-05-08 09:00 | 493 | 491
2018-05-08 09:30 | 483 | 480
2018-05-08 10:00 | 469 | 466
2018-05-08 10:30 | 460 | 456
2018-05-08 11:00 | 456 | 452
2018-05-08 11:30 | 459 | 456
2018-05-08 12:00 | 451 | 447
2018-05-08 12:30 | 452 | 448
2018-05-08 13:00 | 463 | 460
2018-05-08 13:30 | 480 | 477
2018-05-08 14:00 | 475 | 471
2018-05-08 14:30 | 481 | 478
2018-05-08 15:00 | 485 | 482
2018-05-08 15:30 | 492 | 490
2018-05-08 16:00 | 505 | 503
2018-05-08 16:30 | 536 | 534
2018-05-08 17:00 | 564 | 563
2018-05-08 17:30 | 571 | 570
2018-05-08 18:00 | 530 | 529
2018-05-08 18:30 | 599 | 598
2018-05-08 19:00 | 624 | 624
2018-05-08 19:30 | 605 | 604
2018-05-08 20:00 | 580 | 579
2018-05-08 20:30 | 558 | 557
2018-05-08 21:00 | 538 | 537
2018-05-08 21:30 | 513 | 511
2018-05-08 22:00 | 494 | 492
2018-05-08 22:30 | 466 | 464
2018-05-08 23:00 | 441 | 438
2018-05-08 23:30 | 422 | 417
2018-05-09 | 454 | 449
2018-05-09 00:30 | 451 | 447
2018-05-09 01:00 | 439 | 435
2018-05-09 01:30 | 427 | 423
2018-05-09 02:00 | 425 | 420
2018-05-09 02:30 | 416 | 411
2018-05-09 03:00 | 410 | 405
2018-05-09 03:30 | 413 | 408
2018-05-09 04:00 | 414 | 408
2018-05-09 04:30 | 422 | 416
2018-05-09 05:00 | 432 | 427
2018-05-09 05:30 | 446 | 441
2018-05-09 06:00 | 461 | 457
2018-05-09 06:30 | 487 | 484
2018-05-09 07:00 | 517 | 514
2018-05-09 07:30 | 545 | 543
2018-05-09 08:00 | 542 | 541
2018-05-09 08:30 | 533 | 532
2018-05-09 09:00 | 508 | 507
2018-05-09 09:30 | 470 | 469
2018-05-09 10:00 | 444 | 441
2018-05-09 10:30 | 448 | 445
2018-05-09 11:00 | 423 | 420
2018-05-09 11:30 | 414 | 410
2018-05-09 12:00 | 414 | 410
2018-05-09 12:30 | 453 | 450
2018-05-09 13:00 | 480 | 477
2018-05-09 13:30 | 473 | 471
2018-05-09 14:00 | 470 | 468
2018-05-09 14:30 | 492 | 490
2018-05-09 15:00 | 507 | 505
2018-05-09 15:30 | 540 | 539
2018-05-09 16:00 | 547 | 546
2018-05-09 16:30 | 567 | 567
2018-05-09 17:00 | 581 | 581
2018-05-09 17:30 | 620 | 620
2018-05-09 18:00 | 643 | 643
2018-05-09 18:30 | 676 | 676
2018-05-09 19:00 | 684 | 684
2018-05-09 19:30 | 665 | 665
2018-05-09 20:00 | 641 | 641
2018-05-09 20:30 | 618 | 617
2018-05-09 21:00 | 595 | 595
2018-05-09 21:30 | 571 | 570
2018-05-09 22:00 | 539 | 538
2018-05-09 22:30 | 532 | 530
2018-05-09 23:00 | 512 | 510
2018-05-09 23:30 | 501 | 499
2018-05-10 | 487 | 485
2018-05-10 00:30 | 483 | 480
2018-05-10 01:00 | 466 | 463
2018-05-10 01:30 | 458 | 454
2018-05-10 02:00 | 449 | 445
2018-05-10 02:30 | 443 | 439
2018-05-10 03:00 | 446 | 441
2018-05-10 03:30 | 446 | 442
2018-05-10 04:00 | 442 | 437
2018-05-10 04:30 | 448 | 444
2018-05-10 05:00 | 456 | 453
2018-05-10 05:30 | 468 | 464
2018-05-10 06:00 | 483 | 480
2018-05-10 06:30 | 519 | 517
2018-05-10 07:00 | 547 | 545
2018-05-10 07:30 | 571 | 570
2018-05-10 08:00 | 552 | 551
2018-05-10 08:30 | 531 | 530
2018-05-10 09:00 | 497 | 496
2018-05-10 09:30 | 487 | 485
2018-05-10 10:00 | 484 | 482
2018-05-10 10:30 | 478 | 476
2018-05-10 11:00 | 467 | 464
2018-05-10 11:30 | 472 | 470
2018-05-10 12:00 | 471 | 469
2018-05-10 12:30 | 495 | 492
2018-05-10 13:00 | 498 | 496
2018-05-10 13:30 | 495 | 493
2018-05-10 14:00 | 481 | 479
2018-05-10 14:30 | 482 | 480
2018-05-10 15:00 | 495 | 493
2018-05-10 15:30 | 515 | 513
2018-05-10 16:00 | 539 | 537
2018-05-10 16:30 | 560 | 560
2018-05-10 17:00 | 601 | 601
2018-05-10 17:30 | 621 | 621
2018-05-10 18:00 | 643 | 643
2018-05-10 18:30 | 655 | 655
2018-05-10 19:00 | 663 | 663
2018-05-10 19:30 | 642 | 642
2018-05-10 20:00 | 623 | 622
2018-05-10 20:30 | 600 | 599
2018-05-10 21:00 | 599 | 599
2018-05-10 21:30 | 609 | 609
2018-05-10 22:00 | 584 | 583
2018-05-10 22:30 | 557 | 556
2018-05-10 23:00 | 530 | 528
2018-05-10 23:30 | 506 | 504
2018-05-11 | 489 | 486
2018-05-11 00:30 | 474 | 470
2018-05-11 01:00 | 466 | 462
2018-05-11 01:30 | 457 | 453
2018-05-11 02:00 | 452 | 448
2018-05-11 02:30 | 445 | 441
2018-05-11 03:00 | 445 | 440
2018-05-11 03:30 | 442 | 437
2018-05-11 04:00 | 443 | 438
2018-05-11 04:30 | 420 | 415
2018-05-11 05:00 | 381 | 375
2018-05-11 05:30 | 389 | 381
2018-05-11 06:00 | 407 | 401
2018-05-11 06:30 | 440 | 435
2018-05-11 07:00 | 480 | 475
2018-05-11 07:30 | 489 | 486
2018-05-11 08:00 | 432 | 430
2018-05-11 08:30 | 340 | 335
2018-05-11 09:00 | 324 | 315
2018-05-11 09:30 | 308 | 296
2018-05-11 10:00 | 350 | 339
2018-05-11 10:30 | 351 | 343
2018-05-11 11:00 | 364 | 356
2018-05-11 11:30 | 368 | 361
2018-05-11 12:00 | 347 | 340
2018-05-11 12:30 | 330 | 321
2018-05-11 13:00 | 339 | 329
2018-05-11 13:30 | 343 | 334
2018-05-11 14:00 | 377 | 370
2018-05-11 14:30 | 393 | 387
2018-05-11 15:00 | 397 | 392
2018-05-11 15:30 | 396 | 391
2018-05-11 16:00 | 347 | 341
2018-05-11 16:30 | 357 | 350
2018-05-11 17:00 | 380 | 374
2018-05-11 17:30 | 391 | 386
2018-05-11 18:00 | 393 | 389
2018-05-11 18:30 | 420 | 416
2018-05-11 19:00 | 417 | 413
2018-05-11 19:30 | 399 | 395
2018-05-11 20:00 | 384 | 379
2018-05-11 20:30 | 361 | 355
2018-05-11 21:00 | 343 | 336
2018-05-11 21:30 | 326 | 317
2018-05-11 22:00 | 330 | 320
2018-05-11 22:30 | 337 | 327
2018-05-11 23:00 | 316 | 306
2018-05-11 23:30 | 364 | 355
2018-05-12 | 410 | 404
2018-05-12 00:30 | 476 | 472
2018-05-12 01:00 | 458 | 455
2018-05-12 01:30 | 446 | 443
2018-05-12 02:00 | 441 | 437
2018-05-12 02:30 | 436 | 431
2018-05-12 03:00 | 428 | 423
2018-05-12 03:30 | 426 | 421
2018-05-12 04:00 | 421 | 415
2018-05-12 04:30 | 430 | 424
2018-05-12 05:00 | 434 | 428
2018-05-12 05:30 | 440 | 435
2018-05-12 06:00 | 449 | 445
2018-05-12 06:30 | 464 | 460
2018-05-12 07:00 | 462 | 458
2018-05-12 07:30 | 466 | 462
2018-05-12 08:00 | 451 | 447
2018-05-12 08:30 | 429 | 424
2018-05-12 09:00 | 416 | 411
2018-05-12 09:30 | 408 | 402
2018-05-12 10:00 | 389 | 382
2018-05-12 10:30 | 353 | 346
2018-05-12 11:00 | 338 | 330
2018-05-12 11:30 | 331 | 321
2018-05-12 12:00 | 332 | 322
2018-05-12 12:30 | 329 | 319
2018-05-12 13:00 | 338 | 328
2018-05-12 13:30 | 341 | 332
2018-05-12 14:00 | 353 | 344
2018-05-12 14:30 | 366 | 358
2018-05-12 15:00 | 377 | 371
2018-05-12 15:30 | 404 | 398
2018-05-12 16:00 | 434 | 430
2018-05-12 16:30 | 466 | 462
2018-05-12 17:00 | 501 | 499
2018-05-12 17:30 | 537 | 535
2018-05-12 18:00 | 575 | 574
2018-05-12 18:30 | 604 | 604
2018-05-12 19:00 | 599 | 598
2018-05-12 19:30 | 574 | 573
2018-05-12 20:00 | 556 | 555
2018-05-12 20:30 | 491 | 490
2018-05-12 21:00 | 469 | 467
2018-05-12 21:30 | 455 | 452
2018-05-12 22:00 | 460 | 457
2018-05-12 22:30 | 449 | 445
2018-05-12 23:00 | 431 | 426
2018-05-12 23:30 | 414 | 409
2018-05-13 | 403 | 398
2018-05-13 00:30 | 392 | 387
2018-05-13 01:00 | 387 | 381
2018-05-13 01:30 | 411 | 405
2018-05-13 02:00 | 409 | 404
2018-05-13 02:30 | 404 | 399
2018-05-13 03:00 | 398 | 392
2018-05-13 03:30 | 399 | 393
2018-05-13 04:00 | 393 | 387
2018-05-13 04:30 | 394 | 387
2018-05-13 05:00 | 397 | 390
2018-05-13 05:30 | 404 | 398
2018-05-13 06:00 | 409 | 404
2018-05-13 06:30 | 418 | 413
2018-05-13 07:00 | 436 | 431
2018-05-13 07:30 | 436 | 431
2018-05-13 08:00 | 472 | 468
2018-05-13 08:30 | 422 | 418
2018-05-13 09:00 | 410 | 405
2018-05-13 09:30 | 392 | 387
2018-05-13 10:00 | 387 | 381
2018-05-13 10:30 | 373 | 367
2018-05-13 11:00 | 366 | 359
2018-05-13 11:30 | 364 | 356
2018-05-13 12:00 | 350 | 342
2018-05-13 12:30 | 358 | 349
2018-05-13 13:00 | 384 | 376
2018-05-13 13:30 | 397 | 391
2018-05-13 14:00 | 334 | 328
2018-05-13 14:30 | 306 | 297
2018-05-13 15:00 | 322 | 311
2018-05-13 15:30 | 341 | 331
2018-05-13 16:00 | 385 | 378
2018-05-13 16:30 | 421 | 415
2018-05-13 17:00 | 449 | 445
2018-05-13 17:30 | 469 | 466
2018-05-13 18:00 | 504 | 502
2018-05-13 18:30 | 543 | 541
2018-05-13 19:00 | 534 | 533
2018-05-13 19:30 | 515 | 514
2018-05-13 20:00 | 500 | 499
2018-05-13 20:30 | 498 | 496
2018-05-13 21:00 | 488 | 486
2018-05-13 21:30 | 494 | 492
2018-05-13 22:00 | 478 | 476
2018-05-13 22:30 | 455 | 452
2018-05-13 23:00 | 432 | 429
2018-05-13 23:30 | 418 | 414
2018-05-14 | 400 | 396
2018-05-14 00:30 | 395 | 389
2018-05-14 01:00 | 388 | 383
2018-05-14 01:30 | 381 | 374
2018-05-14 02:00 | 378 | 371
2018-05-14 02:30 | 373 | 366
2018-05-14 03:00 | 368 | 361
2018-05-14 03:30 | 370 | 362
2018-05-14 04:00 | 371 | 363
2018-05-14 04:30 | 379 | 371
2018-05-14 05:00 | 389 | 382
2018-05-14 05:30 | 405 | 398
2018-05-14 06:00 | 420 | 414
2018-05-14 06:30 | 455 | 451
2018-05-14 07:00 | 483 | 480
2018-05-14 07:30 | 497 | 494
2018-05-14 08:00 | 473 | 471
2018-05-14 08:30 | 432 | 429
2018-05-14 09:00 | 396 | 391
2018-05-14 09:30 | 374 | 368
2018-05-14 10:00 | 363 | 355
2018-05-14 10:30 | 333 | 324
2018-05-14 11:00 | 282 | 270
2018-05-14 11:30 | 282 | 266
2018-05-14 12:00 | 281 | 264
2018-05-14 12:30 | 285 | 269
2018-05-14 13:00 | 290 | 275
2018-05-14 13:30 | 267 | 252
2018-05-14 14:00 | 220 | 200
2018-05-14 14:30 | 172 | 138
2018-05-14 15:00 | 177 | 139
2018-05-14 15:30 | 189 | 154
2018-05-14 16:00 | 212 | 185
2018-05-14 16:30 | 228 | 205
2018-05-14 17:00 | 225 | 205
2018-05-14 17:30 | 302 | 286
2018-05-14 18:00 | 339 | 329
2018-05-14 18:30 | 377 | 370
2018-05-14 19:00 | 375 | 369
2018-05-14 19:30 | 361 | 354
2018-05-14 20:00 | 337 | 330
2018-05-14 20:30 | 313 | 304
2018-05-14 21:00 | 308 | 297
2018-05-14 21:30 | 294 | 282
2018-05-14 22:00 | 299 | 287
2018-05-14 22:30 | 275 | 262
2018-05-14 23:00 | 321 | 309
2018-05-14 23:30 | 322 | 312
2018-05-15 | 310 | 300
2018-05-15 00:30 | 302 | 289
2018-05-15 01:00 | 289 | 276
2018-05-15 01:30 | 287 | 273
2018-05-15 02:00 | 282 | 267
2018-05-15 02:30 | 280 | 264
2018-05-15 03:00 | 277 | 261
2018-05-15 03:30 | 270 | 254
2018-05-15 04:00 | 275 | 258
2018-05-15 04:30 | 276 | 259
2018-05-15 05:00 | 281 | 265
2018-05-15 05:30 | 298 | 284
2018-05-15 06:00 | 312 | 299
2018-05-15 06:30 | 273 | 258
2018-05-15 07:00 | 292 | 276
2018-05-15 07:30 | 305 | 290
2018-05-15 08:00 | 288 | 273
2018-05-15 08:30 | 263 | 245
2018-05-15 09:00 | 316 | 299
2018-05-15 09:30 | 314 | 299
2018-05-15 10:00 | 281 | 264
2018-05-15 10:30 | 257 | 236
2018-05-15 11:00 | 255 | 231
2018-05-15 11:30 | 255 | 231
2018-05-15 12:00 | 257 | 233
2018-05-15 12:30 | 259 | 236
2018-05-15 13:00 | 264 | 241
2018-05-15 13:30 | 264 | 241
2018-05-15 14:00 | 254 | 231
2018-05-15 14:30 | 189 | 157
2018-05-15 15:00 | 191 | 152
2018-05-15 15:30 | 206 | 170
2018-05-15 16:00 | 226 | 197
2018-05-15 16:30 | 243 | 219
2018-05-15 17:00 | 272 | 252
2018-05-15 17:30 | 310 | 294
2018-05-15 18:00 | 332 | 319
2018-05-15 18:30 | 331 | 320
2018-05-15 19:00 | 376 | 367
2018-05-15 19:30 | 365 | 357
2018-05-15 20:00 | 361 | 353
2018-05-15 20:30 | 348 | 340
2018-05-15 21:00 | 423 | 415
2018-05-15 21:30 | 331 | 324
2018-05-15 22:00 | 307 | 296
2018-05-15 22:30 | 279 | 265
2018-05-15 23:00 | 248 | 229
2018-05-15 23:30 | 221 | 196
2018-05-16 | 237 | 212
2018-05-16 00:30 | 226 | 201
2018-05-16 01:00 | 284 | 264
2018-05-16 01:30 | 337 | 323
2018-05-16 02:00 | 413 | 404
2018-05-16 02:30 | 403 | 397
2018-05-16 03:00 | 394 | 387
2018-05-16 03:30 | 399 | 392
2018-05-16 04:00 | 396 | 390
2018-05-16 04:30 | 405 | 399
2018-05-16 05:00 | 413 | 407
2018-05-16 05:30 | 429 | 424
2018-05-16 06:00 | 444 | 439
2018-05-16 06:30 | 478 | 474
2018-05-16 07:00 | 517 | 514
2018-05-16 07:30 | 539 | 537
2018-05-16 08:00 | 493 | 491
2018-05-16 08:30 | 464 | 461
2018-05-16 09:00 | 458 | 454
2018-05-16 09:30 | 445 | 440
2018-05-16 10:00 | 445 | 440
2018-05-16 10:30 | 435 | 429
2018-05-16 11:00 | 415 | 409
2018-05-16 11:30 | 413 | 405
2018-05-16 12:00 | 419 | 412
2018-05-16 12:30 | 425 | 418
2018-05-16 13:00 | 423 | 415
2018-05-16 13:30 | 431 | 424
2018-05-16 14:00 | 425 | 419
2018-05-16 14:30 | 431 | 425
2018-05-16 15:00 | 450 | 444
2018-05-16 15:30 | 464 | 459
2018-05-16 16:00 | 487 | 483
2018-05-16 16:30 | 494 | 490
2018-05-16 17:00 | 501 | 498
2018-05-16 17:30 | 531 | 528
2018-05-16 18:00 | 563 | 561
2018-05-16 18:30 | 591 | 590
2018-05-16 19:00 | 595 | 594
2018-05-16 19:30 | 595 | 594
2018-05-16 20:00 | 580 | 579
2018-05-16 20:30 | 581 | 580
2018-05-16 21:00 | 571 | 570
2018-05-16 21:30 | 551 | 549
2018-05-16 22:00 | 524 | 522
2018-05-16 22:30 | 496 | 493
2018-05-16 23:00 | 474 | 471
2018-05-16 23:30 | 460 | 456
2018-05-17 | 445 | 441
2018-05-17 00:30 | 437 | 432
2018-05-17 01:00 | 424 | 419
2018-05-17 01:30 | 396 | 390
2018-05-17 02:00 | 330 | 321
2018-05-17 02:30 | 335 | 324
2018-05-17 03:00 | 371 | 362
2018-05-17 03:30 | 397 | 389
2018-05-17 04:00 | 406 | 400
2018-05-17 04:30 | 410 | 404
2018-05-17 05:00 | 416 | 410
2018-05-17 05:30 | 438 | 432
2018-05-17 06:00 | 454 | 450
2018-05-17 06:30 | 487 | 484
2018-05-17 07:00 | 527 | 524
2018-05-17 07:30 | 566 | 564
2018-05-17 08:00 | 583 | 582
2018-05-17 08:30 | 565 | 564
2018-05-17 09:00 | 542 | 541
2018-05-17 09:30 | 522 | 519
2018-05-17 10:00 | 515 | 512
2018-05-17 10:30 | 494 | 491
2018-05-17 11:00 | 484 | 481
2018-05-17 11:30 | 483 | 479
2018-05-17 12:00 | 485 | 481
2018-05-17 12:30 | 488 | 485
2018-05-17 13:00 | 478 | 474
2018-05-17 13:30 | 479 | 476
2018-05-17 14:00 | 481 | 477
2018-05-17 14:30 | 484 | 481
2018-05-17 15:00 | 491 | 488
2018-05-17 15:30 | 511 | 508
2018-05-17 16:00 | 519 | 516
2018-05-17 16:30 | 509 | 507
2018-05-17 17:00 | 524 | 521
2018-05-17 17:30 | 553 | 551
2018-05-17 18:00 | 587 | 585
2018-05-17 18:30 | 619 | 618
2018-05-17 19:00 | 628 | 628
2018-05-17 19:30 | 626 | 626
2018-05-17 20:00 | 612 | 611
2018-05-17 20:30 | 614 | 613
2018-05-17 21:00 | 596 | 595
2018-05-17 21:30 | 573 | 572
2018-05-17 22:00 | 544 | 542
2018-05-17 22:30 | 518 | 516
2018-05-17 23:00 | 488 | 485
2018-05-17 23:30 | 438 | 435
2018-05-18 | 456 | 451
2018-05-18 00:30 | 445 | 441
2018-05-18 01:00 | 438 | 434
2018-05-18 01:30 | 428 | 423
2018-05-18 02:00 | 427 | 422
2018-05-18 02:30 | 417 | 411
2018-05-18 03:00 | 417 | 412
2018-05-18 03:30 | 421 | 415
2018-05-18 04:00 | 416 | 411
2018-05-18 04:30 | 414 | 409
2018-05-18 05:00 | 425 | 420
2018-05-18 05:30 | 447 | 442
2018-05-18 06:00 | 468 | 464
2018-05-18 06:30 | 497 | 494
2018-05-18 07:00 | 514 | 512
2018-05-18 07:30 | 551 | 549
2018-05-18 08:00 | 554 | 554
2018-05-18 08:30 | 495 | 494
2018-05-18 09:00 | 499 | 498
2018-05-18 09:30 | 470 | 469
2018-05-18 10:00 | 446 | 444
2018-05-18 10:30 | 435 | 433
2018-05-18 11:00 | 420 | 417
2018-05-18 11:30 | 412 | 409
2018-05-18 12:00 | 413 | 410
2018-05-18 12:30 | 430 | 427
2018-05-18 13:00 | 432 | 430
2018-05-18 13:30 | 439 | 436
2018-05-18 14:00 | 425 | 423
2018-05-18 14:30 | 436 | 434
2018-05-18 15:00 | 438 | 436
2018-05-18 15:30 | 462 | 460
2018-05-18 16:00 | 471 | 469
2018-05-18 16:30 | 459 | 458
2018-05-18 17:00 | 421 | 420
2018-05-18 17:30 | 495 | 494
2018-05-18 18:00 | 547 | 547
2018-05-18 18:30 | 567 | 566
2018-05-18 19:00 | 567 | 567
2018-05-18 19:30 | 553 | 553
2018-05-18 20:00 | 536 | 536
2018-05-18 20:30 | 541 | 541
2018-05-18 21:00 | 556 | 556
2018-05-18 21:30 | 545 | 545
2018-05-18 22:00 | 526 | 525
2018-05-18 22:30 | 506 | 505
2018-05-18 23:00 | 489 | 488
2018-05-18 23:30 | 470 | 468
2018-05-19 | 453 | 451
2018-05-19 00:30 | 442 | 440
2018-05-19 01:00 | 432 | 430
2018-05-19 01:30 | 422 | 420
2018-05-19 02:00 | 413 | 410
2018-05-19 02:30 | 412 | 410
2018-05-19 03:00 | 412 | 409
2018-05-19 03:30 | 406 | 403
2018-05-19 04:00 | 410 | 406
2018-05-19 04:30 | 408 | 404
2018-05-19 05:00 | 418 | 415
2018-05-19 05:30 | 421 | 418
2018-05-19 06:00 | 429 | 426
2018-05-19 06:30 | 438 | 436
2018-05-19 07:00 | 451 | 449
2018-05-19 07:30 | 464 | 462
2018-05-19 08:00 | 449 | 447
2018-05-19 08:30 | 449 | 447
2018-05-19 09:00 | 444 | 442
2018-05-19 09:30 | 445 | 443
2018-05-19 10:00 | 431 | 429
2018-05-19 10:30 | 413 | 410
2018-05-19 11:00 | 402 | 399
2018-05-19 11:30 | 390 | 386
2018-05-19 12:00 | 402 | 397
2018-05-19 12:30 | 417 | 413
2018-05-19 13:00 | 414 | 411
2018-05-19 13:30 | 407 | 404
2018-05-19 14:00 | 417 | 413
2018-05-19 14:30 | 423 | 420
2018-05-19 15:00 | 432 | 429
2018-05-19 15:30 | 446 | 443
2018-05-19 16:00 | 466 | 464
2018-05-19 16:30 | 489 | 488
2018-05-19 17:00 | 516 | 515
2018-05-19 17:30 | 547 | 546
2018-05-19 18:00 | 568 | 568
2018-05-19 18:30 | 587 | 587
2018-05-19 19:00 | 581 | 580
2018-05-19 19:30 | 559 | 559
2018-05-19 20:00 | 540 | 539
2018-05-19 20:30 | 526 | 525
2018-05-19 21:00 | 505 | 504
2018-05-19 21:30 | 484 | 483
2018-05-19 22:00 | 477 | 475
2018-05-19 22:30 | 463 | 461
2018-05-19 23:00 | 457 | 455
2018-05-19 23:30 | 462 | 459
2018-05-20 | 450 | 448
2018-05-20 00:30 | 434 | 431
2018-05-20 01:00 | 424 | 420
2018-05-20 01:30 | 413 | 409
2018-05-20 02:00 | 405 | 400
2018-05-20 02:30 | 397 | 393
2018-05-20 03:00 | 396 | 391
2018-05-20 03:30 | 396 | 392
2018-05-20 04:00 | 396 | 391
2018-05-20 04:30 | 400 | 395
2018-05-20 05:00 | 406 | 401
2018-05-20 05:30 | 409 | 404
2018-05-20 06:00 | 414 | 410
2018-05-20 06:30 | 427 | 423
2018-05-20 07:00 | 426 | 422
2018-05-20 07:30 | 434 | 430
2018-05-20 08:00 | 443 | 439
2018-05-20 08:30 | 443 | 440
2018-05-20 09:00 | 436 | 434
2018-05-20 09:30 | 426 | 424
2018-05-20 10:00 | 423 | 420
2018-05-20 10:30 | 412 | 409
2018-05-20 11:00 | 429 | 426
2018-05-20 11:30 | 402 | 399
2018-05-20 12:00 | 397 | 394
2018-05-20 12:30 | 394 | 390
2018-05-20 13:00 | 388 | 384
2018-05-20 13:30 | 391 | 387
2018-05-20 14:00 | 382 | 378
2018-05-20 14:30 | 410 | 406
2018-05-20 15:00 | 419 | 416
2018-05-20 15:30 | 423 | 419
2018-05-20 16:00 | 458 | 455
2018-05-20 16:30 | 469 | 467
2018-05-20 17:00 | 476 | 475
2018-05-20 17:30 | 514 | 513
2018-05-20 18:00 | 563 | 562
2018-05-20 18:30 | 590 | 590
2018-05-20 19:00 | 591 | 590
2018-05-20 19:30 | 574 | 574
2018-05-20 20:00 | 554 | 553
2018-05-20 20:30 | 549 | 548
2018-05-20 21:00 | 528 | 527
2018-05-20 21:30 | 529 | 528
2018-05-20 22:00 | 516 | 515
2018-05-20 22:30 | 490 | 490
2018-05-20 23:00 | 470 | 469
2018-05-20 23:30 | 452 | 450
2018-05-21 | 435 | 432
2018-05-21 00:30 | 400 | 397
2018-05-21 01:00 | 423 | 419
2018-05-21 01:30 | 414 | 411
2018-05-21 02:00 | 412 | 408
2018-05-21 02:30 | 406 | 402
2018-05-21 03:00 | 406 | 402
2018-05-21 03:30 | 404 | 399
2018-05-21 04:00 | 411 | 406
2018-05-21 04:30 | 417 | 413
2018-05-21 05:00 | 426 | 422
2018-05-21 05:30 | 441 | 437
2018-05-21 06:00 | 459 | 456
2018-05-21 06:30 | 492 | 490
2018-05-21 07:00 | 520 | 519
2018-05-21 07:30 | 546 | 545
2018-05-21 08:00 | 543 | 543
2018-05-21 08:30 | 515 | 515
2018-05-21 09:00 | 482 | 480
2018-05-21 09:30 | 460 | 459
2018-05-21 10:00 | 450 | 448
2018-05-21 10:30 | 444 | 441
2018-05-21 11:00 | 442 | 439
2018-05-21 11:30 | 430 | 427
2018-05-21 12:00 | 432 | 429
2018-05-21 12:30 | 430 | 427
2018-05-21 13:00 | 438 | 435
2018-05-21 13:30 | 441 | 439
2018-05-21 14:00 | 446 | 443
2018-05-21 14:30 | 429 | 427
2018-05-21 15:00 | 446 | 444
2018-05-21 15:30 | 457 | 455
2018-05-21 16:00 | 488 | 486
2018-05-21 16:30 | 502 | 500
2018-05-21 17:00 | 515 | 514
2018-05-21 17:30 | 495 | 494
2018-05-21 18:00 | 511 | 510
2018-05-21 18:30 | 503 | 502
2018-05-21 19:00 | 530 | 530
2018-05-21 19:30 | 596 | 595
2018-05-21 20:00 | 580 | 580
2018-05-21 20:30 | 578 | 577
2018-05-21 21:00 | 561 | 560
2018-05-21 21:30 | 534 | 533
2018-05-21 22:00 | 507 | 505
2018-05-21 22:30 | 506 | 505
2018-05-21 23:00 | 491 | 489
2018-05-21 23:30 | 470 | 468
2018-05-22 | 450 | 448
2018-05-22 00:30 | 437 | 434
2018-05-22 01:00 | 426 | 422
2018-05-22 01:30 | 420 | 416
2018-05-22 02:00 | 414 | 410
2018-05-22 02:30 | 406 | 402
2018-05-22 03:00 | 407 | 402
2018-05-22 03:30 | 408 | 404
2018-05-22 04:00 | 405 | 400
2018-05-22 04:30 | 413 | 408
2018-05-22 05:00 | 425 | 421
2018-05-22 05:30 | 436 | 433
2018-05-22 06:00 | 455 | 451
2018-05-22 06:30 | 497 | 494
2018-05-22 07:00 | 498 | 496
2018-05-22 07:30 | 549 | 547
2018-05-22 08:00 | 541 | 540
2018-05-22 08:30 | 504 | 503
2018-05-22 09:00 | 472 | 471
2018-05-22 09:30 | 450 | 448
2018-05-22 10:00 | 430 | 427
2018-05-22 10:30 | 430 | 426
2018-05-22 11:00 | 373 | 369
2018-05-22 11:30 | 333 | 329
2018-05-22 12:00 | 396 | 390
2018-05-22 12:30 | 394 | 390
2018-05-22 13:00 | 397 | 393
2018-05-22 13:30 | 363 | 359
2018-05-22 14:00 | 379 | 374
2018-05-22 14:30 | 385 | 380
2018-05-22 15:00 | 396 | 391
2018-05-22 15:30 | 413 | 410
2018-05-22 16:00 | 437 | 434
2018-05-22 16:30 | 473 | 471
2018-05-22 17:00 | 502 | 501
2018-05-22 17:30 | 548 | 547
2018-05-22 18:00 | 563 | 562
2018-05-22 18:30 | 600 | 600
2018-05-22 19:00 | 605 | 605
2018-05-22 19:30 | 585 | 584
2018-05-22 20:00 | 565 | 565
2018-05-22 20:30 | 564 | 563
2018-05-22 21:00 | 570 | 570
2018-05-22 21:30 | 554 | 553
2018-05-22 22:00 | 520 | 520
2018-05-22 22:30 | 494 | 492
2018-05-22 23:00 | 474 | 472
2018-05-22 23:30 | 455 | 451
2018-05-23 | 442 | 438
2018-05-23 00:30 | 432 | 428
2018-05-23 01:00 | 423 | 418
2018-05-23 01:30 | 415 | 409
2018-05-23 02:00 | 410 | 404
2018-05-23 02:30 | 406 | 400
2018-05-23 03:00 | 401 | 395
2018-05-23 03:30 | 406 | 400
2018-05-23 04:00 | 405 | 399
2018-05-23 04:30 | 414 | 408
2018-05-23 05:00 | 423 | 417
2018-05-23 05:30 | 436 | 431
2018-05-23 06:00 | 455 | 450
2018-05-23 06:30 | 490 | 486
2018-05-23 07:00 | 458 | 455
2018-05-23 07:30 | 536 | 534
2018-05-23 08:00 | 512 | 511
2018-05-23 08:30 | 470 | 468
2018-05-23 09:00 | 433 | 430
2018-05-23 09:30 | 416 | 412
2018-05-23 10:00 | 397 | 393
2018-05-23 10:30 | 392 | 386
2018-05-23 11:00 | 393 | 387
2018-05-23 11:30 | 397 | 392
2018-05-23 12:00 | 393 | 388
2018-05-23 12:30 | 390 | 385
2018-05-23 13:00 | 385 | 380
2018-05-23 13:30 | 385 | 380
2018-05-23 14:00 | 390 | 385
2018-05-23 14:30 | 378 | 373
2018-05-23 15:00 | 388 | 383
2018-05-23 15:30 | 418 | 414
2018-05-23 16:00 | 436 | 433
2018-05-23 16:30 | 469 | 467
2018-05-23 17:00 | 507 | 505
2018-05-23 17:30 | 546 | 545
2018-05-23 18:00 | 582 | 582
2018-05-23 18:30 | 619 | 618
2018-05-23 19:00 | 622 | 622
2018-05-23 19:30 | 601 | 601
2018-05-23 20:00 | 583 | 583
2018-05-23 20:30 | 562 | 562
2018-05-23 21:00 | 538 | 538
2018-05-23 21:30 | 515 | 515
2018-05-23 22:00 | 492 | 491
2018-05-23 22:30 | 491 | 489
2018-05-23 23:00 | 472 | 471
2018-05-23 23:30 | 456 | 453
2018-05-24 | 440 | 437
2018-05-24 00:30 | 426 | 423
2018-05-24 01:00 | 417 | 412
2018-05-24 01:30 | 408 | 402
2018-05-24 02:00 | 405 | 400
2018-05-24 02:30 | 397 | 391
2018-05-24 03:00 | 372 | 366
2018-05-24 03:30 | 395 | 389
2018-05-24 04:00 | 406 | 401
2018-05-24 04:30 | 419 | 415
2018-05-24 05:00 | 426 | 422
2018-05-24 05:30 | 437 | 433
2018-05-24 06:00 | 456 | 452
2018-05-24 06:30 | 490 | 487
2018-05-24 07:00 | 483 | 482
2018-05-24 07:30 | 543 | 541
2018-05-24 08:00 | 537 | 536
2018-05-24 08:30 | 511 | 511
2018-05-24 09:00 | 477 | 476
2018-05-24 09:30 | 475 | 473
2018-05-24 10:00 | 445 | 443
2018-05-24 10:30 | 441 | 439
2018-05-24 11:00 | 430 | 428
2018-05-24 11:30 | 435 | 433
2018-05-24 12:00 | 432 | 429
2018-05-24 12:30 | 451 | 448
2018-05-24 13:00 | 443 | 441
2018-05-24 13:30 | 434 | 432
2018-05-24 14:00 | 427 | 424
2018-05-24 14:30 | 444 | 441
2018-05-24 15:00 | 465 | 463
2018-05-24 15:30 | 472 | 470
2018-05-24 16:00 | 504 | 502
2018-05-24 16:30 | 520 | 519
2018-05-24 17:00 | 537 | 536
2018-05-24 17:30 | 558 | 557
2018-05-24 18:00 | 589 | 589
2018-05-24 18:30 | 616 | 615
2018-05-24 19:00 | 623 | 623
2018-05-24 19:30 | 608 | 608
2018-05-24 20:00 | 597 | 597
2018-05-24 20:30 | 575 | 575
2018-05-24 21:00 | 547 | 547
2018-05-24 21:30 | 520 | 520
2018-05-24 22:00 | 491 | 490
2018-05-24 22:30 | 468 | 467
2018-05-24 23:00 | 445 | 444
2018-05-24 23:30 | 429 | 427
2018-05-25 | 413 | 410
2018-05-25 00:30 | 423 | 420
2018-05-25 01:00 | 420 | 418
2018-05-25 01:30 | 413 | 410
2018-05-25 02:00 | 405 | 402
2018-05-25 02:30 | 405 | 401
2018-05-25 03:00 | 407 | 403
2018-05-25 03:30 | 404 | 400
2018-05-25 04:00 | 407 | 402
2018-05-25 04:30 | 409 | 405
2018-05-25 05:00 | 415 | 411
2018-05-25 05:30 | 435 | 432
2018-05-25 06:00 | 455 | 452
2018-05-25 06:30 | 487 | 485
2018-05-25 07:00 | 520 | 518
2018-05-25 07:30 | 558 | 556
2018-05-25 08:00 | 550 | 550
2018-05-25 08:30 | 543 | 543
2018-05-25 09:00 | 524 | 524
2018-05-25 09:30 | 513 | 512
2018-05-25 10:00 | 476 | 475
2018-05-25 10:30 | 468 | 466
2018-05-25 11:00 | 444 | 442
2018-05-25 11:30 | 442 | 440
2018-05-25 12:00 | 456 | 453
2018-05-25 12:30 | 448 | 446
2018-05-25 13:00 | 444 | 442
2018-05-25 13:30 | 461 | 459
2018-05-25 14:00 | 451 | 449
2018-05-25 14:30 | 456 | 453
2018-05-25 15:00 | 442 | 440
2018-05-25 15:30 | 447 | 444
2018-05-25 16:00 | 468 | 465
2018-05-25 16:30 | 478 | 476
2018-05-25 17:00 | 506 | 504
2018-05-25 17:30 | 532 | 531
2018-05-25 18:00 | 531 | 530
2018-05-25 18:30 | 571 | 570
2018-05-25 19:00 | 570 | 569
2018-05-25 19:30 | 547 | 547
2018-05-25 20:00 | 529 | 528
2018-05-25 20:30 | 530 | 529
2018-05-25 21:00 | 516 | 515
2018-05-25 21:30 | 501 | 500
2018-05-25 22:00 | 487 | 485
2018-05-25 22:30 | 491 | 489
2018-05-25 23:00 | 478 | 477
2018-05-25 23:30 | 458 | 456
2018-05-26 | 443 | 441
2018-05-26 00:30 | 435 | 433
2018-05-26 01:00 | 421 | 418
2018-05-26 01:30 | 412 | 409
2018-05-26 02:00 | 406 | 403
2018-05-26 02:30 | 405 | 401
2018-05-26 03:00 | 398 | 394
2018-05-26 03:30 | 392 | 388
2018-05-26 04:00 | 391 | 387
2018-05-26 04:30 | 395 | 390
2018-05-26 05:00 | 400 | 396
2018-05-26 05:30 | 408 | 404
2018-05-26 06:00 | 410 | 406
2018-05-26 06:30 | 419 | 416
2018-05-26 07:00 | 436 | 433
2018-05-26 07:30 | 453 | 450
2018-05-26 08:00 | 461 | 459
2018-05-26 08:30 | 464 | 462
2018-05-26 09:00 | 459 | 457
2018-05-26 09:30 | 444 | 442
2018-05-26 10:00 | 387 | 383
2018-05-26 10:30 | 364 | 359
2018-05-26 11:00 | 398 | 392
2018-05-26 11:30 | 389 | 385
2018-05-26 12:00 | 391 | 386
2018-05-26 12:30 | 392 | 387
2018-05-26 13:00 | 404 | 400
2018-05-26 13:30 | 395 | 391
2018-05-26 14:00 | 370 | 365
2018-05-26 14:30 | 363 | 358
2018-05-26 15:00 | 369 | 364
2018-05-26 15:30 | 391 | 386
2018-05-26 16:00 | 408 | 403
2018-05-26 16:30 | 447 | 444
2018-05-26 17:00 | 475 | 473
2018-05-26 17:30 | 512 | 511
2018-05-26 18:00 | 545 | 544
2018-05-26 18:30 | 570 | 570
2018-05-26 19:00 | 569 | 568
2018-05-26 19:30 | 570 | 569
2018-05-26 20:00 | 565 | 565
2018-05-26 20:30 | 541 | 541
2018-05-26 21:00 | 526 | 525
2018-05-26 21:30 | 519 | 518
2018-05-26 22:00 | 501 | 500
2018-05-26 22:30 | 479 | 478
2018-05-26 23:00 | 464 | 462
2018-05-26 23:30 | 447 | 445
2018-05-27 | 436 | 434
2018-05-27 00:30 | 425 | 422
2018-05-27 01:00 | 414 | 411
2018-05-27 01:30 | 404 | 401
2018-05-27 02:00 | 398 | 394
2018-05-27 02:30 | 397 | 392
2018-05-27 03:00 | 393 | 388
2018-05-27 03:30 | 390 | 385
2018-05-27 04:00 | 361 | 356
2018-05-27 04:30 | 385 | 380
2018-05-27 05:00 | 390 | 385
2018-05-27 05:30 | 395 | 391
2018-05-27 06:00 | 399 | 395
2018-05-27 06:30 | 403 | 398
2018-05-27 07:00 | 412 | 408
2018-05-27 07:30 | 420 | 416
2018-05-27 08:00 | 386 | 383
2018-05-27 08:30 | 366 | 362
2018-05-27 09:00 | 375 | 370
2018-05-27 09:30 | 381 | 376
2018-05-27 10:00 | 373 | 368
2018-05-27 10:30 | 374 | 368
2018-05-27 11:00 | 363 | 357
2018-05-27 11:30 | 363 | 357
2018-05-27 12:00 | 364 | 358
2018-05-27 12:30 | 354 | 348
2018-05-27 13:00 | 348 | 341
2018-05-27 13:30 | 354 | 347
2018-05-27 14:00 | 361 | 355
2018-05-27 14:30 | 349 | 343
2018-05-27 15:00 | 356 | 350
2018-05-27 15:30 | 376 | 370
2018-05-27 16:00 | 415 | 410
2018-05-27 16:30 | 430 | 426
2018-05-27 17:00 | 482 | 479
2018-05-27 17:30 | 537 | 535
2018-05-27 18:00 | 576 | 575
2018-05-27 18:30 | 609 | 609
2018-05-27 19:00 | 603 | 603
2018-05-27 19:30 | 581 | 581
2018-05-27 20:00 | 559 | 559
2018-05-27 20:30 | 539 | 539
2018-05-27 21:00 | 521 | 520
2018-05-27 21:30 | 498 | 497
2018-05-27 22:00 | 477 | 476
2018-05-27 22:30 | 475 | 473
2018-05-27 23:00 | 464 | 462
2018-05-27 23:30 | 443 | 441
2018-05-28 | 429 | 427
2018-05-28 00:30 | 422 | 419
2018-05-28 01:00 | 419 | 416
2018-05-28 01:30 | 415 | 411
2018-05-28 02:00 | 403 | 400
2018-05-28 02:30 | 398 | 393
2018-05-28 03:00 | 393 | 388
2018-05-28 03:30 | 392 | 388
2018-05-28 04:00 | 396 | 391
2018-05-28 04:30 | 399 | 395
2018-05-28 05:00 | 404 | 399
2018-05-28 05:30 | 418 | 414
2018-05-28 06:00 | 440 | 436
2018-05-28 06:30 | 481 | 479
2018-05-28 07:00 | 513 | 511
2018-05-28 07:30 | 543 | 542
2018-05-28 08:00 | 538 | 538
2018-05-28 08:30 | 511 | 511
2018-05-28 09:00 | 501 | 500
2018-05-28 09:30 | 483 | 482
2018-05-28 10:00 | 476 | 474
2018-05-28 10:30 | 467 | 465
2018-05-28 11:00 | 423 | 421
2018-05-28 11:30 | 371 | 367
2018-05-28 12:00 | 390 | 385
2018-05-28 12:30 | 388 | 383
2018-05-28 13:00 | 393 | 388
2018-05-28 13:30 | 363 | 358
2018-05-28 14:00 | 328 | 321
2018-05-28 14:30 | 306 | 297
2018-05-28 15:00 | 254 | 242
2018-05-28 15:30 | 272 | 259
2018-05-28 16:00 | 287 | 275
2018-05-28 16:30 | 301 | 291
2018-05-28 17:00 | 303 | 294
2018-05-28 17:30 | 300 | 291
2018-05-28 18:00 | 347 | 339
2018-05-28 18:30 | 373 | 368
2018-05-28 19:00 | 377 | 373
2018-05-28 19:30 | 359 | 355
2018-05-28 20:00 | 339 | 334
2018-05-28 20:30 | 318 | 312
2018-05-28 21:00 | 321 | 314
2018-05-28 21:30 | 328 | 321
2018-05-28 22:00 | 307 | 299
2018-05-28 22:30 | 284 | 274
2018-05-28 23:00 | 328 | 318
2018-05-28 23:30 | 369 | 362
2018-05-29 | 433 | 429
2018-05-29 00:30 | 425 | 422
2018-05-29 01:00 | 415 | 412
2018-05-29 01:30 | 410 | 407
2018-05-29 02:00 | 409 | 405
2018-05-29 02:30 | 401 | 397
2018-05-29 03:00 | 403 | 399
2018-05-29 03:30 | 403 | 399
2018-05-29 04:00 | 396 | 392
2018-05-29 04:30 | 401 | 397
2018-05-29 05:00 | 410 | 406
2018-05-29 05:30 | 429 | 425
2018-05-29 06:00 | 446 | 442
2018-05-29 06:30 | 448 | 445
2018-05-29 07:00 | 453 | 450
2018-05-29 07:30 | 485 | 482
2018-05-29 08:00 | 500 | 498
2018-05-29 08:30 | 500 | 499
2018-05-29 09:00 | 470 | 469
2018-05-29 09:30 | 460 | 458
2018-05-29 10:00 | 455 | 453
2018-05-29 10:30 | 466 | 464
2018-05-29 11:00 | 453 | 451
2018-05-29 11:30 | 453 | 451
2018-05-29 12:00 | 447 | 444
2018-05-29 12:30 | 454 | 451
2018-05-29 13:00 | 459 | 456
2018-05-29 13:30 | 458 | 456
2018-05-29 14:00 | 438 | 436
2018-05-29 14:30 | 425 | 423
2018-05-29 15:00 | 414 | 411
2018-05-29 15:30 | 426 | 423
2018-05-29 16:00 | 457 | 454
2018-05-29 16:30 | 495 | 493
2018-05-29 17:00 | 523 | 522
2018-05-29 17:30 | 566 | 565
2018-05-29 18:00 | 530 | 530
2018-05-29 18:30 | 573 | 572
2018-05-29 19:00 | 582 | 581
2018-05-29 19:30 | 614 | 614
2018-05-29 20:00 | 617 | 617
2018-05-29 20:30 | 593 | 593
2018-05-29 21:00 | 569 | 569
2018-05-29 21:30 | 549 | 549
2018-05-29 22:00 | 529 | 528
2018-05-29 22:30 | 501 | 500
2018-05-29 23:00 | 478 | 476
2018-05-29 23:30 | 454 | 453
2018-05-30 | 437 | 434
2018-05-30 00:30 | 421 | 418
2018-05-30 01:00 | 411 | 408
2018-05-30 01:30 | 406 | 402
2018-05-30 02:00 | 402 | 398
2018-05-30 02:30 | 397 | 393
2018-05-30 03:00 | 394 | 389
2018-05-30 03:30 | 377 | 372
2018-05-30 04:00 | 391 | 386
2018-05-30 04:30 | 398 | 393
2018-05-30 05:00 | 405 | 400
2018-05-30 05:30 | 416 | 412
2018-05-30 06:00 | 439 | 435
2018-05-30 06:30 | 482 | 479
2018-05-30 07:00 | 509 | 508
2018-05-30 07:30 | 533 | 532
2018-05-30 08:00 | 512 | 511
2018-05-30 08:30 | 474 | 472
2018-05-30 09:00 | 444 | 442
2018-05-30 09:30 | 421 | 418
2018-05-30 10:00 | 402 | 398
2018-05-30 10:30 | 390 | 385
2018-05-30 11:00 | 375 | 370
2018-05-30 11:30 | 370 | 365
2018-05-30 12:00 | 353 | 347
2018-05-30 12:30 | 327 | 319
2018-05-30 13:00 | 329 | 320
2018-05-30 13:30 | 337 | 329
2018-05-30 14:00 | 324 | 316
2018-05-30 14:30 | 335 | 327
2018-05-30 15:00 | 395 | 389
2018-05-30 15:30 | 389 | 385
2018-05-30 16:00 | 423 | 419
2018-05-30 16:30 | 460 | 457
2018-05-30 17:00 | 503 | 501
2018-05-30 17:30 | 542 | 541
2018-05-30 18:00 | 579 | 579
2018-05-30 18:30 | 611 | 611
2018-05-30 19:00 | 615 | 615
2018-05-30 19:30 | 604 | 604
2018-05-30 20:00 | 578 | 577
2018-05-30 20:30 | 551 | 551
2018-05-30 21:00 | 535 | 534
2018-05-30 21:30 | 524 | 523
2018-05-30 22:00 | 501 | 500
2018-05-30 22:30 | 490 | 489
2018-05-30 23:00 | 468 | 467
2018-05-30 23:30 | 449 | 447
2018-05-31 | 432 | 429
2018-05-31 00:30 | 421 | 418
2018-05-31 01:00 | 407 | 403
2018-05-31 01:30 | 400 | 395
2018-05-31 02:00 | 393 | 388
2018-05-31 02:30 | 388 | 384
2018-05-31 03:00 | 387 | 382
2018-05-31 03:30 | 388 | 383
2018-05-31 04:00 | 389 | 384
2018-05-31 04:30 | 395 | 390
2018-05-31 05:00 | 397 | 393
2018-05-31 05:30 | 416 | 412
2018-05-31 06:00 | 439 | 436
2018-05-31 06:30 | 479 | 477
2018-05-31 07:00 | 501 | 500
2018-05-31 07:30 | 495 | 494
2018-05-31 08:00 | 470 | 469
2018-05-31 08:30 | 451 | 449
2018-05-31 09:00 | 424 | 422
2018-05-31 09:30 | 402 | 399
2018-05-31 10:00 | 376 | 372
2018-05-31 10:30 | 370 | 365
2018-05-31 11:00 | 357 | 352
2018-05-31 11:30 | 357 | 351
2018-05-31 12:00 | 356 | 350
2018-05-31 12:30 | 353 | 347
2018-05-31 13:00 | 350 | 344
2018-05-31 13:30 | 361 | 355
2018-05-31 14:00 | 370 | 364
2018-05-31 14:30 | 331 | 325
2018-05-31 15:00 | 301 | 293
2018-05-31 15:30 | 330 | 322
2018-05-31 16:00 | 347 | 340
2018-05-31 16:30 | 370 | 364
2018-05-31 17:00 | 393 | 389
2018-05-31 17:30 | 378 | 374
2018-05-31 18:00 | 336 | 332
2018-05-31 18:30 | 368 | 362
2018-05-31 19:00 | 373 | 368
2018-05-31 19:30 | 358 | 353
2018-05-31 20:00 | 356 | 351
2018-05-31 20:30 | 360 | 354
2018-05-31 21:00 | 364 | 359
2018-05-31 21:30 | 408 | 403
2018-05-31 22:00 | 395 | 391
2018-05-31 22:30 | 368 | 364
2018-05-31 23:00 | 349 | 343
2018-05-31 23:30 | 329 | 322
2018-06-01 | 314 | 306
2018-06-01 00:30 | 302 | 293
2018-06-01 01:00 | 293 | 283
2018-06-01 01:30 | 329 | 320
2018-06-01 02:00 | 401 | 394
2018-06-01 02:30 | 397 | 393
2018-06-01 03:00 | 393 | 389
2018-06-01 03:30 | 393 | 390
2018-06-01 04:00 | 398 | 394
2018-06-01 04:30 | 407 | 404
2018-06-01 05:00 | 405 | 402
2018-06-01 05:30 | 393 | 389
2018-06-01 06:00 | 407 | 403
2018-06-01 06:30 | 432 | 428
2018-06-01 07:00 | 450 | 448
2018-06-01 07:30 | 468 | 466
2018-06-01 08:00 | 466 | 464
2018-06-01 08:30 | 453 | 452
2018-06-01 09:00 | 421 | 419
2018-06-01 09:30 | 391 | 388
2018-06-01 10:00 | 367 | 363
2018-06-01 10:30 | 348 | 344
2018-06-01 11:00 | 335 | 329
2018-06-01 11:30 | 327 | 322
2018-06-01 12:00 | 324 | 318
2018-06-01 12:30 | 322 | 316
2018-06-01 13:00 | 317 | 311
2018-06-01 13:30 | 319 | 312
2018-06-01 14:00 | 317 | 310
2018-06-01 14:30 | 323 | 316
2018-06-01 15:00 | 331 | 325
2018-06-01 15:30 | 348 | 343
2018-06-01 16:00 | 369 | 365
2018-06-01 16:30 | 404 | 401
2018-06-01 17:00 | 456 | 454
2018-06-01 17:30 | 492 | 490
2018-06-01 18:00 | 508 | 508
2018-06-01 18:30 | 540 | 540
2018-06-01 19:00 | 546 | 546
2018-06-01 19:30 | 529 | 528
2018-06-01 20:00 | 507 | 507
2018-06-01 20:30 | 494 | 493
2018-06-01 21:00 | 480 | 479
2018-06-01 21:30 | 463 | 461
2018-06-01 22:00 | 445 | 443
2018-06-01 22:30 | 417 | 415
2018-06-01 23:00 | 425 | 422
2018-06-01 23:30 | 437 | 434
2018-06-02 | 424 | 421
2018-06-02 00:30 | 408 | 405
2018-06-02 01:00 | 397 | 393
2018-06-02 01:30 | 394 | 390
2018-06-02 02:00 | 390 | 385
2018-06-02 02:30 | 382 | 377
2018-06-02 03:00 | 378 | 373
2018-06-02 03:30 | 374 | 369
2018-06-02 04:00 | 377 | 372
2018-06-02 04:30 | 382 | 377
2018-06-02 05:00 | 387 | 383
2018-06-02 05:30 | 399 | 394
2018-06-02 06:00 | 407 | 402
2018-06-02 06:30 | 420 | 416
2018-06-02 07:00 | 422 | 419
2018-06-02 07:30 | 402 | 398
2018-06-02 08:00 | 377 | 374
2018-06-02 08:30 | 333 | 328
2018-06-02 09:00 | 332 | 326
2018-06-02 09:30 | 315 | 308
2018-06-02 10:00 | 303 | 295
2018-06-02 10:30 | 290 | 280
2018-06-02 11:00 | 301 | 290
2018-06-02 11:30 | 288 | 278
2018-06-02 12:00 | 274 | 262
2018-06-02 12:30 | 265 | 251
2018-06-02 13:00 | 266 | 252
2018-06-02 13:30 | 268 | 253
2018-06-02 14:00 | 270 | 256
2018-06-02 14:30 | 286 | 273
2018-06-02 15:00 | 299 | 288
2018-06-02 15:30 | 315 | 304
2018-06-02 16:00 | 341 | 333
2018-06-02 16:30 | 378 | 372
2018-06-02 17:00 | 434 | 429
2018-06-02 17:30 | 487 | 484
2018-06-02 18:00 | 502 | 501
2018-06-02 18:30 | 532 | 532
2018-06-02 19:00 | 530 | 530
2018-06-02 19:30 | 511 | 511
2018-06-02 20:00 | 486 | 486
2018-06-02 20:30 | 473 | 471
2018-06-02 21:00 | 454 | 452
2018-06-02 21:30 | 441 | 439
2018-06-02 22:00 | 427 | 425
2018-06-02 22:30 | 457 | 455
2018-06-02 23:00 | 444 | 442
2018-06-02 23:30 | 434 | 432
2018-06-03 | 421 | 419
2018-06-03 00:30 | 409 | 406
2018-06-03 01:00 | 400 | 396
2018-06-03 01:30 | 398 | 394
2018-06-03 02:00 | 393 | 389
2018-06-03 02:30 | 386 | 382
2018-06-03 03:00 | 382 | 377
2018-06-03 03:30 | 384 | 379
2018-06-03 04:00 | 388 | 383
2018-06-03 04:30 | 386 | 381
2018-06-03 05:00 | 391 | 386
2018-06-03 05:30 | 392 | 387
2018-06-03 06:00 | 399 | 394
2018-06-03 06:30 | 404 | 400
2018-06-03 07:00 | 398 | 395
2018-06-03 07:30 | 381 | 377
2018-06-03 08:00 | 348 | 343
2018-06-03 08:30 | 322 | 315
2018-06-03 09:00 | 306 | 298
2018-06-03 09:30 | 297 | 287
2018-06-03 10:00 | 287 | 277
2018-06-03 10:30 | 280 | 268
2018-06-03 11:00 | 268 | 255
2018-06-03 11:30 | 262 | 247
2018-06-03 12:00 | 266 | 251
2018-06-03 12:30 | 256 | 242
2018-06-03 13:00 | 255 | 241
2018-06-03 13:30 | 256 | 242
2018-06-03 14:00 | 246 | 231
2018-06-03 14:30 | 240 | 225
2018-06-03 15:00 | 252 | 236
2018-06-03 15:30 | 271 | 257
2018-06-03 16:00 | 299 | 289
2018-06-03 16:30 | 344 | 337
2018-06-03 17:00 | 399 | 394
2018-06-03 17:30 | 468 | 466
2018-06-03 18:00 | 516 | 515
2018-06-03 18:30 | 552 | 552
2018-06-03 19:00 | 559 | 559
2018-06-03 19:30 | 540 | 540
2018-06-03 20:00 | 518 | 518
2018-06-03 20:30 | 484 | 484
2018-06-03 21:00 | 459 | 458
2018-06-03 21:30 | 456 | 455
2018-06-03 22:00 | 438 | 436
2018-06-03 22:30 | 461 | 459
2018-06-03 23:00 | 445 | 443
2018-06-03 23:30 | 427 | 424
2018-06-04 | 415 | 412
2018-06-04 00:30 | 406 | 402
2018-06-04 01:00 | 397 | 393
2018-06-04 01:30 | 390 | 386
2018-06-04 02:00 | 386 | 381
2018-06-04 02:30 | 380 | 375
2018-06-04 03:00 | 379 | 373
2018-06-04 03:30 | 377 | 372
2018-06-04 04:00 | 378 | 372
2018-06-04 04:30 | 388 | 383
2018-06-04 05:00 | 403 | 398
2018-06-04 05:30 | 393 | 388
2018-06-04 06:00 | 366 | 361
2018-06-04 06:30 | 397 | 391
2018-06-04 07:00 | 423 | 419
2018-06-04 07:30 | 425 | 422
2018-06-04 08:00 | 391 | 388
2018-06-04 08:30 | 330 | 326
2018-06-04 09:00 | 244 | 236
2018-06-04 09:30 | 141 | 116
2018-06-04 10:00 | 140 | 100
2018-06-04 10:30 | 133 | 90
2018-06-04 11:00 | 130 | 83
2018-06-04 11:30 | 128 | 79
2018-06-04 12:00 | 130 | 82
2018-06-04 12:30 | 124 | 73
2018-06-04 13:00 | 128 | 79
2018-06-04 13:30 | 125 | 77
2018-06-04 14:00 | 141 | 99
2018-06-04 14:30 | 183 | 155
2018-06-04 15:00 | 191 | 168
2018-06-04 15:30 | 205 | 185
2018-06-04 16:00 | 226 | 210
2018-06-04 16:30 | 253 | 241
2018-06-04 17:00 | 307 | 299
2018-06-04 17:30 | 290 | 284
2018-06-04 18:00 | 283 | 276
2018-06-04 18:30 | 340 | 334
2018-06-04 19:00 | 369 | 365
2018-06-04 19:30 | 347 | 344
2018-06-04 20:00 | 328 | 324
2018-06-04 20:30 | 301 | 296
2018-06-04 21:00 | 351 | 346
2018-06-04 21:30 | 343 | 339
2018-06-04 22:00 | 321 | 317
2018-06-04 22:30 | 339 | 334
2018-06-04 23:00 | 374 | 370
2018-06-04 23:30 | 434 | 431
2018-06-05 | 422 | 420
2018-06-05 00:30 | 405 | 402
2018-06-05 01:00 | 395 | 393
2018-06-05 01:30 | 393 | 390
2018-06-05 02:00 | 391 | 388
2018-06-05 02:30 | 389 | 385
2018-06-05 03:00 | 389 | 386
2018-06-05 03:30 | 392 | 387
2018-06-05 04:00 | 388 | 384
2018-06-05 04:30 | 392 | 388
2018-06-05 05:00 | 399 | 395
2018-06-05 05:30 | 418 | 415
2018-06-05 06:00 | 439 | 436
2018-06-05 06:30 | 469 | 467
2018-06-05 07:00 | 489 | 487
2018-06-05 07:30 | 476 | 475
2018-06-05 08:00 | 444 | 443
2018-06-05 08:30 | 399 | 398
2018-06-05 09:00 | 356 | 352
2018-06-05 09:30 | 319 | 314
2018-06-05 10:00 | 312 | 305
2018-06-05 10:30 | 301 | 293
2018-06-05 11:00 | 297 | 289
2018-06-05 11:30 | 292 | 283
2018-06-05 12:00 | 292 | 283
2018-06-05 12:30 | 287 | 277
2018-06-05 13:00 | 288 | 276
2018-06-05 13:30 | 295 | 281
2018-06-05 14:00 | 292 | 278
2018-06-05 14:30 | 258 | 241
2018-06-05 15:00 | 236 | 215
2018-06-05 15:30 | 241 | 217
2018-06-05 16:00 | 265 | 244
2018-06-05 16:30 | 264 | 244
2018-06-05 17:00 | 231 | 210
2018-06-05 17:30 | 201 | 175
2018-06-05 18:00 | 283 | 263
2018-06-05 18:30 | 311 | 297
2018-06-05 19:00 | 289 | 276
2018-06-05 19:30 | 285 | 272
2018-06-05 20:00 | 271 | 257
2018-06-05 20:30 | 363 | 352
2018-06-05 21:00 | 368 | 361
2018-06-05 21:30 | 354 | 346
2018-06-05 22:00 | 329 | 320
2018-06-05 22:30 | 328 | 318
2018-06-05 23:00 | 332 | 322
2018-06-05 23:30 | 317 | 306
2018-06-06 | 301 | 288
2018-06-06 00:30 | 291 | 277
2018-06-06 01:00 | 283 | 267
2018-06-06 01:30 | 277 | 260
2018-06-06 02:00 | 272 | 255
2018-06-06 02:30 | 266 | 247
2018-06-06 03:00 | 263 | 243
2018-06-06 03:30 | 263 | 243
2018-06-06 04:00 | 265 | 245
2018-06-06 04:30 | 271 | 251
2018-06-06 05:00 | 281 | 262
2018-06-06 05:30 | 296 | 279
2018-06-06 06:00 | 309 | 294
2018-06-06 06:30 | 277 | 262
2018-06-06 07:00 | 268 | 251
2018-06-06 07:30 | 282 | 264
2018-06-06 08:00 | 209 | 187
2018-06-06 08:30 | 194 | 164
2018-06-06 09:00 | 187 | 151
2018-06-06 09:30 | 160 | 113
2018-06-06 10:00 | 153 | 98
2018-06-06 10:30 | 195 | 154
2018-06-06 11:00 | 205 | 171
2018-06-06 11:30 | 207 | 175
2018-06-06 12:00 | 207 | 174
2018-06-06 12:30 | 204 | 169
2018-06-06 13:00 | 199 | 163
2018-06-06 13:30 | 202 | 166
2018-06-06 14:00 | 194 | 157
2018-06-06 14:30 | 198 | 161
2018-06-06 15:00 | 143 | 86
2018-06-06 15:30 | 153 | 94
2018-06-06 16:00 | 167 | 115
2018-06-06 16:30 | 194 | 152
2018-06-06 17:00 | 240 | 211
2018-06-06 17:30 | 277 | 257
2018-06-06 18:00 | 313 | 298
2018-06-06 18:30 | 349 | 338
2018-06-06 19:00 | 355 | 345
2018-06-06 19:30 | 343 | 334
2018-06-06 20:00 | 322 | 311
2018-06-06 20:30 | 297 | 283
2018-06-06 21:00 | 271 | 256
2018-06-06 21:30 | 262 | 243
2018-06-06 22:00 | 287 | 269
2018-06-06 22:30 | 313 | 298
2018-06-06 23:00 | 382 | 371
2018-06-06 23:30 | 445 | 438
2018-06-07 | 429 | 425
2018-06-07 00:30 | 415 | 409
2018-06-07 01:00 | 399 | 393
2018-06-07 01:30 | 393 | 386
2018-06-07 02:00 | 391 | 384
2018-06-07 02:30 | 386 | 379
2018-06-07 03:00 | 384 | 376
2018-06-07 03:30 | 385 | 378
2018-06-07 04:00 | 393 | 385
2018-06-07 04:30 | 399 | 392
2018-06-07 05:00 | 409 | 403
2018-06-07 05:30 | 425 | 420
2018-06-07 06:00 | 440 | 435
2018-06-07 06:30 | 474 | 470
2018-06-07 07:00 | 496 | 493
2018-06-07 07:30 | 494 | 491
2018-06-07 08:00 | 468 | 465
2018-06-07 08:30 | 418 | 413
2018-06-07 09:00 | 389 | 382
2018-06-07 09:30 | 368 | 360
2018-06-07 10:00 | 342 | 334
2018-06-07 10:30 | 321 | 312
2018-06-07 11:00 | 325 | 316
2018-06-07 11:30 | 316 | 308
2018-06-07 12:00 | 318 | 306
2018-06-07 12:30 | 319 | 308
2018-06-07 13:00 | 318 | 307
2018-06-07 13:30 | 325 | 313
2018-06-07 14:00 | 306 | 294
2018-06-07 14:30 | 295 | 283
2018-06-07 15:00 | 308 | 295
2018-06-07 15:30 | 320 | 308
2018-06-07 16:00 | 347 | 337
2018-06-07 16:30 | 385 | 377
2018-06-07 17:00 | 417 | 411
2018-06-07 17:30 | 333 | 327
2018-06-07 18:00 | 287 | 277
2018-06-07 18:30 | 328 | 317
2018-06-07 19:00 | 327 | 319
2018-06-07 19:30 | 335 | 327
2018-06-07 20:00 | 330 | 322
2018-06-07 20:30 | 354 | 345
2018-06-07 21:00 | 346 | 338
2018-06-07 21:30 | 325 | 316
2018-06-07 22:00 | 295 | 284
2018-06-07 22:30 | 357 | 347
2018-06-07 23:00 | 439 | 433
2018-06-07 23:30 | 429 | 425
2018-06-08 | 414 | 410
2018-06-08 00:30 | 404 | 400
2018-06-08 01:00 | 395 | 389
2018-06-08 01:30 | 393 | 387
2018-06-08 02:00 | 388 | 381
2018-06-08 02:30 | 383 | 377
2018-06-08 03:00 | 376 | 369
2018-06-08 03:30 | 376 | 369
2018-06-08 04:00 | 380 | 373
2018-06-08 04:30 | 384 | 377
2018-06-08 05:00 | 394 | 387
2018-06-08 05:30 | 412 | 406
2018-06-08 06:00 | 425 | 420
2018-06-08 06:30 | 449 | 444
2018-06-08 07:00 | 478 | 475
2018-06-08 07:30 | 480 | 478
2018-06-08 08:00 | 456 | 453
2018-06-08 08:30 | 415 | 411
2018-06-08 09:00 | 383 | 378
2018-06-08 09:30 | 367 | 360
2018-06-08 10:00 | 348 | 339
2018-06-08 10:30 | 347 | 338
2018-06-08 11:00 | 339 | 329
2018-06-08 11:30 | 341 | 331
2018-06-08 12:00 | 342 | 332
2018-06-08 12:30 | 326 | 316
2018-06-08 13:00 | 329 | 318
2018-06-08 13:30 | 336 | 325
2018-06-08 14:00 | 326 | 315
2018-06-08 14:30 | 243 | 228
2018-06-08 15:00 | 198 | 172
2018-06-08 15:30 | 217 | 188
2018-06-08 16:00 | 226 | 199
2018-06-08 16:30 | 260 | 239
2018-06-08 17:00 | 294 | 278
2018-06-08 17:30 | 297 | 283
2018-06-08 18:00 | 309 | 296
2018-06-08 18:30 | 334 | 323
2018-06-08 19:00 | 333 | 324
2018-06-08 19:30 | 369 | 361
2018-06-08 20:00 | 365 | 358
2018-06-08 20:30 | 346 | 339
2018-06-08 21:00 | 333 | 324
2018-06-08 21:30 | 321 | 311
2018-06-08 22:00 | 298 | 287
2018-06-08 22:30 | 288 | 274
2018-06-08 23:00 | 391 | 380
2018-06-08 23:30 | 425 | 420
2018-06-09 | 412 | 407
2018-06-09 00:30 | 423 | 418
2018-06-09 01:00 | 408 | 403
2018-06-09 01:30 | 403 | 398
2018-06-09 02:00 | 399 | 394
2018-06-09 02:30 | 395 | 389
2018-06-09 03:00 | 396 | 390
2018-06-09 03:30 | 390 | 383
2018-06-09 04:00 | 391 | 385
2018-06-09 04:30 | 397 | 390
2018-06-09 05:00 | 404 | 398
2018-06-09 05:30 | 413 | 408
2018-06-09 06:00 | 416 | 411
2018-06-09 06:30 | 427 | 422
2018-06-09 07:00 | 434 | 429
2018-06-09 07:30 | 429 | 424
2018-06-09 08:00 | 416 | 411
2018-06-09 08:30 | 409 | 404
2018-06-09 09:00 | 411 | 405
2018-06-09 09:30 | 384 | 378
2018-06-09 10:00 | 388 | 380
2018-06-09 10:30 | 370 | 361
2018-06-09 11:00 | 355 | 346
2018-06-09 11:30 | 336 | 325
2018-06-09 12:00 | 338 | 326
2018-06-09 12:30 | 328 | 317
2018-06-09 13:00 | 350 | 339
2018-06-09 13:30 | 364 | 355
2018-06-09 14:00 | 360 | 351
2018-06-09 14:30 | 344 | 334
2018-06-09 15:00 | 360 | 350
2018-06-09 15:30 | 381 | 372
2018-06-09 16:00 | 399 | 391
2018-06-09 16:30 | 438 | 432
2018-06-09 17:00 | 384 | 379
2018-06-09 17:30 | 360 | 352
2018-06-09 18:00 | 390 | 382
2018-06-09 18:30 | 405 | 398
2018-06-09 19:00 | 399 | 392
2018-06-09 19:30 | 380 | 373
2018-06-09 20:00 | 362 | 354
2018-06-09 20:30 | 346 | 337
2018-06-09 21:00 | 335 | 324
2018-06-09 21:30 | 318 | 306
2018-06-09 22:00 | 309 | 296
2018-06-09 22:30 | 310 | 296
2018-06-09 23:00 | 322 | 309
2018-06-09 23:30 | 310 | 297
2018-06-10 | 409 | 399
2018-06-10 00:30 | 393 | 386
2018-06-10 01:00 | 409 | 402
2018-06-10 01:30 | 400 | 394
2018-06-10 02:00 | 396 | 390
2018-06-10 02:30 | 392 | 385
2018-06-10 03:00 | 389 | 381
2018-06-10 03:30 | 389 | 381
2018-06-10 04:00 | 390 | 382
2018-06-10 04:30 | 386 | 378
2018-06-10 05:00 | 388 | 380
2018-06-10 05:30 | 396 | 389
2018-06-10 06:00 | 400 | 393
2018-06-10 06:30 | 413 | 406
2018-06-10 07:00 | 410 | 404
2018-06-10 07:30 | 396 | 389
2018-06-10 08:00 | 379 | 372
2018-06-10 08:30 | 374 | 366
2018-06-10 09:00 | 365 | 356
2018-06-10 09:30 | 363 | 355
2018-06-10 10:00 | 340 | 331
2018-06-10 10:30 | 334 | 323
2018-06-10 11:00 | 329 | 317
2018-06-10 11:30 | 335 | 324
2018-06-10 12:00 | 335 | 323
2018-06-10 12:30 | 331 | 319
2018-06-10 13:00 | 321 | 309
2018-06-10 13:30 | 314 | 302
2018-06-10 14:00 | 300 | 287
2018-06-10 14:30 | 291 | 276
2018-06-10 15:00 | 307 | 292
2018-06-10 15:30 | 312 | 298
2018-06-10 16:00 | 339 | 327
2018-06-10 16:30 | 375 | 365
2018-06-10 17:00 | 425 | 418
2018-06-10 17:30 | 483 | 479
2018-06-10 18:00 | 525 | 523
2018-06-10 18:30 | 565 | 564
2018-06-10 19:00 | 573 | 572
2018-06-10 19:30 | 556 | 556
2018-06-10 20:00 | 533 | 532
2018-06-10 20:30 | 514 | 512
2018-06-10 21:00 | 493 | 491
2018-06-10 21:30 | 473 | 471
2018-06-10 22:00 | 453 | 450
2018-06-10 22:30 | 451 | 448
2018-06-10 23:00 | 461 | 458
2018-06-10 23:30 | 445 | 442
2018-06-11 | 433 | 430
2018-06-11 00:30 | 425 | 421
2018-06-11 01:00 | 411 | 405
2018-06-11 01:30 | 406 | 401
2018-06-11 02:00 | 393 | 387
2018-06-11 02:30 | 391 | 385
2018-06-11 03:00 | 389 | 382
2018-06-11 03:30 | 388 | 381
2018-06-11 04:00 | 392 | 385
2018-06-11 04:30 | 400 | 393
2018-06-11 05:00 | 404 | 397
2018-06-11 05:30 | 423 | 417
2018-06-11 06:00 | 439 | 434
2018-06-11 06:30 | 474 | 470
2018-06-11 07:00 | 502 | 498
2018-06-11 07:30 | 509 | 506
2018-06-11 08:00 | 491 | 488
2018-06-11 08:30 | 438 | 433
2018-06-11 09:00 | 405 | 398
2018-06-11 09:30 | 388 | 378
2018-06-11 10:00 | 363 | 352
2018-06-11 10:30 | 356 | 344
2018-06-11 11:00 | 352 | 339
2018-06-11 11:30 | 345 | 332
2018-06-11 12:00 | 348 | 336
2018-06-11 12:30 | 338 | 325
2018-06-11 13:00 | 334 | 321
2018-06-11 13:30 | 342 | 329
2018-06-11 14:00 | 338 | 324
2018-06-11 14:30 | 326 | 313
2018-06-11 15:00 | 340 | 326
2018-06-11 15:30 | 354 | 342
2018-06-11 16:00 | 386 | 375
2018-06-11 16:30 | 423 | 415
2018-06-11 17:00 | 471 | 465
2018-06-11 17:30 | 525 | 522
2018-06-11 18:00 | 561 | 559
2018-06-11 18:30 | 594 | 593
2018-06-11 19:00 | 601 | 600
2018-06-11 19:30 | 584 | 583
2018-06-11 20:00 | 561 | 560
2018-06-11 20:30 | 543 | 542
2018-06-11 21:00 | 520 | 518
2018-06-11 21:30 | 498 | 496
2018-06-11 22:00 | 472 | 469
2018-06-11 22:30 | 468 | 464
2018-06-11 23:00 | 470 | 466
2018-06-11 23:30 | 451 | 448
2018-06-12 | 437 | 433
2018-06-12 00:30 | 423 | 418
2018-06-12 01:00 | 417 | 411
2018-06-12 01:30 | 410 | 404
2018-06-12 02:00 | 404 | 398
2018-06-12 02:30 | 399 | 392
2018-06-12 03:00 | 399 | 392
2018-06-12 03:30 | 394 | 387
2018-06-12 04:00 | 390 | 383
2018-06-12 04:30 | 383 | 375
2018-06-12 05:00 | 398 | 390
2018-06-12 05:30 | 421 | 414
2018-06-12 06:00 | 441 | 435
2018-06-12 06:30 | 478 | 474
2018-06-12 07:00 | 507 | 503
2018-06-12 07:30 | 509 | 506
2018-06-12 08:00 | 491 | 489
2018-06-12 08:30 | 449 | 446
2018-06-12 09:00 | 406 | 401
2018-06-12 09:30 | 379 | 372
2018-06-12 10:00 | 359 | 350
2018-06-12 10:30 | 353 | 343
2018-06-12 11:00 | 344 | 333
2018-06-12 11:30 | 341 | 330
2018-06-12 12:00 | 343 | 331
2018-06-12 12:30 | 345 | 334
2018-06-12 13:00 | 342 | 331
2018-06-12 13:30 | 302 | 290
2018-06-12 14:00 | 303 | 288
2018-06-12 14:30 | 301 | 286
2018-06-12 15:00 | 353 | 341
2018-06-12 15:30 | 368 | 358
2018-06-12 16:00 | 396 | 388
2018-06-12 16:30 | 401 | 394
2018-06-12 17:00 | 446 | 440
2018-06-12 17:30 | 484 | 481
2018-06-12 18:00 | 534 | 531
2018-06-12 18:30 | 574 | 573
2018-06-12 19:00 | 576 | 575
2018-06-12 19:30 | 559 | 558
2018-06-12 20:00 | 538 | 537
2018-06-12 20:30 | 514 | 513
2018-06-12 21:00 | 484 | 483
2018-06-12 21:30 | 424 | 422
2018-06-12 22:00 | 444 | 438
2018-06-12 22:30 | 441 | 435
2018-06-12 23:00 | 445 | 440
2018-06-12 23:30 | 432 | 426
2018-06-13 | 412 | 405
2018-06-13 00:30 | 398 | 390
2018-06-13 01:00 | 388 | 379
2018-06-13 01:30 | 387 | 378
2018-06-13 02:00 | 382 | 372
2018-06-13 02:30 | 377 | 367
2018-06-13 03:00 | 374 | 363
2018-06-13 03:30 | 378 | 367
2018-06-13 04:00 | 382 | 371
2018-06-13 04:30 | 385 | 375
2018-06-13 05:00 | 390 | 380
2018-06-13 05:30 | 400 | 390
2018-06-13 06:00 | 417 | 409
2018-06-13 06:30 | 453 | 446
2018-06-13 07:00 | 477 | 472
2018-06-13 07:30 | 488 | 484
2018-06-13 08:00 | 480 | 476
2018-06-13 08:30 | 428 | 424
2018-06-13 09:00 | 393 | 388
2018-06-13 09:30 | 361 | 353
2018-06-13 10:00 | 356 | 347
2018-06-13 10:30 | 344 | 334
2018-06-13 11:00 | 330 | 319
2018-06-13 11:30 | 321 | 309
2018-06-13 12:00 | 331 | 318
2018-06-13 12:30 | 314 | 301
2018-06-13 13:00 | 330 | 316
2018-06-13 13:30 | 332 | 319
2018-06-13 14:00 | 319 | 307
2018-06-13 14:30 | 318 | 305
2018-06-13 15:00 | 315 | 302
2018-06-13 15:30 | 337 | 325
2018-06-13 16:00 | 360 | 350
2018-06-13 16:30 | 401 | 393
2018-06-13 17:00 | 447 | 442
2018-06-13 17:30 | 498 | 494
2018-06-13 18:00 | 537 | 534
2018-06-13 18:30 | 561 | 560
2018-06-13 19:00 | 568 | 567
2018-06-13 19:30 | 544 | 543
2018-06-13 20:00 | 524 | 522
2018-06-13 20:30 | 502 | 500
2018-06-13 21:00 | 479 | 477
2018-06-13 21:30 | 459 | 456
2018-06-13 22:00 | 440 | 437
2018-06-13 22:30 | 437 | 434
2018-06-13 23:00 | 447 | 444
2018-06-13 23:30 | 435 | 432
2018-06-14 | 417 | 413
2018-06-14 00:30 | 398 | 392
2018-06-14 01:00 | 388 | 382
2018-06-14 01:30 | 379 | 373
2018-06-14 02:00 | 371 | 364
2018-06-14 02:30 | 365 | 357
2018-06-14 03:00 | 367 | 358
2018-06-14 03:30 | 370 | 362
2018-06-14 04:00 | 364 | 356
2018-06-14 04:30 | 364 | 355
2018-06-14 05:00 | 374 | 366
2018-06-14 05:30 | 374 | 366
2018-06-14 06:00 | 352 | 344
2018-06-14 06:30 | 361 | 354
2018-06-14 07:00 | 401 | 395
2018-06-14 07:30 | 421 | 417
2018-06-14 08:00 | 401 | 397
2018-06-14 08:30 | 366 | 361
2018-06-14 09:00 | 336 | 329
2018-06-14 09:30 | 304 | 295
2018-06-14 10:00 | 292 | 280
2018-06-14 10:30 | 299 | 284
2018-06-14 11:00 | 264 | 246
2018-06-14 11:30 | 274 | 255
2018-06-14 12:00 | 269 | 249
2018-06-14 12:30 | 270 | 251
2018-06-14 13:00 | 247 | 226
2018-06-14 13:30 | 251 | 229
2018-06-14 14:00 | 259 | 239
2018-06-14 14:30 | 272 | 254
2018-06-14 15:00 | 275 | 258
2018-06-14 15:30 | 288 | 272
2018-06-14 16:00 | 302 | 287
2018-06-14 16:30 | 313 | 301
2018-06-14 17:00 | 358 | 348
2018-06-14 17:30 | 393 | 386
2018-06-14 18:00 | 435 | 430
2018-06-14 18:30 | 468 | 464
2018-06-14 19:00 | 473 | 470
2018-06-14 19:30 | 456 | 454
2018-06-14 20:00 | 459 | 456
2018-06-14 20:30 | 478 | 475
2018-06-14 21:00 | 463 | 461
2018-06-14 21:30 | 451 | 447
2018-06-14 22:00 | 439 | 436
2018-06-14 22:30 | 438 | 433
2018-06-14 23:00 | 445 | 441
2018-06-14 23:30 | 435 | 431
2018-06-15 | 427 | 422
2018-06-15 00:30 | 395 | 390
2018-06-15 01:00 | 378 | 371
2018-06-15 01:30 | 396 | 389
2018-06-15 02:00 | 392 | 385
2018-06-15 02:30 | 386 | 379
2018-06-15 03:00 | 384 | 377
2018-06-15 03:30 | 388 | 381
2018-06-15 04:00 | 386 | 379
2018-06-15 04:30 | 394 | 387
2018-06-15 05:00 | 407 | 400
2018-06-15 05:30 | 423 | 417
2018-06-15 06:00 | 431 | 426
2018-06-15 06:30 | 467 | 463
2018-06-15 07:00 | 506 | 503
2018-06-15 07:30 | 525 | 522
2018-06-15 08:00 | 480 | 479
2018-06-15 08:30 | 428 | 426
2018-06-15 09:00 | 399 | 395
2018-06-15 09:30 | 362 | 356
2018-06-15 10:00 | 340 | 332
2018-06-15 10:30 | 330 | 320
2018-06-15 11:00 | 321 | 310
2018-06-15 11:30 | 316 | 304
2018-06-15 12:00 | 323 | 310
2018-06-15 12:30 | 330 | 318
2018-06-15 13:00 | 300 | 286
2018-06-15 13:30 | 313 | 299
2018-06-15 14:00 | 322 | 310
2018-06-15 14:30 | 349 | 338
2018-06-15 15:00 | 353 | 343
2018-06-15 15:30 | 357 | 348
2018-06-15 16:00 | 370 | 362
2018-06-15 16:30 | 379 | 371
2018-06-15 17:00 | 433 | 427
2018-06-15 17:30 | 476 | 472
2018-06-15 18:00 | 513 | 510
2018-06-15 18:30 | 530 | 528
2018-06-15 19:00 | 536 | 535
2018-06-15 19:30 | 513 | 512
2018-06-15 20:00 | 526 | 525
2018-06-15 20:30 | 520 | 519
2018-06-15 21:00 | 511 | 509
2018-06-15 21:30 | 488 | 486
2018-06-15 22:00 | 462 | 460
2018-06-15 22:30 | 445 | 442
2018-06-15 23:00 | 453 | 450
2018-06-15 23:30 | 431 | 428
2018-06-16 | 414 | 410
2018-06-16 00:30 | 404 | 398
2018-06-16 01:00 | 404 | 398
2018-06-16 01:30 | 392 | 385
2018-06-16 02:00 | 384 | 377
2018-06-16 02:30 | 380 | 373
2018-06-16 03:00 | 380 | 372
2018-06-16 03:30 | 381 | 373
2018-06-16 04:00 | 376 | 368
2018-06-16 04:30 | 384 | 377
2018-06-16 05:00 | 392 | 386
2018-06-16 05:30 | 383 | 377
2018-06-16 06:00 | 387 | 381
2018-06-16 06:30 | 407 | 401
2018-06-16 07:00 | 408 | 403
2018-06-16 07:30 | 406 | 402
2018-06-16 08:00 | 415 | 410
2018-06-16 08:30 | 418 | 414
2018-06-16 09:00 | 387 | 382
2018-06-16 09:30 | 351 | 345
2018-06-16 10:00 | 377 | 370
2018-06-16 10:30 | 353 | 347
2018-06-16 11:00 | 320 | 312
2018-06-16 11:30 | 310 | 300
2018-06-16 12:00 | 304 | 293
2018-06-16 12:30 | 295 | 283
2018-06-16 13:00 | 277 | 264
2018-06-16 13:30 | 309 | 297
2018-06-16 14:00 | 322 | 311
2018-06-16 14:30 | 307 | 297
2018-06-16 15:00 | 295 | 284
2018-06-16 15:30 | 301 | 289
2018-06-16 16:00 | 329 | 318
2018-06-16 16:30 | 346 | 338
2018-06-16 17:00 | 399 | 393
2018-06-16 17:30 | 459 | 455
2018-06-16 18:00 | 486 | 484
2018-06-16 18:30 | 499 | 497
2018-06-16 19:00 | 491 | 490
2018-06-16 19:30 | 476 | 474
2018-06-16 20:00 | 461 | 459
2018-06-16 20:30 | 432 | 430
2018-06-16 21:00 | 419 | 416
2018-06-16 21:30 | 406 | 402
2018-06-16 22:00 | 395 | 390
2018-06-16 22:30 | 394 | 389
2018-06-16 23:00 | 401 | 396
2018-06-16 23:30 | 392 | 388
2018-06-17 | 370 | 365
2018-06-17 00:30 | 358 | 352
2018-06-17 01:00 | 349 | 343
2018-06-17 01:30 | 348 | 341
2018-06-17 02:00 | 350 | 342
2018-06-17 02:30 | 339 | 331
2018-06-17 03:00 | 332 | 323
2018-06-17 03:30 | 331 | 321
2018-06-17 04:00 | 326 | 316
2018-06-17 04:30 | 336 | 326
2018-06-17 05:00 | 336 | 327
2018-06-17 05:30 | 338 | 329
2018-06-17 06:00 | 345 | 337
2018-06-17 06:30 | 355 | 348
2018-06-17 07:00 | 356 | 349
2018-06-17 07:30 | 349 | 342
2018-06-17 08:00 | 348 | 340
2018-06-17 08:30 | 357 | 349
2018-06-17 09:00 | 347 | 339
2018-06-17 09:30 | 348 | 340
2018-06-17 10:00 | 334 | 325
2018-06-17 10:30 | 315 | 305
2018-06-17 11:00 | 292 | 280
2018-06-17 11:30 | 291 | 278
2018-06-17 12:00 | 288 | 274
2018-06-17 12:30 | 277 | 263
2018-06-17 13:00 | 266 | 250
2018-06-17 13:30 | 277 | 261
2018-06-17 14:00 | 283 | 268
2018-06-17 14:30 | 290 | 276
2018-06-17 15:00 | 291 | 278
2018-06-17 15:30 | 316 | 304
2018-06-17 16:00 | 328 | 318
2018-06-17 16:30 | 362 | 354
2018-06-17 17:00 | 396 | 390
2018-06-17 17:30 | 478 | 474
2018-06-17 18:00 | 520 | 518
2018-06-17 18:30 | 549 | 548
2018-06-17 19:00 | 523 | 522
2018-06-17 19:30 | 523 | 522
2018-06-17 20:00 | 506 | 505
2018-06-17 20:30 | 478 | 477
2018-06-17 21:00 | 457 | 455
2018-06-17 21:30 | 460 | 458
2018-06-17 22:00 | 451 | 448
2018-06-17 22:30 | 427 | 424
2018-06-17 23:00 | 423 | 420
2018-06-17 23:30 | 406 | 403
2018-06-18 | 397 | 392
2018-06-18 00:30 | 383 | 378
2018-06-18 01:00 | 372 | 367
2018-06-18 01:30 | 369 | 362
2018-06-18 02:00 | 371 | 364
2018-06-18 02:30 | 369 | 362
2018-06-18 03:00 | 366 | 359
2018-06-18 03:30 | 365 | 359
2018-06-18 04:00 | 364 | 357
2018-06-18 04:30 | 373 | 366
2018-06-18 05:00 | 381 | 374
2018-06-18 05:30 | 400 | 394
2018-06-18 06:00 | 410 | 405
2018-06-18 06:30 | 411 | 406
2018-06-18 07:00 | 377 | 372
2018-06-18 07:30 | 387 | 380
2018-06-18 08:00 | 243 | 234
2018-06-18 08:30 | 232 | 212
2018-06-18 09:00 | 335 | 320
2018-06-18 09:30 | 328 | 319
2018-06-18 10:00 | 307 | 298
2018-06-18 10:30 | 290 | 279
2018-06-18 11:00 | 282 | 268
2018-06-18 11:30 | 272 | 256
2018-06-18 12:00 | 265 | 247
2018-06-18 12:30 | 275 | 258
2018-06-18 13:00 | 277 | 261
2018-06-18 13:30 | 275 | 259
2018-06-18 14:00 | 287 | 272
2018-06-18 14:30 | 293 | 279
2018-06-18 15:00 | 303 | 290
2018-06-18 15:30 | 315 | 303
2018-06-18 16:00 | 337 | 327
2018-06-18 16:30 | 358 | 350
2018-06-18 17:00 | 415 | 409
2018-06-18 17:30 | 478 | 474
2018-06-18 18:00 | 505 | 504
2018-06-18 18:30 | 514 | 513
2018-06-18 19:00 | 553 | 551
2018-06-18 19:30 | 555 | 554
2018-06-18 20:00 | 527 | 526
2018-06-18 20:30 | 512 | 510
2018-06-18 21:00 | 474 | 472
2018-06-18 21:30 | 456 | 452
2018-06-18 22:00 | 428 | 424
2018-06-18 22:30 | 428 | 422
2018-06-18 23:00 | 435 | 430
2018-06-18 23:30 | 417 | 412
2018-06-19 | 397 | 392
2018-06-19 00:30 | 391 | 385
2018-06-19 01:00 | 376 | 368
2018-06-19 01:30 | 367 | 360
2018-06-19 02:00 | 366 | 358
2018-06-19 02:30 | 358 | 350
2018-06-19 03:00 | 359 | 351
2018-06-19 03:30 | 363 | 353
2018-06-19 04:00 | 360 | 351
2018-06-19 04:30 | 364 | 354
2018-06-19 05:00 | 373 | 365
2018-06-19 05:30 | 378 | 370
2018-06-19 06:00 | 391 | 384
2018-06-19 06:30 | 434 | 427
2018-06-19 07:00 | 340 | 335
2018-06-19 07:30 | 349 | 339
2018-06-19 08:00 | 400 | 392
2018-06-19 08:30 | 372 | 366
2018-06-19 09:00 | 323 | 315
2018-06-19 09:30 | 306 | 294
2018-06-19 10:00 | 280 | 267
2018-06-19 10:30 | 268 | 251
2018-06-19 11:00 | 257 | 238
2018-06-19 11:30 | 262 | 242
2018-06-19 12:00 | 249 | 229
2018-06-19 12:30 | 249 | 228
2018-06-19 13:00 | 250 | 230
2018-06-19 13:30 | 260 | 241
2018-06-19 14:00 | 259 | 241
2018-06-19 14:30 | 251 | 233
2018-06-19 15:00 | 265 | 247
2018-06-19 15:30 | 287 | 272
2018-06-19 16:00 | 307 | 295
2018-06-19 16:30 | 322 | 313
2018-06-19 17:00 | 383 | 375
2018-06-19 17:30 | 464 | 459
2018-06-19 18:00 | 464 | 461
2018-06-19 18:30 | 471 | 469
2018-06-19 19:00 | 527 | 525
2018-06-19 19:30 | 516 | 515
2018-06-19 20:00 | 506 | 505
2018-06-19 20:30 | 485 | 483
2018-06-19 21:00 | 459 | 456
2018-06-19 21:30 | 467 | 464
2018-06-19 22:00 | 445 | 441
2018-06-19 22:30 | 418 | 414
2018-06-19 23:00 | 411 | 406
2018-06-19 23:30 | 394 | 388
2018-06-20 | 374 | 368
2018-06-20 00:30 | 364 | 355
2018-06-20 01:00 | 356 | 346
2018-06-20 01:30 | 349 | 339
2018-06-20 02:00 | 349 | 340
2018-06-20 02:30 | 344 | 334
2018-06-20 03:00 | 342 | 332
2018-06-20 03:30 | 338 | 328
2018-06-20 04:00 | 339 | 328
2018-06-20 04:30 | 352 | 342
2018-06-20 05:00 | 351 | 342
2018-06-20 05:30 | 374 | 365
2018-06-20 06:00 | 396 | 389
2018-06-20 06:30 | 429 | 423
2018-06-20 07:00 | 457 | 452
2018-06-20 07:30 | 462 | 458
2018-06-20 08:00 | 423 | 419
2018-06-20 08:30 | 362 | 355
2018-06-20 09:00 | 326 | 316
2018-06-20 09:30 | 320 | 307
2018-06-20 10:00 | 290 | 276
2018-06-20 10:30 | 267 | 250
2018-06-20 11:00 | 256 | 235
2018-06-20 11:30 | 256 | 233
2018-06-20 12:00 | 248 | 224
2018-06-20 12:30 | 257 | 234
2018-06-20 13:00 | 248 | 225
2018-06-20 13:30 | 246 | 221
2018-06-20 14:00 | 243 | 218
2018-06-20 14:30 | 239 | 215
2018-06-20 15:00 | 251 | 227
2018-06-20 15:30 | 256 | 234
2018-06-20 16:00 | 282 | 263
2018-06-20 16:30 | 311 | 297
2018-06-20 17:00 | 365 | 355
2018-06-20 17:30 | 433 | 427
2018-06-20 18:00 | 485 | 481
2018-06-20 18:30 | 524 | 521
2018-06-20 19:00 | 539 | 538
2018-06-20 19:30 | 525 | 523
2018-06-20 20:00 | 503 | 502
2018-06-20 20:30 | 458 | 456
2018-06-20 21:00 | 449 | 446
2018-06-20 21:30 | 445 | 441
2018-06-20 22:00 | 432 | 428
2018-06-20 22:30 | 427 | 423
2018-06-20 23:00 | 415 | 410
2018-06-20 23:30 | 392 | 386
2018-06-21 | 373 | 366
2018-06-21 00:30 | 366 | 358
2018-06-21 01:00 | 357 | 348
2018-06-21 01:30 | 350 | 340
2018-06-21 02:00 | 348 | 338
2018-06-21 02:30 | 347 | 337
2018-06-21 03:00 | 344 | 335
2018-06-21 03:30 | 350 | 342
2018-06-21 04:00 | 356 | 348
2018-06-21 04:30 | 363 | 354
2018-06-21 05:00 | 364 | 356
2018-06-21 05:30 | 379 | 371
2018-06-21 06:00 | 403 | 396
2018-06-21 06:30 | 437 | 432
2018-06-21 07:00 | 428 | 423
2018-06-21 07:30 | 451 | 445
2018-06-21 08:00 | 386 | 381
2018-06-21 08:30 | 292 | 282
2018-06-21 09:00 | 256 | 238
2018-06-21 09:30 | 236 | 211
2018-06-21 10:00 | 225 | 195
2018-06-21 10:30 | 201 | 165
2018-06-21 11:00 | 179 | 136
2018-06-21 11:30 | 147 | 86
2018-06-21 12:00 | 122 | 9
2018-06-21 12:30 | 131 | 9
2018-06-21 13:00 | 131 | 15
2018-06-21 13:30 | 132 | 5
2018-06-21 14:00 | 131 | 1
2018-06-21 14:30 | 132 | 2
2018-06-21 15:00 | 130 | 8
2018-06-21 15:30 | 130 | 27
2018-06-21 16:00 | 134 | 48
2018-06-21 16:30 | 144 | 75
2018-06-21 17:00 | 175 | 128
2018-06-21 17:30 | 229 | 198
2018-06-21 18:00 | 276 | 255
2018-06-21 18:30 | 315 | 300
2018-06-21 19:00 | 317 | 306
2018-06-21 19:30 | 297 | 285
2018-06-21 20:00 | 283 | 270
2018-06-21 20:30 | 262 | 247
2018-06-21 21:00 | 243 | 226
2018-06-21 21:30 | 222 | 201
2018-06-21 22:00 | 203 | 176
2018-06-21 22:30 | 200 | 170
2018-06-21 23:00 | 217 | 189
2018-06-21 23:30 | 197 | 167
2018-06-22 | 182 | 147
2018-06-22 00:30 | 235 | 207
2018-06-22 01:00 | 279 | 258
2018-06-22 01:30 | 349 | 336
2018-06-22 02:00 | 341 | 331
2018-06-22 02:30 | 333 | 323
2018-06-22 03:00 | 343 | 332
2018-06-22 03:30 | 346 | 336
2018-06-22 04:00 | 341 | 330
2018-06-22 04:30 | 353 | 343
2018-06-22 05:00 | 359 | 349
2018-06-22 05:30 | 341 | 332
2018-06-22 06:00 | 384 | 375
2018-06-22 06:30 | 415 | 409
2018-06-22 07:00 | 447 | 441
2018-06-22 07:30 | 463 | 459
2018-06-22 08:00 | 450 | 446
2018-06-22 08:30 | 393 | 389
2018-06-22 09:00 | 374 | 368
2018-06-22 09:30 | 359 | 351
2018-06-22 10:00 | 336 | 327
2018-06-22 10:30 | 329 | 319
2018-06-22 11:00 | 306 | 299
2018-06-22 11:30 | 284 | 276
2018-06-22 12:00 | 289 | 282
2018-06-22 12:30 | 278 | 272
2018-06-22 13:00 | 281 | 273
2018-06-22 13:30 | 277 | 270
2018-06-22 14:00 | 271 | 264
2018-06-22 14:30 | 270 | 263
2018-06-22 15:00 | 276 | 269
2018-06-22 15:30 | 295 | 288
2018-06-22 16:00 | 306 | 301
2018-06-22 16:30 | 324 | 319
2018-06-22 17:00 | 369 | 366
2018-06-22 17:30 | 437 | 435
2018-06-22 18:00 | 474 | 473
2018-06-22 18:30 | 493 | 492
2018-06-22 19:00 | 487 | 487
2018-06-22 19:30 | 472 | 472
2018-06-22 20:00 | 456 | 455
2018-06-22 20:30 | 442 | 440
2018-06-22 21:00 | 426 | 424
2018-06-22 21:30 | 406 | 403
2018-06-22 22:00 | 393 | 389
2018-06-22 22:30 | 396 | 392
2018-06-22 23:00 | 410 | 406
2018-06-22 23:30 | 389 | 385
2018-06-23 | 376 | 372
2018-06-23 00:30 | 372 | 367
2018-06-23 01:00 | 355 | 349
2018-06-23 01:30 | 344 | 337
2018-06-23 02:00 | 337 | 329
2018-06-23 02:30 | 331 | 323
2018-06-23 03:00 | 329 | 322
2018-06-23 03:30 | 325 | 317
2018-06-23 04:00 | 328 | 321
2018-06-23 04:30 | 331 | 324
2018-06-23 05:00 | 334 | 328
2018-06-23 05:30 | 354 | 348
2018-06-23 06:00 | 358 | 353
2018-06-23 06:30 | 372 | 366
2018-06-23 07:00 | 380 | 376
2018-06-23 07:30 | 372 | 368
2018-06-23 08:00 | 355 | 351
2018-06-23 08:30 | 341 | 336
2018-06-23 09:00 | 352 | 347
2018-06-23 09:30 | 344 | 339
2018-06-23 10:00 | 332 | 326
2018-06-23 10:30 | 312 | 305
2018-06-23 11:00 | 302 | 295
2018-06-23 11:30 | 279 | 271
2018-06-23 12:00 | 271 | 261
2018-06-23 12:30 | 272 | 261
2018-06-23 13:00 | 276 | 265
2018-06-23 13:30 | 283 | 270
2018-06-23 14:00 | 263 | 248
2018-06-23 14:30 | 253 | 235
2018-06-23 15:00 | 235 | 216
2018-06-23 15:30 | 301 | 285
2018-06-23 16:00 | 331 | 320
2018-06-23 16:30 | 358 | 349
2018-06-23 17:00 | 401 | 395
2018-06-23 17:30 | 433 | 429
2018-06-23 18:00 | 482 | 479
2018-06-23 18:30 | 507 | 505
2018-06-23 19:00 | 491 | 489
2018-06-23 19:30 | 469 | 467
2018-06-23 20:00 | 456 | 453
2018-06-23 20:30 | 429 | 426
2018-06-23 21:00 | 391 | 386
2018-06-23 21:30 | 371 | 365
2018-06-23 22:00 | 361 | 354
2018-06-23 22:30 | 366 | 359
2018-06-23 23:00 | 377 | 369
2018-06-23 23:30 | 371 | 363
2018-06-24 | 348 | 340
2018-06-24 00:30 | 347 | 338
2018-06-24 01:00 | 340 | 330
2018-06-24 01:30 | 329 | 319
2018-06-24 02:00 | 327 | 316
2018-06-24 02:30 | 328 | 317
2018-06-24 03:00 | 327 | 316
2018-06-24 03:30 | 329 | 318
2018-06-24 04:00 | 330 | 319
2018-06-24 04:30 | 326 | 314
2018-06-24 05:00 | 326 | 315
2018-06-24 05:30 | 336 | 325
2018-06-24 06:00 | 346 | 336
2018-06-24 06:30 | 355 | 346
2018-06-24 07:00 | 352 | 343
2018-06-24 07:30 | 338 | 329
2018-06-24 08:00 | 348 | 338
2018-06-24 08:30 | 340 | 330
2018-06-24 09:00 | 323 | 312
2018-06-24 09:30 | 317 | 306
2018-06-24 10:00 | 299 | 287
2018-06-24 10:30 | 300 | 287
2018-06-24 11:00 | 298 | 285
2018-06-24 11:30 | 280 | 266
2018-06-24 12:00 | 284 | 268
2018-06-24 12:30 | 279 | 263
2018-06-24 13:00 | 284 | 268
2018-06-24 13:30 | 283 | 268
2018-06-24 14:00 | 271 | 255
2018-06-24 14:30 | 271 | 254
2018-06-24 15:00 | 278 | 261
2018-06-24 15:30 | 287 | 270
2018-06-24 16:00 | 316 | 302
2018-06-24 16:30 | 351 | 340
2018-06-24 17:00 | 381 | 373
2018-06-24 17:30 | 427 | 421
2018-06-24 18:00 | 458 | 455
2018-06-24 18:30 | 494 | 491
2018-06-24 19:00 | 500 | 498
2018-06-24 19:30 | 489 | 487
2018-06-24 20:00 | 457 | 455
2018-06-24 20:30 | 411 | 408
2018-06-24 21:00 | 411 | 406
2018-06-24 21:30 | 390 | 385
2018-06-24 22:00 | 370 | 363
2018-06-24 22:30 | 378 | 371
2018-06-24 23:00 | 389 | 383
2018-06-24 23:30 | 354 | 347
2018-06-25 | 353 | 345
2018-06-25 00:30 | 345 | 336
2018-06-25 01:00 | 337 | 328
2018-06-25 01:30 | 332 | 322
2018-06-25 02:00 | 321 | 310
2018-06-25 02:30 | 318 | 306
2018-06-25 03:00 | 312 | 300
2018-06-25 03:30 | 312 | 300
2018-06-25 04:00 | 320 | 308
2018-06-25 04:30 | 325 | 314
2018-06-25 05:00 | 331 | 320
2018-06-25 05:30 | 344 | 334
2018-06-25 06:00 | 356 | 347
2018-06-25 06:30 | 389 | 381
2018-06-25 07:00 | 405 | 399
2018-06-25 07:30 | 417 | 412
2018-06-25 08:00 | 434 | 429
2018-06-25 08:30 | 436 | 432
2018-06-25 09:00 | 428 | 424
2018-06-25 09:30 | 403 | 398
2018-06-25 10:00 | 369 | 363
2018-06-25 10:30 | 357 | 349
2018-06-25 11:00 | 341 | 333
2018-06-25 11:30 | 325 | 315
2018-06-25 12:00 | 316 | 305
2018-06-25 12:30 | 343 | 332
2018-06-25 13:00 | 342 | 332
2018-06-25 13:30 | 347 | 338
2018-06-25 14:00 | 341 | 333
2018-06-25 14:30 | 327 | 318
2018-06-25 15:00 | 335 | 326
2018-06-25 15:30 | 374 | 366
2018-06-25 16:00 | 414 | 408
2018-06-25 16:30 | 432 | 428
2018-06-25 17:00 | 453 | 450
2018-06-25 17:30 | 488 | 486
2018-06-25 18:00 | 469 | 468
2018-06-25 18:30 | 463 | 462
2018-06-25 19:00 | 459 | 458
2018-06-25 19:30 | 458 | 456
2018-06-25 20:00 | 455 | 453
2018-06-25 20:30 | 453 | 450
2018-06-25 21:00 | 432 | 429
2018-06-25 21:30 | 411 | 407
2018-06-25 22:00 | 382 | 377
2018-06-25 22:30 | 373 | 367
2018-06-25 23:00 | 389 | 383
2018-06-25 23:30 | 374 | 368
2018-06-26 | 354 | 346
2018-06-26 00:30 | 339 | 330
2018-06-26 01:00 | 335 | 325
2018-06-26 01:30 | 324 | 314
2018-06-26 02:00 | 317 | 306
2018-06-26 02:30 | 315 | 303
2018-06-26 03:00 | 322 | 310
2018-06-26 03:30 | 340 | 329
2018-06-26 04:00 | 345 | 335
2018-06-26 04:30 | 350 | 341
2018-06-26 05:00 | 355 | 346
2018-06-26 05:30 | 368 | 360
2018-06-26 06:00 | 381 | 374
2018-06-26 06:30 | 422 | 416
2018-06-26 07:00 | 444 | 439
2018-06-26 07:30 | 471 | 467
2018-06-26 08:00 | 484 | 481
2018-06-26 08:30 | 471 | 469
2018-06-26 09:00 | 443 | 440
2018-06-26 09:30 | 438 | 435
2018-06-26 10:00 | 438 | 434
2018-06-26 10:30 | 433 | 429
2018-06-26 11:00 | 417 | 412
2018-06-26 11:30 | 382 | 376
2018-06-26 12:00 | 344 | 336
2018-06-26 12:30 | 308 | 298
2018-06-26 13:00 | 313 | 301
2018-06-26 13:30 | 312 | 300
2018-06-26 14:00 | 345 | 335
2018-06-26 14:30 | 344 | 335
2018-06-26 15:00 | 348 | 340
2018-06-26 15:30 | 387 | 380
2018-06-26 16:00 | 409 | 404
2018-06-26 16:30 | 430 | 426
2018-06-26 17:00 | 443 | 439
2018-06-26 17:30 | 478 | 475
2018-06-26 18:00 | 520 | 518
2018-06-26 18:30 | 551 | 550
2018-06-26 19:00 | 554 | 553
2018-06-26 19:30 | 534 | 533
2018-06-26 20:00 | 508 | 507
2018-06-26 20:30 | 480 | 479
2018-06-26 21:00 | 463 | 461
2018-06-26 21:30 | 460 | 457
2018-06-26 22:00 | 435 | 432
2018-06-26 22:30 | 430 | 427
2018-06-26 23:00 | 436 | 432
2018-06-26 23:30 | 413 | 409
2018-06-27 | 393 | 388
2018-06-27 00:30 | 377 | 372
2018-06-27 01:00 | 382 | 376
2018-06-27 01:30 | 366 | 358
2018-06-27 02:00 | 365 | 356
2018-06-27 02:30 | 361 | 352
2018-06-27 03:00 | 351 | 341
2018-06-27 03:30 | 349 | 340
2018-06-27 04:00 | 356 | 346
2018-06-27 04:30 | 332 | 322
2018-06-27 05:00 | 283 | 270
2018-06-27 05:30 | 296 | 281
2018-06-27 06:00 | 321 | 307
2018-06-27 06:30 | 343 | 332
2018-06-27 07:00 | 366 | 356
2018-06-27 07:30 | 339 | 330
2018-06-27 08:00 | 316 | 306
2018-06-27 08:30 | 244 | 231
2018-06-27 09:00 | 220 | 200
2018-06-27 09:30 | 195 | 167
2018-06-27 10:00 | 177 | 140
2018-06-27 10:30 | 179 | 139
2018-06-27 11:00 | 182 | 140
2018-06-27 11:30 | 178 | 126
2018-06-27 12:00 | 167 | 109
2018-06-27 12:30 | 178 | 122
2018-06-27 13:00 | 189 | 140
2018-06-27 13:30 | 188 | 140
2018-06-27 14:00 | 185 | 137
2018-06-27 14:30 | 196 | 151
2018-06-27 15:00 | 190 | 143
2018-06-27 15:30 | 191 | 144
2018-06-27 16:00 | 207 | 165
2018-06-27 16:30 | 217 | 180
2018-06-27 17:00 | 218 | 185
2018-06-27 17:30 | 246 | 219
2018-06-27 18:00 | 274 | 252
2018-06-27 18:30 | 311 | 294
2018-06-27 19:00 | 311 | 296
2018-06-27 19:30 | 293 | 279
2018-06-27 20:00 | 278 | 260
2018-06-27 20:30 | 254 | 234
2018-06-27 21:00 | 259 | 237
2018-06-27 21:30 | 236 | 210
2018-06-27 22:00 | 265 | 241
2018-06-27 22:30 | 262 | 239
2018-06-27 23:00 | 271 | 248
2018-06-27 23:30 | 259 | 236
2018-06-28 | 243 | 216
2018-06-28 00:30 | 294 | 269
2018-06-28 01:00 | 346 | 328
2018-06-28 01:30 | 420 | 408
2018-06-28 02:00 | 410 | 403
2018-06-28 02:30 | 393 | 385
2018-06-28 03:00 | 371 | 361
2018-06-28 03:30 | 367 | 356
2018-06-28 04:00 | 354 | 343
2018-06-28 04:30 | 356 | 344
2018-06-28 05:00 | 364 | 353
2018-06-28 05:30 | 377 | 366
2018-06-28 06:00 | 392 | 382
2018-06-28 06:30 | 428 | 419
2018-06-28 07:00 | 452 | 445
2018-06-28 07:30 | 453 | 447
2018-06-28 08:00 | 453 | 448
2018-06-28 08:30 | 418 | 412
2018-06-28 09:00 | 377 | 368
2018-06-28 09:30 | 392 | 383
2018-06-28 10:00 | 381 | 372
2018-06-28 10:30 | 379 | 369
2018-06-28 11:00 | 378 | 368
2018-06-28 11:30 | 371 | 362
2018-06-28 12:00 | 359 | 349
2018-06-28 12:30 | 345 | 334
2018-06-28 13:00 | 335 | 322
2018-06-28 13:30 | 351 | 339
2018-06-28 14:00 | 343 | 331
2018-06-28 14:30 | 347 | 335
2018-06-28 15:00 | 364 | 353
2018-06-28 15:30 | 374 | 364
2018-06-28 16:00 | 386 | 377
2018-06-28 16:30 | 424 | 417
2018-06-28 17:00 | 447 | 441
2018-06-28 17:30 | 499 | 494
2018-06-28 18:00 | 525 | 522
2018-06-28 18:30 | 563 | 561
2018-06-28 19:00 | 562 | 561
2018-06-28 19:30 | 537 | 536
2018-06-28 20:00 | 523 | 522
2018-06-28 20:30 | 497 | 495
2018-06-28 21:00 | 474 | 471
2018-06-28 21:30 | 445 | 442
2018-06-28 22:00 | 419 | 414
2018-06-28 22:30 | 420 | 415
2018-06-28 23:00 | 431 | 425
2018-06-28 23:30 | 408 | 402
2018-06-29 | 391 | 384
2018-06-29 00:30 | 376 | 367
2018-06-29 01:00 | 366 | 355
2018-06-29 01:30 | 367 | 356
2018-06-29 02:00 | 361 | 350
2018-06-29 02:30 | 361 | 349
2018-06-29 03:00 | 353 | 342
2018-06-29 03:30 | 350 | 338
2018-06-29 04:00 | 352 | 339
2018-06-29 04:30 | 355 | 342
2018-06-29 05:00 | 358 | 346
2018-06-29 05:30 | 373 | 361
2018-06-29 06:00 | 388 | 377
2018-06-29 06:30 | 418 | 409
2018-06-29 07:00 | 450 | 443
2018-06-29 07:30 | 429 | 424
2018-06-29 08:00 | 450 | 445
2018-06-29 08:30 | 435 | 430
2018-06-29 09:00 | 408 | 402
2018-06-29 09:30 | 391 | 384
2018-06-29 10:00 | 379 | 371
2018-06-29 10:30 | 373 | 364
2018-06-29 11:00 | 361 | 352
2018-06-29 11:30 | 349 | 339
2018-06-29 12:00 | 340 | 328
2018-06-29 12:30 | 337 | 325
2018-06-29 13:00 | 329 | 316
2018-06-29 13:30 | 313 | 299
2018-06-29 14:00 | 308 | 289
2018-06-29 14:30 | 306 | 289
2018-06-29 15:00 | 309 | 292
2018-06-29 15:30 | 327 | 311
2018-06-29 16:00 | 336 | 322
2018-06-29 16:30 | 366 | 354
2018-06-29 17:00 | 396 | 387
2018-06-29 17:30 | 439 | 433
2018-06-29 18:00 | 477 | 472
2018-06-29 18:30 | 506 | 503
2018-06-29 19:00 | 509 | 506
2018-06-29 19:30 | 489 | 487
2018-06-29 20:00 | 471 | 467
2018-06-29 20:30 | 449 | 445
2018-06-29 21:00 | 433 | 427
2018-06-29 21:30 | 420 | 414
2018-06-29 22:00 | 400 | 394
2018-06-29 22:30 | 382 | 373
2018-06-29 23:00 | 363 | 353
2018-06-29 23:30 | 372 | 361
2018-06-30 | 391 | 381
2018-06-30 00:30 | 382 | 372
2018-06-30 01:00 | 374 | 363
2018-06-30 01:30 | 368 | 356
2018-06-30 02:00 | 357 | 345
2018-06-30 02:30 | 353 | 341
2018-06-30 03:00 | 347 | 335
2018-06-30 03:30 | 348 | 336
2018-06-30 04:00 | 345 | 333
2018-06-30 04:30 | 345 | 333
2018-06-30 05:00 | 350 | 338
2018-06-30 05:30 | 355 | 343
2018-06-30 06:00 | 357 | 345
2018-06-30 06:30 | 382 | 371
2018-06-30 07:00 | 383 | 374
2018-06-30 07:30 | 375 | 365
2018-06-30 08:00 | 357 | 347
2018-06-30 08:30 | 350 | 339
2018-06-30 09:00 | 352 | 340
2018-06-30 09:30 | 350 | 339
2018-06-30 10:00 | 351 | 340
2018-06-30 10:30 | 348 | 337
2018-06-30 11:00 | 333 | 321
2018-06-30 11:30 | 325 | 312
2018-06-30 12:00 | 320 | 305
2018-06-30 12:30 | 312 | 297
2018-06-30 13:00 | 314 | 298
2018-06-30 13:30 | 306 | 290
2018-06-30 14:00 | 305 | 289
2018-06-30 14:30 | 297 | 280
2018-06-30 15:00 | 309 | 292
2018-06-30 15:30 | 334 | 320
2018-06-30 16:00 | 353 | 341
2018-06-30 16:30 | 369 | 357
2018-06-30 17:00 | 415 | 406
2018-06-30 17:30 | 445 | 439
2018-06-30 18:00 | 471 | 466
2018-06-30 18:30 | 483 | 479
2018-06-30 19:00 | 470 | 467
2018-06-30 19:30 | 463 | 459
2018-06-30 20:00 | 445 | 441
2018-06-30 20:30 | 431 | 426
2018-06-30 21:00 | 417 | 411
2018-06-30 21:30 | 400 | 393
2018-06-30 22:00 | 389 | 381
2018-06-30 22:30 | 394 | 385
2018-06-30 23:00 | 398 | 390
2018-06-30 23:30 | 384 | 375
2018-07-01 | 373 | 364
2018-07-01 00:30 | 367 | 357
2018-07-01 01:00 | 364 | 353
2018-07-01 01:30 | 354 | 343
2018-07-01 02:00 | 344 | 332
2018-07-01 02:30 | 344 | 331
2018-07-01 03:00 | 337 | 324
2018-07-01 03:30 | 344 | 332
2018-07-01 04:00 | 347 | 334
2018-07-01 04:30 | 344 | 331
2018-07-01 05:00 | 345 | 333
2018-07-01 05:30 | 352 | 339
2018-07-01 06:00 | 356 | 344
2018-07-01 06:30 | 335 | 323
2018-07-01 07:00 | 351 | 338
2018-07-01 07:30 | 352 | 340
2018-07-01 08:00 | 348 | 335
2018-07-01 08:30 | 350 | 337
2018-07-01 09:00 | 341 | 329
2018-07-01 09:30 | 340 | 327
2018-07-01 10:00 | 338 | 325
2018-07-01 10:30 | 308 | 293
2018-07-01 11:00 | 297 | 280
2018-07-01 11:30 | 294 | 276
2018-07-01 12:00 | 293 | 274
2018-07-01 12:30 | 305 | 287
2018-07-01 13:00 | 303 | 286
2018-07-01 13:30 | 310 | 292
2018-07-01 14:00 | 304 | 287
2018-07-01 14:30 | 307 | 290
2018-07-01 15:00 | 347 | 332
2018-07-01 15:30 | 374 | 363
2018-07-01 16:00 | 387 | 377
2018-07-01 16:30 | 379 | 370
2018-07-01 17:00 | 412 | 403
2018-07-01 17:30 | 432 | 425
2018-07-01 18:00 | 470 | 466
2018-07-01 18:30 | 492 | 489
2018-07-01 19:00 | 492 | 490
2018-07-01 19:30 | 474 | 472
2018-07-01 20:00 | 454 | 450
2018-07-01 20:30 | 446 | 442
2018-07-01 21:00 | 430 | 425
2018-07-01 21:30 | 415 | 410
2018-07-01 22:00 | 401 | 394
2018-07-01 22:30 | 426 | 419
2018-07-01 23:00 | 417 | 411
2018-07-01 23:30 | 399 | 393
2018-07-02 | 379 | 371
2018-07-02 00:30 | 367 | 358
2018-07-02 01:00 | 358 | 348
2018-07-02 01:30 | 354 | 343
2018-07-02 02:00 | 352 | 341
2018-07-02 02:30 | 344 | 333
2018-07-02 03:00 | 342 | 330
2018-07-02 03:30 | 353 | 341
2018-07-02 04:00 | 356 | 345
2018-07-02 04:30 | 340 | 328
2018-07-02 05:00 | 357 | 345
2018-07-02 05:30 | 368 | 358
2018-07-02 06:00 | 346 | 336
2018-07-02 06:30 | 348 | 336
2018-07-02 07:00 | 374 | 363
2018-07-02 07:30 | 399 | 390
2018-07-02 08:00 | 405 | 398
2018-07-02 08:30 | 414 | 407
2018-07-02 09:00 | 422 | 415
2018-07-02 09:30 | 400 | 393
2018-07-02 10:00 | 369 | 361
2018-07-02 10:30 | 364 | 355
2018-07-02 11:00 | 368 | 358
2018-07-02 11:30 | 342 | 331
2018-07-02 12:00 | 330 | 318
2018-07-02 12:30 | 339 | 326
2018-07-02 13:00 | 358 | 346
2018-07-02 13:30 | 347 | 337
2018-07-02 14:00 | 349 | 338
2018-07-02 14:30 | 335 | 323
2018-07-02 15:00 | 362 | 351
2018-07-02 15:30 | 378 | 369
2018-07-02 16:00 | 388 | 380
2018-07-02 16:30 | 324 | 315
2018-07-02 17:00 | 284 | 271
2018-07-02 17:30 | 323 | 308
2018-07-02 18:00 | 351 | 340
2018-07-02 18:30 | 383 | 374
2018-07-02 19:00 | 383 | 375
2018-07-02 19:30 | 372 | 365
2018-07-02 20:00 | 367 | 358
2018-07-02 20:30 | 345 | 336
2018-07-02 21:00 | 446 | 437
2018-07-02 21:30 | 467 | 462
2018-07-02 22:00 | 448 | 444
2018-07-02 22:30 | 457 | 452
2018-07-02 23:00 | 440 | 436
2018-07-02 23:30 | 439 | 434
2018-07-03 | 430 | 424
2018-07-03 00:30 | 411 | 405
2018-07-03 01:00 | 402 | 394
2018-07-03 01:30 | 397 | 388
2018-07-03 02:00 | 389 | 379
2018-07-03 02:30 | 383 | 373
2018-07-03 03:00 | 377 | 367
2018-07-03 03:30 | 381 | 371
2018-07-03 04:00 | 386 | 376
2018-07-03 04:30 | 385 | 375
2018-07-03 05:00 | 389 | 378
2018-07-03 05:30 | 401 | 391
2018-07-03 06:00 | 411 | 403
2018-07-03 06:30 | 413 | 404
2018-07-03 07:00 | 437 | 430
2018-07-03 07:30 | 433 | 426
2018-07-03 08:00 | 401 | 393
2018-07-03 08:30 | 357 | 348
2018-07-03 09:00 | 331 | 318
2018-07-03 09:30 | 336 | 322
2018-07-03 10:00 | 318 | 304
2018-07-03 10:30 | 304 | 288
2018-07-03 11:00 | 301 | 282
2018-07-03 11:30 | 322 | 304
2018-07-03 12:00 | 302 | 285
2018-07-03 12:30 | 290 | 270
2018-07-03 13:00 | 300 | 281
2018-07-03 13:30 | 314 | 296
2018-07-03 14:00 | 334 | 318
2018-07-03 14:30 | 328 | 313
2018-07-03 15:00 | 340 | 326
2018-07-03 15:30 | 354 | 341
2018-07-03 16:00 | 353 | 341
2018-07-03 16:30 | 293 | 279
2018-07-03 17:00 | 254 | 233
2018-07-03 17:30 | 309 | 288
2018-07-03 18:00 | 347 | 333
2018-07-03 18:30 | 378 | 368
2018-07-03 19:00 | 397 | 390
2018-07-03 19:30 | 397 | 389
2018-07-03 20:00 | 376 | 368
2018-07-03 20:30 | 355 | 345
2018-07-03 21:00 | 446 | 437
2018-07-03 21:30 | 492 | 486
2018-07-03 22:00 | 478 | 474
2018-07-03 22:30 | 467 | 463
2018-07-03 23:00 | 465 | 460
2018-07-03 23:30 | 450 | 445
2018-07-04 | 430 | 424
2018-07-04 00:30 | 403 | 396
2018-07-04 01:00 | 386 | 377
2018-07-04 01:30 | 370 | 361
2018-07-04 02:00 | 357 | 346
2018-07-04 02:30 | 360 | 348
2018-07-04 03:00 | 353 | 341
2018-07-04 03:30 | 349 | 336
2018-07-04 04:00 | 352 | 339
2018-07-04 04:30 | 360 | 348
2018-07-04 05:00 | 368 | 356
2018-07-04 05:30 | 379 | 368
2018-07-04 06:00 | 396 | 385
2018-07-04 06:30 | 412 | 403
2018-07-04 07:00 | 410 | 402
2018-07-04 07:30 | 426 | 419
2018-07-04 08:00 | 398 | 391
2018-07-04 08:30 | 310 | 300
2018-07-04 09:00 | 316 | 303
2018-07-04 09:30 | 348 | 335
2018-07-04 10:00 | 321 | 309
2018-07-04 10:30 | 316 | 301
2018-07-04 11:00 | 329 | 315
2018-07-04 11:30 | 335 | 321
2018-07-04 12:00 | 314 | 300
2018-07-04 12:30 | 310 | 294
2018-07-04 13:00 | 301 | 284
2018-07-04 13:30 | 291 | 274
2018-07-04 14:00 | 289 | 270
2018-07-04 14:30 | 298 | 280
2018-07-04 15:00 | 317 | 301
2018-07-04 15:30 | 324 | 310
2018-07-04 16:00 | 339 | 326
2018-07-04 16:30 | 355 | 344
2018-07-04 17:00 | 325 | 314
2018-07-04 17:30 | 306 | 293
2018-07-04 18:00 | 336 | 322
2018-07-04 18:30 | 374 | 364
2018-07-04 19:00 | 386 | 378
2018-07-04 19:30 | 368 | 360
2018-07-04 20:00 | 355 | 347
2018-07-04 20:30 | 341 | 331
2018-07-04 21:00 | 317 | 305
2018-07-04 21:30 | 418 | 407
2018-07-04 22:00 | 424 | 417
2018-07-04 22:30 | 400 | 393
2018-07-04 23:00 | 373 | 365
2018-07-04 23:30 | 362 | 353
2018-07-05 | 322 | 310
2018-07-05 00:30 | 328 | 314
2018-07-05 01:00 | 315 | 300
2018-07-05 01:30 | 310 | 294
2018-07-05 02:00 | 338 | 323
2018-07-05 02:30 | 347 | 334
2018-07-05 03:00 | 352 | 339
2018-07-05 03:30 | 351 | 339
2018-07-05 04:00 | 351 | 339
2018-07-05 04:30 | 358 | 347
2018-07-05 05:00 | 366 | 355
2018-07-05 05:30 | 378 | 368
2018-07-05 06:00 | 393 | 383
2018-07-05 06:30 | 412 | 404
2018-07-05 07:00 | 416 | 409
2018-07-05 07:30 | 427 | 420
2018-07-05 08:00 | 398 | 391
2018-07-05 08:30 | 363 | 355
2018-07-05 09:00 | 338 | 328
2018-07-05 09:30 | 306 | 293
2018-07-05 10:00 | 289 | 273
2018-07-05 10:30 | 276 | 257
2018-07-05 11:00 | 298 | 279
2018-07-05 11:30 | 304 | 287
2018-07-05 12:00 | 298 | 281
2018-07-05 12:30 | 291 | 274
2018-07-05 13:00 | 289 | 271
2018-07-05 13:30 | 275 | 256
2018-07-05 14:00 | 263 | 243
2018-07-05 14:30 | 266 | 244
2018-07-05 15:00 | 274 | 252
2018-07-05 15:30 | 290 | 270
2018-07-05 16:00 | 299 | 281
2018-07-05 16:30 | 317 | 301
2018-07-05 17:00 | 358 | 345
2018-07-05 17:30 | 443 | 434
2018-07-05 18:00 | 478 | 471
2018-07-05 18:30 | 513 | 509
2018-07-05 19:00 | 528 | 525
2018-07-05 19:30 | 517 | 515
2018-07-05 20:00 | 523 | 521
2018-07-05 20:30 | 528 | 526
2018-07-05 21:00 | 516 | 514
2018-07-05 21:30 | 489 | 487
2018-07-05 22:00 | 463 | 460
2018-07-05 22:30 | 436 | 432
2018-07-05 23:00 | 416 | 410
2018-07-05 23:30 | 390 | 383
2018-07-06 | 377 | 369
2018-07-06 00:30 | 367 | 358
2018-07-06 01:00 | 356 | 346
2018-07-06 01:30 | 341 | 330
2018-07-06 02:00 | 337 | 326
2018-07-06 02:30 | 333 | 320
2018-07-06 03:00 | 336 | 323
2018-07-06 03:30 | 331 | 318
2018-07-06 04:00 | 333 | 320
2018-07-06 04:30 | 342 | 328
2018-07-06 05:00 | 353 | 340
2018-07-06 05:30 | 360 | 348
2018-07-06 06:00 | 377 | 367
2018-07-06 06:30 | 397 | 388
2018-07-06 07:00 | 391 | 383
2018-07-06 07:30 | 388 | 380
2018-07-06 08:00 | 362 | 353
2018-07-06 08:30 | 341 | 331
2018-07-06 09:00 | 317 | 306
2018-07-06 09:30 | 302 | 289
2018-07-06 10:00 | 311 | 297
2018-07-06 10:30 | 301 | 287
2018-07-06 11:00 | 289 | 273
2018-07-06 11:30 | 282 | 265
2018-07-06 12:00 | 276 | 257
2018-07-06 12:30 | 307 | 290
2018-07-06 13:00 | 295 | 279
2018-07-06 13:30 | 304 | 288
2018-07-06 14:00 | 328 | 306
2018-07-06 14:30 | 358 | 304
2018-07-06 15:00 | 354 | 298
2018-07-06 15:30 | 387 | 335
2018-07-06 16:00 | 388 | 339
2018-07-06 16:30 | 380 | 357
2018-07-06 17:00 | 410 | 398
2018-07-06 17:30 | 458 | 450
2018-07-06 18:00 | 482 | 476
2018-07-06 18:30 | 508 | 503
2018-07-06 19:00 | 520 | 515
2018-07-06 19:30 | 508 | 503
2018-07-06 20:00 | 498 | 494
2018-07-06 20:30 | 500 | 495
2018-07-06 21:00 | 488 | 483
2018-07-06 21:30 | 494 | 489
2018-07-06 22:00 | 476 | 471
2018-07-06 22:30 | 454 | 448
2018-07-06 23:00 | 440 | 433
2018-07-06 23:30 | 420 | 412
2018-07-07 | 405 | 396
2018-07-07 00:30 | 393 | 382
2018-07-07 01:00 | 376 | 364
2018-07-07 01:30 | 372 | 360
2018-07-07 02:00 | 359 | 346
2018-07-07 02:30 | 359 | 345
2018-07-07 03:00 | 362 | 348
2018-07-07 03:30 | 357 | 343
2018-07-07 04:00 | 359 | 345
2018-07-07 04:30 | 360 | 346
2018-07-07 05:00 | 363 | 348
2018-07-07 05:30 | 369 | 355
2018-07-07 06:00 | 374 | 360
2018-07-07 06:30 | 386 | 373
2018-07-07 07:00 | 361 | 348
2018-07-07 07:30 | 298 | 281
2018-07-07 08:00 | 308 | 288
2018-07-07 08:30 | 356 | 340
2018-07-07 09:00 | 345 | 331
2018-07-07 09:30 | 363 | 350
2018-07-07 10:00 | 349 | 336
2018-07-07 10:30 | 337 | 323
2018-07-07 11:00 | 326 | 311
2018-07-07 11:30 | 322 | 305
2018-07-07 12:00 | 319 | 302
2018-07-07 12:30 | 303 | 285
2018-07-07 13:00 | 297 | 278
2018-07-07 13:30 | 305 | 286
2018-07-07 14:00 | 314 | 296
2018-07-07 14:30 | 323 | 306
2018-07-07 15:00 | 317 | 301
2018-07-07 15:30 | 347 | 332
2018-07-07 16:00 | 351 | 339
2018-07-07 16:30 | 393 | 381
2018-07-07 17:00 | 403 | 394
2018-07-07 17:30 | 451 | 444
2018-07-07 18:00 | 465 | 460
2018-07-07 18:30 | 493 | 488
2018-07-07 19:00 | 489 | 486
2018-07-07 19:30 | 470 | 467
2018-07-07 20:00 | 472 | 467
2018-07-07 20:30 | 457 | 453
2018-07-07 21:00 | 450 | 445
2018-07-07 21:30 | 438 | 433
2018-07-07 22:00 | 433 | 427
2018-07-07 22:30 | 399 | 392
2018-07-07 23:00 | 393 | 385
2018-07-07 23:30 | 384 | 375
2018-07-08 | 382 | 373
2018-07-08 00:30 | 377 | 368
2018-07-08 01:00 | 366 | 356
2018-07-08 01:30 | 358 | 347
2018-07-08 02:00 | 355 | 344
2018-07-08 02:30 | 346 | 334
2018-07-08 03:00 | 337 | 324
2018-07-08 03:30 | 336 | 323
2018-07-08 04:00 | 330 | 316
2018-07-08 04:30 | 327 | 313
2018-07-08 05:00 | 326 | 311
2018-07-08 05:30 | 332 | 318
2018-07-08 06:00 | 330 | 316
2018-07-08 06:30 | 325 | 311
2018-07-08 07:00 | 295 | 281
2018-07-08 07:30 | 416 | 406
2018-07-08 08:00 | 451 | 398
2018-07-08 08:30 | 436 | 373
2018-07-08 09:00 | 379 | 300
2018-07-08 09:30 | 393 | 350
2018-07-08 10:00 | 435 | 383
2018-07-08 10:30 | 441 | 365
2018-07-08 11:00 | 363 | 269
2018-07-08 11:30 | 291 | 252
2018-07-08 12:00 | 267 | 227
2018-07-08 12:30 | 249 | 203
2018-07-08 13:00 | 264 | 218
2018-07-08 13:30 | 280 | 242
2018-07-08 14:00 | 280 | 236
2018-07-08 14:30 | 267 | 205
2018-07-08 15:00 | 254 | 209
2018-07-08 15:30 | 279 | 239
2018-07-08 16:00 | 286 | 249
2018-07-08 16:30 | 312 | 280
2018-07-08 17:00 | 358 | 334
2018-07-08 17:30 | 434 | 418
2018-07-08 18:00 | 494 | 484
2018-07-08 18:30 | 529 | 523
2018-07-08 19:00 | 530 | 526
2018-07-08 19:30 | 506 | 502
2018-07-08 20:00 | 486 | 481
2018-07-08 20:30 | 462 | 456
2018-07-08 21:00 | 446 | 439
2018-07-08 21:30 | 422 | 414
2018-07-08 22:00 | 410 | 399
2018-07-08 22:30 | 401 | 390
2018-07-08 23:00 | 391 | 379
2018-07-08 23:30 | 379 | 366
2018-07-09 | 367 | 353
2018-07-09 00:30 | 349 | 334
2018-07-09 01:00 | 339 | 322
2018-07-09 01:30 | 332 | 313
2018-07-09 02:00 | 334 | 314
2018-07-09 02:30 | 332 | 313
2018-07-09 03:00 | 327 | 307
2018-07-09 03:30 | 333 | 313
2018-07-09 04:00 | 339 | 320
2018-07-09 04:30 | 335 | 317
2018-07-09 05:00 | 344 | 326
2018-07-09 05:30 | 356 | 339
2018-07-09 06:00 | 360 | 344
2018-07-09 06:30 | 372 | 357
2018-07-09 07:00 | 384 | 371
2018-07-09 07:30 | 380 | 368
2018-07-09 08:00 | 334 | 321
2018-07-09 08:30 | 311 | 295
2018-07-09 09:00 | 274 | 252
2018-07-09 09:30 | 287 | 262
2018-07-09 10:00 | 282 | 257
2018-07-09 10:30 | 276 | 250
2018-07-09 11:00 | 270 | 242
2018-07-09 11:30 | 252 | 223
2018-07-09 12:00 | 249 | 219
2018-07-09 12:30 | 222 | 188
2018-07-09 13:00 | 181 | 135
2018-07-09 13:30 | 184 | 133
2018-07-09 14:00 | 190 | 140
2018-07-09 14:30 | 200 | 156
2018-07-09 15:00 | 205 | 163
2018-07-09 15:30 | 198 | 156
2018-07-09 16:00 | 185 | 134
2018-07-09 16:30 | 186 | 134
2018-07-09 17:00 | 179 | 124
2018-07-09 17:30 | 233 | 194
2018-07-09 18:00 | 268 | 239
2018-07-09 18:30 | 296 | 274
2018-07-09 19:00 | 303 | 285
2018-07-09 19:30 | 290 | 272
2018-07-09 20:00 | 267 | 244
2018-07-09 20:30 | 273 | 248
2018-07-09 21:00 | 260 | 233
2018-07-09 21:30 | 253 | 225
2018-07-09 22:00 | 250 | 222
2018-07-09 22:30 | 226 | 193
2018-07-09 23:00 | 209 | 171
2018-07-09 23:30 | 193 | 149
2018-07-10 | 241 | 205
2018-07-10 00:30 | 283 | 255
2018-07-10 01:00 | 349 | 330
2018-07-10 01:30 | 337 | 322
2018-07-10 02:00 | 329 | 313
2018-07-10 02:30 | 322 | 305
2018-07-10 03:00 | 326 | 309
2018-07-10 03:30 | 328 | 312
2018-07-10 04:00 | 331 | 315
2018-07-10 04:30 | 331 | 315
2018-07-10 05:00 | 348 | 332
2018-07-10 05:30 | 366 | 353
2018-07-10 06:00 | 386 | 374
2018-07-10 06:30 | 404 | 393
2018-07-10 07:00 | 396 | 386
2018-07-10 07:30 | 396 | 386
2018-07-10 08:00 | 356 | 344
2018-07-10 08:30 | 325 | 309
2018-07-10 09:00 | 308 | 289
2018-07-10 09:30 | 314 | 293
2018-07-10 10:00 | 303 | 283
2018-07-10 10:30 | 283 | 261
2018-07-10 11:00 | 273 | 250
2018-07-10 11:30 | 279 | 255
2018-07-10 12:00 | 265 | 241
2018-07-10 12:30 | 265 | 239
2018-07-10 13:00 | 261 | 235
2018-07-10 13:30 | 263 | 236
2018-07-10 14:00 | 268 | 241
2018-07-10 14:30 | 278 | 252
2018-07-10 15:00 | 284 | 261
2018-07-10 15:30 | 302 | 281
2018-07-10 16:00 | 321 | 303
2018-07-10 16:30 | 335 | 319
2018-07-10 17:00 | 377 | 365
2018-07-10 17:30 | 446 | 439
2018-07-10 18:00 | 488 | 483
2018-07-10 18:30 | 499 | 496
2018-07-10 19:00 | 527 | 525
2018-07-10 19:30 | 515 | 513
2018-07-10 20:00 | 494 | 491
2018-07-10 20:30 | 467 | 463
2018-07-10 21:00 | 435 | 430
2018-07-10 21:30 | 431 | 425
2018-07-10 22:00 | 410 | 404
2018-07-10 22:30 | 408 | 400
2018-07-10 23:00 | 389 | 380
2018-07-10 23:30 | 381 | 371
2018-07-11 | 365 | 355
2018-07-11 00:30 | 352 | 340
2018-07-11 01:00 | 343 | 330
2018-07-11 01:30 | 331 | 316
2018-07-11 02:00 | 332 | 316
2018-07-11 02:30 | 327 | 312
2018-07-11 03:00 | 333 | 317
2018-07-11 03:30 | 321 | 305
2018-07-11 04:00 | 323 | 306
2018-07-11 04:30 | 336 | 320
2018-07-11 05:00 | 335 | 320
2018-07-11 05:30 | 349 | 334
2018-07-11 06:00 | 363 | 349
2018-07-11 06:30 | 386 | 375
2018-07-11 07:00 | 402 | 392
2018-07-11 07:30 | 403 | 394
2018-07-11 08:00 | 370 | 361
2018-07-11 08:30 | 344 | 333
2018-07-11 09:00 | 338 | 319
2018-07-11 09:30 | 320 | 296
2018-07-11 10:00 | 301 | 277
2018-07-11 10:30 | 316 | 285
2018-07-11 11:00 | 302 | 279
2018-07-11 11:30 | 260 | 236
2018-07-11 12:00 | 264 | 236
2018-07-11 12:30 | 264 | 237
2018-07-11 13:00 | 271 | 246
2018-07-11 13:30 | 278 | 253
2018-07-11 14:00 | 271 | 245
2018-07-11 14:30 | 263 | 234
2018-07-11 15:00 | 283 | 259
2018-07-11 15:30 | 294 | 262
2018-07-11 16:00 | 310 | 285
2018-07-11 16:30 | 340 | 320
2018-07-11 17:00 | 376 | 364
2018-07-11 17:30 | 368 | 359
2018-07-11 18:00 | 351 | 341
2018-07-11 18:30 | 389 | 380
2018-07-11 19:00 | 395 | 388
2018-07-11 19:30 | 377 | 370
2018-07-11 20:00 | 359 | 351
2018-07-11 20:30 | 336 | 326
2018-07-11 21:00 | 310 | 298
2018-07-11 21:30 | 362 | 350
2018-07-11 22:00 | 418 | 410
2018-07-11 22:30 | 399 | 393
2018-07-11 23:00 | 385 | 378
2018-07-11 23:30 | 365 | 358
2018-07-12 | 349 | 340
2018-07-12 00:30 | 370 | 359
2018-07-12 01:00 | 357 | 347
2018-07-12 01:30 | 347 | 335
2018-07-12 02:00 | 340 | 327
2018-07-12 02:30 | 330 | 317
2018-07-12 03:00 | 334 | 320
2018-07-12 03:30 | 344 | 331
2018-07-12 04:00 | 342 | 330
2018-07-12 04:30 | 343 | 331
2018-07-12 05:00 | 354 | 342
2018-07-12 05:30 | 364 | 353
2018-07-12 06:00 | 377 | 367
2018-07-12 06:30 | 393 | 384
2018-07-12 07:00 | 378 | 369
2018-07-12 07:30 | 405 | 397
2018-07-12 08:00 | 382 | 374
2018-07-12 08:30 | 359 | 351
2018-07-12 09:00 | 336 | 324
2018-07-12 09:30 | 302 | 282
2018-07-12 10:00 | 273 | 247
2018-07-12 10:30 | 269 | 242
2018-07-12 11:00 | 262 | 229
2018-07-12 11:30 | 255 | 226
2018-07-12 12:00 | 247 | 217
2018-07-12 12:30 | 221 | 185
2018-07-12 13:00 | 185 | 138
2018-07-12 13:30 | 199 | 151
2018-07-12 14:00 | 206 | 161
2018-07-12 14:30 | 189 | 141
2018-07-12 15:00 | 193 | 145
2018-07-12 15:30 | 180 | 129
2018-07-12 16:00 | 256 | 223
2018-07-12 16:30 | 269 | 229
2018-07-12 17:00 | 309 | 262
2018-07-12 17:30 | 294 | 258
2018-07-12 18:00 | 283 | 265
2018-07-12 18:30 | 311 | 295
2018-07-12 19:00 | 329 | 315
2018-07-12 19:30 | 311 | 298
2018-07-12 20:00 | 290 | 276
2018-07-12 20:30 | 270 | 253
2018-07-12 21:00 | 254 | 234
2018-07-12 21:30 | 236 | 212
2018-07-12 22:00 | 216 | 186
2018-07-12 22:30 | 195 | 158
2018-07-12 23:00 | 182 | 137
2018-07-12 23:30 | 191 | 147
2018-07-13 | 187 | 143
2018-07-13 00:30 | 225 | 189
2018-07-13 01:00 | 264 | 235
2018-07-13 01:30 | 333 | 314
2018-07-13 02:00 | 334 | 319
2018-07-13 02:30 | 330 | 316
2018-07-13 03:00 | 323 | 309
2018-07-13 03:30 | 328 | 313
2018-07-13 04:00 | 318 | 302
2018-07-13 04:30 | 322 | 306
2018-07-13 05:00 | 339 | 324
2018-07-13 05:30 | 353 | 339
2018-07-13 06:00 | 361 | 349
2018-07-13 06:30 | 383 | 372
2018-07-13 07:00 | 379 | 369
2018-07-13 07:30 | 388 | 379
2018-07-13 08:00 | 350 | 341
2018-07-13 08:30 | 312 | 300
2018-07-13 09:00 | 282 | 265
2018-07-13 09:30 | 260 | 237
2018-07-13 10:00 | 245 | 219
2018-07-13 10:30 | 239 | 210
2018-07-13 11:00 | 221 | 187
2018-07-13 11:30 | 199 | 158
2018-07-13 12:00 | 217 | 179
2018-07-13 12:30 | 215 | 178
2018-07-13 13:00 | 221 | 183
2018-07-13 13:30 | 212 | 175
2018-07-13 14:00 | 168 | 115
2018-07-13 14:30 | 189 | 146
2018-07-13 15:00 | 238 | 212
2018-07-13 15:30 | 260 | 233
2018-07-13 16:00 | 286 | 248
2018-07-13 16:30 | 332 | 294
2018-07-13 17:00 | 299 | 286
2018-07-13 17:30 | 281 | 269
2018-07-13 18:00 | 278 | 266
2018-07-13 18:30 | 286 | 274
2018-07-13 19:00 | 291 | 280
2018-07-13 19:30 | 314 | 303
2018-07-13 20:00 | 332 | 323
2018-07-13 20:30 | 322 | 314
2018-07-13 21:00 | 284 | 274
2018-07-13 21:30 | 277 | 266
2018-07-13 22:00 | 264 | 250
2018-07-13 22:30 | 247 | 231
2018-07-13 23:00 | 215 | 195
2018-07-13 23:30 | 289 | 272
2018-07-14 | 348 | 337
2018-07-14 00:30 | 345 | 337
2018-07-14 01:00 | 337 | 330
2018-07-14 01:30 | 330 | 321
2018-07-14 02:00 | 327 | 318
2018-07-14 02:30 | 326 | 316
2018-07-14 03:00 | 318 | 308
2018-07-14 03:30 | 319 | 308
2018-07-14 04:00 | 326 | 315
2018-07-14 04:30 | 323 | 313
2018-07-14 05:00 | 330 | 319
2018-07-14 05:30 | 340 | 330
2018-07-14 06:00 | 341 | 331
2018-07-14 06:30 | 349 | 340
2018-07-14 07:00 | 342 | 333
2018-07-14 07:30 | 342 | 334
2018-07-14 08:00 | 308 | 299
2018-07-14 08:30 | 278 | 265
2018-07-14 09:00 | 252 | 234
2018-07-14 09:30 | 239 | 217
2018-07-14 10:00 | 227 | 202
2018-07-14 10:30 | 206 | 176
2018-07-14 11:00 | 204 | 171
2018-07-14 11:30 | 195 | 161
2018-07-14 12:00 | 191 | 153
2018-07-14 12:30 | 191 | 155
2018-07-14 13:00 | 182 | 142
2018-07-14 13:30 | 195 | 143
2018-07-14 14:00 | 185 | 148
2018-07-14 14:30 | 194 | 159
2018-07-14 15:00 | 197 | 164
2018-07-14 15:30 | 211 | 181
2018-07-14 16:00 | 241 | 216
2018-07-14 16:30 | 269 | 249
2018-07-14 17:00 | 320 | 306
2018-07-14 17:30 | 400 | 392
2018-07-14 18:00 | 453 | 449
2018-07-14 18:30 | 485 | 483
2018-07-14 19:00 | 489 | 487
2018-07-14 19:30 | 481 | 479
2018-07-14 20:00 | 468 | 466
2018-07-14 20:30 | 436 | 433
2018-07-14 21:00 | 424 | 421
2018-07-14 21:30 | 407 | 403
2018-07-14 22:00 | 398 | 393
2018-07-14 22:30 | 383 | 378
2018-07-14 23:00 | 375 | 368
2018-07-14 23:30 | 374 | 367
2018-07-15 | 363 | 355
2018-07-15 00:30 | 356 | 347
2018-07-15 01:00 | 345 | 336
2018-07-15 01:30 | 336 | 326
2018-07-15 02:00 | 328 | 317
2018-07-15 02:30 | 321 | 309
2018-07-15 03:00 | 318 | 306
2018-07-15 03:30 | 317 | 304
2018-07-15 04:00 | 317 | 305
2018-07-15 04:30 | 309 | 296
2018-07-15 05:00 | 317 | 303
2018-07-15 05:30 | 321 | 308
2018-07-15 06:00 | 304 | 290
2018-07-15 06:30 | 332 | 318
2018-07-15 07:00 | 316 | 303
2018-07-15 07:30 | 313 | 299
2018-07-15 08:00 | 269 | 253
2018-07-15 08:30 | 250 | 230
2018-07-15 09:00 | 231 | 209
2018-07-15 09:30 | 215 | 189
2018-07-15 10:00 | 171 | 134
2018-07-15 10:30 | 144 | 88
2018-07-15 11:00 | 140 | 76
2018-07-15 11:30 | 138 | 69
2018-07-15 12:00 | 140 | 71
2018-07-15 12:30 | 143 | 77
2018-07-15 13:00 | 137 | 67
2018-07-15 13:30 | 137 | 66
2018-07-15 14:00 | 156 | 99
2018-07-15 14:30 | 190 | 149
2018-07-15 15:00 | 202 | 167
2018-07-15 15:30 | 234 | 204
2018-07-15 16:00 | 268 | 245
2018-07-15 16:30 | 308 | 291
2018-07-15 17:00 | 345 | 332
2018-07-15 17:30 | 418 | 410
2018-07-15 18:00 | 472 | 468
2018-07-15 18:30 | 467 | 464
2018-07-15 19:00 | 489 | 487
2018-07-15 19:30 | 497 | 495
2018-07-15 20:00 | 471 | 468
2018-07-15 20:30 | 454 | 451
2018-07-15 21:00 | 433 | 429
2018-07-15 21:30 | 418 | 413
2018-07-15 22:00 | 400 | 394
2018-07-15 22:30 | 377 | 370
2018-07-15 23:00 | 351 | 342
2018-07-15 23:30 | 355 | 345
2018-07-16 | 352 | 342
2018-07-16 00:30 | 353 | 342
2018-07-16 01:00 | 342 | 332
2018-07-16 01:30 | 334 | 322
2018-07-16 02:00 | 332 | 319
2018-07-16 02:30 | 331 | 318
2018-07-16 03:00 | 329 | 316
2018-07-16 03:30 | 321 | 307
2018-07-16 04:00 | 323 | 309
2018-07-16 04:30 | 318 | 304
2018-07-16 05:00 | 330 | 315
2018-07-16 05:30 | 354 | 342
2018-07-16 06:00 | 362 | 352
2018-07-16 06:30 | 386 | 377
2018-07-16 07:00 | 395 | 387
2018-07-16 07:30 | 424 | 418
2018-07-16 08:00 | 380 | 375
2018-07-16 08:30 | 334 | 326
2018-07-16 09:00 | 285 | 272
2018-07-16 09:30 | 257 | 240
2018-07-16 10:00 | 206 | 179
2018-07-16 10:30 | 171 | 129
2018-07-16 11:00 | 175 | 126
2018-07-16 11:30 | 180 | 118
2018-07-16 12:00 | 166 | 123
2018-07-16 12:30 | 154 | 106
2018-07-16 13:00 | 127 | 59
2018-07-16 13:30 | 135 | 63
2018-07-16 14:00 | 139 | 72
2018-07-16 14:30 | 158 | 107
2018-07-16 15:00 | 198 | 164
2018-07-16 15:30 | 222 | 196
2018-07-16 16:00 | 202 | 173
2018-07-16 16:30 | 166 | 129
2018-07-16 17:00 | 201 | 169
2018-07-16 17:30 | 254 | 232
2018-07-16 18:00 | 300 | 285
2018-07-16 18:30 | 331 | 321
2018-07-16 19:00 | 342 | 333
2018-07-16 19:30 | 328 | 320
2018-07-16 20:00 | 312 | 303
2018-07-16 20:30 | 283 | 272
2018-07-16 21:00 | 267 | 254
2018-07-16 21:30 | 250 | 234
2018-07-16 22:00 | 227 | 207
2018-07-16 22:30 | 205 | 181
2018-07-16 23:00 | 187 | 155
2018-07-16 23:30 | 191 | 158
2018-07-17 | 247 | 224
2018-07-17 00:30 | 284 | 268
2018-07-17 01:00 | 361 | 351
2018-07-17 01:30 | 353 | 345
2018-07-17 02:00 | 349 | 341
2018-07-17 02:30 | 330 | 321
2018-07-17 03:00 | 346 | 338
2018-07-17 03:30 | 343 | 335
2018-07-17 04:00 | 344 | 335
2018-07-17 04:30 | 346 | 337
2018-07-17 05:00 | 350 | 341
2018-07-17 05:30 | 372 | 364
2018-07-17 06:00 | 390 | 384
2018-07-17 06:30 | 421 | 416
2018-07-17 07:00 | 431 | 427
2018-07-17 07:30 | 440 | 436
2018-07-17 08:00 | 403 | 400
2018-07-17 08:30 | 349 | 343
2018-07-17 09:00 | 296 | 287
2018-07-17 09:30 | 256 | 242
2018-07-17 10:00 | 244 | 224
2018-07-17 10:30 | 236 | 213
2018-07-17 11:00 | 227 | 202
2018-07-17 11:30 | 233 | 206
2018-07-17 12:00 | 223 | 195
2018-07-17 12:30 | 227 | 201
2018-07-17 13:00 | 239 | 217
2018-07-17 13:30 | 231 | 209
2018-07-17 14:00 | 238 | 215
2018-07-17 14:30 | 271 | 251
2018-07-17 15:00 | 272 | 256
2018-07-17 15:30 | 277 | 262
2018-07-17 16:00 | 309 | 295
2018-07-17 16:30 | 354 | 344
2018-07-17 17:00 | 378 | 372
2018-07-17 17:30 | 416 | 412
2018-07-17 18:00 | 470 | 468
2018-07-17 18:30 | 523 | 522
2018-07-17 19:00 | 532 | 532
2018-07-17 19:30 | 526 | 526
2018-07-17 20:00 | 505 | 504
2018-07-17 20:30 | 479 | 478
2018-07-17 21:00 | 457 | 455
2018-07-17 21:30 | 463 | 461
2018-07-17 22:00 | 447 | 445
2018-07-17 22:30 | 412 | 409
2018-07-17 23:00 | 379 | 376
2018-07-17 23:30 | 379 | 374
2018-07-18 | 382 | 377
2018-07-18 00:30 | 367 | 362
2018-07-18 01:00 | 355 | 348
2018-07-18 01:30 | 348 | 341
2018-07-18 02:00 | 344 | 336
2018-07-18 02:30 | 336 | 329
2018-07-18 03:00 | 332 | 324
2018-07-18 03:30 | 333 | 325
2018-07-18 04:00 | 328 | 320
2018-07-18 04:30 | 330 | 321
2018-07-18 05:00 | 329 | 321
2018-07-18 05:30 | 345 | 338
2018-07-18 06:00 | 367 | 361
2018-07-18 06:30 | 348 | 342
2018-07-18 07:00 | 366 | 359
2018-07-18 07:30 | 374 | 369
2018-07-18 08:00 | 362 | 357
2018-07-18 08:30 | 325 | 318
2018-07-18 09:00 | 294 | 284
2018-07-18 09:30 | 348 | 338
2018-07-18 10:00 | 361 | 353
2018-07-18 10:30 | 337 | 327
2018-07-18 11:00 | 297 | 285
2018-07-18 11:30 | 251 | 234
2018-07-18 12:00 | 245 | 224
2018-07-18 12:30 | 251 | 231
2018-07-18 13:00 | 252 | 231
2018-07-18 13:30 | 247 | 227
2018-07-18 14:00 | 255 | 235
2018-07-18 14:30 | 270 | 250
2018-07-18 15:00 | 273 | 255
2018-07-18 15:30 | 275 | 258
2018-07-18 16:00 | 305 | 290
2018-07-18 16:30 | 298 | 284
2018-07-18 17:00 | 321 | 309
2018-07-18 17:30 | 273 | 261
2018-07-18 18:00 | 307 | 295
2018-07-18 18:30 | 335 | 328
2018-07-18 19:00 | 350 | 343
2018-07-18 19:30 | 338 | 332
2018-07-18 20:00 | 322 | 315
2018-07-18 20:30 | 337 | 330
2018-07-18 21:00 | 320 | 313
2018-07-18 21:30 | 299 | 289
2018-07-18 22:00 | 278 | 266
2018-07-18 22:30 | 303 | 292
2018-07-18 23:00 | 288 | 278
2018-07-18 23:30 | 357 | 348
2018-07-19 | 350 | 344
2018-07-19 00:30 | 341 | 334
2018-07-19 01:00 | 328 | 320
2018-07-19 01:30 | 318 | 309
2018-07-19 02:00 | 313 | 303
2018-07-19 02:30 | 315 | 304
2018-07-19 03:00 | 311 | 301
2018-07-19 03:30 | 306 | 296
2018-07-19 04:00 | 311 | 300
2018-07-19 04:30 | 322 | 312
2018-07-19 05:00 | 326 | 317
2018-07-19 05:30 | 355 | 346
2018-07-19 06:00 | 366 | 359
2018-07-19 06:30 | 361 | 354
2018-07-19 07:00 | 358 | 352
2018-07-19 07:30 | 366 | 360
2018-07-19 08:00 | 341 | 336
2018-07-19 08:30 | 300 | 291
2018-07-19 09:00 | 352 | 342
2018-07-19 09:30 | 347 | 338
2018-07-19 10:00 | 348 | 338
2018-07-19 10:30 | 322 | 312
2018-07-19 11:00 | 276 | 262
2018-07-19 11:30 | 274 | 252
2018-07-19 12:00 | 277 | 252
2018-07-19 12:30 | 266 | 248
2018-07-19 13:00 | 254 | 235
2018-07-19 13:30 | 268 | 239
2018-07-19 14:00 | 283 | 263
2018-07-19 14:30 | 294 | 278
2018-07-19 15:00 | 298 | 285
2018-07-19 15:30 | 310 | 298
2018-07-19 16:00 | 314 | 306
2018-07-19 16:30 | 310 | 301
2018-07-19 17:00 | 320 | 311
2018-07-19 17:30 | 259 | 249
2018-07-19 18:00 | 287 | 275
2018-07-19 18:30 | 315 | 307
2018-07-19 19:00 | 330 | 323
2018-07-19 19:30 | 315 | 309
2018-07-19 20:00 | 301 | 294
2018-07-19 20:30 | 276 | 267
2018-07-19 21:00 | 261 | 249
2018-07-19 21:30 | 245 | 231
2018-07-19 22:00 | 221 | 204
2018-07-19 22:30 | 262 | 246
2018-07-19 23:00 | 287 | 275
2018-07-19 23:30 | 359 | 350
2018-07-20 | 358 | 351
2018-07-20 00:30 | 348 | 342
2018-07-20 01:00 | 328 | 320
2018-07-20 01:30 | 317 | 308
2018-07-20 02:00 | 315 | 305
2018-07-20 02:30 | 311 | 301
2018-07-20 03:00 | 310 | 300
2018-07-20 03:30 | 313 | 303
2018-07-20 04:00 | 317 | 307
2018-07-20 04:30 | 315 | 306
2018-07-20 05:00 | 323 | 314
2018-07-20 05:30 | 305 | 296
2018-07-20 06:00 | 336 | 327
2018-07-20 06:30 | 336 | 328
2018-07-20 07:00 | 328 | 321
2018-07-20 07:30 | 321 | 314
2018-07-20 08:00 | 284 | 275
2018-07-20 08:30 | 256 | 243
2018-07-20 09:00 | 239 | 220
2018-07-20 09:30 | 268 | 249
2018-07-20 10:00 | 262 | 243
2018-07-20 10:30 | 245 | 226
2018-07-20 11:00 | 217 | 192
2018-07-20 11:30 | 215 | 187
2018-07-20 12:00 | 194 | 163
2018-07-20 12:30 | 187 | 152
2018-07-20 13:00 | 205 | 173
2018-07-20 13:30 | 214 | 186
2018-07-20 14:00 | 220 | 194
2018-07-20 14:30 | 291 | 272
2018-07-20 15:00 | 328 | 310
2018-07-20 15:30 | 321 | 307
2018-07-20 16:00 | 343 | 334
2018-07-20 16:30 | 333 | 326
2018-07-20 17:00 | 338 | 330
2018-07-20 17:30 | 256 | 246
2018-07-20 18:00 | 279 | 265
2018-07-20 18:30 | 302 | 291
2018-07-20 19:00 | 308 | 299
2018-07-20 19:30 | 293 | 284
2018-07-20 20:00 | 274 | 264
2018-07-20 20:30 | 255 | 244
2018-07-20 21:00 | 247 | 235
2018-07-20 21:30 | 276 | 265
2018-07-20 22:00 | 269 | 259
2018-07-20 22:30 | 327 | 319
2018-07-20 23:00 | 305 | 298
2018-07-20 23:30 | 373 | 367
2018-07-21 | 367 | 363
2018-07-21 00:30 | 351 | 345
2018-07-21 01:00 | 340 | 334
2018-07-21 01:30 | 329 | 322
2018-07-21 02:00 | 321 | 314
2018-07-21 02:30 | 318 | 310
2018-07-21 03:00 | 319 | 311
2018-07-21 03:30 | 327 | 319
2018-07-21 04:00 | 329 | 322
2018-07-21 04:30 | 330 | 323
2018-07-21 05:00 | 328 | 321
2018-07-21 05:30 | 335 | 328
2018-07-21 06:00 | 340 | 333
2018-07-21 06:30 | 305 | 298
2018-07-21 07:00 | 278 | 270
2018-07-21 07:30 | 273 | 262
2018-07-21 08:00 | 230 | 215
2018-07-21 08:30 | 200 | 178
2018-07-21 09:00 | 215 | 191
2018-07-21 09:30 | 196 | 167
2018-07-21 10:00 | 179 | 144
2018-07-21 10:30 | 182 | 138
2018-07-21 11:00 | 167 | 123
2018-07-21 11:30 | 152 | 109
2018-07-21 12:00 | 154 | 109
2018-07-21 12:30 | 154 | 110
2018-07-21 13:00 | 153 | 109
2018-07-21 13:30 | 148 | 102
2018-07-21 14:00 | 148 | 104
2018-07-21 14:30 | 158 | 113
2018-07-21 15:00 | 167 | 131
2018-07-21 15:30 | 187 | 157
2018-07-21 16:00 | 222 | 199
2018-07-21 16:30 | 266 | 251
2018-07-21 17:00 | 323 | 313
2018-07-21 17:30 | 388 | 382
2018-07-21 18:00 | 434 | 430
2018-07-21 18:30 | 429 | 427
2018-07-21 19:00 | 419 | 417
2018-07-21 19:30 | 405 | 402
2018-07-21 20:00 | 389 | 386
2018-07-21 20:30 | 368 | 365
2018-07-21 21:00 | 359 | 354
2018-07-21 21:30 | 349 | 343
2018-07-21 22:00 | 341 | 335
2018-07-21 22:30 | 323 | 316
2018-07-21 23:00 | 299 | 290
2018-07-21 23:30 | 313 | 302
2018-07-22 | 345 | 336
2018-07-22 00:30 | 337 | 329
2018-07-22 01:00 | 327 | 318
2018-07-22 01:30 | 324 | 315
2018-07-22 02:00 | 313 | 303
2018-07-22 02:30 | 311 | 301
2018-07-22 03:00 | 305 | 295
2018-07-22 03:30 | 295 | 284
2018-07-22 04:00 | 307 | 297
2018-07-22 04:30 | 304 | 294
2018-07-22 05:00 | 307 | 296
2018-07-22 05:30 | 311 | 301
2018-07-22 06:00 | 312 | 302
2018-07-22 06:30 | 283 | 272
2018-07-22 07:00 | 257 | 244
2018-07-22 07:30 | 258 | 243
2018-07-22 08:00 | 242 | 225
2018-07-22 08:30 | 257 | 239
2018-07-22 09:00 | 254 | 235
2018-07-22 09:30 | 216 | 193
2018-07-22 10:00 | 199 | 171
2018-07-22 10:30 | 198 | 166
2018-07-22 11:00 | 189 | 155
2018-07-22 11:30 | 185 | 150
2018-07-22 12:00 | 181 | 145
2018-07-22 12:30 | 173 | 134
2018-07-22 13:00 | 190 | 153
2018-07-22 13:30 | 199 | 163
2018-07-22 14:00 | 197 | 162
2018-07-22 14:30 | 195 | 161
2018-07-22 15:00 | 225 | 197
2018-07-22 15:30 | 237 | 212
2018-07-22 16:00 | 264 | 243
2018-07-22 16:30 | 299 | 282
2018-07-22 17:00 | 349 | 337
2018-07-22 17:30 | 351 | 343
2018-07-22 18:00 | 393 | 388
2018-07-22 18:30 | 421 | 417
2018-07-22 19:00 | 442 | 440
2018-07-22 19:30 | 426 | 423
2018-07-22 20:00 | 408 | 405
2018-07-22 20:30 | 388 | 384
2018-07-22 21:00 | 374 | 370
2018-07-22 21:30 | 381 | 376
2018-07-22 22:00 | 378 | 373
2018-07-22 22:30 | 379 | 374
2018-07-22 23:00 | 365 | 359
2018-07-22 23:30 | 347 | 341
2018-07-23 | 336 | 328
2018-07-23 00:30 | 321 | 312
2018-07-23 01:00 | 312 | 302
2018-07-23 01:30 | 310 | 300
2018-07-23 02:00 | 304 | 293
2018-07-23 02:30 | 310 | 298
2018-07-23 03:00 | 312 | 302
2018-07-23 03:30 | 310 | 299
2018-07-23 04:00 | 310 | 299
2018-07-23 04:30 | 315 | 304
2018-07-23 05:00 | 322 | 312
2018-07-23 05:30 | 329 | 320
2018-07-23 06:00 | 347 | 339
2018-07-23 06:30 | 329 | 321
2018-07-23 07:00 | 340 | 331
2018-07-23 07:30 | 358 | 350
2018-07-23 08:00 | 343 | 335
2018-07-23 08:30 | 354 | 346
2018-07-23 09:00 | 318 | 308
2018-07-23 09:30 | 282 | 270
2018-07-23 10:00 | 267 | 251
2018-07-23 10:30 | 261 | 243
2018-07-23 11:00 | 252 | 233
2018-07-23 11:30 | 251 | 231
2018-07-23 12:00 | 249 | 229
2018-07-23 12:30 | 258 | 238
2018-07-23 13:00 | 265 | 247
2018-07-23 13:30 | 279 | 263
2018-07-23 14:00 | 261 | 244
2018-07-23 14:30 | 266 | 249
2018-07-23 15:00 | 292 | 277
2018-07-23 15:30 | 309 | 295
2018-07-23 16:00 | 353 | 342
2018-07-23 16:30 | 388 | 381
2018-07-23 17:00 | 413 | 409
2018-07-23 17:30 | 401 | 397
2018-07-23 18:00 | 451 | 447
2018-07-23 18:30 | 487 | 484
2018-07-23 19:00 | 500 | 498
2018-07-23 19:30 | 483 | 482
2018-07-23 20:00 | 459 | 457
2018-07-23 20:30 | 436 | 433
2018-07-23 21:00 | 414 | 411
2018-07-23 21:30 | 390 | 386
2018-07-23 22:00 | 369 | 364
2018-07-23 22:30 | 370 | 365
2018-07-23 23:00 | 379 | 373
2018-07-23 23:30 | 373 | 368
2018-07-24 | 346 | 340
2018-07-24 00:30 | 338 | 330
2018-07-24 01:00 | 341 | 333
2018-07-24 01:30 | 340 | 332
2018-07-24 02:00 | 335 | 327
2018-07-24 02:30 | 338 | 329
2018-07-24 03:00 | 335 | 327
2018-07-24 03:30 | 326 | 317
2018-07-24 04:00 | 331 | 322
2018-07-24 04:30 | 333 | 324
2018-07-24 05:00 | 342 | 333
2018-07-24 05:30 | 355 | 347
2018-07-24 06:00 | 374 | 367
2018-07-24 06:30 | 358 | 351
2018-07-24 07:00 | 365 | 358
2018-07-24 07:30 | 375 | 369
2018-07-24 08:00 | 356 | 350
2018-07-24 08:30 | 314 | 307
2018-07-24 09:00 | 325 | 315
2018-07-24 09:30 | 290 | 279
2018-07-24 10:00 | 288 | 275
2018-07-24 10:30 | 281 | 265
2018-07-24 11:00 | 282 | 267
2018-07-24 11:30 | 293 | 279
2018-07-24 12:00 | 265 | 250
2018-07-24 12:30 | 251 | 235
2018-07-24 13:00 | 271 | 254
2018-07-24 13:30 | 279 | 263
2018-07-24 14:00 | 277 | 261
2018-07-24 14:30 | 295 | 280
2018-07-24 15:00 | 331 | 319
2018-07-24 15:30 | 345 | 336
2018-07-24 16:00 | 333 | 324
2018-07-24 16:30 | 382 | 374
2018-07-24 17:00 | 417 | 412
2018-07-24 17:30 | 409 | 405
2018-07-24 18:00 | 445 | 442
2018-07-24 18:30 | 480 | 479
2018-07-24 19:00 | 499 | 498
2018-07-24 19:30 | 487 | 486
2018-07-24 20:00 | 465 | 464
2018-07-24 20:30 | 466 | 464
2018-07-24 21:00 | 435 | 434
2018-07-24 21:30 | 454 | 452
2018-07-24 22:00 | 447 | 445
2018-07-24 22:30 | 419 | 417
2018-07-24 23:00 | 389 | 386
2018-07-24 23:30 | 358 | 355
2018-07-25 | 338 | 332
2018-07-25 00:30 | 328 | 321
2018-07-25 01:00 | 321 | 313
2018-07-25 01:30 | 317 | 308
2018-07-25 02:00 | 312 | 303
2018-07-25 02:30 | 310 | 301
2018-07-25 03:00 | 305 | 296
2018-07-25 03:30 | 313 | 304
2018-07-25 04:00 | 322 | 314
2018-07-25 04:30 | 336 | 328
2018-07-25 05:00 | 336 | 329
2018-07-25 05:30 | 350 | 343
2018-07-25 06:00 | 365 | 359
2018-07-25 06:30 | 342 | 336
2018-07-25 07:00 | 357 | 352
2018-07-25 07:30 | 380 | 375
2018-07-25 08:00 | 363 | 358
2018-07-25 08:30 | 331 | 324
2018-07-25 09:00 | 343 | 334
2018-07-25 09:30 | 309 | 298
2018-07-25 10:00 | 289 | 273
2018-07-25 10:30 | 275 | 253
2018-07-25 11:00 | 285 | 266
2018-07-25 11:30 | 279 | 264
2018-07-25 12:00 | 265 | 250
2018-07-25 12:30 | 258 | 241
2018-07-25 13:00 | 271 | 254
2018-07-25 13:30 | 296 | 281
2018-07-25 14:00 | 292 | 280
2018-07-25 14:30 | 302 | 290
2018-07-25 15:00 | 285 | 273
2018-07-25 15:30 | 326 | 314
2018-07-25 16:00 | 328 | 318
2018-07-25 16:30 | 302 | 292
2018-07-25 17:00 | 303 | 294
2018-07-25 17:30 | 294 | 284
2018-07-25 18:00 | 309 | 300
2018-07-25 18:30 | 336 | 329
2018-07-25 19:00 | 330 | 324
2018-07-25 19:30 | 306 | 300
2018-07-25 20:00 | 291 | 283
2018-07-25 20:30 | 275 | 265
2018-07-25 21:00 | 249 | 237
2018-07-25 21:30 | 264 | 251
2018-07-25 22:00 | 256 | 242
2018-07-25 22:30 | 232 | 216
2018-07-25 23:00 | 325 | 312
2018-07-25 23:30 | 350 | 342
2018-07-26 | 336 | 329
2018-07-26 00:30 | 328 | 321
2018-07-26 01:00 | 327 | 319
2018-07-26 01:30 | 323 | 314
2018-07-26 02:00 | 324 | 316
2018-07-26 02:30 | 323 | 315
2018-07-26 03:00 | 313 | 304
2018-07-26 03:30 | 304 | 294
2018-07-26 04:00 | 303 | 292
2018-07-26 04:30 | 310 | 300
2018-07-26 05:00 | 312 | 302
2018-07-26 05:30 | 327 | 317
2018-07-26 06:00 | 351 | 343
2018-07-26 06:30 | 379 | 373
2018-07-26 07:00 | 391 | 386
2018-07-26 07:30 | 367 | 362
2018-07-26 08:00 | 347 | 341
2018-07-26 08:30 | 321 | 313
2018-07-26 09:00 | 287 | 276
2018-07-26 09:30 | 276 | 262
2018-07-26 10:00 | 255 | 238
2018-07-26 10:30 | 249 | 221
2018-07-26 11:00 | 244 | 210
2018-07-26 11:30 | 240 | 204
2018-07-26 12:00 | 219 | 178
2018-07-26 12:30 | 210 | 170
2018-07-26 13:00 | 218 | 177
2018-07-26 13:30 | 219 | 190
2018-07-26 14:00 | 226 | 199
2018-07-26 14:30 | 243 | 219
2018-07-26 15:00 | 269 | 250
2018-07-26 15:30 | 278 | 253
2018-07-26 16:00 | 305 | 273
2018-07-26 16:30 | 344 | 318
2018-07-26 17:00 | 333 | 315
2018-07-26 17:30 | 316 | 305
2018-07-26 18:00 | 304 | 295
2018-07-26 18:30 | 349 | 340
2018-07-26 19:00 | 354 | 347
2018-07-26 19:30 | 331 | 324
2018-07-26 20:00 | 316 | 308
2018-07-26 20:30 | 327 | 318
2018-07-26 21:00 | 327 | 318
2018-07-26 21:30 | 361 | 352
2018-07-26 22:00 | 340 | 333
2018-07-26 22:30 | 313 | 305
2018-07-26 23:00 | 353 | 345
2018-07-26 23:30 | 363 | 356
2018-07-27 | 346 | 340
2018-07-27 00:30 | 339 | 332
2018-07-27 01:00 | 327 | 318
2018-07-27 01:30 | 319 | 310
2018-07-27 02:00 | 341 | 332
2018-07-27 02:30 | 344 | 336
2018-07-27 03:00 | 299 | 290
2018-07-27 03:30 | 332 | 323
2018-07-27 04:00 | 325 | 317
2018-07-27 04:30 | 341 | 332
2018-07-27 05:00 | 333 | 325
2018-07-27 05:30 | 334 | 326
2018-07-27 06:00 | 354 | 346
2018-07-27 06:30 | 350 | 343
2018-07-27 07:00 | 350 | 343
2018-07-27 07:30 | 372 | 367
2018-07-27 08:00 | 376 | 371
2018-07-27 08:30 | 349 | 343
2018-07-27 09:00 | 304 | 296
2018-07-27 09:30 | 269 | 257
2018-07-27 10:00 | 242 | 220
2018-07-27 10:30 | 229 | 208
2018-07-27 11:00 | 231 | 207
2018-07-27 11:30 | 221 | 197
2018-07-27 12:00 | 205 | 178
2018-07-27 12:30 | 187 | 155
2018-07-27 13:00 | 177 | 142
2018-07-27 13:30 | 174 | 138
2018-07-27 14:00 | 192 | 161
2018-07-27 14:30 | 232 | 207
2018-07-27 15:00 | 229 | 205
2018-07-27 15:30 | 223 | 197
2018-07-27 16:00 | 274 | 253
2018-07-27 16:30 | 285 | 269
2018-07-27 17:00 | 308 | 295
2018-07-27 17:30 | 354 | 344
2018-07-27 18:00 | 345 | 337
2018-07-27 18:30 | 360 | 354
2018-07-27 19:00 | 378 | 373
2018-07-27 19:30 | 366 | 361
2018-07-27 20:00 | 339 | 333
2018-07-27 20:30 | 324 | 317
2018-07-27 21:00 | 303 | 294
2018-07-27 21:30 | 291 | 281
2018-07-27 22:00 | 265 | 252
2018-07-27 22:30 | 305 | 293
2018-07-27 23:00 | 353 | 345
2018-07-27 23:30 | 362 | 356
2018-07-28 | 348 | 342
2018-07-28 00:30 | 336 | 329
2018-07-28 01:00 | 328 | 320
2018-07-28 01:30 | 313 | 304
2018-07-28 02:00 | 310 | 300
2018-07-28 02:30 | 309 | 300
2018-07-28 03:00 | 309 | 299
2018-07-28 03:30 | 306 | 296
2018-07-28 04:00 | 306 | 296
2018-07-28 04:30 | 337 | 328
2018-07-28 05:00 | 329 | 321
2018-07-28 05:30 | 337 | 329
2018-07-28 06:00 | 315 | 306
2018-07-28 06:30 | 315 | 305
2018-07-28 07:00 | 305 | 295
2018-07-28 07:30 | 321 | 311
2018-07-28 08:00 | 298 | 288
2018-07-28 08:30 | 263 | 250
2018-07-28 09:00 | 242 | 218
2018-07-28 09:30 | 213 | 188
2018-07-28 10:00 | 223 | 196
2018-07-28 10:30 | 212 | 186
2018-07-28 11:00 | 211 | 184
2018-07-28 11:30 | 195 | 165
2018-07-28 12:00 | 178 | 142
2018-07-28 12:30 | 171 | 134
2018-07-28 13:00 | 181 | 146
2018-07-28 13:30 | 176 | 141
2018-07-28 14:00 | 173 | 137
2018-07-28 14:30 | 175 | 139
2018-07-28 15:00 | 188 | 155
2018-07-28 15:30 | 204 | 174
2018-07-28 16:00 | 231 | 206
2018-07-28 16:30 | 237 | 216
2018-07-28 17:00 | 292 | 276
2018-07-28 17:30 | 367 | 358
2018-07-28 18:00 | 424 | 420
2018-07-28 18:30 | 459 | 456
2018-07-28 19:00 | 463 | 461
2018-07-28 19:30 | 446 | 445
2018-07-28 20:00 | 428 | 426
2018-07-28 20:30 | 403 | 400
2018-07-28 21:00 | 384 | 381
2018-07-28 21:30 | 371 | 367
2018-07-28 22:00 | 360 | 355
2018-07-28 22:30 | 370 | 365
2018-07-28 23:00 | 354 | 350
2018-07-28 23:30 | 366 | 361
2018-07-29 | 353 | 348
2018-07-29 00:30 | 338 | 333
2018-07-29 01:00 | 331 | 325
2018-07-29 01:30 | 328 | 321
2018-07-29 02:00 | 316 | 308
2018-07-29 02:30 | 314 | 306
2018-07-29 03:00 | 318 | 310
2018-07-29 03:30 | 321 | 314
2018-07-29 04:00 | 311 | 304
2018-07-29 04:30 | 310 | 302
2018-07-29 05:00 | 317 | 309
2018-07-29 05:30 | 329 | 322
2018-07-29 06:00 | 296 | 288
2018-07-29 06:30 | 304 | 295
2018-07-29 07:00 | 293 | 283
2018-07-29 07:30 | 279 | 268
2018-07-29 08:00 | 244 | 231
2018-07-29 08:30 | 220 | 202
2018-07-29 09:00 | 206 | 183
2018-07-29 09:30 | 184 | 157
2018-07-29 10:00 | 210 | 186
2018-07-29 10:30 | 208 | 185
2018-07-29 11:00 | 192 | 165
2018-07-29 11:30 | 186 | 160
2018-07-29 12:00 | 165 | 135
2018-07-29 12:30 | 163 | 131
2018-07-29 13:00 | 170 | 140
2018-07-29 13:30 | 171 | 141
2018-07-29 14:00 | 171 | 140
2018-07-29 14:30 | 187 | 161
2018-07-29 15:00 | 200 | 176
2018-07-29 15:30 | 231 | 211
2018-07-29 16:00 | 264 | 249
2018-07-29 16:30 | 272 | 259
2018-07-29 17:00 | 334 | 325
2018-07-29 17:30 | 411 | 406
2018-07-29 18:00 | 472 | 470
2018-07-29 18:30 | 520 | 519
2018-07-29 19:00 | 535 | 534
2018-07-29 19:30 | 514 | 513
2018-07-29 20:00 | 493 | 493
2018-07-29 20:30 | 480 | 480
2018-07-29 21:00 | 451 | 450
2018-07-29 21:30 | 430 | 429
2018-07-29 22:00 | 406 | 404
2018-07-29 22:30 | 415 | 413
2018-07-29 23:00 | 391 | 389
2018-07-29 23:30 | 371 | 369
2018-07-30 | 360 | 357
2018-07-30 00:30 | 344 | 340
2018-07-30 01:00 | 334 | 330
2018-07-30 01:30 | 308 | 304
2018-07-30 02:00 | 325 | 320
2018-07-30 02:30 | 322 | 316
2018-07-30 03:00 | 323 | 317
2018-07-30 03:30 | 321 | 315
2018-07-30 04:00 | 321 | 315
2018-07-30 04:30 | 324 | 319
2018-07-30 05:00 | 330 | 325
2018-07-30 05:30 | 343 | 338
2018-07-30 06:00 | 330 | 325
2018-07-30 06:30 | 349 | 344
2018-07-30 07:00 | 361 | 357
2018-07-30 07:30 | 377 | 373
2018-07-30 08:00 | 341 | 338
2018-07-30 08:30 | 280 | 274
2018-07-30 09:00 | 241 | 230
2018-07-30 09:30 | 207 | 188
2018-07-30 10:00 | 209 | 188
2018-07-30 10:30 | 192 | 169
2018-07-30 11:00 | 171 | 137
2018-07-30 11:30 | 147 | 97
2018-07-30 12:00 | 146 | 93
2018-07-30 12:30 | 143 | 96
2018-07-30 13:00 | 136 | 88
2018-07-30 13:30 | 136 | 85
2018-07-30 14:00 | 144 | 96
2018-07-30 14:30 | 185 | 153
2018-07-30 15:00 | 209 | 184
2018-07-30 15:30 | 224 | 203
2018-07-30 16:00 | 275 | 259
2018-07-30 16:30 | 281 | 269
2018-07-30 17:00 | 346 | 336
2018-07-30 17:30 | 421 | 417
2018-07-30 18:00 | 506 | 505
2018-07-30 18:30 | 544 | 544
2018-07-30 19:00 | 549 | 549
2018-07-30 19:30 | 518 | 518
2018-07-30 20:00 | 493 | 493
2018-07-30 20:30 | 476 | 475
2018-07-30 21:00 | 451 | 450
2018-07-30 21:30 | 429 | 428
2018-07-30 22:00 | 409 | 408
2018-07-30 22:30 | 413 | 411
2018-07-30 23:00 | 384 | 382
2018-07-30 23:30 | 384 | 382
2018-07-31 | 364 | 362
2018-07-31 00:30 | 363 | 360
2018-07-31 01:00 | 350 | 348
2018-07-31 01:30 | 338 | 335
2018-07-31 02:00 | 314 | 309
2018-07-31 02:30 | 318 | 312
2018-07-31 03:00 | 313 | 306
2018-07-31 03:30 | 315 | 308
2018-07-31 04:00 | 312 | 305
2018-07-31 04:30 | 325 | 318
2018-07-31 05:00 | 334 | 328
2018-07-31 05:30 | 351 | 345
2018-07-31 06:00 | 351 | 346
2018-07-31 06:30 | 377 | 372
2018-07-31 07:00 | 398 | 395
2018-07-31 07:30 | 403 | 400
2018-07-31 08:00 | 349 | 346
2018-07-31 08:30 | 280 | 274
2018-07-31 09:00 | 242 | 230
2018-07-31 09:30 | 211 | 194
2018-07-31 10:00 | 221 | 197
2018-07-31 10:30 | 212 | 184
2018-07-31 11:00 | 153 | 118
2018-07-31 11:30 | 152 | 106
2018-07-31 12:00 | 152 | 115
2018-07-31 12:30 | 160 | 123
2018-07-31 13:00 | 148 | 105
2018-07-31 13:30 | 173 | 141
2018-07-31 14:00 | 183 | 153
2018-07-31 14:30 | 165 | 158
2018-07-31 15:00 | 199 | 197
2018-07-31 15:30 | 217 | 216
2018-07-31 16:00 | 262 | 261
2018-07-31 16:30 | 283 | 272
2018-07-31 17:00 | 345 | 336
2018-07-31 17:30 | 431 | 426
2018-07-31 18:00 | 489 | 487
2018-07-31 18:30 | 527 | 527
2018-07-31 19:00 | 534 | 534
2018-07-31 19:30 | 521 | 521
2018-07-31 20:00 | 496 | 496
2018-07-31 20:30 | 473 | 473
2018-07-31 21:00 | 445 | 445
2018-07-31 21:30 | 379 | 378
2018-07-31 22:00 | 394 | 391
2018-07-31 22:30 | 400 | 397
2018-07-31 23:00 | 381 | 378
2018-07-31 23:30 | 373 | 370
2018-08-01 | 352 | 349
2018-08-01 00:30 | 339 | 335
2018-08-01 01:00 | 327 | 322
2018-08-01 01:30 | 319 | 314
2018-08-01 02:00 | 318 | 313
2018-08-01 02:30 | 285 | 278
2018-08-01 03:00 | 266 | 258
2018-08-01 03:30 | 238 | 229
2018-08-01 04:00 | 247 | 236
2018-08-01 04:30 | 258 | 247
2018-08-01 05:00 | 252 | 242
2018-08-01 05:30 | 269 | 259
2018-08-01 06:00 | 236 | 226
2018-08-01 06:30 | 224 | 210
2018-08-01 07:00 | 236 | 223
2018-08-01 07:30 | 183 | 167
2018-08-01 08:00 | 142 | 112
2018-08-01 08:30 | 111 | 56
2018-08-01 09:00 | 151 | 110
2018-08-01 09:30 | 178 | 140
2018-08-01 10:00 | 179 | 135
2018-08-01 10:30 | 131 | 61
2018-08-01 11:00 | 118 | 41
2018-08-01 11:30 | 122 | 58
2018-08-01 12:00 | 124 | 62
2018-08-01 12:30 | 118 | 48
2018-08-01 13:00 | 118 | 51
2018-08-01 13:30 | 130 | 73
2018-08-01 14:00 | 128 | 67
2018-08-01 14:30 | 124 | 52
2018-08-01 15:00 | 115 | 40
2018-08-01 15:30 | 122 | 61
2018-08-01 16:00 | 132 | 78
2018-08-01 16:30 | 133 | 74
2018-08-01 17:00 | 140 | 87
2018-08-01 17:30 | 191 | 161
2018-08-01 18:00 | 241 | 223
2018-08-01 18:30 | 281 | 271
2018-08-01 19:00 | 260 | 253
2018-08-01 19:30 | 265 | 258
2018-08-01 20:00 | 251 | 244
2018-08-01 20:30 | 232 | 224
2018-08-01 21:00 | 219 | 209
2018-08-01 21:30 | 200 | 187
2018-08-01 22:00 | 205 | 191
2018-08-01 22:30 | 206 | 193
2018-08-01 23:00 | 186 | 171
2018-08-01 23:30 | 171 | 152
2018-08-02 | 222 | 206
2018-08-02 00:30 | 273 | 263
2018-08-02 01:00 | 332 | 325
2018-08-02 01:30 | 332 | 326
2018-08-02 02:00 | 338 | 331
2018-08-02 02:30 | 331 | 324
2018-08-02 03:00 | 330 | 322
2018-08-02 03:30 | 329 | 320
2018-08-02 04:00 | 329 | 320
2018-08-02 04:30 | 340 | 331
2018-08-02 05:00 | 351 | 344
2018-08-02 05:30 | 363 | 356
2018-08-02 06:00 | 350 | 343
2018-08-02 06:30 | 371 | 365
2018-08-02 07:00 | 386 | 380
2018-08-02 07:30 | 380 | 375
2018-08-02 08:00 | 358 | 352
2018-08-02 08:30 | 288 | 279
2018-08-02 09:00 | 257 | 245
2018-08-02 09:30 | 233 | 215
2018-08-02 10:00 | 236 | 215
2018-08-02 10:30 | 220 | 199
2018-08-02 11:00 | 223 | 199
2018-08-02 11:30 | 217 | 191
2018-08-02 12:00 | 214 | 187
2018-08-02 12:30 | 217 | 189
2018-08-02 13:00 | 217 | 189
2018-08-02 13:30 | 218 | 191
2018-08-02 14:00 | 224 | 197
2018-08-02 14:30 | 232 | 206
2018-08-02 15:00 | 237 | 211
2018-08-02 15:30 | 253 | 230
2018-08-02 16:00 | 282 | 263
2018-08-02 16:30 | 296 | 280
2018-08-02 17:00 | 342 | 330
2018-08-02 17:30 | 416 | 409
2018-08-02 18:00 | 476 | 473
2018-08-02 18:30 | 511 | 510
2018-08-02 19:00 | 512 | 511
2018-08-02 19:30 | 504 | 503
2018-08-02 20:00 | 488 | 487
2018-08-02 20:30 | 474 | 472
2018-08-02 21:00 | 450 | 448
2018-08-02 21:30 | 423 | 420
2018-08-02 22:00 | 401 | 398
2018-08-02 22:30 | 437 | 433
2018-08-02 23:00 | 422 | 419
2018-08-02 23:30 | 395 | 391
2018-08-03 | 379 | 375
2018-08-03 00:30 | 369 | 364
2018-08-03 01:00 | 348 | 342
2018-08-03 01:30 | 343 | 336
2018-08-03 02:00 | 339 | 331
2018-08-03 02:30 | 340 | 332
2018-08-03 03:00 | 330 | 322
2018-08-03 03:30 | 328 | 319
2018-08-03 04:00 | 331 | 322
2018-08-03 04:30 | 329 | 321
2018-08-03 05:00 | 334 | 325
2018-08-03 05:30 | 346 | 338
2018-08-03 06:00 | 339 | 331
2018-08-03 06:30 | 363 | 356
2018-08-03 07:00 | 373 | 367
2018-08-03 07:30 | 373 | 367
2018-08-03 08:00 | 331 | 324
2018-08-03 08:30 | 271 | 259
2018-08-03 09:00 | 236 | 219
2018-08-03 09:30 | 210 | 186
2018-08-03 10:00 | 236 | 212
2018-08-03 10:30 | 214 | 188
2018-08-03 11:00 | 224 | 197
2018-08-03 11:30 | 225 | 199
2018-08-03 12:00 | 250 | 219
2018-08-03 12:30 | 230 | 196
2018-08-03 13:00 | 235 | 202
2018-08-03 13:30 | 226 | 201
2018-08-03 14:00 | 253 | 231
2018-08-03 14:30 | 254 | 235
2018-08-03 15:00 | 250 | 232
2018-08-03 15:30 | 257 | 239
2018-08-03 16:00 | 277 | 260
2018-08-03 16:30 | 293 | 278
2018-08-03 17:00 | 339 | 329
2018-08-03 17:30 | 405 | 398
2018-08-03 18:00 | 472 | 468
2018-08-03 18:30 | 509 | 508
2018-08-03 19:00 | 500 | 499
2018-08-03 19:30 | 479 | 478
2018-08-03 20:00 | 455 | 454
2018-08-03 20:30 | 429 | 427
2018-08-03 21:00 | 410 | 408
2018-08-03 21:30 | 408 | 405
2018-08-03 22:00 | 392 | 388
2018-08-03 22:30 | 418 | 414
2018-08-03 23:00 | 402 | 399
2018-08-03 23:30 | 403 | 399
2018-08-04 | 389 | 385
2018-08-04 00:30 | 379 | 374
2018-08-04 01:00 | 354 | 348
2018-08-04 01:30 | 352 | 345
2018-08-04 02:00 | 349 | 341
2018-08-04 02:30 | 346 | 339
2018-08-04 03:00 | 338 | 331
2018-08-04 03:30 | 343 | 335
2018-08-04 04:00 | 335 | 328
2018-08-04 04:30 | 329 | 321
2018-08-04 05:00 | 333 | 325
2018-08-04 05:30 | 350 | 342
2018-08-04 06:00 | 313 | 305
2018-08-04 06:30 | 327 | 318
2018-08-04 07:00 | 321 | 312
2018-08-04 07:30 | 340 | 331
2018-08-04 08:00 | 320 | 311
2018-08-04 08:30 | 288 | 276
2018-08-04 09:00 | 266 | 250
2018-08-04 09:30 | 251 | 232
2018-08-04 10:00 | 258 | 239
2018-08-04 10:30 | 231 | 209
2018-08-04 11:00 | 205 | 178
2018-08-04 11:30 | 203 | 174
2018-08-04 12:00 | 200 | 170
2018-08-04 12:30 | 188 | 157
2018-08-04 13:00 | 189 | 156
2018-08-04 13:30 | 202 | 172
2018-08-04 14:00 | 189 | 156
2018-08-04 14:30 | 206 | 169
2018-08-04 15:00 | 206 | 163
2018-08-04 15:30 | 223 | 188
2018-08-04 16:00 | 256 | 226
2018-08-04 16:30 | 257 | 231
2018-08-04 17:00 | 308 | 287
2018-08-04 17:30 | 378 | 368
2018-08-04 18:00 | 430 | 425
2018-08-04 18:30 | 462 | 460
2018-08-04 19:00 | 480 | 479
2018-08-04 19:30 | 464 | 463
2018-08-04 20:00 | 437 | 436
2018-08-04 20:30 | 422 | 421
2018-08-04 21:00 | 428 | 427
2018-08-04 21:30 | 418 | 417
2018-08-04 22:00 | 400 | 398
2018-08-04 22:30 | 414 | 412
2018-08-04 23:00 | 402 | 399
2018-08-04 23:30 | 392 | 389
2018-08-05 | 390 | 386
2018-08-05 00:30 | 374 | 370
2018-08-05 01:00 | 358 | 354
2018-08-05 01:30 | 350 | 346
2018-08-05 02:00 | 354 | 349
2018-08-05 02:30 | 343 | 337
2018-08-05 03:00 | 340 | 335
2018-08-05 03:30 | 339 | 334
2018-08-05 04:00 | 337 | 332
2018-08-05 04:30 | 317 | 311
2018-08-05 05:00 | 340 | 334
2018-08-05 05:30 | 351 | 346
2018-08-05 06:00 | 334 | 329
2018-08-05 06:30 | 345 | 339
2018-08-05 07:00 | 325 | 319
2018-08-05 07:30 | 311 | 304
2018-08-05 08:00 | 276 | 267
2018-08-05 08:30 | 246 | 232
2018-08-05 09:00 | 220 | 202
2018-08-05 09:30 | 213 | 192
2018-08-05 10:00 | 222 | 201
2018-08-05 10:30 | 214 | 192
2018-08-05 11:00 | 182 | 156
2018-08-05 11:30 | 187 | 157
2018-08-05 12:00 | 183 | 152
2018-08-05 12:30 | 166 | 134
2018-08-05 13:00 | 171 | 139
2018-08-05 13:30 | 173 | 144
2018-08-05 14:00 | 182 | 155
2018-08-05 14:30 | 174 | 146
2018-08-05 15:00 | 174 | 145
2018-08-05 15:30 | 210 | 185
2018-08-05 16:00 | 259 | 240
2018-08-05 16:30 | 249 | 232
2018-08-05 17:00 | 301 | 288
2018-08-05 17:30 | 390 | 382
2018-08-05 18:00 | 467 | 464
2018-08-05 18:30 | 522 | 521
2018-08-05 19:00 | 495 | 495
2018-08-05 19:30 | 475 | 474
2018-08-05 20:00 | 481 | 479
2018-08-05 20:30 | 462 | 461
2018-08-05 21:00 | 444 | 442
2018-08-05 21:30 | 423 | 420
2018-08-05 22:00 | 388 | 384
2018-08-05 22:30 | 399 | 394
2018-08-05 23:00 | 380 | 376
2018-08-05 23:30 | 380 | 375
2018-08-06 | 379 | 373
2018-08-06 00:30 | 367 | 361
2018-08-06 01:00 | 352 | 345
2018-08-06 01:30 | 345 | 338
2018-08-06 02:00 | 351 | 344
2018-08-06 02:30 | 336 | 329
2018-08-06 03:00 | 328 | 320
2018-08-06 03:30 | 332 | 324
2018-08-06 04:00 | 343 | 335
2018-08-06 04:30 | 351 | 344
2018-08-06 05:00 | 343 | 336
2018-08-06 05:30 | 361 | 355
2018-08-06 06:00 | 347 | 341
2018-08-06 06:30 | 373 | 367
2018-08-06 07:00 | 381 | 376
2018-08-06 07:30 | 396 | 391
2018-08-06 08:00 | 361 | 356
2018-08-06 08:30 | 308 | 299
2018-08-06 09:00 | 277 | 263
2018-08-06 09:30 | 252 | 234
2018-08-06 10:00 | 264 | 247
2018-08-06 10:30 | 245 | 228
2018-08-06 11:00 | 221 | 202
2018-08-06 11:30 | 220 | 198
2018-08-06 12:00 | 217 | 192
2018-08-06 12:30 | 231 | 207
2018-08-06 13:00 | 228 | 205
2018-08-06 13:30 | 232 | 210
2018-08-06 14:00 | 249 | 229
2018-08-06 14:30 | 262 | 244
2018-08-06 15:00 | 286 | 271
2018-08-06 15:30 | 342 | 331
2018-08-06 16:00 | 336 | 327
2018-08-06 16:30 | 327 | 318
2018-08-06 17:00 | 324 | 316
2018-08-06 17:30 | 344 | 338
2018-08-06 18:00 | 360 | 354
2018-08-06 18:30 | 388 | 384
2018-08-06 19:00 | 357 | 354
2018-08-06 19:30 | 354 | 350
2018-08-06 20:00 | 358 | 353
2018-08-06 20:30 | 345 | 341
2018-08-06 21:00 | 327 | 321
2018-08-06 21:30 | 362 | 357
2018-08-06 22:00 | 366 | 362
2018-08-06 22:30 | 320 | 315
2018-08-06 23:00 | 413 | 408
2018-08-06 23:30 | 401 | 398
2018-08-07 | 388 | 385
2018-08-07 00:30 | 378 | 374
2018-08-07 01:00 | 369 | 365
2018-08-07 01:30 | 357 | 352
2018-08-07 02:00 | 352 | 347
2018-08-07 02:30 | 352 | 346
2018-08-07 03:00 | 364 | 359
2018-08-07 03:30 | 363 | 359
2018-08-07 04:00 | 373 | 368
2018-08-07 04:30 | 383 | 379
2018-08-07 05:00 | 395 | 392
2018-08-07 05:30 | 413 | 409
2018-08-07 06:00 | 394 | 391
2018-08-07 06:30 | 420 | 417
2018-08-07 07:00 | 443 | 440
2018-08-07 07:30 | 461 | 459
2018-08-07 08:00 | 465 | 463
2018-08-07 08:30 | 454 | 452
2018-08-07 09:00 | 430 | 427
2018-08-07 09:30 | 371 | 366
2018-08-07 10:00 | 428 | 420
2018-08-07 10:30 | 397 | 391
2018-08-07 11:00 | 379 | 371
2018-08-07 11:30 | 384 | 376
2018-08-07 12:00 | 368 | 360
2018-08-07 12:30 | 357 | 349
2018-08-07 13:00 | 370 | 361
2018-08-07 13:30 | 338 | 328
2018-08-07 14:00 | 328 | 316
2018-08-07 14:30 | 330 | 318
2018-08-07 15:00 | 355 | 344
2018-08-07 15:30 | 390 | 381
2018-08-07 16:00 | 421 | 414
2018-08-07 16:30 | 408 | 403
2018-08-07 17:00 | 374 | 368
2018-08-07 17:30 | 346 | 337
2018-08-07 18:00 | 359 | 352
2018-08-07 18:30 | 393 | 388
2018-08-07 19:00 | 410 | 406
2018-08-07 19:30 | 384 | 381
2018-08-07 20:00 | 352 | 348
2018-08-07 20:30 | 322 | 316
2018-08-07 21:00 | 299 | 291
2018-08-07 21:30 | 283 | 274
2018-08-07 22:00 | 319 | 309
2018-08-07 22:30 | 316 | 308
2018-08-07 23:00 | 359 | 353
2018-08-07 23:30 | 360 | 356
2018-08-08 | 353 | 348
2018-08-08 00:30 | 349 | 343
2018-08-08 01:00 | 337 | 330
2018-08-08 01:30 | 326 | 318
2018-08-08 02:00 | 305 | 295
2018-08-08 02:30 | 324 | 314
2018-08-08 03:00 | 313 | 303
2018-08-08 03:30 | 317 | 308
2018-08-08 04:00 | 319 | 309
2018-08-08 04:30 | 330 | 321
2018-08-08 05:00 | 330 | 321
2018-08-08 05:30 | 344 | 335
2018-08-08 06:00 | 288 | 278
2018-08-08 06:30 | 234 | 219
2018-08-08 07:00 | 196 | 175
2018-08-08 07:30 | 186 | 161
2018-08-08 08:00 | 188 | 163
2018-08-08 08:30 | 173 | 144
2018-08-08 09:00 | 142 | 100
2018-08-08 09:30 | 181 | 149
2018-08-08 10:00 | 202 | 175
2018-08-08 10:30 | 251 | 230
2018-08-08 11:00 | 244 | 225
2018-08-08 11:30 | 237 | 218
2018-08-08 12:00 | 244 | 225
2018-08-08 12:30 | 245 | 227
2018-08-08 13:00 | 236 | 217
2018-08-08 13:30 | 230 | 210
2018-08-08 14:00 | 225 | 204
2018-08-08 14:30 | 232 | 211
2018-08-08 15:00 | 243 | 223
2018-08-08 15:30 | 266 | 249
2018-08-08 16:00 | 290 | 277
2018-08-08 16:30 | 290 | 278
2018-08-08 17:00 | 281 | 270
2018-08-08 17:30 | 282 | 271
2018-08-08 18:00 | 313 | 304
2018-08-08 18:30 | 328 | 321
2018-08-08 19:00 | 320 | 315
2018-08-08 19:30 | 338 | 334
2018-08-08 20:00 | 302 | 296
2018-08-08 20:30 | 274 | 267
2018-08-08 21:00 | 297 | 290
2018-08-08 21:30 | 308 | 300
2018-08-08 22:00 | 321 | 314
2018-08-08 22:30 | 366 | 361
2018-08-08 23:00 | 400 | 396
2018-08-08 23:30 | 386 | 383
2018-08-09 | 371 | 368
2018-08-09 00:30 | 361 | 357
2018-08-09 01:00 | 354 | 349
2018-08-09 01:30 | 346 | 340
2018-08-09 02:00 | 338 | 332
2018-08-09 02:30 | 327 | 320
2018-08-09 03:00 | 323 | 316
2018-08-09 03:30 | 323 | 317
2018-08-09 04:00 | 323 | 316
2018-08-09 04:30 | 326 | 319
2018-08-09 05:00 | 338 | 332
2018-08-09 05:30 | 356 | 350
2018-08-09 06:00 | 339 | 333
2018-08-09 06:30 | 370 | 364
2018-08-09 07:00 | 346 | 341
2018-08-09 07:30 | 326 | 321
2018-08-09 08:00 | 291 | 284
2018-08-09 08:30 | 275 | 265
2018-08-09 09:00 | 223 | 208
2018-08-09 09:30 | 201 | 179
2018-08-09 10:00 | 214 | 191
2018-08-09 10:30 | 198 | 173
2018-08-09 11:00 | 191 | 163
2018-08-09 11:30 | 184 | 155
2018-08-09 12:00 | 191 | 164
2018-08-09 12:30 | 197 | 170
2018-08-09 13:00 | 200 | 172
2018-08-09 13:30 | 210 | 183
2018-08-09 14:00 | 201 | 175
2018-08-09 14:30 | 208 | 183
2018-08-09 15:00 | 209 | 184
2018-08-09 15:30 | 234 | 213
2018-08-09 16:00 | 250 | 231
2018-08-09 16:30 | 202 | 180
2018-08-09 17:00 | 237 | 216
2018-08-09 17:30 | 251 | 234
2018-08-09 18:00 | 304 | 288
2018-08-09 18:30 | 347 | 336
2018-08-09 19:00 | 356 | 348
2018-08-09 19:30 | 350 | 343
2018-08-09 20:00 | 332 | 325
2018-08-09 20:30 | 306 | 297
2018-08-09 21:00 | 292 | 281
2018-08-09 21:30 | 307 | 296
2018-08-09 22:00 | 312 | 302
2018-08-09 22:30 | 305 | 295
2018-08-09 23:00 | 308 | 298
2018-08-09 23:30 | 303 | 293
2018-08-10 | 286 | 275
2018-08-10 00:30 | 282 | 269
2018-08-10 01:00 | 333 | 322
2018-08-10 01:30 | 334 | 324
2018-08-10 02:00 | 327 | 318
2018-08-10 02:30 | 327 | 317
2018-08-10 03:00 | 325 | 315
2018-08-10 03:30 | 323 | 313
2018-08-10 04:00 | 325 | 315
2018-08-10 04:30 | 329 | 320
2018-08-10 05:00 | 344 | 335
2018-08-10 05:30 | 348 | 340
2018-08-10 06:00 | 331 | 323
2018-08-10 06:30 | 282 | 271
2018-08-10 07:00 | 168 | 145
2018-08-10 07:30 | 178 | 146
2018-08-10 08:00 | 168 | 131
2018-08-10 08:30 | 175 | 137
2018-08-10 09:00 | 162 | 119
2018-08-10 09:30 | 142 | 88
2018-08-10 10:00 | 205 | 169
2018-08-10 10:30 | 137 | 86
2018-08-10 11:00 | 136 | 75
2018-08-10 11:30 | 148 | 94
2018-08-10 12:00 | 148 | 95
2018-08-10 12:30 | 148 | 94
2018-08-10 13:00 | 157 | 108
2018-08-10 13:30 | 188 | 150
2018-08-10 14:00 | 186 | 151
2018-08-10 14:30 | 209 | 178
2018-08-10 15:00 | 229 | 201
2018-08-10 15:30 | 272 | 252
2018-08-10 16:00 | 299 | 280
2018-08-10 16:30 | 305 | 291
2018-08-10 17:00 | 334 | 323
2018-08-10 17:30 | 387 | 380
2018-08-10 18:00 | 437 | 432
2018-08-10 18:30 | 472 | 469
2018-08-10 19:00 | 485 | 483
2018-08-10 19:30 | 472 | 471
2018-08-10 20:00 | 457 | 455
2018-08-10 20:30 | 429 | 427
2018-08-10 21:00 | 416 | 412
2018-08-10 21:30 | 431 | 428
2018-08-10 22:00 | 419 | 416
2018-08-10 22:30 | 425 | 422
2018-08-10 23:00 | 407 | 403
2018-08-10 23:30 | 380 | 376
2018-08-11 | 364 | 359
2018-08-11 00:30 | 357 | 351
2018-08-11 01:00 | 347 | 340
2018-08-11 01:30 | 352 | 345
2018-08-11 02:00 | 343 | 337
2018-08-11 02:30 | 336 | 328
2018-08-11 03:00 | 332 | 324
2018-08-11 03:30 | 324 | 316
2018-08-11 04:00 | 327 | 319
2018-08-11 04:30 | 334 | 326
2018-08-11 05:00 | 334 | 326
2018-08-11 05:30 | 342 | 334
2018-08-11 06:00 | 320 | 312
2018-08-11 06:30 | 319 | 310
2018-08-11 07:00 | 310 | 300
2018-08-11 07:30 | 305 | 295
2018-08-11 08:00 | 262 | 249
2018-08-11 08:30 | 241 | 222
2018-08-11 09:00 | 246 | 224
2018-08-11 09:30 | 235 | 212
2018-08-11 10:00 | 232 | 209
2018-08-11 10:30 | 202 | 174
2018-08-11 11:00 | 192 | 159
2018-08-11 11:30 | 134 | 79
2018-08-11 12:00 | 130 | 65
2018-08-11 12:30 | 159 | 112
2018-08-11 13:00 | 175 | 138
2018-08-11 13:30 | 176 | 142
2018-08-11 14:00 | 176 | 139
2018-08-11 14:30 | 179 | 143
2018-08-11 15:00 | 187 | 155
2018-08-11 15:30 | 200 | 171
2018-08-11 16:00 | 222 | 197
2018-08-11 16:30 | 250 | 228
2018-08-11 17:00 | 302 | 286
2018-08-11 17:30 | 370 | 361
2018-08-11 18:00 | 432 | 428
2018-08-11 18:30 | 471 | 469
2018-08-11 19:00 | 479 | 478
2018-08-11 19:30 | 470 | 469
2018-08-11 20:00 | 455 | 454
2018-08-11 20:30 | 441 | 439
2018-08-11 21:00 | 429 | 427
2018-08-11 21:30 | 432 | 429
2018-08-11 22:00 | 410 | 407
2018-08-11 22:30 | 415 | 412
2018-08-11 23:00 | 400 | 397
2018-08-11 23:30 | 380 | 376
2018-08-12 | 369 | 363
2018-08-12 00:30 | 363 | 358
2018-08-12 01:00 | 345 | 339
2018-08-12 01:30 | 336 | 329
2018-08-12 02:00 | 331 | 323
2018-08-12 02:30 | 329 | 321
2018-08-12 03:00 | 321 | 313
2018-08-12 03:30 | 321 | 313
2018-08-12 04:00 | 325 | 317
2018-08-12 04:30 | 321 | 313
2018-08-12 05:00 | 320 | 312
2018-08-12 05:30 | 323 | 314
2018-08-12 06:00 | 298 | 290
2018-08-12 06:30 | 300 | 291
2018-08-12 07:00 | 289 | 280
2018-08-12 07:30 | 270 | 259
2018-08-12 08:00 | 223 | 206
2018-08-12 08:30 | 207 | 183
2018-08-12 09:00 | 188 | 159
2018-08-12 09:30 | 171 | 137
2018-08-12 10:00 | 205 | 176
2018-08-12 10:30 | 199 | 170
2018-08-12 11:00 | 179 | 147
2018-08-12 11:30 | 165 | 129
2018-08-12 12:00 | 159 | 120
2018-08-12 12:30 | 153 | 112
2018-08-12 13:00 | 158 | 117
2018-08-12 13:30 | 157 | 116
2018-08-12 14:00 | 164 | 124
2018-08-12 14:30 | 171 | 134
2018-08-12 15:00 | 178 | 143
2018-08-12 15:30 | 215 | 189
2018-08-12 16:00 | 263 | 244
2018-08-12 16:30 | 266 | 251
2018-08-12 17:00 | 288 | 276
2018-08-12 17:30 | 362 | 354
2018-08-12 18:00 | 429 | 425
2018-08-12 18:30 | 477 | 474
2018-08-12 19:00 | 494 | 493
2018-08-12 19:30 | 487 | 485
2018-08-12 20:00 | 467 | 466
2018-08-12 20:30 | 441 | 440
2018-08-12 21:00 | 426 | 423
2018-08-12 21:30 | 434 | 431
2018-08-12 22:00 | 413 | 410
2018-08-12 22:30 | 421 | 417
2018-08-12 23:00 | 405 | 401
2018-08-12 23:30 | 385 | 381
2018-08-13 | 371 | 366
2018-08-13 00:30 | 364 | 359
2018-08-13 01:00 | 351 | 346
2018-08-13 01:30 | 345 | 339
2018-08-13 02:00 | 337 | 330
2018-08-13 02:30 | 336 | 328
2018-08-13 03:00 | 326 | 318
2018-08-13 03:30 | 322 | 313
2018-08-13 04:00 | 330 | 321
2018-08-13 04:30 | 325 | 316
2018-08-13 05:00 | 334 | 326
2018-08-13 05:30 | 348 | 340
2018-08-13 06:00 | 332 | 325
2018-08-13 06:30 | 358 | 351
2018-08-13 07:00 | 366 | 360
2018-08-13 07:30 | 373 | 368
2018-08-13 08:00 | 324 | 318
2018-08-13 08:30 | 264 | 253
2018-08-13 09:00 | 228 | 209
2018-08-13 09:30 | 205 | 178
2018-08-13 10:00 | 216 | 188
2018-08-13 10:30 | 206 | 179
2018-08-13 11:00 | 194 | 165
2018-08-13 11:30 | 189 | 156
2018-08-13 12:00 | 190 | 151
2018-08-13 12:30 | 194 | 153
2018-08-13 13:00 | 197 | 155
2018-08-13 13:30 | 198 | 156
2018-08-13 14:00 | 212 | 175
2018-08-13 14:30 | 216 | 183
2018-08-13 15:00 | 228 | 197
2018-08-13 15:30 | 238 | 208
2018-08-13 16:00 | 270 | 245
2018-08-13 16:30 | 276 | 254
2018-08-13 17:00 | 323 | 305
2018-08-13 17:30 | 387 | 375
2018-08-13 18:00 | 429 | 422
2018-08-13 18:30 | 469 | 466
2018-08-13 19:00 | 477 | 475
2018-08-13 19:30 | 483 | 481
2018-08-13 20:00 | 464 | 462
2018-08-13 20:30 | 435 | 432
2018-08-13 21:00 | 435 | 432
2018-08-13 21:30 | 442 | 438
2018-08-13 22:00 | 416 | 413
2018-08-13 22:30 | 418 | 414
2018-08-13 23:00 | 393 | 388
2018-08-13 23:30 | 375 | 370
2018-08-14 | 372 | 365
2018-08-14 00:30 | 364 | 357
2018-08-14 01:00 | 350 | 342
2018-08-14 01:30 | 344 | 335
2018-08-14 02:00 | 321 | 312
2018-08-14 02:30 | 328 | 319
2018-08-14 03:00 | 334 | 324
2018-08-14 03:30 | 333 | 323
2018-08-14 04:00 | 336 | 327
2018-08-14 04:30 | 330 | 321
2018-08-14 05:00 | 338 | 328
2018-08-14 05:30 | 353 | 344
2018-08-14 06:00 | 344 | 335
2018-08-14 06:30 | 365 | 357
2018-08-14 07:00 | 384 | 377
2018-08-14 07:30 | 385 | 379
2018-08-14 08:00 | 336 | 328
2018-08-14 08:30 | 279 | 266
2018-08-14 09:00 | 264 | 248
2018-08-14 09:30 | 243 | 222
2018-08-14 10:00 | 243 | 218
2018-08-14 10:30 | 229 | 202
2018-08-14 11:00 | 221 | 191
2018-08-14 11:30 | 221 | 191
2018-08-14 12:00 | 216 | 184
2018-08-14 12:30 | 211 | 179
2018-08-14 13:00 | 218 | 187
2018-08-14 13:30 | 228 | 199
2018-08-14 14:00 | 227 | 197
2018-08-14 14:30 | 230 | 203
2018-08-14 15:00 | 233 | 208
2018-08-14 15:30 | 266 | 246
2018-08-14 16:00 | 311 | 298
2018-08-14 16:30 | 289 | 276
2018-08-14 17:00 | 325 | 313
2018-08-14 17:30 | 399 | 392
2018-08-14 18:00 | 472 | 469
2018-08-14 18:30 | 517 | 515
2018-08-14 19:00 | 553 | 551
2018-08-14 19:30 | 544 | 542
2018-08-14 20:00 | 510 | 508
2018-08-14 20:30 | 494 | 491
2018-08-14 21:00 | 470 | 466
2018-08-14 21:30 | 449 | 444
2018-08-14 22:00 | 417 | 416
2018-08-14 22:30 | 424 | 422
2018-08-14 23:00 | 423 | 422
2018-08-14 23:30 | 401 | 399
2018-08-15 | 376 | 373
2018-08-15 00:30 | 358 | 355
2018-08-15 01:00 | 341 | 337
2018-08-15 01:30 | 338 | 333
2018-08-15 02:00 | 338 | 333
2018-08-15 02:30 | 331 | 326
2018-08-15 03:00 | 334 | 328
2018-08-15 03:30 | 326 | 320
2018-08-15 04:00 | 323 | 317
2018-08-15 04:30 | 329 | 323
2018-08-15 05:00 | 344 | 339
2018-08-15 05:30 | 350 | 346
2018-08-15 06:00 | 340 | 335
2018-08-15 06:30 | 373 | 369
2018-08-15 07:00 | 373 | 369
2018-08-15 07:30 | 404 | 401
2018-08-15 08:00 | 385 | 382
2018-08-15 08:30 | 357 | 353
2018-08-15 09:00 | 272 | 265
2018-08-15 09:30 | 244 | 233
2018-08-15 10:00 | 260 | 249
2018-08-15 10:30 | 220 | 206
2018-08-15 11:00 | 218 | 201
2018-08-15 11:30 | 200 | 178
2018-08-15 12:00 | 220 | 199
2018-08-15 12:30 | 208 | 186
2018-08-15 13:00 | 212 | 188
2018-08-15 13:30 | 211 | 188
2018-08-15 14:00 | 210 | 188
2018-08-15 14:30 | 227 | 207
2018-08-15 15:00 | 224 | 204
2018-08-15 15:30 | 233 | 215
2018-08-15 16:00 | 255 | 239
2018-08-15 16:30 | 261 | 248
2018-08-15 17:00 | 315 | 305
2018-08-15 17:30 | 396 | 390
2018-08-15 18:00 | 408 | 405
2018-08-15 18:30 | 447 | 445
2018-08-15 19:00 | 472 | 471
2018-08-15 19:30 | 452 | 451
2018-08-15 20:00 | 438 | 437
2018-08-15 20:30 | 416 | 415
2018-08-15 21:00 | 431 | 429
2018-08-15 21:30 | 440 | 439
2018-08-15 22:00 | 428 | 426
2018-08-15 22:30 | 423 | 421
2018-08-15 23:00 | 400 | 397
2018-08-15 23:30 | 376 | 374
2018-08-16 | 358 | 354
2018-08-16 00:30 | 358 | 353
2018-08-16 01:00 | 345 | 339
2018-08-16 01:30 | 336 | 330
2018-08-16 02:00 | 332 | 325
2018-08-16 02:30 | 326 | 318
2018-08-16 03:00 | 330 | 323
2018-08-16 03:30 | 331 | 324
2018-08-16 04:00 | 343 | 336
2018-08-16 04:30 | 345 | 338
2018-08-16 05:00 | 351 | 345
2018-08-16 05:30 | 371 | 365
2018-08-16 06:00 | 355 | 350
2018-08-16 06:30 | 347 | 342
2018-08-16 07:00 | 356 | 351
2018-08-16 07:30 | 354 | 348
2018-08-16 08:00 | 317 | 311
2018-08-16 08:30 | 305 | 297
2018-08-16 09:00 | 263 | 251
2018-08-16 09:30 | 229 | 210
2018-08-16 10:00 | 233 | 211
2018-08-16 10:30 | 220 | 201
2018-08-16 11:00 | 246 | 228
2018-08-16 11:30 | 220 | 200
2018-08-16 12:00 | 204 | 173
2018-08-16 12:30 | 178 | 133
2018-08-16 13:00 | 190 | 146
2018-08-16 13:30 | 193 | 150
2018-08-16 14:00 | 200 | 159
2018-08-16 14:30 | 210 | 172
2018-08-16 15:00 | 189 | 146
2018-08-16 15:30 | 169 | 118
2018-08-16 16:00 | 145 | 79
2018-08-16 16:30 | 143 | 67
2018-08-16 17:00 | 173 | 121
2018-08-16 17:30 | 229 | 199
2018-08-16 18:00 | 242 | 222
2018-08-16 18:30 | 271 | 257
2018-08-16 19:00 | 285 | 273
2018-08-16 19:30 | 272 | 259
2018-08-16 20:00 | 249 | 233
2018-08-16 20:30 | 232 | 214
2018-08-16 21:00 | 248 | 229
2018-08-16 21:30 | 295 | 280
2018-08-16 22:00 | 299 | 286
2018-08-16 22:30 | 270 | 256
2018-08-16 23:00 | 341 | 329
2018-08-16 23:30 | 388 | 380
2018-08-17 | 373 | 367
2018-08-17 00:30 | 350 | 343
2018-08-17 01:00 | 353 | 345
2018-08-17 01:30 | 347 | 339
2018-08-17 02:00 | 343 | 334
2018-08-17 02:30 | 340 | 331
2018-08-17 03:00 | 336 | 327
2018-08-17 03:30 | 333 | 323
2018-08-17 04:00 | 333 | 323
2018-08-17 04:30 | 332 | 322
2018-08-17 05:00 | 339 | 329
2018-08-17 05:30 | 352 | 343
2018-08-17 06:00 | 335 | 327
2018-08-17 06:30 | 327 | 318
2018-08-17 07:00 | 333 | 323
2018-08-17 07:30 | 317 | 307
2018-08-17 08:00 | 276 | 264
2018-08-17 08:30 | 265 | 248
2018-08-17 09:00 | 237 | 215
2018-08-17 09:30 | 215 | 186
2018-08-17 10:00 | 251 | 226
2018-08-17 10:30 | 243 | 220
2018-08-17 11:00 | 237 | 212
2018-08-17 11:30 | 235 | 208
2018-08-17 12:00 | 237 | 211
2018-08-17 12:30 | 242 | 217
2018-08-17 13:00 | 238 | 213
2018-08-17 13:30 | 237 | 211
2018-08-17 14:00 | 226 | 198
2018-08-17 14:30 | 230 | 202
2018-08-17 15:00 | 229 | 200
2018-08-17 15:30 | 241 | 213
2018-08-17 16:00 | 268 | 243
2018-08-17 16:30 | 277 | 257
2018-08-17 17:00 | 331 | 315
2018-08-17 17:30 | 367 | 356
2018-08-17 18:00 | 420 | 414
2018-08-17 18:30 | 429 | 424
2018-08-17 19:00 | 435 | 432
2018-08-17 19:30 | 422 | 418
2018-08-17 20:00 | 413 | 409
2018-08-17 20:30 | 411 | 407
2018-08-17 21:00 | 395 | 390
2018-08-17 21:30 | 406 | 401
2018-08-17 22:00 | 398 | 393
2018-08-17 22:30 | 398 | 393
2018-08-17 23:00 | 381 | 375
2018-08-17 23:30 | 363 | 356
2018-08-18 | 348 | 340
2018-08-18 00:30 | 365 | 356
2018-08-18 01:00 | 353 | 344
2018-08-18 01:30 | 358 | 349
2018-08-18 02:00 | 362 | 354
2018-08-18 02:30 | 360 | 352
2018-08-18 03:00 | 346 | 337
2018-08-18 03:30 | 328 | 317
2018-08-18 04:00 | 323 | 311
2018-08-18 04:30 | 327 | 315
2018-08-18 05:00 | 331 | 321
2018-08-18 05:30 | 336 | 325
2018-08-18 06:00 | 314 | 303
2018-08-18 06:30 | 277 | 264
2018-08-18 07:00 | 265 | 248
2018-08-18 07:30 | 255 | 237
2018-08-18 08:00 | 209 | 183
2018-08-18 08:30 | 201 | 167
2018-08-18 09:00 | 187 | 146
2018-08-18 09:30 | 179 | 136
2018-08-18 10:00 | 219 | 187
2018-08-18 10:30 | 214 | 183
2018-08-18 11:00 | 207 | 175
2018-08-18 11:30 | 204 | 171
2018-08-18 12:00 | 195 | 160
2018-08-18 12:30 | 196 | 161
2018-08-18 13:00 | 197 | 163
2018-08-18 13:30 | 195 | 161
2018-08-18 14:00 | 178 | 140
2018-08-18 14:30 | 185 | 148
2018-08-18 15:00 | 201 | 167
2018-08-18 15:30 | 206 | 173
2018-08-18 16:00 | 217 | 188
2018-08-18 16:30 | 239 | 214
2018-08-18 17:00 | 302 | 285
2018-08-18 17:30 | 348 | 336
2018-08-18 18:00 | 409 | 402
2018-08-18 18:30 | 418 | 413
2018-08-18 19:00 | 423 | 419
2018-08-18 19:30 | 409 | 405
2018-08-18 20:00 | 389 | 384
2018-08-18 20:30 | 390 | 384
2018-08-18 21:00 | 377 | 371
2018-08-18 21:30 | 391 | 384
2018-08-18 22:00 | 376 | 369
2018-08-18 22:30 | 390 | 383
2018-08-18 23:00 | 375 | 368
2018-08-18 23:30 | 358 | 351
2018-08-19 | 348 | 339
2018-08-19 00:30 | 379 | 370
2018-08-19 01:00 | 358 | 351
2018-08-19 01:30 | 346 | 338
2018-08-19 02:00 | 349 | 339
2018-08-19 02:30 | 339 | 329
2018-08-19 03:00 | 328 | 318
2018-08-19 03:30 | 329 | 318
2018-08-19 04:00 | 329 | 318
2018-08-19 04:30 | 323 | 312
2018-08-19 05:00 | 324 | 312
2018-08-19 05:30 | 337 | 326
2018-08-19 06:00 | 307 | 296
2018-08-19 06:30 | 275 | 260
2018-08-19 07:00 | 239 | 220
2018-08-19 07:30 | 218 | 193
2018-08-19 08:00 | 175 | 136
2018-08-19 08:30 | 174 | 128
2018-08-19 09:00 | 160 | 107
2018-08-19 09:30 | 154 | 96
2018-08-19 10:00 | 197 | 154
2018-08-19 10:30 | 202 | 164
2018-08-19 11:00 | 191 | 150
2018-08-19 11:30 | 184 | 140
2018-08-19 12:00 | 180 | 137
2018-08-19 12:30 | 171 | 129
2018-08-19 13:00 | 169 | 125
2018-08-19 13:30 | 169 | 125
2018-08-19 14:00 | 162 | 114
2018-08-19 14:30 | 167 | 121
2018-08-19 15:00 | 173 | 129
2018-08-19 15:30 | 192 | 156
2018-08-19 16:00 | 223 | 194
2018-08-19 16:30 | 245 | 221
2018-08-19 17:00 | 303 | 286
2018-08-19 17:30 | 353 | 342
2018-08-19 18:00 | 416 | 409
2018-08-19 18:30 | 441 | 437
2018-08-19 19:00 | 460 | 456
2018-08-19 19:30 | 440 | 437
2018-08-19 20:00 | 424 | 420
2018-08-19 20:30 | 420 | 416
2018-08-19 21:00 | 405 | 399
2018-08-19 21:30 | 405 | 399
2018-08-19 22:00 | 397 | 391
2018-08-19 22:30 | 393 | 387
2018-08-19 23:00 | 369 | 362
2018-08-19 23:30 | 351 | 342
2018-08-20 | 340 | 331
2018-08-20 00:30 | 332 | 322
2018-08-20 01:00 | 334 | 323
2018-08-20 01:30 | 337 | 326
2018-08-20 02:00 | 332 | 320
2018-08-20 02:30 | 314 | 302
2018-08-20 03:00 | 314 | 301
2018-08-20 03:30 | 326 | 313
2018-08-20 04:00 | 327 | 314
2018-08-20 04:30 | 338 | 326
2018-08-20 05:00 | 345 | 334
2018-08-20 05:30 | 355 | 345
2018-08-20 06:00 | 337 | 326
2018-08-20 06:30 | 315 | 303
2018-08-20 07:00 | 320 | 308
2018-08-20 07:30 | 309 | 297
2018-08-20 08:00 | 261 | 245
2018-08-20 08:30 | 240 | 216
2018-08-20 09:00 | 199 | 168
2018-08-20 09:30 | 202 | 168
2018-08-20 10:00 | 227 | 197
2018-08-20 10:30 | 212 | 181
2018-08-20 11:00 | 205 | 171
2018-08-20 11:30 | 198 | 163
2018-08-20 12:00 | 188 | 151
2018-08-20 12:30 | 196 | 159
2018-08-20 13:00 | 193 | 155
2018-08-20 13:30 | 191 | 153
2018-08-20 14:00 | 174 | 132
2018-08-20 14:30 | 183 | 144
2018-08-20 15:00 | 195 | 159
2018-08-20 15:30 | 211 | 180
2018-08-20 16:00 | 236 | 211
2018-08-20 16:30 | 238 | 217
2018-08-20 17:00 | 291 | 275
2018-08-20 17:30 | 328 | 317
2018-08-20 18:00 | 395 | 389
2018-08-20 18:30 | 440 | 437
2018-08-20 19:00 | 463 | 461
2018-08-20 19:30 | 446 | 444
2018-08-20 20:00 | 429 | 427
2018-08-20 20:30 | 396 | 393
2018-08-20 21:00 | 401 | 397
2018-08-20 21:30 | 420 | 417
2018-08-20 22:00 | 398 | 395
2018-08-20 22:30 | 403 | 399
2018-08-20 23:00 | 382 | 378
2018-08-20 23:30 | 330 | 325
2018-08-21 | 317 | 310
2018-08-21 00:30 | 315 | 307
2018-08-21 01:00 | 312 | 304
2018-08-21 01:30 | 283 | 274
2018-08-21 02:00 | 268 | 257
2018-08-21 02:30 | 261 | 249
2018-08-21 03:00 | 262 | 249
2018-08-21 03:30 | 266 | 252
2018-08-21 04:00 | 259 | 246
2018-08-21 04:30 | 249 | 234
2018-08-21 05:00 | 249 | 234
2018-08-21 05:30 | 264 | 248
2018-08-21 06:00 | 275 | 262
2018-08-21 06:30 | 319 | 308
2018-08-21 07:00 | 339 | 331
2018-08-21 07:30 | 198 | 186
2018-08-21 08:00 | 136 | 96
2018-08-21 08:30 | 121 | 49
2018-08-21 09:00 | 123 | 36
2018-08-21 09:30 | 156 | 94
2018-08-21 10:00 | 179 | 134
2018-08-21 10:30 | 171 | 126
2018-08-21 11:00 | 167 | 120
2018-08-21 11:30 | 184 | 143
2018-08-21 12:00 | 166 | 120
2018-08-21 12:30 | 171 | 127
2018-08-21 13:00 | 164 | 118
2018-08-21 13:30 | 164 | 119
2018-08-21 14:00 | 155 | 105
2018-08-21 14:30 | 156 | 107
2018-08-21 15:00 | 163 | 116
2018-08-21 15:30 | 177 | 134
2018-08-21 16:00 | 205 | 172
2018-08-21 16:30 | 204 | 173
2018-08-21 17:00 | 251 | 229
2018-08-21 17:30 | 318 | 306
2018-08-21 18:00 | 378 | 371
2018-08-21 18:30 | 430 | 426
2018-08-21 19:00 | 457 | 455
2018-08-21 19:30 | 392 | 390
2018-08-21 20:00 | 263 | 258
2018-08-21 20:30 | 245 | 233
2018-08-21 21:00 | 230 | 216
2018-08-21 21:30 | 328 | 317
2018-08-21 22:00 | 331 | 324
2018-08-21 22:30 | 354 | 348
2018-08-21 23:00 | 334 | 328
2018-08-21 23:30 | 304 | 297
2018-08-22 | 286 | 277
2018-08-22 00:30 | 286 | 276
2018-08-22 01:00 | 275 | 265
2018-08-22 01:30 | 272 | 260
2018-08-22 02:00 | 272 | 261
2018-08-22 02:30 | 271 | 259
2018-08-22 03:00 | 266 | 253
2018-08-22 03:30 | 271 | 259
2018-08-22 04:00 | 270 | 258
2018-08-22 04:30 | 274 | 262
2018-08-22 05:00 | 269 | 258
2018-08-22 05:30 | 284 | 272
2018-08-22 06:00 | 277 | 266
2018-08-22 06:30 | 309 | 299
2018-08-22 07:00 | 333 | 326
2018-08-22 07:30 | 353 | 347
2018-08-22 08:00 | 324 | 316
2018-08-22 08:30 | 275 | 265
2018-08-22 09:00 | 250 | 231
2018-08-22 09:30 | 221 | 195
2018-08-22 10:00 | 195 | 161
2018-08-22 10:30 | 170 | 122
2018-08-22 11:00 | 173 | 116
2018-08-22 11:30 | 169 | 107
2018-08-22 12:00 | 170 | 106
2018-08-22 12:30 | 171 | 107
2018-08-22 13:00 | 158 | 103
2018-08-22 13:30 | 164 | 118
2018-08-22 14:00 | 155 | 108
2018-08-22 14:30 | 161 | 117
2018-08-22 15:00 | 167 | 127
2018-08-22 15:30 | 185 | 150
2018-08-22 16:00 | 202 | 172
2018-08-22 16:30 | 207 | 182
2018-08-22 17:00 | 249 | 229
2018-08-22 17:30 | 286 | 272
2018-08-22 18:00 | 292 | 281
2018-08-22 18:30 | 320 | 312
2018-08-22 19:00 | 362 | 355
2018-08-22 19:30 | 370 | 365
2018-08-22 20:00 | 344 | 339
2018-08-22 20:30 | 322 | 316
2018-08-22 21:00 | 298 | 290
2018-08-22 21:30 | 343 | 336
2018-08-22 22:00 | 389 | 383
2018-08-22 22:30 | 431 | 427
2018-08-22 23:00 | 424 | 421
2018-08-22 23:30 | 395 | 392
2018-08-23 | 376 | 372
2018-08-23 00:30 | 380 | 375
2018-08-23 01:00 | 374 | 368
2018-08-23 01:30 | 368 | 363
2018-08-23 02:00 | 359 | 353
2018-08-23 02:30 | 342 | 335
2018-08-23 03:00 | 348 | 341
2018-08-23 03:30 | 340 | 332
2018-08-23 04:00 | 346 | 338
2018-08-23 04:30 | 353 | 346
2018-08-23 05:00 | 364 | 358
2018-08-23 05:30 | 381 | 375
2018-08-23 06:00 | 367 | 361
2018-08-23 06:30 | 402 | 397
2018-08-23 07:00 | 437 | 432
2018-08-23 07:30 | 437 | 434
2018-08-23 08:00 | 385 | 380
2018-08-23 08:30 | 333 | 327
2018-08-23 09:00 | 278 | 269
2018-08-23 09:30 | 248 | 234
2018-08-23 10:00 | 252 | 237
2018-08-23 10:30 | 242 | 224
2018-08-23 11:00 | 236 | 215
2018-08-23 11:30 | 223 | 200
2018-08-23 12:00 | 216 | 190
2018-08-23 12:30 | 213 | 187
2018-08-23 13:00 | 214 | 189
2018-08-23 13:30 | 216 | 189
2018-08-23 14:00 | 199 | 171
2018-08-23 14:30 | 204 | 177
2018-08-23 15:00 | 211 | 184
2018-08-23 15:30 | 224 | 200
2018-08-23 16:00 | 230 | 208
2018-08-23 16:30 | 242 | 223
2018-08-23 17:00 | 288 | 273
2018-08-23 17:30 | 303 | 292
2018-08-23 18:00 | 321 | 312
2018-08-23 18:30 | 316 | 309
2018-08-23 19:00 | 354 | 349
2018-08-23 19:30 | 365 | 360
2018-08-23 20:00 | 347 | 343
2018-08-23 20:30 | 318 | 312
2018-08-23 21:00 | 292 | 284
2018-08-23 21:30 | 358 | 350
2018-08-23 22:00 | 403 | 399
2018-08-23 22:30 | 435 | 431
2018-08-23 23:00 | 412 | 410
2018-08-23 23:30 | 397 | 394
2018-08-24 | 375 | 371
2018-08-24 00:30 | 374 | 370
2018-08-24 01:00 | 364 | 359
2018-08-24 01:30 | 353 | 347
2018-08-24 02:00 | 347 | 341
2018-08-24 02:30 | 344 | 337
2018-08-24 03:00 | 344 | 337
2018-08-24 03:30 | 348 | 341
2018-08-24 04:00 | 350 | 343
2018-08-24 04:30 | 352 | 345
2018-08-24 05:00 | 358 | 351
2018-08-24 05:30 | 369 | 363
2018-08-24 06:00 | 351 | 345
2018-08-24 06:30 | 377 | 371
2018-08-24 07:00 | 403 | 398
2018-08-24 07:30 | 405 | 400
2018-08-24 08:00 | 355 | 350
2018-08-24 08:30 | 300 | 290
2018-08-24 09:00 | 262 | 247
2018-08-24 09:30 | 259 | 240
2018-08-24 10:00 | 259 | 239
2018-08-24 10:30 | 240 | 222
2018-08-24 11:00 | 234 | 214
2018-08-24 11:30 | 225 | 204
2018-08-24 12:00 | 224 | 201
2018-08-24 12:30 | 228 | 207
2018-08-24 13:00 | 223 | 202
2018-08-24 13:30 | 220 | 197
2018-08-24 14:00 | 206 | 182
2018-08-24 14:30 | 223 | 200
2018-08-24 15:00 | 223 | 203
2018-08-24 15:30 | 228 | 209
2018-08-24 16:00 | 281 | 263
2018-08-24 16:30 | 312 | 298
2018-08-24 17:00 | 359 | 351
2018-08-24 17:30 | 405 | 399
2018-08-24 18:00 | 413 | 410
2018-08-24 18:30 | 429 | 427
2018-08-24 19:00 | 448 | 446
2018-08-24 19:30 | 437 | 436
2018-08-24 20:00 | 417 | 415
2018-08-24 20:30 | 406 | 403
2018-08-24 21:00 | 407 | 404
2018-08-24 21:30 | 398 | 395
2018-08-24 22:00 | 367 | 363
2018-08-24 22:30 | 375 | 370
2018-08-24 23:00 | 362 | 357
2018-08-24 23:30 | 345 | 340
2018-08-25 | 338 | 333
2018-08-25 00:30 | 353 | 347
2018-08-25 01:00 | 343 | 337
2018-08-25 01:30 | 334 | 328
2018-08-25 02:00 | 327 | 320
2018-08-25 02:30 | 340 | 333
2018-08-25 03:00 | 335 | 328
2018-08-25 03:30 | 329 | 322
2018-08-25 04:00 | 329 | 322
2018-08-25 04:30 | 331 | 323
2018-08-25 05:00 | 337 | 330
2018-08-25 05:30 | 344 | 338
2018-08-25 06:00 | 312 | 305
2018-08-25 06:30 | 293 | 284
2018-08-25 07:00 | 309 | 300
2018-08-25 07:30 | 295 | 286
2018-08-25 08:00 | 255 | 244
2018-08-25 08:30 | 288 | 275
2018-08-25 09:00 | 244 | 230
2018-08-25 09:30 | 251 | 235
2018-08-25 10:00 | 300 | 286
2018-08-25 10:30 | 302 | 291
2018-08-25 11:00 | 275 | 264
2018-08-25 11:30 | 270 | 256
2018-08-25 12:00 | 288 | 275
2018-08-25 12:30 | 277 | 265
2018-08-25 13:00 | 241 | 224
2018-08-25 13:30 | 279 | 263
2018-08-25 14:00 | 281 | 268
2018-08-25 14:30 | 275 | 262
2018-08-25 15:00 | 290 | 277
2018-08-25 15:30 | 297 | 285
2018-08-25 16:00 | 302 | 292
2018-08-25 16:30 | 301 | 290
2018-08-25 17:00 | 355 | 346
2018-08-25 17:30 | 392 | 387
2018-08-25 18:00 | 328 | 324
2018-08-25 18:30 | 290 | 284
2018-08-25 19:00 | 295 | 287
2018-08-25 19:30 | 340 | 333
2018-08-25 20:00 | 343 | 338
2018-08-25 20:30 | 323 | 317
2018-08-25 21:00 | 326 | 320
2018-08-25 21:30 | 424 | 419
2018-08-25 22:00 | 439 | 437
2018-08-25 22:30 | 452 | 451
2018-08-25 23:00 | 427 | 425
2018-08-25 23:30 | 409 | 407
2018-08-26 | 404 | 401
2018-08-26 00:30 | 424 | 421
2018-08-26 01:00 | 414 | 411
2018-08-26 01:30 | 412 | 409
2018-08-26 02:00 | 402 | 399
2018-08-26 02:30 | 392 | 388
2018-08-26 03:00 | 395 | 391
2018-08-26 03:30 | 392 | 388
2018-08-26 04:00 | 394 | 391
2018-08-26 04:30 | 394 | 390
2018-08-26 05:00 | 394 | 391
2018-08-26 05:30 | 396 | 392
2018-08-26 06:00 | 367 | 363
2018-08-26 06:30 | 359 | 354
2018-08-26 07:00 | 342 | 336
2018-08-26 07:30 | 328 | 321
2018-08-26 08:00 | 316 | 308
2018-08-26 08:30 | 280 | 270
2018-08-26 09:00 | 274 | 261
2018-08-26 09:30 | 262 | 248
2018-08-26 10:00 | 309 | 298
2018-08-26 10:30 | 307 | 299
2018-08-26 11:00 | 321 | 313
2018-08-26 11:30 | 286 | 277
2018-08-26 12:00 | 286 | 275
2018-08-26 12:30 | 246 | 233
2018-08-26 13:00 | 249 | 233
2018-08-26 13:30 | 266 | 250
2018-08-26 14:00 | 267 | 254
2018-08-26 14:30 | 281 | 268
2018-08-26 15:00 | 294 | 282
2018-08-26 15:30 | 248 | 234
2018-08-26 16:00 | 269 | 254
2018-08-26 16:30 | 273 | 259
2018-08-26 17:00 | 344 | 334
2018-08-26 17:30 | 411 | 405
2018-08-26 18:00 | 443 | 440
2018-08-26 18:30 | 479 | 478
2018-08-26 19:00 | 476 | 475
2018-08-26 19:30 | 484 | 483
2018-08-26 20:00 | 485 | 484
2018-08-26 20:30 | 461 | 460
2018-08-26 21:00 | 450 | 449
2018-08-26 21:30 | 436 | 434
2018-08-26 22:00 | 414 | 411
2018-08-26 22:30 | 440 | 437
2018-08-26 23:00 | 429 | 427
2018-08-26 23:30 | 407 | 404
2018-08-27 | 394 | 391
2018-08-27 00:30 | 395 | 391
2018-08-27 01:00 | 377 | 374
2018-08-27 01:30 | 358 | 353
2018-08-27 02:00 | 355 | 349
2018-08-27 02:30 | 352 | 346
2018-08-27 03:00 | 347 | 340
2018-08-27 03:30 | 353 | 347
2018-08-27 04:00 | 366 | 360
2018-08-27 04:30 | 363 | 357
2018-08-27 05:00 | 362 | 356
2018-08-27 05:30 | 381 | 375
2018-08-27 06:00 | 367 | 361
2018-08-27 06:30 | 379 | 373
2018-08-27 07:00 | 395 | 390
2018-08-27 07:30 | 367 | 362
2018-08-27 08:00 | 303 | 296
2018-08-27 08:30 | 254 | 241
2018-08-27 09:00 | 219 | 202
2018-08-27 09:30 | 195 | 173
2018-08-27 10:00 | 203 | 180
2018-08-27 10:30 | 199 | 174
2018-08-27 11:00 | 195 | 169
2018-08-27 11:30 | 200 | 175
2018-08-27 12:00 | 200 | 176
2018-08-27 12:30 | 203 | 179
2018-08-27 13:00 | 211 | 189
2018-08-27 13:30 | 214 | 193
2018-08-27 14:00 | 201 | 179
2018-08-27 14:30 | 214 | 194
2018-08-27 15:00 | 226 | 207
2018-08-27 15:30 | 245 | 229
2018-08-27 16:00 | 262 | 248
2018-08-27 16:30 | 268 | 255
2018-08-27 17:00 | 324 | 314
2018-08-27 17:30 | 384 | 379
2018-08-27 18:00 | 274 | 270
2018-08-27 18:30 | 252 | 245
2018-08-27 19:00 | 283 | 276
2018-08-27 19:30 | 293 | 286
2018-08-27 20:00 | 296 | 290
2018-08-27 20:30 | 274 | 267
2018-08-27 21:00 | 287 | 278
2018-08-27 21:30 | 408 | 402
2018-08-27 22:00 | 384 | 382
2018-08-27 22:30 | 414 | 411
2018-08-27 23:00 | 404 | 401
2018-08-27 23:30 | 380 | 377
2018-08-28 | 360 | 357
2018-08-28 00:30 | 364 | 359
2018-08-28 01:00 | 354 | 349
2018-08-28 01:30 | 339 | 334
2018-08-28 02:00 | 335 | 329
2018-08-28 02:30 | 330 | 324
2018-08-28 03:00 | 332 | 325
2018-08-28 03:30 | 336 | 329
2018-08-28 04:00 | 341 | 335
2018-08-28 04:30 | 340 | 333
2018-08-28 05:00 | 341 | 335
2018-08-28 05:30 | 359 | 353
2018-08-28 06:00 | 342 | 337
2018-08-28 06:30 | 337 | 331
2018-08-28 07:00 | 343 | 337
2018-08-28 07:30 | 320 | 314
2018-08-28 08:00 | 271 | 262
2018-08-28 08:30 | 259 | 246
2018-08-28 09:00 | 227 | 209
2018-08-28 09:30 | 234 | 207
2018-08-28 10:00 | 247 | 220
2018-08-28 10:30 | 240 | 213
2018-08-28 11:00 | 236 | 206
2018-08-28 11:30 | 231 | 204
2018-08-28 12:00 | 230 | 202
2018-08-28 12:30 | 228 | 202
2018-08-28 13:00 | 226 | 200
2018-08-28 13:30 | 227 | 204
2018-08-28 14:00 | 215 | 192
2018-08-28 14:30 | 223 | 203
2018-08-28 15:00 | 247 | 231
2018-08-28 15:30 | 259 | 244
2018-08-28 16:00 | 289 | 277
2018-08-28 16:30 | 294 | 284
2018-08-28 17:00 | 328 | 320
2018-08-28 17:30 | 324 | 317
2018-08-28 18:00 | 281 | 274
2018-08-28 18:30 | 307 | 300
2018-08-28 19:00 | 302 | 295
2018-08-28 19:30 | 304 | 297
2018-08-28 20:00 | 289 | 281
2018-08-28 20:30 | 275 | 266
2018-08-28 21:00 | 253 | 242
2018-08-28 21:30 | 270 | 259
2018-08-28 22:00 | 260 | 249
2018-08-28 22:30 | 278 | 268
2018-08-28 23:00 | 368 | 361
2018-08-28 23:30 | 376 | 372
2018-08-29 | 363 | 359
2018-08-29 00:30 | 371 | 367
2018-08-29 01:00 | 353 | 348
2018-08-29 01:30 | 342 | 337
2018-08-29 02:00 | 339 | 333
2018-08-29 02:30 | 339 | 333
2018-08-29 03:00 | 338 | 331
2018-08-29 03:30 | 337 | 331
2018-08-29 04:00 | 335 | 329
2018-08-29 04:30 | 342 | 336
2018-08-29 05:00 | 340 | 334
2018-08-29 05:30 | 360 | 354
2018-08-29 06:00 | 341 | 336
2018-08-29 06:30 | 313 | 307
2018-08-29 07:00 | 299 | 292
2018-08-29 07:30 | 266 | 258
2018-08-29 08:00 | 216 | 203
2018-08-29 08:30 | 224 | 207
2018-08-29 09:00 | 207 | 187
2018-08-29 09:30 | 211 | 190
2018-08-29 10:00 | 237 | 219
2018-08-29 10:30 | 228 | 210
2018-08-29 11:00 | 220 | 200
2018-08-29 11:30 | 223 | 201
2018-08-29 12:00 | 219 | 200
2018-08-29 12:30 | 223 | 203
2018-08-29 13:00 | 234 | 216
2018-08-29 13:30 | 234 | 216
2018-08-29 14:00 | 225 | 206
2018-08-29 14:30 | 228 | 209
2018-08-29 15:00 | 247 | 230
2018-08-29 15:30 | 276 | 263
2018-08-29 16:00 | 285 | 274
2018-08-29 16:30 | 275 | 263
2018-08-29 17:00 | 339 | 329
2018-08-29 17:30 | 399 | 394
2018-08-29 18:00 | 430 | 427
2018-08-29 18:30 | 467 | 465
2018-08-29 19:00 | 487 | 485
2018-08-29 19:30 | 452 | 451
2018-08-29 20:00 | 416 | 414
2018-08-29 20:30 | 409 | 407
2018-08-29 21:00 | 404 | 401
2018-08-29 21:30 | 383 | 379
2018-08-29 22:00 | 382 | 377
2018-08-29 22:30 | 402 | 398
2018-08-29 23:00 | 380 | 376
2018-08-29 23:30 | 388 | 384
2018-08-30 | 374 | 369
2018-08-30 00:30 | 369 | 364
2018-08-30 01:00 | 345 | 339
2018-08-30 01:30 | 337 | 330
2018-08-30 02:00 | 331 | 324
2018-08-30 02:30 | 321 | 313
2018-08-30 03:00 | 325 | 317
2018-08-30 03:30 | 326 | 318
2018-08-30 04:00 | 342 | 334
2018-08-30 04:30 | 350 | 343
2018-08-30 05:00 | 354 | 347
2018-08-30 05:30 | 367 | 361
2018-08-30 06:00 | 326 | 319
2018-08-30 06:30 | 356 | 349
2018-08-30 07:00 | 338 | 331
2018-08-30 07:30 | 307 | 300
2018-08-30 08:00 | 283 | 273
2018-08-30 08:30 | 275 | 261
2018-08-30 09:00 | 250 | 234
2018-08-30 09:30 | 264 | 247
2018-08-30 10:00 | 337 | 324
2018-08-30 10:30 | 294 | 283
2018-08-30 11:00 | 287 | 274
2018-08-30 11:30 | 262 | 247
2018-08-30 12:00 | 251 | 234
2018-08-30 12:30 | 252 | 234
2018-08-30 13:00 | 253 | 234
2018-08-30 13:30 | 256 | 238
2018-08-30 14:00 | 261 | 244
2018-08-30 14:30 | 264 | 246
2018-08-30 15:00 | 263 | 245
2018-08-30 15:30 | 266 | 249
2018-08-30 16:00 | 299 | 285
2018-08-30 16:30 | 305 | 293
2018-08-30 17:00 | 350 | 341
2018-08-30 17:30 | 392 | 387
2018-08-30 18:00 | 437 | 434
2018-08-30 18:30 | 468 | 466
2018-08-30 19:00 | 470 | 469
2018-08-30 19:30 | 453 | 452
2018-08-30 20:00 | 436 | 434
2018-08-30 20:30 | 404 | 401
2018-08-30 21:00 | 399 | 396
2018-08-30 21:30 | 392 | 388
2018-08-30 22:00 | 386 | 382
2018-08-30 22:30 | 416 | 413
2018-08-30 23:00 | 400 | 397
2018-08-30 23:30 | 388 | 384
2018-08-31 | 370 | 367
2018-08-31 00:30 | 361 | 356
2018-08-31 01:00 | 326 | 321
2018-08-31 01:30 | 330 | 324
2018-08-31 02:00 | 323 | 316
2018-08-31 02:30 | 328 | 321
2018-08-31 03:00 | 327 | 321
2018-08-31 03:30 | 330 | 323
2018-08-31 04:00 | 318 | 311
2018-08-31 04:30 | 327 | 320
2018-08-31 05:00 | 341 | 335
2018-08-31 05:30 | 358 | 353
2018-08-31 06:00 | 338 | 333
2018-08-31 06:30 | 327 | 320
2018-08-31 07:00 | 343 | 337
2018-08-31 07:30 | 327 | 322
2018-08-31 08:00 | 309 | 302
2018-08-31 08:30 | 275 | 265
2018-08-31 09:00 | 244 | 230
2018-08-31 09:30 | 217 | 201
2018-08-31 10:00 | 240 | 223
2018-08-31 10:30 | 233 | 216
2018-08-31 11:00 | 216 | 199
2018-08-31 11:30 | 216 | 197
2018-08-31 12:00 | 212 | 192
2018-08-31 12:30 | 217 | 197
2018-08-31 13:00 | 212 | 191
2018-08-31 13:30 | 210 | 189
2018-08-31 14:00 | 208 | 187
2018-08-31 14:30 | 203 | 182
2018-08-31 15:00 | 199 | 177
2018-08-31 15:30 | 221 | 201
2018-08-31 16:00 | 254 | 238
2018-08-31 16:30 | 258 | 245
2018-08-31 17:00 | 303 | 293
2018-08-31 17:30 | 347 | 340
2018-08-31 18:00 | 395 | 392
2018-08-31 18:30 | 417 | 415
2018-08-31 19:00 | 428 | 426
2018-08-31 19:30 | 436 | 435
2018-08-31 20:00 | 420 | 420
2018-08-31 20:30 | 404 | 403
2018-08-31 21:00 | 388 | 387
2018-08-31 21:30 | 370 | 369
2018-08-31 22:00 | 357 | 356
2018-08-31 22:30 | 376 | 374
2018-08-31 23:00 | 369 | 367
2018-08-31 23:30 | 362 | 361
2018-09-01 | 346 | 344
2018-09-01 00:30 | 363 | 361
2018-09-01 01:00 | 353 | 351
2018-09-01 01:30 | 343 | 341
2018-09-01 02:00 | 334 | 332
2018-09-01 02:30 | 336 | 332
2018-09-01 03:00 | 335 | 332
2018-09-01 03:30 | 324 | 321
2018-09-01 04:00 | 324 | 321
2018-09-01 04:30 | 331 | 327
2018-09-01 05:00 | 338 | 335
2018-09-01 05:30 | 345 | 342
2018-09-01 06:00 | 320 | 316
2018-09-01 06:30 | 322 | 318
2018-09-01 07:00 | 327 | 323
2018-09-01 07:30 | 312 | 309
2018-09-01 08:00 | 285 | 281
2018-09-01 08:30 | 203 | 194
2018-09-01 09:00 | 206 | 192
2018-09-01 09:30 | 197 | 180
2018-09-01 10:00 | 210 | 194
2018-09-01 10:30 | 204 | 188
2018-09-01 11:00 | 196 | 179
2018-09-01 11:30 | 192 | 173
2018-09-01 12:00 | 189 | 169
2018-09-01 12:30 | 196 | 176
2018-09-01 13:00 | 188 | 170
2018-09-01 13:30 | 187 | 169
2018-09-01 14:00 | 181 | 161
2018-09-01 14:30 | 185 | 165
2018-09-01 15:00 | 207 | 190
2018-09-01 15:30 | 244 | 230
2018-09-01 16:00 | 262 | 252
2018-09-01 16:30 | 276 | 269
2018-09-01 17:00 | 314 | 308
2018-09-01 17:30 | 359 | 355
2018-09-01 18:00 | 407 | 405
2018-09-01 18:30 | 440 | 439
2018-09-01 19:00 | 440 | 440
2018-09-01 19:30 | 434 | 433
2018-09-01 20:00 | 425 | 425
2018-09-01 20:30 | 406 | 406
2018-09-01 21:00 | 390 | 389
2018-09-01 21:30 | 366 | 366
2018-09-01 22:00 | 354 | 353
2018-09-01 22:30 | 386 | 385
2018-09-01 23:00 | 375 | 374
2018-09-01 23:30 | 355 | 354
2018-09-02 | 363 | 362
2018-09-02 00:30 | 371 | 369
2018-09-02 01:00 | 347 | 345
2018-09-02 01:30 | 346 | 344
2018-09-02 02:00 | 337 | 335
2018-09-02 02:30 | 335 | 333
2018-09-02 03:00 | 334 | 331
2018-09-02 03:30 | 331 | 328
2018-09-02 04:00 | 334 | 331
2018-09-02 04:30 | 328 | 325
2018-09-02 05:00 | 336 | 333
2018-09-02 05:30 | 339 | 336
2018-09-02 06:00 | 309 | 306
2018-09-02 06:30 | 323 | 319
2018-09-02 07:00 | 310 | 307
2018-09-02 07:30 | 282 | 278
2018-09-02 08:00 | 256 | 250
2018-09-02 08:30 | 219 | 209
2018-09-02 09:00 | 191 | 176
2018-09-02 09:30 | 183 | 165
2018-09-02 10:00 | 200 | 183
2018-09-02 10:30 | 190 | 174
2018-09-02 11:00 | 181 | 162
2018-09-02 11:30 | 182 | 163
2018-09-02 12:00 | 181 | 162
2018-09-02 12:30 | 183 | 164
2018-09-02 13:00 | 181 | 162
2018-09-02 13:30 | 182 | 163
2018-09-02 14:00 | 173 | 153
2018-09-02 14:30 | 182 | 163
2018-09-02 15:00 | 198 | 180
2018-09-02 15:30 | 214 | 198
2018-09-02 16:00 | 236 | 223
2018-09-02 16:30 | 243 | 233
2018-09-02 17:00 | 288 | 281
2018-09-02 17:30 | 339 | 335
2018-09-02 18:00 | 397 | 395
2018-09-02 18:30 | 389 | 388
2018-09-02 19:00 | 397 | 396
2018-09-02 19:30 | 408 | 408
2018-09-02 20:00 | 395 | 395
2018-09-02 20:30 | 388 | 388
2018-09-02 21:00 | 389 | 388
2018-09-02 21:30 | 365 | 364
2018-09-02 22:00 | 338 | 337
2018-09-02 22:30 | 364 | 362
2018-09-02 23:00 | 348 | 347
2018-09-02 23:30 | 356 | 354
2018-09-03 | 349 | 347
2018-09-03 00:30 | 351 | 349
2018-09-03 01:00 | 341 | 339
2018-09-03 01:30 | 342 | 340
2018-09-03 02:00 | 337 | 335
2018-09-03 02:30 | 333 | 330
2018-09-03 03:00 | 336 | 333
2018-09-03 03:30 | 329 | 327
2018-09-03 04:00 | 332 | 329
2018-09-03 04:30 | 334 | 332
2018-09-03 05:00 | 345 | 343
2018-09-03 05:30 | 348 | 346
2018-09-03 06:00 | 332 | 330
2018-09-03 06:30 | 332 | 329
2018-09-03 07:00 | 322 | 320
2018-09-03 07:30 | 295 | 292
2018-09-03 08:00 | 215 | 209
2018-09-03 08:30 | 205 | 193
2018-09-03 09:00 | 174 | 157
2018-09-03 09:30 | 165 | 143
2018-09-03 10:00 | 186 | 165
2018-09-03 10:30 | 182 | 162
2018-09-03 11:00 | 170 | 148
2018-09-03 11:30 | 175 | 154
2018-09-03 12:00 | 184 | 164
2018-09-03 12:30 | 190 | 170
2018-09-03 13:00 | 190 | 171
2018-09-03 13:30 | 196 | 178
2018-09-03 14:00 | 199 | 182
2018-09-03 14:30 | 224 | 209
2018-09-03 15:00 | 231 | 218
2018-09-03 15:30 | 252 | 241
2018-09-03 16:00 | 279 | 271
2018-09-03 16:30 | 228 | 220
2018-09-03 17:00 | 256 | 247
2018-09-03 17:30 | 234 | 225
2018-09-03 18:00 | 230 | 222
2018-09-03 18:30 | 306 | 300
2018-09-03 19:00 | 320 | 316
2018-09-03 19:30 | 307 | 304
2018-09-03 20:00 | 314 | 310
2018-09-03 20:30 | 281 | 277
2018-09-03 21:00 | 282 | 277
2018-09-03 21:30 | 271 | 266
2018-09-03 22:00 | 249 | 242
2018-09-03 22:30 | 293 | 287
2018-09-03 23:00 | 349 | 345
2018-09-03 23:30 | 402 | 400
2018-09-04 | 392 | 390
2018-09-04 00:30 | 391 | 390
2018-09-04 01:00 | 381 | 380
2018-09-04 01:30 | 379 | 377
2018-09-04 02:00 | 370 | 369
2018-09-04 02:30 | 370 | 368
2018-09-04 03:00 | 364 | 362
2018-09-04 03:30 | 358 | 356
2018-09-04 04:00 | 359 | 356
2018-09-04 04:30 | 369 | 366
2018-09-04 05:00 | 376 | 374
2018-09-04 05:30 | 389 | 387
2018-09-04 06:00 | 382 | 380
2018-09-04 06:30 | 412 | 410
2018-09-04 07:00 | 357 | 355
2018-09-04 07:30 | 365 | 363
2018-09-04 08:00 | 319 | 315
2018-09-04 08:30 | 296 | 291
2018-09-04 09:00 | 272 | 266
2018-09-04 09:30 | 266 | 259
2018-09-04 10:00 | 250 | 242
2018-09-04 10:30 | 250 | 242
2018-09-04 11:00 | 264 | 254
2018-09-04 11:30 | 248 | 239
2018-09-04 12:00 | 256 | 247
2018-09-04 12:30 | 260 | 251
2018-09-04 13:00 | 272 | 264
2018-09-04 13:30 | 274 | 266
2018-09-04 14:00 | 283 | 276
2018-09-04 14:30 | 266 | 260
2018-09-04 15:00 | 301 | 296
2018-09-04 15:30 | 307 | 301
2018-09-04 16:00 | 275 | 270
2018-09-04 16:30 | 284 | 278
2018-09-04 17:00 | 343 | 338
2018-09-04 17:30 | 355 | 352
2018-09-04 18:00 | 298 | 295
2018-09-04 18:30 | 306 | 302
2018-09-04 19:00 | 315 | 312
2018-09-04 19:30 | 341 | 339
2018-09-04 20:00 | 384 | 382
2018-09-04 20:30 | 417 | 415
2018-09-04 21:00 | 396 | 394
2018-09-04 21:30 | 369 | 367
2018-09-04 22:00 | 349 | 347
2018-09-04 22:30 | 340 | 337
2018-09-04 23:00 | 425 | 423
2018-09-04 23:30 | 420 | 419
2018-09-05 | 407 | 406
2018-09-05 00:30 | 402 | 401
2018-09-05 01:00 | 384 | 382
2018-09-05 01:30 | 376 | 374
2018-09-05 02:00 | 372 | 370
2018-09-05 02:30 | 372 | 370
2018-09-05 03:00 | 368 | 366
2018-09-05 03:30 | 364 | 362
2018-09-05 04:00 | 369 | 367
2018-09-05 04:30 | 375 | 372
2018-09-05 05:00 | 382 | 379
2018-09-05 05:30 | 397 | 395
2018-09-05 06:00 | 395 | 393
2018-09-05 06:30 | 422 | 420
2018-09-05 07:00 | 380 | 379
2018-09-05 07:30 | 348 | 346
2018-09-05 08:00 | 310 | 307
2018-09-05 08:30 | 260 | 254
2018-09-05 09:00 | 271 | 263
2018-09-05 09:30 | 267 | 259
2018-09-05 10:00 | 290 | 282
2018-09-05 10:30 | 303 | 297
2018-09-05 11:00 | 277 | 271
2018-09-05 11:30 | 269 | 262
2018-09-05 12:00 | 243 | 234
2018-09-05 12:30 | 248 | 240
2018-09-05 13:00 | 254 | 246
2018-09-05 13:30 | 258 | 250
2018-09-05 14:00 | 244 | 236
2018-09-05 14:30 | 243 | 234
2018-09-05 15:00 | 264 | 255
2018-09-05 15:30 | 287 | 280
2018-09-05 16:00 | 293 | 287
2018-09-05 16:30 | 298 | 293
2018-09-05 17:00 | 396 | 392
2018-09-05 17:30 | 411 | 409
2018-09-05 18:00 | 384 | 383
2018-09-05 18:30 | 423 | 421
2018-09-05 19:00 | 458 | 457
2018-09-05 19:30 | 454 | 453
2018-09-05 20:00 | 443 | 442
2018-09-05 20:30 | 439 | 438
2018-09-05 21:00 | 446 | 445
2018-09-05 21:30 | 444 | 443
2018-09-05 22:00 | 453 | 452
2018-09-05 22:30 | 480 | 479
2018-09-05 23:00 | 452 | 451
2018-09-05 23:30 | 414 | 413
2018-09-06 | 399 | 398
2018-09-06 00:30 | 396 | 394
2018-09-06 01:00 | 386 | 384
2018-09-06 01:30 | 372 | 370
2018-09-06 02:00 | 361 | 358
2018-09-06 02:30 | 353 | 350
2018-09-06 03:00 | 346 | 343
2018-09-06 03:30 | 347 | 344
2018-09-06 04:00 | 351 | 348
2018-09-06 04:30 | 356 | 353
2018-09-06 05:00 | 367 | 364
2018-09-06 05:30 | 389 | 386
2018-09-06 06:00 | 367 | 365
2018-09-06 06:30 | 375 | 373
2018-09-06 07:00 | 331 | 328
2018-09-06 07:30 | 311 | 308
2018-09-06 08:00 | 286 | 282
2018-09-06 08:30 | 257 | 251
2018-09-06 09:00 | 275 | 267
2018-09-06 09:30 | 267 | 259
2018-09-06 10:00 | 254 | 245
2018-09-06 10:30 | 259 | 250
2018-09-06 11:00 | 254 | 245
2018-09-06 11:30 | 235 | 225
2018-09-06 12:00 | 258 | 249
2018-09-06 12:30 | 301 | 294
2018-09-06 13:00 | 291 | 285
2018-09-06 13:30 | 326 | 321
2018-09-06 14:00 | 308 | 304
2018-09-06 14:30 | 298 | 293
2018-09-06 15:00 | 307 | 302
2018-09-06 15:30 | 299 | 293
2018-09-06 16:00 | 347 | 343
2018-09-06 16:30 | 330 | 326
2018-09-06 17:00 | 338 | 333
2018-09-06 17:30 | 387 | 384
2018-09-06 18:00 | 442 | 440
2018-09-06 18:30 | 478 | 478
2018-09-06 19:00 | 453 | 452
2018-09-06 19:30 | 451 | 451
2018-09-06 20:00 | 443 | 443
2018-09-06 20:30 | 434 | 434
2018-09-06 21:00 | 399 | 397
2018-09-06 21:30 | 434 | 432
2018-09-06 22:00 | 413 | 411
2018-09-06 22:30 | 455 | 453
2018-09-06 23:00 | 444 | 443
2018-09-06 23:30 | 426 | 425
2018-09-07 | 413 | 412
2018-09-07 00:30 | 409 | 407
2018-09-07 01:00 | 395 | 393
2018-09-07 01:30 | 386 | 384
2018-09-07 02:00 | 377 | 375
2018-09-07 02:30 | 370 | 367
2018-09-07 03:00 | 367 | 363
2018-09-07 03:30 | 366 | 362
2018-09-07 04:00 | 362 | 359
2018-09-07 04:30 | 364 | 361
2018-09-07 05:00 | 378 | 375
2018-09-07 05:30 | 386 | 383
2018-09-07 06:00 | 378 | 375
2018-09-07 06:30 | 394 | 392
2018-09-07 07:00 | 351 | 349
2018-09-07 07:30 | 329 | 326
2018-09-07 08:00 | 313 | 309
2018-09-07 08:30 | 312 | 306
2018-09-07 09:00 | 274 | 267
2018-09-07 09:30 | 216 | 204
2018-09-07 10:00 | 203 | 186
2018-09-07 10:30 | 215 | 197
2018-09-07 11:00 | 219 | 202
2018-09-07 11:30 | 216 | 200
2018-09-07 12:00 | 219 | 202
2018-09-07 12:30 | 213 | 195
2018-09-07 13:00 | 214 | 197
2018-09-07 13:30 | 217 | 200
2018-09-07 14:00 | 211 | 194
2018-09-07 14:30 | 223 | 208
2018-09-07 15:00 | 239 | 225
2018-09-07 15:30 | 269 | 258
2018-09-07 16:00 | 295 | 286
2018-09-07 16:30 | 315 | 308
2018-09-07 17:00 | 366 | 361
2018-09-07 17:30 | 444 | 441
2018-09-07 18:00 | 479 | 478
2018-09-07 18:30 | 458 | 457
2018-09-07 19:00 | 471 | 470
2018-09-07 19:30 | 485 | 485
2018-09-07 20:00 | 468 | 468
2018-09-07 20:30 | 458 | 458
2018-09-07 21:00 | 456 | 456
2018-09-07 21:30 | 440 | 440
2018-09-07 22:00 | 403 | 403
2018-09-07 22:30 | 429 | 428
2018-09-07 23:00 | 425 | 424
2018-09-07 23:30 | 407 | 406
2018-09-08 | 389 | 387
2018-09-08 00:30 | 375 | 372
2018-09-08 01:00 | 363 | 360
2018-09-08 01:30 | 358 | 355
2018-09-08 02:00 | 354 | 350
2018-09-08 02:30 | 342 | 338
2018-09-08 03:00 | 330 | 326
2018-09-08 03:30 | 320 | 316
2018-09-08 04:00 | 307 | 302
2018-09-08 04:30 | 306 | 301
2018-09-08 05:00 | 309 | 304
2018-09-08 05:30 | 325 | 320
2018-09-08 06:00 | 307 | 302
2018-09-08 06:30 | 305 | 301
2018-09-08 07:00 | 303 | 298
2018-09-08 07:30 | 277 | 271
2018-09-08 08:00 | 243 | 233
2018-09-08 08:30 | 229 | 217
2018-09-08 09:00 | 236 | 222
2018-09-08 09:30 | 224 | 211
2018-09-08 10:00 | 209 | 196
2018-09-08 10:30 | 222 | 208
2018-09-08 11:00 | 222 | 208
2018-09-08 11:30 | 223 | 209
2018-09-08 12:00 | 223 | 208
2018-09-08 12:30 | 228 | 213
2018-09-08 13:00 | 210 | 194
2018-09-08 13:30 | 212 | 195
2018-09-08 14:00 | 180 | 160
2018-09-08 14:30 | 179 | 156
2018-09-08 15:00 | 198 | 178
2018-09-08 15:30 | 212 | 195
2018-09-08 16:00 | 252 | 239
2018-09-08 16:30 | 265 | 254
2018-09-08 17:00 | 310 | 303
2018-09-08 17:30 | 385 | 381
2018-09-08 18:00 | 430 | 429
2018-09-08 18:30 | 489 | 488
2018-09-08 19:00 | 515 | 515
2018-09-08 19:30 | 493 | 493
2018-09-08 20:00 | 469 | 469
2018-09-08 20:30 | 442 | 442
2018-09-08 21:00 | 426 | 426
2018-09-08 21:30 | 408 | 407
2018-09-08 22:00 | 404 | 403
2018-09-08 22:30 | 437 | 436
2018-09-08 23:00 | 421 | 421
2018-09-08 23:30 | 405 | 404
2018-09-09 | 400 | 399
2018-09-09 00:30 | 398 | 397
2018-09-09 01:00 | 379 | 378
2018-09-09 01:30 | 368 | 366
2018-09-09 02:00 | 366 | 363
2018-09-09 02:30 | 357 | 355
2018-09-09 03:00 | 357 | 355
2018-09-09 03:30 | 364 | 362
2018-09-09 04:00 | 364 | 363
2018-09-09 04:30 | 363 | 362
2018-09-09 05:00 | 357 | 356
2018-09-09 05:30 | 354 | 352
2018-09-09 06:00 | 330 | 328
2018-09-09 06:30 | 338 | 336
2018-09-09 07:00 | 328 | 326
2018-09-09 07:30 | 266 | 263
2018-09-09 08:00 | 212 | 204
2018-09-09 08:30 | 189 | 175
2018-09-09 09:00 | 168 | 149
2018-09-09 09:30 | 160 | 139
2018-09-09 10:00 | 153 | 130
2018-09-09 10:30 | 153 | 129
2018-09-09 11:00 | 145 | 119
2018-09-09 11:30 | 150 | 125
2018-09-09 12:00 | 159 | 135
2018-09-09 12:30 | 160 | 138
2018-09-09 13:00 | 157 | 133
2018-09-09 13:30 | 164 | 142
2018-09-09 14:00 | 162 | 140
2018-09-09 14:30 | 160 | 138
2018-09-09 15:00 | 175 | 154
2018-09-09 15:30 | 194 | 175
2018-09-09 16:00 | 223 | 207
2018-09-09 16:30 | 271 | 260
2018-09-09 17:00 | 310 | 304
2018-09-09 17:30 | 391 | 387
2018-09-09 18:00 | 455 | 454
2018-09-09 18:30 | 442 | 441
2018-09-09 19:00 | 436 | 436
2018-09-09 19:30 | 456 | 455
2018-09-09 20:00 | 393 | 392
2018-09-09 20:30 | 392 | 391
2018-09-09 21:00 | 412 | 411
2018-09-09 21:30 | 400 | 399
2018-09-09 22:00 | 383 | 381
2018-09-09 22:30 | 388 | 387
2018-09-09 23:00 | 372 | 370
2018-09-09 23:30 | 358 | 355
2018-09-10 | 350 | 347
2018-09-10 00:30 | 340 | 337
2018-09-10 01:00 | 333 | 329
2018-09-10 01:30 | 327 | 324
2018-09-10 02:00 | 318 | 314
2018-09-10 02:30 | 310 | 306
2018-09-10 03:00 | 308 | 303
2018-09-10 03:30 | 316 | 311
2018-09-10 04:00 | 315 | 311
2018-09-10 04:30 | 313 | 309
2018-09-10 05:00 | 317 | 313
2018-09-10 05:30 | 330 | 326
2018-09-10 06:00 | 318 | 315
2018-09-10 06:30 | 347 | 344
2018-09-10 07:00 | 329 | 326
2018-09-10 07:30 | 311 | 308
2018-09-10 08:00 | 275 | 268
2018-09-10 08:30 | 239 | 228
2018-09-10 09:00 | 210 | 195
2018-09-10 09:30 | 184 | 163
2018-09-10 10:00 | 176 | 152
2018-09-10 10:30 | 166 | 141
2018-09-10 11:00 | 158 | 132
2018-09-10 11:30 | 162 | 137
2018-09-10 12:00 | 170 | 147
2018-09-10 12:30 | 170 | 147
2018-09-10 13:00 | 173 | 152
2018-09-10 13:30 | 182 | 162
2018-09-10 14:00 | 175 | 154
2018-09-10 14:30 | 167 | 145
2018-09-10 15:00 | 191 | 170
2018-09-10 15:30 | 211 | 194
2018-09-10 16:00 | 231 | 218
2018-09-10 16:30 | 250 | 240
2018-09-10 17:00 | 329 | 322
2018-09-10 17:30 | 435 | 433
2018-09-10 18:00 | 493 | 493
2018-09-10 18:30 | 454 | 454
2018-09-10 19:00 | 427 | 427
2018-09-10 19:30 | 482 | 482
2018-09-10 20:00 | 480 | 480
2018-09-10 20:30 | 455 | 455
2018-09-10 21:00 | 436 | 435
2018-09-10 21:30 | 409 | 408
2018-09-10 22:00 | 385 | 383
2018-09-10 22:30 | 408 | 406
2018-09-10 23:00 | 383 | 382
2018-09-10 23:30 | 366 | 364
2018-09-11 | 353 | 351
2018-09-11 00:30 | 347 | 345
2018-09-11 01:00 | 333 | 329
2018-09-11 01:30 | 323 | 320
2018-09-11 02:00 | 302 | 298
2018-09-11 02:30 | 295 | 290
2018-09-11 03:00 | 300 | 295
2018-09-11 03:30 | 304 | 299
2018-09-11 04:00 | 308 | 303
2018-09-11 04:30 | 316 | 311
2018-09-11 05:00 | 329 | 324
2018-09-11 05:30 | 343 | 339
2018-09-11 06:00 | 330 | 327
2018-09-11 06:30 | 363 | 360
2018-09-11 07:00 | 346 | 344
2018-09-11 07:30 | 314 | 311
2018-09-11 08:00 | 271 | 266
2018-09-11 08:30 | 270 | 263
2018-09-11 09:00 | 225 | 217
2018-09-11 09:30 | 209 | 196
2018-09-11 10:00 | 222 | 208
2018-09-11 10:30 | 225 | 212
2018-09-11 11:00 | 191 | 176
2018-09-11 11:30 | 163 | 144
2018-09-11 12:00 | 174 | 152
2018-09-11 12:30 | 171 | 150
2018-09-11 13:00 | 210 | 193
2018-09-11 13:30 | 219 | 206
2018-09-11 14:00 | 201 | 187
2018-09-11 14:30 | 221 | 207
2018-09-11 15:00 | 222 | 210
2018-09-11 15:30 | 207 | 194
2018-09-11 16:00 | 222 | 210
2018-09-11 16:30 | 252 | 243
2018-09-11 17:00 | 319 | 313
2018-09-11 17:30 | 357 | 353
2018-09-11 18:00 | 421 | 419
2018-09-11 18:30 | 489 | 489
2018-09-11 19:00 | 517 | 517
2018-09-11 19:30 | 510 | 510
2018-09-11 20:00 | 498 | 498
2018-09-11 20:30 | 493 | 493
2018-09-11 21:00 | 484 | 484
2018-09-11 21:30 | 459 | 459
2018-09-11 22:00 | 430 | 430
2018-09-11 22:30 | 426 | 425
2018-09-11 23:00 | 395 | 394
2018-09-11 23:30 | 381 | 379
2018-09-12 | 366 | 364
2018-09-12 00:30 | 363 | 360
2018-09-12 01:00 | 346 | 344
2018-09-12 01:30 | 338 | 335
2018-09-12 02:00 | 268 | 264
2018-09-12 02:30 | 257 | 251
2018-09-12 03:00 | 257 | 250
2018-09-12 03:30 | 261 | 254
2018-09-12 04:00 | 308 | 302
2018-09-12 04:30 | 330 | 326
2018-09-12 05:00 | 331 | 327
2018-09-12 05:30 | 354 | 351
2018-09-12 06:00 | 345 | 342
2018-09-12 06:30 | 361 | 358
2018-09-12 07:00 | 364 | 361
2018-09-12 07:30 | 366 | 364
2018-09-12 08:00 | 332 | 330
2018-09-12 08:30 | 310 | 307
2018-09-12 09:00 | 298 | 294
2018-09-12 09:30 | 246 | 241
2018-09-12 10:00 | 231 | 222
2018-09-12 10:30 | 231 | 221
2018-09-12 11:00 | 215 | 205
2018-09-12 11:30 | 189 | 176
2018-09-12 12:00 | 203 | 189
2018-09-12 12:30 | 205 | 192
2018-09-12 13:00 | 231 | 220
2018-09-12 13:30 | 283 | 275
2018-09-12 14:00 | 251 | 244
2018-09-12 14:30 | 226 | 218
2018-09-12 15:00 | 244 | 236
2018-09-12 15:30 | 278 | 272
2018-09-12 16:00 | 296 | 291
2018-09-12 16:30 | 339 | 335
2018-09-12 17:00 | 394 | 392
2018-09-12 17:30 | 430 | 429
2018-09-12 18:00 | 480 | 479
2018-09-12 18:30 | 515 | 514
2018-09-12 19:00 | 522 | 522
2018-09-12 19:30 | 512 | 512
2018-09-12 20:00 | 500 | 500
2018-09-12 20:30 | 501 | 501
2018-09-12 21:00 | 491 | 491
2018-09-12 21:30 | 469 | 469
2018-09-12 22:00 | 437 | 436
2018-09-12 22:30 | 435 | 434
2018-09-12 23:00 | 419 | 418
2018-09-12 23:30 | 398 | 397
2018-09-13 | 379 | 378
2018-09-13 00:30 | 371 | 369
2018-09-13 01:00 | 351 | 349
2018-09-13 01:30 | 349 | 346
2018-09-13 02:00 | 347 | 345
2018-09-13 02:30 | 339 | 336
2018-09-13 03:00 | 337 | 334
2018-09-13 03:30 | 335 | 331
2018-09-13 04:00 | 347 | 343
2018-09-13 04:30 | 356 | 352
2018-09-13 05:00 | 365 | 362
2018-09-13 05:30 | 387 | 384
2018-09-13 06:00 | 383 | 380
2018-09-13 06:30 | 404 | 402
2018-09-13 07:00 | 393 | 391
2018-09-13 07:30 | 386 | 384
2018-09-13 08:00 | 335 | 333
2018-09-13 08:30 | 298 | 293
2018-09-13 09:00 | 290 | 284
2018-09-13 09:30 | 271 | 265
2018-09-13 10:00 | 267 | 259
2018-09-13 10:30 | 246 | 238
2018-09-13 11:00 | 261 | 252
2018-09-13 11:30 | 246 | 237
2018-09-13 12:00 | 207 | 197
2018-09-13 12:30 | 241 | 231
2018-09-13 13:00 | 239 | 230
2018-09-13 13:30 | 258 | 250
2018-09-13 14:00 | 239 | 231
2018-09-13 14:30 | 200 | 189
2018-09-13 15:00 | 233 | 222
2018-09-13 15:30 | 264 | 255
2018-09-13 16:00 | 279 | 271
2018-09-13 16:30 | 287 | 279
2018-09-13 17:00 | 337 | 332
2018-09-13 17:30 | 408 | 406
2018-09-13 18:00 | 473 | 472
2018-09-13 18:30 | 508 | 507
2018-09-13 19:00 | 521 | 521
2018-09-13 19:30 | 507 | 507
2018-09-13 20:00 | 483 | 483
2018-09-13 20:30 | 473 | 473
2018-09-13 21:00 | 468 | 468
2018-09-13 21:30 | 440 | 440
2018-09-13 22:00 | 418 | 417
2018-09-13 22:30 | 409 | 408
2018-09-13 23:00 | 389 | 388
2018-09-13 23:30 | 368 | 366
2018-09-14 | 349 | 346
2018-09-14 00:30 | 349 | 345
2018-09-14 01:00 | 343 | 339
2018-09-14 01:30 | 333 | 329
2018-09-14 02:00 | 325 | 321
2018-09-14 02:30 | 326 | 321
2018-09-14 03:00 | 335 | 330
2018-09-14 03:30 | 329 | 325
2018-09-14 04:00 | 327 | 323
2018-09-14 04:30 | 338 | 334
2018-09-14 05:00 | 342 | 338
2018-09-14 05:30 | 353 | 349
2018-09-14 06:00 | 339 | 335
2018-09-14 06:30 | 358 | 354
2018-09-14 07:00 | 328 | 324
2018-09-14 07:30 | 284 | 279
2018-09-14 08:00 | 237 | 229
2018-09-14 08:30 | 206 | 193
2018-09-14 09:00 | 192 | 175
2018-09-14 09:30 | 175 | 155
2018-09-14 10:00 | 130 | 96
2018-09-14 10:30 | 108 | 57
2018-09-14 11:00 | 105 | 48
2018-09-14 11:30 | 99 | 32
2018-09-14 12:00 | 106 | 45
2018-09-14 12:30 | 114 | 61
2018-09-14 13:00 | 122 | 79
2018-09-14 13:30 | 131 | 93
2018-09-14 14:00 | 123 | 84
2018-09-14 14:30 | 129 | 92
2018-09-14 15:00 | 144 | 112
2018-09-14 15:30 | 168 | 144
2018-09-14 16:00 | 216 | 198
2018-09-14 16:30 | 252 | 240
2018-09-14 17:00 | 301 | 292
2018-09-14 17:30 | 376 | 370
2018-09-14 18:00 | 442 | 439
2018-09-14 18:30 | 467 | 465
2018-09-14 19:00 | 478 | 477
2018-09-14 19:30 | 468 | 467
2018-09-14 20:00 | 391 | 390
2018-09-14 20:30 | 368 | 365
2018-09-14 21:00 | 358 | 354
2018-09-14 21:30 | 350 | 346
2018-09-14 22:00 | 339 | 335
2018-09-14 22:30 | 348 | 344
2018-09-14 23:00 | 324 | 319
2018-09-14 23:30 | 304 | 298
2018-09-15 | 283 | 276
2018-09-15 00:30 | 285 | 277
2018-09-15 01:00 | 270 | 263
2018-09-15 01:30 | 286 | 278
2018-09-15 02:00 | 311 | 304
2018-09-15 02:30 | 322 | 316
2018-09-15 03:00 | 316 | 310
2018-09-15 03:30 | 315 | 309
2018-09-15 04:00 | 324 | 318
2018-09-15 04:30 | 323 | 317
2018-09-15 05:00 | 319 | 313
2018-09-15 05:30 | 334 | 328
2018-09-15 06:00 | 342 | 337
2018-09-15 06:30 | 327 | 322
2018-09-15 07:00 | 283 | 277
2018-09-15 07:30 | 266 | 258
2018-09-15 08:00 | 239 | 229
2018-09-15 08:30 | 212 | 197
2018-09-15 09:00 | 206 | 187
2018-09-15 09:30 | 205 | 186
2018-09-15 10:00 | 175 | 151
2018-09-15 10:30 | 192 | 170
2018-09-15 11:00 | 204 | 185
2018-09-15 11:30 | 169 | 147
2018-09-15 12:00 | 154 | 125
2018-09-15 12:30 | 153 | 122
2018-09-15 13:00 | 154 | 123
2018-09-15 13:30 | 148 | 114
2018-09-15 14:00 | 147 | 113
2018-09-15 14:30 | 153 | 122
2018-09-15 15:00 | 172 | 147
2018-09-15 15:30 | 200 | 179
2018-09-15 16:00 | 218 | 201
2018-09-15 16:30 | 258 | 244
2018-09-15 17:00 | 310 | 300
2018-09-15 17:30 | 388 | 383
2018-09-15 18:00 | 450 | 448
2018-09-15 18:30 | 483 | 482
2018-09-15 19:00 | 486 | 485
2018-09-15 19:30 | 485 | 485
2018-09-15 20:00 | 481 | 481
2018-09-15 20:30 | 476 | 475
2018-09-15 21:00 | 472 | 472
2018-09-15 21:30 | 447 | 447
2018-09-15 22:00 | 428 | 427
2018-09-15 22:30 | 417 | 415
2018-09-15 23:00 | 445 | 443
2018-09-15 23:30 | 414 | 413
2018-09-16 | 403 | 402
2018-09-16 00:30 | 408 | 406
2018-09-16 01:00 | 383 | 381
2018-09-16 01:30 | 372 | 370
2018-09-16 02:00 | 371 | 368
2018-09-16 02:30 | 377 | 374
2018-09-16 03:00 | 373 | 371
2018-09-16 03:30 | 364 | 361
2018-09-16 04:00 | 366 | 363
2018-09-16 04:30 | 364 | 361
2018-09-16 05:00 | 365 | 362
2018-09-16 05:30 | 367 | 363
2018-09-16 06:00 | 369 | 366
2018-09-16 06:30 | 368 | 365
2018-09-16 07:00 | 330 | 326
2018-09-16 07:30 | 272 | 266
2018-09-16 08:00 | 210 | 199
2018-09-16 08:30 | 183 | 164
2018-09-16 09:00 | 190 | 169
2018-09-16 09:30 | 164 | 141
2018-09-16 10:00 | 143 | 114
2018-09-16 10:30 | 129 | 91
2018-09-16 11:00 | 117 | 70
2018-09-16 11:30 | 120 | 73
2018-09-16 12:00 | 120 | 76
2018-09-16 12:30 | 118 | 71
2018-09-16 13:00 | 119 | 69
2018-09-16 13:30 | 121 | 70
2018-09-16 14:00 | 119 | 67
2018-09-16 14:30 | 121 | 78
2018-09-16 15:00 | 137 | 101
2018-09-16 15:30 | 159 | 133
2018-09-16 16:00 | 196 | 178
2018-09-16 16:30 | 262 | 249
2018-09-16 17:00 | 312 | 304
2018-09-16 17:30 | 364 | 360
2018-09-16 18:00 | 445 | 443
2018-09-16 18:30 | 496 | 495
2018-09-16 19:00 | 577 | 577
2018-09-16 19:30 | 570 | 570
2018-09-16 20:00 | 560 | 560
2018-09-16 20:30 | 573 | 572
2018-09-16 21:00 | 578 | 578
2018-09-16 21:30 | 559 | 559
2018-09-16 22:00 | 538 | 538
2018-09-16 22:30 | 512 | 512
2018-09-16 23:00 | 490 | 490
2018-09-16 23:30 | 480 | 480
2018-09-17 | 474 | 473
2018-09-17 00:30 | 477 | 476
2018-09-17 01:00 | 458 | 457
2018-09-17 01:30 | 451 | 449
2018-09-17 02:00 | 452 | 450
2018-09-17 02:30 | 448 | 446
2018-09-17 03:00 | 445 | 443
2018-09-17 03:30 | 435 | 433
2018-09-17 04:00 | 430 | 428
2018-09-17 04:30 | 446 | 444
2018-09-17 05:00 | 440 | 438
2018-09-17 05:30 | 452 | 450
2018-09-17 06:00 | 465 | 463
2018-09-17 06:30 | 484 | 483
2018-09-17 07:00 | 457 | 456
2018-09-17 07:30 | 429 | 427
2018-09-17 08:00 | 374 | 372
2018-09-17 08:30 | 314 | 309
2018-09-17 09:00 | 307 | 300
2018-09-17 09:30 | 266 | 256
2018-09-17 10:00 | 223 | 208
2018-09-17 10:30 | 159 | 127
2018-09-17 11:00 | 215 | 186
2018-09-17 11:30 | 208 | 182
2018-09-17 12:00 | 200 | 172
2018-09-17 12:30 | 186 | 155
2018-09-17 13:00 | 177 | 144
2018-09-17 13:30 | 158 | 116
2018-09-17 14:00 | 180 | 142
2018-09-17 14:30 | 202 | 170
2018-09-17 15:00 | 226 | 200
2018-09-17 15:30 | 247 | 226
2018-09-17 16:00 | 293 | 277
2018-09-17 16:30 | 328 | 317
2018-09-17 17:00 | 393 | 386
2018-09-17 17:30 | 463 | 459
2018-09-17 18:00 | 530 | 528
2018-09-17 18:30 | 559 | 559
2018-09-17 19:00 | 577 | 577
2018-09-17 19:30 | 566 | 565
2018-09-17 20:00 | 553 | 552
2018-09-17 20:30 | 561 | 561
2018-09-17 21:00 | 548 | 548
2018-09-17 21:30 | 528 | 528
2018-09-17 22:00 | 503 | 502
2018-09-17 22:30 | 468 | 466
2018-09-17 23:00 | 445 | 443
2018-09-17 23:30 | 421 | 418
2018-09-18 | 400 | 396
2018-09-18 00:30 | 401 | 396
2018-09-18 01:00 | 379 | 374
2018-09-18 01:30 | 377 | 370
2018-09-18 02:00 | 381 | 374
2018-09-18 02:30 | 379 | 373
2018-09-18 03:00 | 385 | 379
2018-09-18 03:30 | 385 | 379
2018-09-18 04:00 | 387 | 380
2018-09-18 04:30 | 387 | 380
2018-09-18 05:00 | 392 | 385
2018-09-18 05:30 | 386 | 380
2018-09-18 06:00 | 403 | 397
2018-09-18 06:30 | 420 | 414
2018-09-18 07:00 | 413 | 408
2018-09-18 07:30 | 417 | 412
2018-09-18 08:00 | 412 | 407
2018-09-18 08:30 | 375 | 368
2018-09-18 09:00 | 390 | 383
2018-09-18 09:30 | 321 | 313
2018-09-18 10:00 | 281 | 269
2018-09-18 10:30 | 262 | 249
2018-09-18 11:00 | 294 | 280
2018-09-18 11:30 | 273 | 259
2018-09-18 12:00 | 270 | 254
2018-09-18 12:30 | 255 | 239
2018-09-18 13:00 | 294 | 278
2018-09-18 13:30 | 275 | 261
2018-09-18 14:00 | 307 | 295
2018-09-18 14:30 | 229 | 215
2018-09-18 15:00 | 266 | 248
2018-09-18 15:30 | 273 | 257
2018-09-18 16:00 | 305 | 293
2018-09-18 16:30 | 328 | 318
2018-09-18 17:00 | 382 | 373
2018-09-18 17:30 | 446 | 435
2018-09-18 18:00 | 520 | 514
2018-09-18 18:30 | 561 | 560
2018-09-18 19:00 | 539 | 539
2018-09-18 19:30 | 529 | 529
2018-09-18 20:00 | 551 | 551
2018-09-18 20:30 | 581 | 581
2018-09-18 21:00 | 556 | 556
2018-09-18 21:30 | 531 | 531
2018-09-18 22:00 | 490 | 489
2018-09-18 22:30 | 442 | 441
2018-09-18 23:00 | 425 | 425
2018-09-18 23:30 | 403 | 403
2018-09-19 | 382 | 381
2018-09-19 00:30 | 380 | 377
2018-09-19 01:00 | 368 | 364
2018-09-19 01:30 | 360 | 356
2018-09-19 02:00 | 338 | 332
2018-09-19 02:30 | 338 | 331
2018-09-19 03:00 | 332 | 325
2018-09-19 03:30 | 331 | 324
2018-09-19 04:00 | 329 | 322
2018-09-19 04:30 | 332 | 324
2018-09-19 05:00 | 333 | 326
2018-09-19 05:30 | 349 | 342
2018-09-19 06:00 | 363 | 357
2018-09-19 06:30 | 382 | 376
2018-09-19 07:00 | 351 | 345
2018-09-19 07:30 | 341 | 335
2018-09-19 08:00 | 294 | 286
2018-09-19 08:30 | 247 | 234
2018-09-19 09:00 | 247 | 230
2018-09-19 09:30 | 246 | 229
2018-09-19 10:00 | 166 | 138
2018-09-19 10:30 | 195 | 163
2018-09-19 11:00 | 182 | 150
2018-09-19 11:30 | 149 | 107
2018-09-19 12:00 | 155 | 107
2018-09-19 12:30 | 154 | 100
2018-09-19 13:00 | 182 | 137
2018-09-19 13:30 | 194 | 152
2018-09-19 14:00 | 195 | 155
2018-09-19 14:30 | 189 | 146
2018-09-19 15:00 | 188 | 147
2018-09-19 15:30 | 196 | 156
2018-09-19 16:00 | 239 | 209
2018-09-19 16:30 | 273 | 252
2018-09-19 17:00 | 333 | 317
2018-09-19 17:30 | 318 | 306
2018-09-19 18:00 | 306 | 295
2018-09-19 18:30 | 353 | 343
2018-09-19 19:00 | 390 | 381
2018-09-19 19:30 | 396 | 389
2018-09-19 20:00 | 377 | 369
2018-09-19 20:30 | 364 | 355
2018-09-19 21:00 | 348 | 338
2018-09-19 21:30 | 333 | 321
2018-09-19 22:00 | 303 | 289
2018-09-19 22:30 | 288 | 271
2018-09-19 23:00 | 277 | 258
2018-09-19 23:30 | 256 | 237
2018-09-20 | 241 | 219
2018-09-20 00:30 | 296 | 276
2018-09-20 01:00 | 360 | 346
2018-09-20 01:30 | 348 | 338
2018-09-20 02:00 | 339 | 328
2018-09-20 02:30 | 339 | 328
2018-09-20 03:00 | 339 | 328
2018-09-20 03:30 | 343 | 332
2018-09-20 04:00 | 333 | 322
2018-09-20 04:30 | 342 | 330
2018-09-20 05:00 | 346 | 335
2018-09-20 05:30 | 358 | 347
2018-09-20 06:00 | 378 | 368
2018-09-20 06:30 | 387 | 379
2018-09-20 07:00 | 335 | 326
2018-09-20 07:30 | 301 | 288
2018-09-20 08:00 | 247 | 228
2018-09-20 08:30 | 236 | 212
2018-09-20 09:00 | 234 | 207
2018-09-20 09:30 | 192 | 159
2018-09-20 10:00 | 169 | 128
2018-09-20 10:30 | 136 | 73
2018-09-20 11:00 | 134 | 63
2018-09-20 11:30 | 170 | 119
2018-09-20 12:00 | 127 | 51
2018-09-20 12:30 | 154 | 96
2018-09-20 13:00 | 126 | 50
2018-09-20 13:30 | 128 | 44
2018-09-20 14:00 | 129 | 53
2018-09-20 14:30 | 165 | 125
2018-09-20 15:00 | 185 | 155
2018-09-20 15:30 | 209 | 186
2018-09-20 16:00 | 253 | 235
2018-09-20 16:30 | 288 | 275
2018-09-20 17:00 | 364 | 356
2018-09-20 17:30 | 395 | 389
2018-09-20 18:00 | 367 | 363
2018-09-20 18:30 | 329 | 324
2018-09-20 19:00 | 375 | 370
2018-09-20 19:30 | 380 | 378
2018-09-20 20:00 | 370 | 367
2018-09-20 20:30 | 389 | 386
2018-09-20 21:00 | 375 | 372
2018-09-20 21:30 | 355 | 351
2018-09-20 22:00 | 331 | 327
2018-09-20 22:30 | 305 | 299
2018-09-20 23:00 | 340 | 334
2018-09-20 23:30 | 397 | 393
2018-09-21 | 386 | 383
2018-09-21 00:30 | 380 | 377
2018-09-21 01:00 | 364 | 361
2018-09-21 01:30 | 366 | 362
2018-09-21 02:00 | 371 | 367
2018-09-21 02:30 | 381 | 377
2018-09-21 03:00 | 377 | 373
2018-09-21 03:30 | 370 | 366
2018-09-21 04:00 | 372 | 367
2018-09-21 04:30 | 364 | 360
2018-09-21 05:00 | 382 | 378
2018-09-21 05:30 | 384 | 381
2018-09-21 06:00 | 385 | 382
2018-09-21 06:30 | 398 | 395
2018-09-21 07:00 | 344 | 341
2018-09-21 07:30 | 298 | 292
2018-09-21 08:00 | 243 | 233
2018-09-21 08:30 | 214 | 197
2018-09-21 09:00 | 225 | 207
2018-09-21 09:30 | 222 | 202
2018-09-21 10:00 | 202 | 180
2018-09-21 10:30 | 210 | 187
2018-09-21 11:00 | 218 | 196
2018-09-21 11:30 | 176 | 147
2018-09-21 12:00 | 179 | 147
2018-09-21 12:30 | 162 | 124
2018-09-21 13:00 | 166 | 130
2018-09-21 13:30 | 171 | 136
2018-09-21 14:00 | 153 | 114
2018-09-21 14:30 | 160 | 123
2018-09-21 15:00 | 185 | 155
2018-09-21 15:30 | 218 | 193
2018-09-21 16:00 | 281 | 264
2018-09-21 16:30 | 303 | 291
2018-09-21 17:00 | 332 | 323
2018-09-21 17:30 | 310 | 302
2018-09-21 18:00 | 340 | 333
2018-09-21 18:30 | 351 | 346
2018-09-21 19:00 | 376 | 371
2018-09-21 19:30 | 372 | 368
2018-09-21 20:00 | 354 | 349
2018-09-21 20:30 | 351 | 346
2018-09-21 21:00 | 349 | 344
2018-09-21 21:30 | 335 | 330
2018-09-21 22:00 | 317 | 311
2018-09-21 22:30 | 288 | 280
2018-09-21 23:00 | 286 | 277
2018-09-21 23:30 | 303 | 293
2018-09-22 | 305 | 296
2018-09-22 00:30 | 366 | 359
2018-09-22 01:00 | 367 | 361
2018-09-22 01:30 | 357 | 352
2018-09-22 02:00 | 347 | 341
2018-09-22 02:30 | 345 | 338
2018-09-22 03:00 | 347 | 340
2018-09-22 03:30 | 339 | 332
2018-09-22 04:00 | 338 | 331
2018-09-22 04:30 | 353 | 346
2018-09-22 05:00 | 349 | 344
2018-09-22 05:30 | 362 | 356
2018-09-22 06:00 | 367 | 362
2018-09-22 06:30 | 353 | 348
2018-09-22 07:00 | 303 | 296
2018-09-22 07:30 | 245 | 234
2018-09-22 08:00 | 196 | 176
2018-09-22 08:30 | 186 | 157
2018-09-22 09:00 | 205 | 179
2018-09-22 09:30 | 195 | 169
2018-09-22 10:00 | 177 | 150
2018-09-22 10:30 | 176 | 146
2018-09-22 11:00 | 181 | 152
2018-09-22 11:30 | 204 | 180
2018-09-22 12:00 | 176 | 149
2018-09-22 12:30 | 180 | 152
2018-09-22 13:00 | 169 | 137
2018-09-22 13:30 | 154 | 117
2018-09-22 14:00 | 155 | 116
2018-09-22 14:30 | 152 | 119
2018-09-22 15:00 | 185 | 158
2018-09-22 15:30 | 181 | 155
2018-09-22 16:00 | 188 | 163
2018-09-22 16:30 | 241 | 223
2018-09-22 17:00 | 320 | 309
2018-09-22 17:30 | 389 | 383
2018-09-22 18:00 | 462 | 459
2018-09-22 18:30 | 515 | 513
2018-09-22 19:00 | 540 | 539
2018-09-22 19:30 | 530 | 530
2018-09-22 20:00 | 511 | 510
2018-09-22 20:30 | 509 | 509
2018-09-22 21:00 | 505 | 505
2018-09-22 21:30 | 494 | 494
2018-09-22 22:00 | 463 | 463
2018-09-22 22:30 | 449 | 449
2018-09-22 23:00 | 431 | 431
2018-09-22 23:30 | 409 | 409
2018-09-23 | 388 | 387
2018-09-23 00:30 | 403 | 401
2018-09-23 01:00 | 395 | 393
2018-09-23 01:30 | 364 | 362
2018-09-23 02:00 | 349 | 346
2018-09-23 02:30 | 362 | 359
2018-09-23 03:00 | 357 | 355
2018-09-23 03:30 | 360 | 358
2018-09-23 04:00 | 357 | 355
2018-09-23 04:30 | 345 | 342
2018-09-23 05:00 | 335 | 332
2018-09-23 05:30 | 352 | 349
2018-09-23 06:00 | 361 | 358
2018-09-23 06:30 | 335 | 332
2018-09-23 07:00 | 264 | 260
2018-09-23 07:30 | 199 | 189
2018-09-23 08:00 | 163 | 145
2018-09-23 08:30 | 146 | 121
2018-09-23 09:00 | 165 | 143
2018-09-23 09:30 | 122 | 92
2018-09-23 10:00 | 115 | 80
2018-09-23 10:30 | 124 | 92
2018-09-23 11:00 | 118 | 86
2018-09-23 11:30 | 126 | 93
2018-09-23 12:00 | 113 | 77
2018-09-23 12:30 | 113 | 76
2018-09-23 13:00 | 109 | 69
2018-09-23 13:30 | 136 | 107
2018-09-23 14:00 | 130 | 100
2018-09-23 14:30 | 130 | 101
2018-09-23 15:00 | 133 | 105
2018-09-23 15:30 | 152 | 130
2018-09-23 16:00 | 172 | 153
2018-09-23 16:30 | 215 | 201
2018-09-23 17:00 | 268 | 259
2018-09-23 17:30 | 383 | 379
2018-09-23 18:00 | 483 | 482
2018-09-23 18:30 | 521 | 520
2018-09-23 19:00 | 562 | 562
2018-09-23 19:30 | 546 | 546
2018-09-23 20:00 | 517 | 517
2018-09-23 20:30 | 515 | 515
2018-09-23 21:00 | 515 | 515
2018-09-23 21:30 | 483 | 482
2018-09-23 22:00 | 474 | 474
2018-09-23 22:30 | 450 | 449
2018-09-23 23:00 | 415 | 414
2018-09-23 23:30 | 402 | 401
2018-09-24 | 385 | 383
2018-09-24 00:30 | 381 | 379
2018-09-24 01:00 | 355 | 353
2018-09-24 01:30 | 350 | 346
2018-09-24 02:00 | 341 | 338
2018-09-24 02:30 | 349 | 345
2018-09-24 03:00 | 356 | 353
2018-09-24 03:30 | 354 | 350
2018-09-24 04:00 | 355 | 352
2018-09-24 04:30 | 356 | 352
2018-09-24 05:00 | 364 | 360
2018-09-24 05:30 | 377 | 374
2018-09-24 06:00 | 379 | 377
2018-09-24 06:30 | 390 | 388
2018-09-24 07:00 | 333 | 331
2018-09-24 07:30 | 261 | 256
2018-09-24 08:00 | 206 | 196
2018-09-24 08:30 | 181 | 166
2018-09-24 09:00 | 194 | 179
2018-09-24 09:30 | 206 | 191
2018-09-24 10:00 | 172 | 154
2018-09-24 10:30 | 167 | 144
2018-09-24 11:00 | 160 | 135
2018-09-24 11:30 | 163 | 139
2018-09-24 12:00 | 169 | 145
2018-09-24 12:30 | 175 | 152
2018-09-24 13:00 | 219 | 201
2018-09-24 13:30 | 188 | 173
2018-09-24 14:00 | 174 | 154
2018-09-24 14:30 | 169 | 147
2018-09-24 15:00 | 165 | 142
2018-09-24 15:30 | 188 | 168
2018-09-24 16:00 | 215 | 201
2018-09-24 16:30 | 284 | 275
2018-09-24 17:00 | 402 | 398
2018-09-24 17:30 | 396 | 394
2018-09-24 18:00 | 381 | 380
2018-09-24 18:30 | 412 | 410
2018-09-24 19:00 | 442 | 441
2018-09-24 19:30 | 437 | 436
2018-09-24 20:00 | 425 | 425
2018-09-24 20:30 | 412 | 411
2018-09-24 21:00 | 403 | 402
2018-09-24 21:30 | 392 | 391
2018-09-24 22:00 | 362 | 361
2018-09-24 22:30 | 339 | 337
2018-09-24 23:00 | 343 | 341
2018-09-24 23:30 | 400 | 397
2018-09-25 | 392 | 391
2018-09-25 00:30 | 381 | 380
2018-09-25 01:00 | 378 | 376
2018-09-25 01:30 | 369 | 367
2018-09-25 02:00 | 362 | 360
2018-09-25 02:30 | 360 | 358
2018-09-25 03:00 | 356 | 353
2018-09-25 03:30 | 358 | 355
2018-09-25 04:00 | 359 | 356
2018-09-25 04:30 | 353 | 350
2018-09-25 05:00 | 360 | 357
2018-09-25 05:30 | 376 | 373
2018-09-25 06:00 | 386 | 384
2018-09-25 06:30 | 399 | 397
2018-09-25 07:00 | 365 | 363
2018-09-25 07:30 | 296 | 293
2018-09-25 08:00 | 251 | 244
2018-09-25 08:30 | 221 | 210
2018-09-25 09:00 | 254 | 242
2018-09-25 09:30 | 265 | 256
2018-09-25 10:00 | 225 | 216
2018-09-25 10:30 | 206 | 194
2018-09-25 11:00 | 228 | 216
2018-09-25 11:30 | 233 | 222
2018-09-25 12:00 | 220 | 208
2018-09-25 12:30 | 216 | 204
2018-09-25 13:00 | 202 | 190
2018-09-25 13:30 | 200 | 186
2018-09-25 14:00 | 176 | 161
2018-09-25 14:30 | 228 | 215
2018-09-25 15:00 | 187 | 174
2018-09-25 15:30 | 218 | 204
2018-09-25 16:00 | 272 | 263
2018-09-25 16:30 | 296 | 290
2018-09-25 17:00 | 354 | 350
2018-09-25 17:30 | 405 | 403
2018-09-25 18:00 | 471 | 470
2018-09-25 18:30 | 519 | 519
2018-09-25 19:00 | 541 | 541
2018-09-25 19:30 | 541 | 541
2018-09-25 20:00 | 522 | 522
2018-09-25 20:30 | 522 | 522
2018-09-25 21:00 | 505 | 505
2018-09-25 21:30 | 491 | 491
2018-09-25 22:00 | 473 | 472
2018-09-25 22:30 | 438 | 438
2018-09-25 23:00 | 417 | 417
2018-09-25 23:30 | 399 | 398
2018-09-26 | 383 | 381
2018-09-26 00:30 | 379 | 377
2018-09-26 01:00 | 362 | 360
2018-09-26 01:30 | 371 | 368
2018-09-26 02:00 | 359 | 356
2018-09-26 02:30 | 359 | 356
2018-09-26 03:00 | 348 | 345
2018-09-26 03:30 | 357 | 354
2018-09-26 04:00 | 366 | 364
2018-09-26 04:30 | 349 | 347
2018-09-26 05:00 | 354 | 351
2018-09-26 05:30 | 372 | 369
2018-09-26 06:00 | 379 | 377
2018-09-26 06:30 | 387 | 385
2018-09-26 07:00 | 350 | 348
2018-09-26 07:30 | 297 | 293
2018-09-26 08:00 | 264 | 256
2018-09-26 08:30 | 222 | 211
2018-09-26 09:00 | 220 | 206
2018-09-26 09:30 | 217 | 203
2018-09-26 10:00 | 198 | 181
2018-09-26 10:30 | 189 | 170
2018-09-26 11:00 | 180 | 160
2018-09-26 11:30 | 156 | 132
2018-09-26 12:00 | 162 | 135
2018-09-26 12:30 | 166 | 140
2018-09-26 13:00 | 184 | 156
2018-09-26 13:30 | 207 | 184
2018-09-26 14:00 | 181 | 156
2018-09-26 14:30 | 191 | 166
2018-09-26 15:00 | 197 | 174
2018-09-26 15:30 | 253 | 235
2018-09-26 16:00 | 288 | 277
2018-09-26 16:30 | 293 | 285
2018-09-26 17:00 | 278 | 270
2018-09-26 17:30 | 263 | 254
2018-09-26 18:00 | 343 | 335
2018-09-26 18:30 | 361 | 356
2018-09-26 19:00 | 403 | 399
2018-09-26 19:30 | 385 | 382
2018-09-26 20:00 | 376 | 373
2018-09-26 20:30 | 358 | 354
2018-09-26 21:00 | 347 | 342
2018-09-26 21:30 | 330 | 325
2018-09-26 22:00 | 316 | 310
2018-09-26 22:30 | 334 | 328
2018-09-26 23:00 | 401 | 397
2018-09-26 23:30 | 400 | 397
2018-09-27 | 394 | 391
2018-09-27 00:30 | 407 | 404
2018-09-27 01:00 | 407 | 404
2018-09-27 01:30 | 404 | 401
2018-09-27 02:00 | 392 | 389
2018-09-27 02:30 | 381 | 378
2018-09-27 03:00 | 378 | 374
2018-09-27 03:30 | 383 | 379
2018-09-27 04:00 | 387 | 383
2018-09-27 04:30 | 387 | 384
2018-09-27 05:00 | 391 | 388
2018-09-27 05:30 | 408 | 405
2018-09-27 06:00 | 420 | 417
2018-09-27 06:30 | 417 | 415
2018-09-27 07:00 | 375 | 372
2018-09-27 07:30 | 323 | 318
2018-09-27 08:00 | 282 | 274
2018-09-27 08:30 | 265 | 253
2018-09-27 09:00 | 297 | 285
2018-09-27 09:30 | 266 | 254
2018-09-27 10:00 | 257 | 245
2018-09-27 10:30 | 220 | 205
2018-09-27 11:00 | 199 | 180
2018-09-27 11:30 | 197 | 175
2018-09-27 12:00 | 187 | 165
2018-09-27 12:30 | 186 | 162
2018-09-27 13:00 | 164 | 137
2018-09-27 13:30 | 156 | 125
2018-09-27 14:00 | 139 | 102
2018-09-27 14:30 | 161 | 129
2018-09-27 15:00 | 198 | 169
2018-09-27 15:30 | 233 | 209
2018-09-27 16:00 | 289 | 275
2018-09-27 16:30 | 313 | 303
2018-09-27 17:00 | 334 | 328
2018-09-27 17:30 | 405 | 399
2018-09-27 18:00 | 415 | 411
2018-09-27 18:30 | 428 | 425
2018-09-27 19:00 | 416 | 413
2018-09-27 19:30 | 415 | 412
2018-09-27 20:00 | 410 | 407
2018-09-27 20:30 | 418 | 415
2018-09-27 21:00 | 405 | 402
2018-09-27 21:30 | 383 | 379
2018-09-27 22:00 | 370 | 366
2018-09-27 22:30 | 399 | 395
2018-09-27 23:00 | 437 | 434
2018-09-27 23:30 | 409 | 407
2018-09-28 | 390 | 387
2018-09-28 00:30 | 386 | 382
2018-09-28 01:00 | 369 | 364
2018-09-28 01:30 | 358 | 352
2018-09-28 02:00 | 351 | 345
2018-09-28 02:30 | 343 | 337
2018-09-28 03:00 | 345 | 338
2018-09-28 03:30 | 342 | 335
2018-09-28 04:00 | 353 | 346
2018-09-28 04:30 | 366 | 360
2018-09-28 05:00 | 360 | 354
2018-09-28 05:30 | 365 | 360
2018-09-28 06:00 | 385 | 380
2018-09-28 06:30 | 391 | 386
2018-09-28 07:00 | 345 | 340
2018-09-28 07:30 | 287 | 278
2018-09-28 08:00 | 281 | 269
2018-09-28 08:30 | 270 | 256
2018-09-28 09:00 | 260 | 245
2018-09-28 09:30 | 231 | 214
2018-09-28 10:00 | 200 | 175
2018-09-28 10:30 | 169 | 136
2018-09-28 11:00 | 191 | 158
2018-09-28 11:30 | 181 | 147
2018-09-28 12:00 | 177 | 143
2018-09-28 12:30 | 168 | 129
2018-09-28 13:00 | 169 | 131
2018-09-28 13:30 | 169 | 132
2018-09-28 14:00 | 178 | 143
2018-09-28 14:30 | 173 | 137
2018-09-28 15:00 | 222 | 194
2018-09-28 15:30 | 215 | 191
2018-09-28 16:00 | 233 | 211
2018-09-28 16:30 | 278 | 261
2018-09-28 17:00 | 321 | 310
2018-09-28 17:30 | 405 | 398
2018-09-28 18:00 | 462 | 458
2018-09-28 18:30 | 503 | 501
2018-09-28 19:00 | 539 | 538
2018-09-28 19:30 | 553 | 552
2018-09-28 20:00 | 488 | 487
2018-09-28 20:30 | 522 | 520
2018-09-28 21:00 | 518 | 517
2018-09-28 21:30 | 498 | 497
2018-09-28 22:00 | 473 | 471
2018-09-28 22:30 | 456 | 454
2018-09-28 23:00 | 443 | 440
2018-09-28 23:30 | 423 | 419
2018-09-29 | 405 | 402
2018-09-29 00:30 | 399 | 395
2018-09-29 01:00 | 384 | 379
2018-09-29 01:30 | 377 | 372
2018-09-29 02:00 | 367 | 361
2018-09-29 02:30 | 361 | 355
2018-09-29 03:00 | 349 | 343
2018-09-29 03:30 | 340 | 333
2018-09-29 04:00 | 337 | 330
2018-09-29 04:30 | 345 | 338
2018-09-29 05:00 | 349 | 343
2018-09-29 05:30 | 357 | 351
2018-09-29 06:00 | 354 | 348
2018-09-29 06:30 | 343 | 336
2018-09-29 07:00 | 276 | 267
2018-09-29 07:30 | 220 | 204
2018-09-29 08:00 | 185 | 159
2018-09-29 08:30 | 173 | 140
2018-09-29 09:00 | 203 | 175
2018-09-29 09:30 | 171 | 137
2018-09-29 10:00 | 158 | 118
2018-09-29 10:30 | 147 | 99
2018-09-29 11:00 | 135 | 80
2018-09-29 11:30 | 137 | 83
2018-09-29 12:00 | 135 | 79
2018-09-29 12:30 | 129 | 70
2018-09-29 13:00 | 131 | 70
2018-09-29 13:30 | 143 | 88
2018-09-29 14:00 | 134 | 82
2018-09-29 14:30 | 150 | 106
2018-09-29 15:00 | 160 | 118
2018-09-29 15:30 | 187 | 152
2018-09-29 16:00 | 214 | 187
2018-09-29 16:30 | 250 | 231
2018-09-29 17:00 | 310 | 296
2018-09-29 17:30 | 394 | 387
2018-09-29 18:00 | 456 | 453
2018-09-29 18:30 | 488 | 486
2018-09-29 19:00 | 526 | 525
2018-09-29 19:30 | 522 | 521
2018-09-29 20:00 | 502 | 501
2018-09-29 20:30 | 516 | 515
2018-09-29 21:00 | 497 | 496
2018-09-29 21:30 | 475 | 474
2018-09-29 22:00 | 460 | 458
2018-09-29 22:30 | 441 | 439
2018-09-29 23:00 | 429 | 426
2018-09-29 23:30 | 414 | 411
2018-09-30 | 399 | 396
2018-09-30 00:30 | 395 | 392
2018-09-30 01:00 | 388 | 384
2018-09-30 01:30 | 382 | 378
2018-09-30 02:00 | 373 | 369
2018-09-30 02:30 | 361 | 357
2018-09-30 03:00 | 348 | 343
2018-09-30 03:30 | 356 | 350
2018-09-30 04:00 | 344 | 338
2018-09-30 04:30 | 344 | 338
2018-09-30 05:00 | 355 | 349
2018-09-30 05:30 | 354 | 349
2018-09-30 06:00 | 351 | 345
2018-09-30 06:30 | 331 | 325
2018-09-30 07:00 | 260 | 252
2018-09-30 07:30 | 214 | 198
2018-09-30 08:00 | 177 | 151
2018-09-30 08:30 | 168 | 136
2018-09-30 09:00 | 189 | 160
2018-09-30 09:30 | 162 | 129
2018-09-30 10:00 | 142 | 97
2018-09-30 10:30 | 126 | 72
2018-09-30 11:00 | 123 | 64
2018-09-30 11:30 | 126 | 65
2018-09-30 12:00 | 129 | 67
2018-09-30 12:30 | 124 | 66
2018-09-30 13:00 | 123 | 63
2018-09-30 13:30 | 125 | 70
2018-09-30 14:00 | 127 | 74
2018-09-30 14:30 | 132 | 81
2018-09-30 15:00 | 154 | 109
2018-09-30 15:30 | 169 | 135
2018-09-30 16:00 | 199 | 173
2018-09-30 16:30 | 253 | 235
2018-09-30 17:00 | 332 | 320
2018-09-30 17:30 | 420 | 414
2018-09-30 18:00 | 481 | 478
2018-09-30 18:30 | 525 | 524
2018-09-30 19:00 | 543 | 542
2018-09-30 19:30 | 527 | 527
2018-09-30 20:00 | 505 | 505
2018-09-30 20:30 | 524 | 523
2018-09-30 21:00 | 512 | 511
2018-09-30 21:30 | 488 | 487
2018-09-30 22:00 | 468 | 467
2018-09-30 22:30 | 438 | 436
2018-09-30 23:00 | 427 | 424
2018-09-30 23:30 | 409 | 406
2018-10-01 | 384 | 380
2018-10-01 00:30 | 379 | 374
2018-10-01 01:00 | 364 | 359
2018-10-01 01:30 | 365 | 359
2018-10-01 02:00 | 356 | 350
2018-10-01 02:30 | 364 | 357
2018-10-01 03:00 | 359 | 353
2018-10-01 03:30 | 354 | 347
2018-10-01 04:00 | 353 | 347
2018-10-01 04:30 | 354 | 347
2018-10-01 05:00 | 360 | 354
2018-10-01 05:30 | 362 | 356
2018-10-01 06:00 | 362 | 356
2018-10-01 06:30 | 365 | 359
2018-10-01 07:00 | 361 | 355
2018-10-01 07:30 | 300 | 293
2018-10-01 08:00 | 284 | 273
2018-10-01 08:30 | 246 | 232
2018-10-01 09:00 | 267 | 252
2018-10-01 09:30 | 241 | 225
2018-10-01 10:00 | 206 | 184
2018-10-01 10:30 | 218 | 195
2018-10-01 11:00 | 205 | 181
2018-10-01 11:30 | 173 | 142
2018-10-01 12:00 | 175 | 142
2018-10-01 12:30 | 166 | 128
2018-10-01 13:00 | 136 | 86
2018-10-01 13:30 | 132 | 76
2018-10-01 14:00 | 141 | 90
2018-10-01 14:30 | 150 | 105
2018-10-01 15:00 | 165 | 125
2018-10-01 15:30 | 189 | 156
2018-10-01 16:00 | 238 | 214
2018-10-01 16:30 | 272 | 255
2018-10-01 17:00 | 333 | 322
2018-10-01 17:30 | 418 | 412
2018-10-01 18:00 | 512 | 509
2018-10-01 18:30 | 513 | 512
2018-10-01 19:00 | 519 | 519
2018-10-01 19:30 | 534 | 533
2018-10-01 20:00 | 513 | 512
2018-10-01 20:30 | 517 | 516
2018-10-01 21:00 | 498 | 497
2018-10-01 21:30 | 487 | 486
2018-10-01 22:00 | 481 | 480
2018-10-01 22:30 | 446 | 445
2018-10-01 23:00 | 433 | 431
2018-10-01 23:30 | 424 | 422
2018-10-02 | 419 | 417
2018-10-02 00:30 | 395 | 393
2018-10-02 01:00 | 391 | 387
2018-10-02 01:30 | 374 | 371
2018-10-02 02:00 | 372 | 368
2018-10-02 02:30 | 371 | 366
2018-10-02 03:00 | 368 | 363
2018-10-02 03:30 | 351 | 346
2018-10-02 04:00 | 349 | 343
2018-10-02 04:30 | 350 | 345
2018-10-02 05:00 | 353 | 347
2018-10-02 05:30 | 359 | 353
2018-10-02 06:00 | 372 | 367
2018-10-02 06:30 | 385 | 380
2018-10-02 07:00 | 346 | 342
2018-10-02 07:30 | 304 | 297
2018-10-02 08:00 | 275 | 265
2018-10-02 08:30 | 270 | 258
2018-10-02 09:00 | 253 | 239
2018-10-02 09:30 | 256 | 241
2018-10-02 10:00 | 271 | 257
2018-10-02 10:30 | 229 | 214
2018-10-02 11:00 | 248 | 231
2018-10-02 11:30 | 217 | 198
2018-10-02 12:00 | 198 | 175
2018-10-02 12:30 | 156 | 122
2018-10-02 13:00 | 168 | 134
2018-10-02 13:30 | 169 | 138
2018-10-02 14:00 | 175 | 145
2018-10-02 14:30 | 200 | 175
2018-10-02 15:00 | 171 | 140
2018-10-02 15:30 | 200 | 172
2018-10-02 16:00 | 221 | 201
2018-10-02 16:30 | 255 | 240
2018-10-02 17:00 | 279 | 267
2018-10-02 17:30 | 260 | 249
2018-10-02 18:00 | 306 | 296
2018-10-02 18:30 | 358 | 351
2018-10-02 19:00 | 380 | 376
2018-10-02 19:30 | 379 | 376
2018-10-02 20:00 | 361 | 358
2018-10-02 20:30 | 331 | 327
2018-10-02 21:00 | 326 | 321
2018-10-02 21:30 | 442 | 437
2018-10-02 22:00 | 448 | 446
2018-10-02 22:30 | 419 | 417
2018-10-02 23:00 | 396 | 394
2018-10-02 23:30 | 384 | 381
2018-10-03 | 394 | 390
2018-10-03 00:30 | 393 | 389
2018-10-03 01:00 | 375 | 372
2018-10-03 01:30 | 363 | 358
2018-10-03 02:00 | 345 | 340
2018-10-03 02:30 | 336 | 330
2018-10-03 03:00 | 333 | 327
2018-10-03 03:30 | 346 | 339
2018-10-03 04:00 | 332 | 326
2018-10-03 04:30 | 339 | 332
2018-10-03 05:00 | 346 | 340
2018-10-03 05:30 | 369 | 363
2018-10-03 06:00 | 382 | 377
2018-10-03 06:30 | 388 | 384
2018-10-03 07:00 | 349 | 345
2018-10-03 07:30 | 301 | 294
2018-10-03 08:00 | 248 | 237
2018-10-03 08:30 | 239 | 223
2018-10-03 09:00 | 214 | 194
2018-10-03 09:30 | 201 | 177
2018-10-03 10:00 | 202 | 176
2018-10-03 10:30 | 209 | 183
2018-10-03 11:00 | 200 | 172
2018-10-03 11:30 | 214 | 188
2018-10-03 12:00 | 250 | 230
2018-10-03 12:30 | 202 | 180
2018-10-03 13:00 | 190 | 162
2018-10-03 13:30 | 186 | 156
2018-10-03 14:00 | 193 | 164
2018-10-03 14:30 | 222 | 200
2018-10-03 15:00 | 205 | 183
2018-10-03 15:30 | 230 | 208
2018-10-03 16:00 | 283 | 268
2018-10-03 16:30 | 374 | 365
2018-10-03 17:00 | 349 | 343
2018-10-03 17:30 | 294 | 287
2018-10-03 18:00 | 347 | 339
2018-10-03 18:30 | 380 | 375
2018-10-03 19:00 | 389 | 386
2018-10-03 19:30 | 395 | 392
2018-10-03 20:00 | 366 | 362
2018-10-03 20:30 | 339 | 334
2018-10-03 21:00 | 347 | 341
2018-10-03 21:30 | 392 | 387
2018-10-03 22:00 | 380 | 375
2018-10-03 22:30 | 280 | 274
2018-10-03 23:00 | 239 | 226
2018-10-03 23:30 | 233 | 218
2018-10-04 | 368 | 357
2018-10-04 00:30 | 390 | 385
2018-10-04 01:00 | 381 | 377
2018-10-04 01:30 | 374 | 370
2018-10-04 02:00 | 373 | 369
2018-10-04 02:30 | 379 | 374
2018-10-04 03:00 | 377 | 373
2018-10-04 03:30 | 385 | 380
2018-10-04 04:00 | 381 | 377
2018-10-04 04:30 | 385 | 380
2018-10-04 05:00 | 367 | 363
2018-10-04 05:30 | 377 | 372
2018-10-04 06:00 | 387 | 382
2018-10-04 06:30 | 386 | 382
2018-10-04 07:00 | 317 | 311
2018-10-04 07:30 | 270 | 260
2018-10-04 08:00 | 246 | 232
2018-10-04 08:30 | 220 | 201
2018-10-04 09:00 | 213 | 191
2018-10-04 09:30 | 204 | 181
2018-10-04 10:00 | 197 | 169
2018-10-04 10:30 | 200 | 170
2018-10-04 11:00 | 190 | 159
2018-10-04 11:30 | 178 | 144
2018-10-04 12:00 | 185 | 152
2018-10-04 12:30 | 179 | 147
2018-10-04 13:00 | 171 | 137
2018-10-04 13:30 | 155 | 118
2018-10-04 14:00 | 178 | 146
2018-10-04 14:30 | 217 | 194
2018-10-04 15:00 | 232 | 213
2018-10-04 15:30 | 304 | 291
2018-10-04 16:00 | 324 | 314
2018-10-04 16:30 | 323 | 314
2018-10-04 17:00 | 380 | 373
2018-10-04 17:30 | 369 | 364
2018-10-04 18:00 | 384 | 379
2018-10-04 18:30 | 406 | 402
2018-10-04 19:00 | 426 | 424
2018-10-04 19:30 | 408 | 406
2018-10-04 20:00 | 373 | 371
2018-10-04 20:30 | 378 | 375
2018-10-04 21:00 | 365 | 362
2018-10-04 21:30 | 487 | 484
2018-10-04 22:00 | 509 | 508
2018-10-04 22:30 | 479 | 478
2018-10-04 23:00 | 461 | 460
2018-10-04 23:30 | 437 | 436
2018-10-05 | 421 | 419
2018-10-05 00:30 | 445 | 443
2018-10-05 01:00 | 424 | 422
2018-10-05 01:30 | 424 | 422
2018-10-05 02:00 | 420 | 417
2018-10-05 02:30 | 420 | 417
2018-10-05 03:00 | 396 | 393
2018-10-05 03:30 | 394 | 390
2018-10-05 04:00 | 384 | 380
2018-10-05 04:30 | 385 | 381
2018-10-05 05:00 | 397 | 392
2018-10-05 05:30 | 417 | 413
2018-10-05 06:00 | 428 | 425
2018-10-05 06:30 | 421 | 419
2018-10-05 07:00 | 392 | 388
2018-10-05 07:30 | 355 | 350
2018-10-05 08:00 | 319 | 312
2018-10-05 08:30 | 302 | 292
2018-10-05 09:00 | 334 | 324
2018-10-05 09:30 | 329 | 320
2018-10-05 10:00 | 259 | 248
2018-10-05 10:30 | 229 | 211
2018-10-05 11:00 | 216 | 193
2018-10-05 11:30 | 198 | 173
2018-10-05 12:00 | 193 | 166
2018-10-05 12:30 | 147 | 112
2018-10-05 13:00 | 226 | 191
2018-10-05 13:30 | 201 | 171
2018-10-05 14:00 | 193 | 157
2018-10-05 14:30 | 220 | 187
2018-10-05 15:00 | 248 | 223
2018-10-05 15:30 | 263 | 242
2018-10-05 16:00 | 281 | 263
2018-10-05 16:30 | 345 | 335
2018-10-05 17:00 | 396 | 391
2018-10-05 17:30 | 438 | 435
2018-10-05 18:00 | 507 | 506
2018-10-05 18:30 | 542 | 542
2018-10-05 19:00 | 546 | 546
2018-10-05 19:30 | 557 | 557
2018-10-05 20:00 | 550 | 550
2018-10-05 20:30 | 533 | 533
2018-10-05 21:00 | 521 | 521
2018-10-05 21:30 | 569 | 568
2018-10-05 22:00 | 556 | 556
2018-10-05 22:30 | 488 | 487
2018-10-05 23:00 | 490 | 489
2018-10-05 23:30 | 461 | 460
2018-10-06 | 457 | 455
2018-10-06 00:30 | 460 | 457
2018-10-06 01:00 | 443 | 440
2018-10-06 01:30 | 436 | 433
2018-10-06 02:00 | 425 | 422
2018-10-06 02:30 | 419 | 415
2018-10-06 03:00 | 412 | 409
2018-10-06 03:30 | 409 | 405
2018-10-06 04:00 | 412 | 408
2018-10-06 04:30 | 418 | 414
2018-10-06 05:00 | 417 | 413
2018-10-06 05:30 | 427 | 423
2018-10-06 06:00 | 431 | 428
2018-10-06 06:30 | 417 | 413
2018-10-06 07:00 | 394 | 390
2018-10-06 07:30 | 359 | 353
2018-10-06 08:00 | 319 | 310
2018-10-06 08:30 | 298 | 285
2018-10-06 09:00 | 264 | 250
2018-10-06 09:30 | 272 | 256
2018-10-06 10:00 | 241 | 224
2018-10-06 10:30 | 227 | 205
2018-10-06 11:00 | 206 | 183
2018-10-06 11:30 | 184 | 154
2018-10-06 12:00 | 190 | 160
2018-10-06 12:30 | 193 | 153
2018-10-06 13:00 | 191 | 151
2018-10-06 13:30 | 181 | 139
2018-10-06 14:00 | 184 | 144
2018-10-06 14:30 | 204 | 169
2018-10-06 15:00 | 217 | 186
2018-10-06 15:30 | 237 | 216
2018-10-06 16:00 | 278 | 261
2018-10-06 16:30 | 321 | 309
2018-10-06 17:00 | 365 | 357
2018-10-06 17:30 | 404 | 398
2018-10-06 18:00 | 502 | 500
2018-10-06 18:30 | 556 | 555
2018-10-06 19:00 | 576 | 576
2018-10-06 19:30 | 568 | 567
2018-10-06 20:00 | 551 | 551
2018-10-06 20:30 | 538 | 537
2018-10-06 21:00 | 534 | 533
2018-10-06 21:30 | 550 | 549
2018-10-06 22:00 | 528 | 527
2018-10-06 22:30 | 472 | 470
2018-10-06 23:00 | 480 | 477
2018-10-06 23:30 | 471 | 468
2018-10-07 | 464 | 461
2018-10-07 00:30 | 457 | 454
2018-10-07 01:00 | 440 | 437
2018-10-07 01:30 | 431 | 428
2018-10-07 02:00 | 434 | 430
2018-10-07 02:30 | 430 | 427
2018-10-07 03:00 | 438 | 435
2018-10-07 03:30 | 438 | 435
2018-10-07 04:00 | 419 | 416
2018-10-07 04:30 | 405 | 402
2018-10-07 05:00 | 409 | 405
2018-10-07 05:30 | 417 | 413
2018-10-07 06:00 | 416 | 413
2018-10-07 06:30 | 408 | 404
2018-10-07 07:00 | 367 | 362
2018-10-07 07:30 | 306 | 299
2018-10-07 08:00 | 322 | 312
2018-10-07 08:30 | 309 | 297
2018-10-07 09:00 | 291 | 279
2018-10-07 09:30 | 233 | 217
2018-10-07 10:00 | 215 | 191
2018-10-07 10:30 | 231 | 209
2018-10-07 11:00 | 210 | 186
2018-10-07 11:30 | 186 | 155
2018-10-07 12:00 | 155 | 113
2018-10-07 12:30 | 157 | 116
2018-10-07 13:00 | 157 | 116
2018-10-07 13:30 | 157 | 116
2018-10-07 14:00 | 174 | 138
2018-10-07 14:30 | 185 | 153
2018-10-07 15:00 | 202 | 175
2018-10-07 15:30 | 223 | 199
2018-10-07 16:00 | 253 | 233
2018-10-07 16:30 | 301 | 285
2018-10-07 17:00 | 356 | 346
2018-10-07 17:30 | 393 | 386
2018-10-07 18:00 | 472 | 468
2018-10-07 18:30 | 511 | 510
2018-10-07 19:00 | 522 | 521
2018-10-07 19:30 | 533 | 533
2018-10-07 20:00 | 553 | 552
2018-10-07 20:30 | 538 | 537
2018-10-07 21:00 | 524 | 524
2018-10-07 21:30 | 537 | 536
2018-10-07 22:00 | 517 | 516
2018-10-07 22:30 | 487 | 485
2018-10-07 23:00 | 457 | 455
2018-10-07 23:30 | 442 | 439
2018-10-08 | 428 | 424
2018-10-08 00:30 | 430 | 426
2018-10-08 01:00 | 416 | 411
2018-10-08 01:30 | 409 | 404
2018-10-08 02:00 | 404 | 400
2018-10-08 02:30 | 399 | 394
2018-10-08 03:00 | 401 | 396
2018-10-08 03:30 | 412 | 407
2018-10-08 04:00 | 399 | 395
2018-10-08 04:30 | 397 | 392
2018-10-08 05:00 | 413 | 408
2018-10-08 05:30 | 423 | 418
2018-10-08 06:00 | 440 | 436
2018-10-08 06:30 | 453 | 449
2018-10-08 07:00 | 418 | 414
2018-10-08 07:30 | 378 | 372
2018-10-08 08:00 | 346 | 338
2018-10-08 08:30 | 321 | 313
2018-10-08 09:00 | 307 | 297
2018-10-08 09:30 | 285 | 272
2018-10-08 10:00 | 262 | 242
2018-10-08 10:30 | 252 | 226
2018-10-08 11:00 | 235 | 207
2018-10-08 11:30 | 216 | 182
2018-10-08 12:00 | 181 | 136
2018-10-08 12:30 | 179 | 132
2018-10-08 13:00 | 170 | 119
2018-10-08 13:30 | 161 | 106
2018-10-08 14:00 | 170 | 118
2018-10-08 14:30 | 189 | 144
2018-10-08 15:00 | 195 | 154
2018-10-08 15:30 | 176 | 145
2018-10-08 16:00 | 177 | 147
2018-10-08 16:30 | 169 | 138
2018-10-08 17:00 | 220 | 197
2018-10-08 17:30 | 232 | 213
2018-10-08 18:00 | 320 | 308
2018-10-08 18:30 | 366 | 360
2018-10-08 19:00 | 391 | 388
2018-10-08 19:30 | 423 | 421
2018-10-08 20:00 | 401 | 400
2018-10-08 20:30 | 426 | 424
2018-10-08 21:00 | 406 | 405
2018-10-08 21:30 | 413 | 411
2018-10-08 22:00 | 382 | 380
2018-10-08 22:30 | 353 | 350
2018-10-08 23:00 | 336 | 331
2018-10-08 23:30 | 310 | 304
2018-10-09 | 297 | 289
2018-10-09 00:30 | 297 | 288
2018-10-09 01:00 | 286 | 276
2018-10-09 01:30 | 300 | 290
2018-10-09 02:00 | 303 | 293
2018-10-09 02:30 | 296 | 286
2018-10-09 03:00 | 285 | 275
2018-10-09 03:30 | 287 | 276
2018-10-09 04:00 | 287 | 276
2018-10-09 04:30 | 285 | 273
2018-10-09 05:00 | 291 | 280
2018-10-09 05:30 | 308 | 298
2018-10-09 06:00 | 313 | 303
2018-10-09 06:30 | 309 | 299
2018-10-09 07:00 | 219 | 205
2018-10-09 07:30 | 239 | 220
2018-10-09 08:00 | 234 | 214
2018-10-09 08:30 | 223 | 202
2018-10-09 09:00 | 178 | 143
2018-10-09 09:30 | 139 | 67
2018-10-09 10:00 | 181 | 129
2018-10-09 10:30 | 193 | 132
2018-10-09 11:00 | 190 | 129
2018-10-09 11:30 | 190 | 120
2018-10-09 12:00 | 194 | 133
2018-10-09 12:30 | 181 | 116
2018-10-09 13:00 | 187 | 116
2018-10-09 13:30 | 165 | 94
2018-10-09 14:00 | 150 | 93
2018-10-09 14:30 | 162 | 121
2018-10-09 15:00 | 165 | 127
2018-10-09 15:30 | 192 | 163
2018-10-09 16:00 | 227 | 201
2018-10-09 16:30 | 313 | 298
2018-10-09 17:00 | 326 | 317
2018-10-09 17:30 | 376 | 369
2018-10-09 18:00 | 400 | 395
2018-10-09 18:30 | 358 | 354
2018-10-09 19:00 | 410 | 405
2018-10-09 19:30 | 419 | 416
2018-10-09 20:00 | 450 | 447
2018-10-09 20:30 | 414 | 412
2018-10-09 21:00 | 403 | 400
2018-10-09 21:30 | 425 | 421
2018-10-09 22:00 | 405 | 402
2018-10-09 22:30 | 375 | 371
2018-10-09 23:00 | 350 | 344
2018-10-09 23:30 | 324 | 317
2018-10-10 | 318 | 309
2018-10-10 00:30 | 320 | 310
2018-10-10 01:00 | 296 | 285
2018-10-10 01:30 | 286 | 274
2018-10-10 02:00 | 283 | 270
2018-10-10 02:30 | 293 | 279
2018-10-10 03:00 | 283 | 270
2018-10-10 03:30 | 277 | 263
2018-10-10 04:00 | 283 | 269
2018-10-10 04:30 | 297 | 284
2018-10-10 05:00 | 298 | 286
2018-10-10 05:30 | 327 | 316
2018-10-10 06:00 | 338 | 329
2018-10-10 06:30 | 344 | 335
2018-10-10 07:00 | 257 | 246
2018-10-10 07:30 | 196 | 175
2018-10-10 08:00 | 165 | 131
2018-10-10 08:30 | 149 | 103
2018-10-10 09:00 | 140 | 84
2018-10-10 09:30 | 128 | 57
2018-10-10 10:00 | 118 | 24
2018-10-10 10:30 | 124 | 34
2018-10-10 11:00 | 122 | 36
2018-10-10 11:30 | 116 | 14
2018-10-10 12:00 | 118 | 11
2018-10-10 12:30 | 116 | 5
2018-10-10 13:00 | 115 | 10
2018-10-10 13:30 | 111 | 17
2018-10-10 14:00 | 110 | 19
2018-10-10 14:30 | 113 | 35
2018-10-10 15:00 | 115 | 49
2018-10-10 15:30 | 128 | 76
2018-10-10 16:00 | 199 | 171
2018-10-10 16:30 | 255 | 239
2018-10-10 17:00 | 318 | 309
2018-10-10 17:30 | 385 | 380
2018-10-10 18:00 | 390 | 387
2018-10-10 18:30 | 413 | 411
2018-10-10 19:00 | 409 | 407
2018-10-10 19:30 | 442 | 440
2018-10-10 20:00 | 431 | 429
2018-10-10 20:30 | 403 | 401
2018-10-10 21:00 | 423 | 420
2018-10-10 21:30 | 428 | 426
2018-10-10 22:00 | 404 | 402
2018-10-10 22:30 | 428 | 425
2018-10-10 23:00 | 483 | 481
2018-10-10 23:30 | 472 | 471
2018-10-11 | 449 | 447
2018-10-11 00:30 | 441 | 439
2018-10-11 01:00 | 439 | 437
2018-10-11 01:30 | 446 | 443
2018-10-11 02:00 | 444 | 442
2018-10-11 02:30 | 447 | 445
2018-10-11 03:00 | 442 | 439
2018-10-11 03:30 | 442 | 440
2018-10-11 04:00 | 448 | 445
2018-10-11 04:30 | 457 | 454
2018-10-11 05:00 | 460 | 458
2018-10-11 05:30 | 467 | 464
2018-10-11 06:00 | 469 | 467
2018-10-11 06:30 | 447 | 445
2018-10-11 07:00 | 387 | 385
2018-10-11 07:30 | 402 | 398
2018-10-11 08:00 | 393 | 389
2018-10-11 08:30 | 386 | 381
2018-10-11 09:00 | 329 | 323
2018-10-11 09:30 | 280 | 271
2018-10-11 10:00 | 245 | 232
2018-10-11 10:30 | 236 | 219
2018-10-11 11:00 | 228 | 210
2018-10-11 11:30 | 230 | 212
2018-10-11 12:00 | 233 | 215
2018-10-11 12:30 | 241 | 224
2018-10-11 13:00 | 230 | 213
2018-10-11 13:30 | 242 | 225
2018-10-11 14:00 | 256 | 241
2018-10-11 14:30 | 262 | 248
2018-10-11 15:00 | 264 | 251
2018-10-11 15:30 | 291 | 280
2018-10-11 16:00 | 356 | 348
2018-10-11 16:30 | 392 | 387
2018-10-11 17:00 | 401 | 398
2018-10-11 17:30 | 457 | 454
2018-10-11 18:00 | 537 | 536
2018-10-11 18:30 | 595 | 595
2018-10-11 19:00 | 617 | 617
2018-10-11 19:30 | 640 | 640
2018-10-11 20:00 | 616 | 616
2018-10-11 20:30 | 591 | 591
2018-10-11 21:00 | 577 | 576
2018-10-11 21:30 | 590 | 590
2018-10-11 22:00 | 577 | 577
2018-10-11 22:30 | 556 | 555
2018-10-11 23:00 | 525 | 525
2018-10-11 23:30 | 506 | 504
2018-10-12 | 479 | 477
2018-10-12 00:30 | 478 | 476
2018-10-12 01:00 | 461 | 459
2018-10-12 01:30 | 464 | 462
2018-10-12 02:00 | 455 | 453
2018-10-12 02:30 | 449 | 447
2018-10-12 03:00 | 438 | 436
2018-10-12 03:30 | 437 | 435
2018-10-12 04:00 | 421 | 419
2018-10-12 04:30 | 441 | 438
2018-10-12 05:00 | 447 | 444
2018-10-12 05:30 | 460 | 458
2018-10-12 06:00 | 465 | 463
2018-10-12 06:30 | 472 | 471
2018-10-12 07:00 | 448 | 446
2018-10-12 07:30 | 414 | 412
2018-10-12 08:00 | 387 | 383
2018-10-12 08:30 | 376 | 370
2018-10-12 09:00 | 340 | 333
2018-10-12 09:30 | 302 | 293
2018-10-12 10:00 | 269 | 257
2018-10-12 10:30 | 274 | 260
2018-10-12 11:00 | 291 | 278
2018-10-12 11:30 | 276 | 263
2018-10-12 12:00 | 260 | 245
2018-10-12 12:30 | 250 | 234
2018-10-12 13:00 | 273 | 258
2018-10-12 13:30 | 271 | 258
2018-10-12 14:00 | 246 | 231
2018-10-12 14:30 | 286 | 271
2018-10-12 15:00 | 283 | 270
2018-10-12 15:30 | 321 | 310
2018-10-12 16:00 | 340 | 330
2018-10-12 16:30 | 397 | 390
2018-10-12 17:00 | 406 | 401
2018-10-12 17:30 | 483 | 479
2018-10-12 18:00 | 503 | 502
2018-10-12 18:30 | 530 | 529
2018-10-12 19:00 | 547 | 546
2018-10-12 19:30 | 556 | 556
2018-10-12 20:00 | 550 | 549
2018-10-12 20:30 | 552 | 551
2018-10-12 21:00 | 519 | 518
2018-10-12 21:30 | 496 | 495
2018-10-12 22:00 | 513 | 512
2018-10-12 22:30 | 461 | 460
2018-10-12 23:00 | 448 | 446
2018-10-12 23:30 | 449 | 447
2018-10-13 | 490 | 488
2018-10-13 00:30 | 498 | 496
2018-10-13 01:00 | 464 | 463
2018-10-13 01:30 | 472 | 470
2018-10-13 02:00 | 470 | 469
2018-10-13 02:30 | 447 | 445
2018-10-13 03:00 | 440 | 438
2018-10-13 03:30 | 439 | 437
2018-10-13 04:00 | 440 | 437
2018-10-13 04:30 | 445 | 443
2018-10-13 05:00 | 456 | 453
2018-10-13 05:30 | 469 | 467
2018-10-13 06:00 | 469 | 467
2018-10-13 06:30 | 470 | 469
2018-10-13 07:00 | 459 | 458
2018-10-13 07:30 | 457 | 454
2018-10-13 08:00 | 400 | 397
2018-10-13 08:30 | 346 | 341
2018-10-13 09:00 | 360 | 353
2018-10-13 09:30 | 394 | 389
2018-10-13 10:00 | 428 | 424
2018-10-13 10:30 | 388 | 384
2018-10-13 11:00 | 365 | 359
2018-10-13 11:30 | 369 | 362
2018-10-13 12:00 | 371 | 365
2018-10-13 12:30 | 378 | 373
2018-10-13 13:00 | 329 | 322
2018-10-13 13:30 | 373 | 366
2018-10-13 14:00 | 375 | 369
2018-10-13 14:30 | 365 | 359
2018-10-13 15:00 | 407 | 401
2018-10-13 15:30 | 434 | 430
2018-10-13 16:00 | 481 | 477
2018-10-13 16:30 | 478 | 476
2018-10-13 17:00 | 476 | 474
2018-10-13 17:30 | 462 | 460
2018-10-13 18:00 | 495 | 494
2018-10-13 18:30 | 532 | 530
2018-10-13 19:00 | 533 | 532
2018-10-13 19:30 | 537 | 536
2018-10-13 20:00 | 516 | 515
2018-10-13 20:30 | 528 | 527
2018-10-13 21:00 | 513 | 512
2018-10-13 21:30 | 504 | 503
2018-10-13 22:00 | 476 | 475
2018-10-13 22:30 | 463 | 461
2018-10-13 23:00 | 455 | 453
2018-10-13 23:30 | 449 | 447
2018-10-14 | 435 | 432
2018-10-14 00:30 | 433 | 431
2018-10-14 01:00 | 425 | 422
2018-10-14 01:30 | 424 | 421
2018-10-14 02:00 | 417 | 414
2018-10-14 02:30 | 415 | 412
2018-10-14 03:00 | 420 | 416
2018-10-14 03:30 | 423 | 420
2018-10-14 04:00 | 413 | 410
2018-10-14 04:30 | 416 | 413
2018-10-14 05:00 | 427 | 424
2018-10-14 05:30 | 428 | 425
2018-10-14 06:00 | 409 | 405
2018-10-14 06:30 | 405 | 401
2018-10-14 07:00 | 386 | 382
2018-10-14 07:30 | 371 | 365
2018-10-14 08:00 | 386 | 380
2018-10-14 08:30 | 348 | 341
2018-10-14 09:00 | 302 | 294
2018-10-14 09:30 | 268 | 256
2018-10-14 10:00 | 271 | 257
2018-10-14 10:30 | 252 | 235
2018-10-14 11:00 | 222 | 201
2018-10-14 11:30 | 226 | 204
2018-10-14 12:00 | 224 | 201
2018-10-14 12:30 | 217 | 192
2018-10-14 13:00 | 217 | 192
2018-10-14 13:30 | 186 | 157
2018-10-14 14:00 | 174 | 139
2018-10-14 14:30 | 196 | 165
2018-10-14 15:00 | 243 | 221
2018-10-14 15:30 | 274 | 257
2018-10-14 16:00 | 308 | 296
2018-10-14 16:30 | 326 | 316
2018-10-14 17:00 | 349 | 341
2018-10-14 17:30 | 404 | 399
2018-10-14 18:00 | 462 | 459
2018-10-14 18:30 | 526 | 525
2018-10-14 19:00 | 557 | 556
2018-10-14 19:30 | 585 | 584
2018-10-14 20:00 | 568 | 568
2018-10-14 20:30 | 541 | 541
2018-10-14 21:00 | 537 | 536
2018-10-14 21:30 | 536 | 535
2018-10-14 22:00 | 517 | 516
2018-10-14 22:30 | 497 | 495
2018-10-14 23:00 | 472 | 470
2018-10-14 23:30 | 445 | 443
2018-10-15 | 432 | 430
2018-10-15 00:30 | 433 | 430
2018-10-15 01:00 | 410 | 407
2018-10-15 01:30 | 398 | 394
2018-10-15 02:00 | 388 | 383
2018-10-15 02:30 | 392 | 388
2018-10-15 03:00 | 386 | 382
2018-10-15 03:30 | 391 | 387
2018-10-15 04:00 | 395 | 391
2018-10-15 04:30 | 409 | 405
2018-10-15 05:00 | 424 | 420
2018-10-15 05:30 | 428 | 426
2018-10-15 06:00 | 438 | 436
2018-10-15 06:30 | 458 | 456
2018-10-15 07:00 | 431 | 428
2018-10-15 07:30 | 455 | 452
2018-10-15 08:00 | 441 | 439
2018-10-15 08:30 | 428 | 425
2018-10-15 09:00 | 407 | 403
2018-10-15 09:30 | 388 | 384
2018-10-15 10:00 | 371 | 366
2018-10-15 10:30 | 356 | 350
2018-10-15 11:00 | 324 | 317
2018-10-15 11:30 | 310 | 301
2018-10-15 12:00 | 290 | 280
2018-10-15 12:30 | 284 | 273
2018-10-15 13:00 | 272 | 260
2018-10-15 13:30 | 279 | 267
2018-10-15 14:00 | 302 | 292
2018-10-15 14:30 | 309 | 300
2018-10-15 15:00 | 333 | 325
2018-10-15 15:30 | 355 | 348
2018-10-15 16:00 | 410 | 405
2018-10-15 16:30 | 432 | 429
2018-10-15 17:00 | 450 | 447
2018-10-15 17:30 | 506 | 504
2018-10-15 18:00 | 561 | 560
2018-10-15 18:30 | 582 | 581
2018-10-15 19:00 | 609 | 609
2018-10-15 19:30 | 625 | 625
2018-10-15 20:00 | 600 | 600
2018-10-15 20:30 | 587 | 587
2018-10-15 21:00 | 581 | 581
2018-10-15 21:30 | 560 | 560
2018-10-15 22:00 | 529 | 528
2018-10-15 22:30 | 508 | 507
2018-10-15 23:00 | 479 | 478
2018-10-15 23:30 | 476 | 474
2018-10-16 | 452 | 449
2018-10-16 00:30 | 446 | 443
2018-10-16 01:00 | 440 | 436
2018-10-16 01:30 | 439 | 436
2018-10-16 02:00 | 438 | 435
2018-10-16 02:30 | 430 | 427
2018-10-16 03:00 | 425 | 421
2018-10-16 03:30 | 429 | 425
2018-10-16 04:00 | 431 | 427
2018-10-16 04:30 | 431 | 427
2018-10-16 05:00 | 439 | 435
2018-10-16 05:30 | 447 | 444
2018-10-16 06:00 | 463 | 460
2018-10-16 06:30 | 471 | 469
2018-10-16 07:00 | 462 | 459
2018-10-16 07:30 | 449 | 446
2018-10-16 08:00 | 458 | 455
2018-10-16 08:30 | 423 | 420
2018-10-16 09:00 | 370 | 366
2018-10-16 09:30 | 347 | 341
2018-10-16 10:00 | 276 | 268
2018-10-16 10:30 | 282 | 271
2018-10-16 11:00 | 276 | 265
2018-10-16 11:30 | 275 | 262
2018-10-16 12:00 | 272 | 258
2018-10-16 12:30 | 300 | 286
2018-10-16 13:00 | 296 | 283
2018-10-16 13:30 | 294 | 282
2018-10-16 14:00 | 298 | 286
2018-10-16 14:30 | 330 | 320
2018-10-16 15:00 | 378 | 371
2018-10-16 15:30 | 469 | 465
2018-10-16 16:00 | 452 | 450
2018-10-16 16:30 | 535 | 533
2018-10-16 17:00 | 578 | 578
2018-10-16 17:30 | 569 | 569
2018-10-16 18:00 | 585 | 585
2018-10-16 18:30 | 601 | 601
2018-10-16 19:00 | 638 | 638
2018-10-16 19:30 | 674 | 674
2018-10-16 20:00 | 662 | 662
2018-10-16 20:30 | 631 | 631
2018-10-16 21:00 | 596 | 596
2018-10-16 21:30 | 606 | 605
2018-10-16 22:00 | 576 | 575
2018-10-16 22:30 | 546 | 546
2018-10-16 23:00 | 522 | 522
2018-10-16 23:30 | 503 | 502
2018-10-17 | 491 | 489
2018-10-17 00:30 | 477 | 475
2018-10-17 01:00 | 477 | 475
2018-10-17 01:30 | 470 | 467
2018-10-17 02:00 | 457 | 454
2018-10-17 02:30 | 450 | 447
2018-10-17 03:00 | 449 | 446
2018-10-17 03:30 | 446 | 444
2018-10-17 04:00 | 439 | 437
2018-10-17 04:30 | 448 | 445
2018-10-17 05:00 | 446 | 444
2018-10-17 05:30 | 467 | 464
2018-10-17 06:00 | 473 | 471
2018-10-17 06:30 | 466 | 465
2018-10-17 07:00 | 460 | 458
2018-10-17 07:30 | 489 | 487
2018-10-17 08:00 | 460 | 459
2018-10-17 08:30 | 373 | 370
2018-10-17 09:00 | 300 | 293
2018-10-17 09:30 | 261 | 249
2018-10-17 10:00 | 286 | 275
2018-10-17 10:30 | 244 | 233
2018-10-17 11:00 | 261 | 248
2018-10-17 11:30 | 273 | 262
2018-10-17 12:00 | 261 | 250
2018-10-17 12:30 | 282 | 271
2018-10-17 13:00 | 277 | 268
2018-10-17 13:30 | 284 | 275
2018-10-17 14:00 | 277 | 268
2018-10-17 14:30 | 289 | 281
2018-10-17 15:00 | 307 | 300
2018-10-17 15:30 | 337 | 332
2018-10-17 16:00 | 335 | 331
2018-10-17 16:30 | 395 | 391
2018-10-17 17:00 | 440 | 437
2018-10-17 17:30 | 488 | 486
2018-10-17 18:00 | 543 | 542
2018-10-17 18:30 | 585 | 584
2018-10-17 19:00 | 594 | 593
2018-10-17 19:30 | 645 | 645
2018-10-17 20:00 | 637 | 637
2018-10-17 20:30 | 611 | 611
2018-10-17 21:00 | 597 | 597
2018-10-17 21:30 | 574 | 574
2018-10-17 22:00 | 560 | 560
2018-10-17 22:30 | 526 | 525
2018-10-17 23:00 | 475 | 475
2018-10-17 23:30 | 461 | 460
2018-10-18 | 449 | 447
2018-10-18 00:30 | 432 | 430
2018-10-18 01:00 | 420 | 418
2018-10-18 01:30 | 422 | 421
2018-10-18 02:00 | 433 | 432
2018-10-18 02:30 | 434 | 433
2018-10-18 03:00 | 420 | 419
2018-10-18 03:30 | 424 | 423
2018-10-18 04:00 | 427 | 425
2018-10-18 04:30 | 422 | 420
2018-10-18 05:00 | 415 | 413
2018-10-18 05:30 | 396 | 394
2018-10-18 06:00 | 374 | 373
2018-10-18 06:30 | 376 | 374
2018-10-18 07:00 | 392 | 390
2018-10-18 07:30 | 377 | 376
2018-10-18 08:00 | 365 | 363
2018-10-18 08:30 | 358 | 355
2018-10-18 09:00 | 334 | 331
2018-10-18 09:30 | 322 | 318
2018-10-18 10:00 | 282 | 273
2018-10-18 10:30 | 283 | 273
2018-10-18 11:00 | 234 | 220
2018-10-18 11:30 | 203 | 181
2018-10-18 12:00 | 260 | 241
2018-10-18 12:30 | 249 | 233
2018-10-18 13:00 | 244 | 225
2018-10-18 13:30 | 212 | 194
2018-10-18 14:00 | 202 | 181
2018-10-18 14:30 | 244 | 225
2018-10-18 15:00 | 248 | 234
2018-10-18 15:30 | 281 | 269
2018-10-18 16:00 | 351 | 342
2018-10-18 16:30 | 403 | 398
2018-10-18 17:00 | 444 | 442
2018-10-18 17:30 | 468 | 466
2018-10-18 18:00 | 491 | 490
2018-10-18 18:30 | 532 | 532
2018-10-18 19:00 | 556 | 555
2018-10-18 19:30 | 585 | 584
2018-10-18 20:00 | 578 | 578
2018-10-18 20:30 | 578 | 578
2018-10-18 21:00 | 601 | 601
2018-10-18 21:30 | 577 | 577
2018-10-18 22:00 | 558 | 557
2018-10-18 22:30 | 517 | 516
2018-10-18 23:00 | 477 | 475
2018-10-18 23:30 | 444 | 442
2018-10-19 | 438 | 434
2018-10-19 00:30 | 418 | 414
2018-10-19 01:00 | 424 | 420
2018-10-19 01:30 | 443 | 439
2018-10-19 02:00 | 441 | 437
2018-10-19 02:30 | 428 | 424
2018-10-19 03:00 | 422 | 418
2018-10-19 03:30 | 418 | 414
2018-10-19 04:00 | 416 | 411
2018-10-19 04:30 | 415 | 410
2018-10-19 05:00 | 415 | 410
2018-10-19 05:30 | 408 | 403
2018-10-19 06:00 | 396 | 391
2018-10-19 06:30 | 377 | 371
2018-10-19 07:00 | 366 | 358
2018-10-19 07:30 | 321 | 311
2018-10-19 08:00 | 341 | 330
2018-10-19 08:30 | 300 | 289
2018-10-19 09:00 | 312 | 300
2018-10-19 09:30 | 310 | 298
2018-10-19 10:00 | 276 | 263
2018-10-19 10:30 | 292 | 277
2018-10-19 11:00 | 298 | 285
2018-10-19 11:30 | 293 | 281
2018-10-19 12:00 | 284 | 273
2018-10-19 12:30 | 269 | 255
2018-10-19 13:00 | 256 | 240
2018-10-19 13:30 | 258 | 241
2018-10-19 14:00 | 270 | 256
2018-10-19 14:30 | 271 | 258
2018-10-19 15:00 | 277 | 264
2018-10-19 15:30 | 301 | 290
2018-10-19 16:00 | 323 | 314
2018-10-19 16:30 | 360 | 353
2018-10-19 17:00 | 388 | 381
2018-10-19 17:30 | 406 | 401
2018-10-19 18:00 | 426 | 422
2018-10-19 18:30 | 440 | 438
2018-10-19 19:00 | 477 | 476
2018-10-19 19:30 | 512 | 511
2018-10-19 20:00 | 503 | 503
2018-10-19 20:30 | 488 | 487
2018-10-19 21:00 | 480 | 479
2018-10-19 21:30 | 483 | 481
2018-10-19 22:00 | 447 | 445
2018-10-19 22:30 | 421 | 419
2018-10-19 23:00 | 411 | 408
2018-10-19 23:30 | 407 | 404
2018-10-20 | 392 | 388
2018-10-20 00:30 | 395 | 391
2018-10-20 01:00 | 369 | 364
2018-10-20 01:30 | 368 | 362
2018-10-20 02:00 | 362 | 356
2018-10-20 02:30 | 364 | 357
2018-10-20 03:00 | 348 | 341
2018-10-20 03:30 | 352 | 345
2018-10-20 04:00 | 351 | 344
2018-10-20 04:30 | 364 | 356
2018-10-20 05:00 | 374 | 367
2018-10-20 05:30 | 371 | 364
2018-10-20 06:00 | 353 | 346
2018-10-20 06:30 | 326 | 317
2018-10-20 07:00 | 298 | 286
2018-10-20 07:30 | 267 | 252
2018-10-20 08:00 | 259 | 242
2018-10-20 08:30 | 253 | 235
2018-10-20 09:00 | 264 | 245
2018-10-20 09:30 | 287 | 271
2018-10-20 10:00 | 258 | 241
2018-10-20 10:30 | 236 | 216
2018-10-20 11:00 | 237 | 216
2018-10-20 11:30 | 222 | 199
2018-10-20 12:00 | 231 | 207
2018-10-20 12:30 | 228 | 203
2018-10-20 13:00 | 210 | 184
2018-10-20 13:30 | 218 | 191
2018-10-20 14:00 | 249 | 226
2018-10-20 14:30 | 240 | 219
2018-10-20 15:00 | 232 | 210
2018-10-20 15:30 | 265 | 245
2018-10-20 16:00 | 310 | 295
2018-10-20 16:30 | 343 | 332
2018-10-20 17:00 | 343 | 334
2018-10-20 17:30 | 426 | 420
2018-10-20 18:00 | 526 | 523
2018-10-20 18:30 | 551 | 550
2018-10-20 19:00 | 574 | 573
2018-10-20 19:30 | 589 | 588
2018-10-20 20:00 | 589 | 589
2018-10-20 20:30 | 571 | 571
2018-10-20 21:00 | 544 | 543
2018-10-20 21:30 | 524 | 524
2018-10-20 22:00 | 497 | 496
2018-10-20 22:30 | 481 | 479
2018-10-20 23:00 | 450 | 448
2018-10-20 23:30 | 432 | 429
2018-10-21 | 426 | 422
2018-10-21 00:30 | 414 | 411
2018-10-21 01:00 | 396 | 392
2018-10-21 01:30 | 377 | 373
2018-10-21 02:00 | 407 | 402
2018-10-21 02:30 | 401 | 397
2018-10-21 03:00 | 406 | 402
2018-10-21 03:30 | 400 | 395
2018-10-21 04:00 | 386 | 382
2018-10-21 04:30 | 406 | 402
2018-10-21 05:00 | 426 | 422
2018-10-21 05:30 | 413 | 410
2018-10-21 06:00 | 389 | 385
2018-10-21 06:30 | 376 | 371
2018-10-21 07:00 | 326 | 319
2018-10-21 07:30 | 292 | 282
2018-10-21 08:00 | 280 | 269
2018-10-21 08:30 | 292 | 280
2018-10-21 09:00 | 287 | 275
2018-10-21 09:30 | 293 | 281
2018-10-21 10:00 | 265 | 250
2018-10-21 10:30 | 272 | 255
2018-10-21 11:00 | 237 | 218
2018-10-21 11:30 | 228 | 205
2018-10-21 12:00 | 223 | 199
2018-10-21 12:30 | 224 | 200
2018-10-21 13:00 | 225 | 201
2018-10-21 13:30 | 223 | 199
2018-10-21 14:00 | 226 | 202
2018-10-21 14:30 | 241 | 219
2018-10-21 15:00 | 255 | 237
2018-10-21 15:30 | 279 | 263
2018-10-21 16:00 | 294 | 280
2018-10-21 16:30 | 355 | 345
2018-10-21 17:00 | 413 | 407
2018-10-21 17:30 | 489 | 486
2018-10-21 18:00 | 546 | 544
2018-10-21 18:30 | 619 | 619
2018-10-21 19:00 | 647 | 647
2018-10-21 19:30 | 636 | 636
2018-10-21 20:00 | 604 | 604
2018-10-21 20:30 | 590 | 590
2018-10-21 21:00 | 592 | 591
2018-10-21 21:30 | 578 | 577
2018-10-21 22:00 | 558 | 557
2018-10-21 22:30 | 529 | 528
2018-10-21 23:00 | 510 | 508
2018-10-21 23:30 | 499 | 497
2018-10-22 | 495 | 493
2018-10-22 00:30 | 490 | 488
2018-10-22 01:00 | 467 | 465
2018-10-22 01:30 | 444 | 442
2018-10-22 02:00 | 452 | 451
2018-10-22 02:30 | 445 | 443
2018-10-22 03:00 | 454 | 452
2018-10-22 03:30 | 461 | 460
2018-10-22 04:00 | 459 | 457
2018-10-22 04:30 | 467 | 465
2018-10-22 05:00 | 474 | 472
2018-10-22 05:30 | 474 | 472
2018-10-22 06:00 | 488 | 486
2018-10-22 06:30 | 501 | 500
2018-10-22 07:00 | 488 | 487
2018-10-22 07:30 | 464 | 462
2018-10-22 08:00 | 410 | 408
2018-10-22 08:30 | 368 | 363
2018-10-22 09:00 | 373 | 367
2018-10-22 09:30 | 308 | 301
2018-10-22 10:00 | 294 | 284
2018-10-22 10:30 | 291 | 280
2018-10-22 11:00 | 287 | 275
2018-10-22 11:30 | 284 | 272
2018-10-22 12:00 | 289 | 278
2018-10-22 12:30 | 294 | 282
2018-10-22 13:00 | 322 | 312
2018-10-22 13:30 | 302 | 293
2018-10-22 14:00 | 335 | 326
2018-10-22 14:30 | 348 | 340
2018-10-22 15:00 | 343 | 337
2018-10-22 15:30 | 354 | 347
2018-10-22 16:00 | 395 | 390
2018-10-22 16:30 | 445 | 442
2018-10-22 17:00 | 486 | 484
2018-10-22 17:30 | 552 | 550
2018-10-22 18:00 | 627 | 627
2018-10-22 18:30 | 629 | 629
2018-10-22 19:00 | 621 | 620
2018-10-22 19:30 | 650 | 650
2018-10-22 20:00 | 670 | 670
2018-10-22 20:30 | 650 | 650
2018-10-22 21:00 | 634 | 634
2018-10-22 21:30 | 629 | 628
2018-10-22 22:00 | 604 | 604
2018-10-22 22:30 | 564 | 564
2018-10-22 23:00 | 531 | 531
2018-10-22 23:30 | 511 | 510
2018-10-23 | 491 | 489
2018-10-23 00:30 | 476 | 473
2018-10-23 01:00 | 459 | 456
2018-10-23 01:30 | 441 | 437
2018-10-23 02:00 | 431 | 427
2018-10-23 02:30 | 439 | 435
2018-10-23 03:00 | 442 | 438
2018-10-23 03:30 | 455 | 451
2018-10-23 04:00 | 450 | 446
2018-10-23 04:30 | 458 | 455
2018-10-23 05:00 | 460 | 456
2018-10-23 05:30 | 477 | 474
2018-10-23 06:00 | 488 | 486
2018-10-23 06:30 | 476 | 473
2018-10-23 07:00 | 391 | 388
2018-10-23 07:30 | 325 | 318
2018-10-23 08:00 | 376 | 366
2018-10-23 08:30 | 376 | 368
2018-10-23 09:00 | 349 | 336
2018-10-23 09:30 | 342 | 331
2018-10-23 10:00 | 335 | 324
2018-10-23 10:30 | 319 | 307
2018-10-23 11:00 | 326 | 313
2018-10-23 11:30 | 298 | 285
2018-10-23 12:00 | 248 | 231
2018-10-23 12:30 | 255 | 238
2018-10-23 13:00 | 239 | 221
2018-10-23 13:30 | 209 | 188
2018-10-23 14:00 | 240 | 220
2018-10-23 14:30 | 264 | 247
2018-10-23 15:00 | 288 | 275
2018-10-23 15:30 | 284 | 274
2018-10-23 16:00 | 281 | 271
2018-10-23 16:30 | 362 | 354
2018-10-23 17:00 | 328 | 323
2018-10-23 17:30 | 405 | 399
2018-10-23 18:00 | 466 | 463
2018-10-23 18:30 | 488 | 485
2018-10-23 19:00 | 423 | 421
2018-10-23 19:30 | 454 | 452
2018-10-23 20:00 | 493 | 491
2018-10-23 20:30 | 487 | 486
2018-10-23 21:00 | 466 | 464
2018-10-23 21:30 | 461 | 458
2018-10-23 22:00 | 442 | 440
2018-10-23 22:30 | 398 | 395
2018-10-23 23:00 | 364 | 359
2018-10-23 23:30 | 347 | 340
2018-10-24 | 344 | 335
2018-10-24 00:30 | 346 | 337
2018-10-24 01:00 | 331 | 322
2018-10-24 01:30 | 312 | 301
2018-10-24 02:00 | 303 | 291
2018-10-24 02:30 | 306 | 293
2018-10-24 03:00 | 315 | 303
2018-10-24 03:30 | 310 | 298
2018-10-24 04:00 | 306 | 294
2018-10-24 04:30 | 288 | 275
2018-10-24 05:00 | 316 | 303
2018-10-24 05:30 | 339 | 328
2018-10-24 06:00 | 314 | 304
2018-10-24 06:30 | 257 | 243
2018-10-24 07:00 | 222 | 201
2018-10-24 07:30 | 201 | 171
2018-10-24 08:00 | 198 | 159
2018-10-24 08:30 | 210 | 175
2018-10-24 09:00 | 188 | 151
2018-10-24 09:30 | 225 | 192
2018-10-24 10:00 | 204 | 173
2018-10-24 10:30 | 189 | 151
2018-10-24 11:00 | 188 | 146
2018-10-24 11:30 | 191 | 150
2018-10-24 12:00 | 197 | 157
2018-10-24 12:30 | 195 | 156
2018-10-24 13:00 | 196 | 163
2018-10-24 13:30 | 214 | 187
2018-10-24 14:00 | 220 | 196
2018-10-24 14:30 | 234 | 214
2018-10-24 15:00 | 244 | 226
2018-10-24 15:30 | 224 | 206
2018-10-24 16:00 | 258 | 242
2018-10-24 16:30 | 325 | 313
2018-10-24 17:00 | 316 | 308
2018-10-24 17:30 | 329 | 320
2018-10-24 18:00 | 402 | 394
2018-10-24 18:30 | 490 | 485
2018-10-24 19:00 | 440 | 438
2018-10-24 19:30 | 502 | 500
2018-10-24 20:00 | 479 | 477
2018-10-24 20:30 | 443 | 441
2018-10-24 21:00 | 415 | 412
2018-10-24 21:30 | 419 | 415
2018-10-24 22:00 | 396 | 391
2018-10-24 22:30 | 360 | 354
2018-10-24 23:00 | 333 | 325
2018-10-24 23:30 | 345 | 336
2018-10-25 | 385 | 377
2018-10-25 00:30 | 386 | 380
2018-10-25 01:00 | 366 | 359
2018-10-25 01:30 | 353 | 345
2018-10-25 02:00 | 352 | 344
2018-10-25 02:30 | 369 | 360
2018-10-25 03:00 | 371 | 364
2018-10-25 03:30 | 375 | 368
2018-10-25 04:00 | 385 | 378
2018-10-25 04:30 | 391 | 385
2018-10-25 05:00 | 426 | 420
2018-10-25 05:30 | 433 | 429
2018-10-25 06:00 | 397 | 392
2018-10-25 06:30 | 389 | 383
2018-10-25 07:00 | 352 | 344
2018-10-25 07:30 | 301 | 289
2018-10-25 08:00 | 296 | 280
2018-10-25 08:30 | 293 | 277
2018-10-25 09:00 | 270 | 252
2018-10-25 09:30 | 239 | 216
2018-10-25 10:00 | 216 | 188
2018-10-25 10:30 | 206 | 176
2018-10-25 11:00 | 196 | 163
2018-10-25 11:30 | 224 | 194
2018-10-25 12:00 | 185 | 150
2018-10-25 12:30 | 185 | 147
2018-10-25 13:00 | 189 | 152
2018-10-25 13:30 | 198 | 164
2018-10-25 14:00 | 218 | 188
2018-10-25 14:30 | 222 | 194
2018-10-25 15:00 | 239 | 215
2018-10-25 15:30 | 274 | 254
2018-10-25 16:00 | 287 | 271
2018-10-25 16:30 | 358 | 348
2018-10-25 17:00 | 385 | 377
2018-10-25 17:30 | 441 | 435
2018-10-25 18:00 | 524 | 521
2018-10-25 18:30 | 596 | 595
2018-10-25 19:00 | 637 | 637
2018-10-25 19:30 | 642 | 642
2018-10-25 20:00 | 641 | 641
2018-10-25 20:30 | 615 | 615
2018-10-25 21:00 | 628 | 628
2018-10-25 21:30 | 592 | 592
2018-10-25 22:00 | 570 | 570
2018-10-25 22:30 | 523 | 523
2018-10-25 23:00 | 492 | 491
2018-10-25 23:30 | 468 | 464
2018-10-26 | 434 | 430
2018-10-26 00:30 | 423 | 419
2018-10-26 01:00 | 407 | 401
2018-10-26 01:30 | 408 | 402
2018-10-26 02:00 | 387 | 382
2018-10-26 02:30 | 387 | 381
2018-10-26 03:00 | 393 | 388
2018-10-26 03:30 | 422 | 417
2018-10-26 04:00 | 426 | 422
2018-10-26 04:30 | 423 | 419
2018-10-26 05:00 | 428 | 424
2018-10-26 05:30 | 442 | 438
2018-10-26 06:00 | 431 | 428
2018-10-26 06:30 | 402 | 399
2018-10-26 07:00 | 368 | 362
2018-10-26 07:30 | 329 | 321
2018-10-26 08:00 | 311 | 299
2018-10-26 08:30 | 300 | 286
2018-10-26 09:00 | 289 | 274
2018-10-26 09:30 | 266 | 249
2018-10-26 10:00 | 242 | 222
2018-10-26 10:30 | 222 | 199
2018-10-26 11:00 | 240 | 199
2018-10-26 11:30 | 239 | 203
2018-10-26 12:00 | 244 | 220
2018-10-26 12:30 | 245 | 223
2018-10-26 13:00 | 252 | 223
2018-10-26 13:30 | 249 | 217
2018-10-26 14:00 | 247 | 228
2018-10-26 14:30 | 260 | 241
2018-10-26 15:00 | 277 | 261
2018-10-26 15:30 | 294 | 278
2018-10-26 16:00 | 299 | 287
2018-10-26 16:30 | 328 | 317
2018-10-26 17:00 | 402 | 394
2018-10-26 17:30 | 429 | 423
2018-10-26 18:00 | 509 | 505
2018-10-26 18:30 | 551 | 549
2018-10-26 19:00 | 600 | 599
2018-10-26 19:30 | 634 | 634
2018-10-26 20:00 | 635 | 635
2018-10-26 20:30 | 617 | 617
2018-10-26 21:00 | 598 | 598
2018-10-26 21:30 | 595 | 595
2018-10-26 22:00 | 582 | 582
2018-10-26 22:30 | 556 | 555
2018-10-26 23:00 | 532 | 532
2018-10-26 23:30 | 502 | 502
2018-10-27 | 489 | 489
2018-10-27 00:30 | 488 | 486
2018-10-27 01:00 | 464 | 462
2018-10-27 01:30 | 448 | 446
2018-10-27 02:00 | 443 | 440
2018-10-27 02:30 | 437 | 434
2018-10-27 03:00 | 442 | 439
2018-10-27 03:30 | 444 | 441
2018-10-27 04:00 | 433 | 430
2018-10-27 04:30 | 434 | 431
2018-10-27 05:00 | 443 | 440
2018-10-27 05:30 | 449 | 446
2018-10-27 06:00 | 435 | 432
2018-10-27 06:30 | 403 | 399
2018-10-27 07:00 | 327 | 320
2018-10-27 07:30 | 271 | 257
2018-10-27 08:00 | 255 | 236
2018-10-27 08:30 | 233 | 211
2018-10-27 09:00 | 227 | 202
2018-10-27 09:30 | 208 | 180
2018-10-27 10:00 | 178 | 141
2018-10-27 10:30 | 168 | 126
2018-10-27 11:00 | 168 | 125
2018-10-27 11:30 | 172 | 131
2018-10-27 12:00 | 175 | 135
2018-10-27 12:30 | 183 | 145
2018-10-27 13:00 | 183 | 145
2018-10-27 13:30 | 200 | 165
2018-10-27 14:00 | 201 | 168
2018-10-27 14:30 | 213 | 182
2018-10-27 15:00 | 235 | 209
2018-10-27 15:30 | 270 | 249
2018-10-27 16:00 | 305 | 289
2018-10-27 16:30 | 360 | 349
2018-10-27 17:00 | 389 | 381
2018-10-27 17:30 | 489 | 483
2018-10-27 18:00 | 570 | 567
2018-10-27 18:30 | 594 | 594
2018-10-27 19:00 | 602 | 602
2018-10-27 19:30 | 598 | 598
2018-10-27 20:00 | 577 | 577
2018-10-27 20:30 | 546 | 545
2018-10-27 21:00 | 516 | 515
2018-10-27 21:30 | 532 | 532
2018-10-27 22:00 | 515 | 514
2018-10-27 22:30 | 491 | 490
2018-10-27 23:00 | 492 | 491
2018-10-27 23:30 | 473 | 472
2018-10-28 | 452 | 450
2018-10-28 00:30 | 456 | 453
2018-10-28 01:00 | 444 | 441
2018-10-28 01:30 | 436 | 433
2018-10-28 02:00 | 434 | 430
2018-10-28 02:30 | 431 | 427
2018-10-28 03:00 | 423 | 419
2018-10-28 03:30 | 398 | 394
2018-10-28 04:00 | 402 | 397
2018-10-28 04:30 | 398 | 393
2018-10-28 05:00 | 401 | 395
2018-10-28 05:30 | 427 | 422
2018-10-28 06:00 | 432 | 428
2018-10-28 06:30 | 395 | 390
2018-10-28 07:00 | 310 | 301
2018-10-28 07:30 | 256 | 240
2018-10-28 08:00 | 231 | 209
2018-10-28 08:30 | 217 | 191
2018-10-28 09:00 | 217 | 190
2018-10-28 09:30 | 206 | 177
2018-10-28 10:00 | 196 | 164
2018-10-28 10:30 | 201 | 170
2018-10-28 11:00 | 212 | 184
2018-10-28 11:30 | 213 | 185
2018-10-28 12:00 | 220 | 193
2018-10-28 12:30 | 225 | 199
2018-10-28 13:00 | 238 | 213
2018-10-28 13:30 | 231 | 207
2018-10-28 14:00 | 246 | 224
2018-10-28 14:30 | 246 | 225
2018-10-28 15:00 | 246 | 226
2018-10-28 15:30 | 272 | 255
2018-10-28 16:00 | 313 | 299
2018-10-28 16:30 | 378 | 370
2018-10-28 17:00 | 456 | 451
2018-10-28 17:30 | 513 | 510
2018-10-28 18:00 | 614 | 612
2018-10-28 18:30 | 656 | 656
2018-10-28 19:00 | 675 | 675
2018-10-28 19:30 | 675 | 675
2018-10-28 20:00 | 667 | 667
2018-10-28 20:30 | 646 | 646
2018-10-28 21:00 | 641 | 641
2018-10-28 21:30 | 638 | 638
2018-10-28 22:00 | 599 | 599
2018-10-28 22:30 | 586 | 586
2018-10-28 23:00 | 570 | 570
2018-10-28 23:30 | 559 | 558
2018-10-29 | 544 | 543
2018-10-29 00:30 | 541 | 540
2018-10-29 01:00 | 524 | 522
2018-10-29 01:30 | 511 | 509
2018-10-29 02:00 | 493 | 491
2018-10-29 02:30 | 488 | 487
2018-10-29 03:00 | 496 | 495
2018-10-29 03:30 | 490 | 489
2018-10-29 04:00 | 485 | 483
2018-10-29 04:30 | 490 | 489
2018-10-29 05:00 | 493 | 492
2018-10-29 05:30 | 503 | 502
2018-10-29 06:00 | 506 | 505
2018-10-29 06:30 | 509 | 508
2018-10-29 07:00 | 465 | 463
2018-10-29 07:30 | 418 | 414
2018-10-29 08:00 | 391 | 385
2018-10-29 08:30 | 389 | 382
2018-10-29 09:00 | 352 | 345
2018-10-29 09:30 | 325 | 316
2018-10-29 10:00 | 316 | 305
2018-10-29 10:30 | 315 | 305
2018-10-29 11:00 | 319 | 309
2018-10-29 11:30 | 329 | 320
2018-10-29 12:00 | 343 | 334
2018-10-29 12:30 | 354 | 346
2018-10-29 13:00 | 359 | 351
2018-10-29 13:30 | 356 | 348
2018-10-29 14:00 | 349 | 342
2018-10-29 14:30 | 363 | 356
2018-10-29 15:00 | 368 | 361
2018-10-29 15:30 | 391 | 385
2018-10-29 16:00 | 431 | 425
2018-10-29 16:30 | 522 | 519
2018-10-29 17:00 | 601 | 600
2018-10-29 17:30 | 624 | 623
2018-10-29 18:00 | 673 | 673
2018-10-29 18:30 | 706 | 706
2018-10-29 19:00 | 731 | 731
2018-10-29 19:30 | 731 | 730
2018-10-29 20:00 | 707 | 707
2018-10-29 20:30 | 697 | 696
2018-10-29 21:00 | 677 | 677
2018-10-29 21:30 | 655 | 655
2018-10-29 22:00 | 621 | 621
2018-10-29 22:30 | 599 | 599
2018-10-29 23:00 | 579 | 578
2018-10-29 23:30 | 553 | 552
2018-10-30 | 535 | 535
2018-10-30 00:30 | 532 | 531
2018-10-30 01:00 | 506 | 505
2018-10-30 01:30 | 496 | 495
2018-10-30 02:00 | 484 | 482
2018-10-30 02:30 | 476 | 474
2018-10-30 03:00 | 458 | 456
2018-10-30 03:30 | 451 | 449
2018-10-30 04:00 | 453 | 451
2018-10-30 04:30 | 479 | 477
2018-10-30 05:00 | 485 | 483
2018-10-30 05:30 | 502 | 500
2018-10-30 06:00 | 506 | 505
2018-10-30 06:30 | 518 | 516
2018-10-30 07:00 | 449 | 447
2018-10-30 07:30 | 450 | 446
2018-10-30 08:00 | 448 | 444
2018-10-30 08:30 | 440 | 436
2018-10-30 09:00 | 449 | 444
2018-10-30 09:30 | 408 | 404
2018-10-30 10:00 | 372 | 366
2018-10-30 10:30 | 334 | 326
2018-10-30 11:00 | 336 | 326
2018-10-30 11:30 | 336 | 327
2018-10-30 12:00 | 331 | 322
2018-10-30 12:30 | 342 | 332
2018-10-30 13:00 | 334 | 325
2018-10-30 13:30 | 318 | 308
2018-10-30 14:00 | 337 | 327
2018-10-30 14:30 | 357 | 349
2018-10-30 15:00 | 373 | 366
2018-10-30 15:30 | 396 | 390
2018-10-30 16:00 | 513 | 509
2018-10-30 16:30 | 601 | 599
2018-10-30 17:00 | 630 | 630
2018-10-30 17:30 | 655 | 655
2018-10-30 18:00 | 665 | 665
2018-10-30 18:30 | 677 | 677
2018-10-30 19:00 | 682 | 682
2018-10-30 19:30 | 697 | 697
2018-10-30 20:00 | 692 | 692
2018-10-30 20:30 | 672 | 672
2018-10-30 21:00 | 659 | 659
2018-10-30 21:30 | 653 | 653
2018-10-30 22:00 | 627 | 627
2018-10-30 22:30 | 593 | 592
2018-10-30 23:00 | 562 | 561
2018-10-30 23:30 | 541 | 540
2018-10-31 | 532 | 531
2018-10-31 00:30 | 533 | 532
2018-10-31 01:00 | 509 | 508
2018-10-31 01:30 | 500 | 498
2018-10-31 02:00 | 489 | 488
2018-10-31 02:30 | 483 | 481
2018-10-31 03:00 | 475 | 474
2018-10-31 03:30 | 472 | 471
2018-10-31 04:00 | 469 | 467
2018-10-31 04:30 | 467 | 465
2018-10-31 05:00 | 464 | 462
2018-10-31 05:30 | 482 | 480
2018-10-31 06:00 | 477 | 475
2018-10-31 06:30 | 451 | 449
2018-10-31 07:00 | 430 | 427
2018-10-31 07:30 | 414 | 409
2018-10-31 08:00 | 390 | 385
2018-10-31 08:30 | 379 | 372
2018-10-31 09:00 | 295 | 287
2018-10-31 09:30 | 319 | 307
2018-10-31 10:00 | 300 | 289
2018-10-31 10:30 | 305 | 294
2018-10-31 11:00 | 302 | 291
2018-10-31 11:30 | 306 | 296
2018-10-31 12:00 | 287 | 277
2018-10-31 12:30 | 294 | 284
2018-10-31 13:00 | 316 | 307
2018-10-31 13:30 | 306 | 297
2018-10-31 14:00 | 323 | 314
2018-10-31 14:30 | 334 | 326
2018-10-31 15:00 | 369 | 362
2018-10-31 15:30 | 411 | 406
2018-10-31 16:00 | 397 | 393
2018-10-31 16:30 | 427 | 422
2018-10-31 17:00 | 403 | 399
2018-10-31 17:30 | 460 | 456
2018-10-31 18:00 | 530 | 527
2018-10-31 18:30 | 552 | 551
2018-10-31 19:00 | 578 | 578
2018-10-31 19:30 | 579 | 579
2018-10-31 20:00 | 623 | 622
2018-10-31 20:30 | 638 | 638
2018-10-31 21:00 | 679 | 679
2018-10-31 21:30 | 659 | 659
2018-10-31 22:00 | 611 | 611
2018-10-31 22:30 | 600 | 600
2018-10-31 23:00 | 564 | 563
2018-10-31 23:30 | 543 | 542
2018-11-01 | 527 | 526
2018-11-01 00:30 | 531 | 529
2018-11-01 01:00 | 505 | 504
2018-11-01 01:30 | 486 | 485
2018-11-01 02:00 | 477 | 475
2018-11-01 02:30 | 467 | 465
2018-11-01 03:00 | 470 | 468
2018-11-01 03:30 | 468 | 466
2018-11-01 04:00 | 469 | 467
2018-11-01 04:30 | 470 | 468
2018-11-01 05:00 | 470 | 468
2018-11-01 05:30 | 481 | 479
2018-11-01 06:00 | 479 | 478
2018-11-01 06:30 | 470 | 468
2018-11-01 07:00 | 426 | 423
2018-11-01 07:30 | 406 | 401
2018-11-01 08:00 | 431 | 425
2018-11-01 08:30 | 380 | 374
2018-11-01 09:00 | 340 | 332
2018-11-01 09:30 | 316 | 306
2018-11-01 10:00 | 312 | 299
2018-11-01 10:30 | 284 | 270
2018-11-01 11:00 | 265 | 250
2018-11-01 11:30 | 267 | 251
2018-11-01 12:00 | 207 | 187
2018-11-01 12:30 | 214 | 190
2018-11-01 13:00 | 247 | 226
2018-11-01 13:30 | 247 | 228
2018-11-01 14:00 | 240 | 221
2018-11-01 14:30 | 296 | 280
2018-11-01 15:00 | 256 | 242
2018-11-01 15:30 | 237 | 221
2018-11-01 16:00 | 266 | 251
2018-11-01 16:30 | 249 | 235
2018-11-01 17:00 | 295 | 283
2018-11-01 17:30 | 314 | 304
2018-11-01 18:00 | 357 | 350
2018-11-01 18:30 | 387 | 383
2018-11-01 19:00 | 403 | 400
2018-11-01 19:30 | 411 | 409
2018-11-01 20:00 | 423 | 421
2018-11-01 20:30 | 472 | 470
2018-11-01 21:00 | 502 | 501
2018-11-01 21:30 | 594 | 593
2018-11-01 22:00 | 611 | 611
2018-11-01 22:30 | 574 | 574
2018-11-01 23:00 | 552 | 552
2018-11-01 23:30 | 539 | 538
2018-11-02 | 468 | 468
2018-11-02 00:30 | 456 | 454
2018-11-02 01:00 | 436 | 433
2018-11-02 01:30 | 421 | 418
2018-11-02 02:00 | 421 | 418
2018-11-02 02:30 | 420 | 416
2018-11-02 03:00 | 408 | 404
2018-11-02 03:30 | 395 | 392
2018-11-02 04:00 | 462 | 458
2018-11-02 04:30 | 445 | 443
2018-11-02 05:00 | 408 | 405
2018-11-02 05:30 | 443 | 439
2018-11-02 06:00 | 415 | 412
2018-11-02 06:30 | 406 | 402
2018-11-02 07:00 | 383 | 377
2018-11-02 07:30 | 337 | 328
2018-11-02 08:00 | 295 | 283
2018-11-02 08:30 | 294 | 279
2018-11-02 09:00 | 295 | 281
2018-11-02 09:30 | 304 | 292
2018-11-02 10:00 | 280 | 267
2018-11-02 10:30 | 260 | 244
2018-11-02 11:00 | 215 | 193
2018-11-02 11:30 | 189 | 160
2018-11-02 12:00 | 209 | 180
2018-11-02 12:30 | 189 | 158
2018-11-02 13:00 | 191 | 159
2018-11-02 13:30 | 172 | 134
2018-11-02 14:00 | 188 | 154
2018-11-02 14:30 | 188 | 155
2018-11-02 15:00 | 149 | 105
2018-11-02 15:30 | 145 | 94
2018-11-02 16:00 | 132 | 67
2018-11-02 16:30 | 140 | 76
2018-11-02 17:00 | 175 | 134
2018-11-02 17:30 | 201 | 169
2018-11-02 18:00 | 255 | 234
2018-11-02 18:30 | 352 | 341
2018-11-02 19:00 | 306 | 299
2018-11-02 19:30 | 340 | 333
2018-11-02 20:00 | 388 | 383
2018-11-02 20:30 | 391 | 388
2018-11-02 21:00 | 396 | 393
2018-11-02 21:30 | 447 | 444
2018-11-02 22:00 | 513 | 511
2018-11-02 22:30 | 492 | 490
2018-11-02 23:00 | 470 | 468
2018-11-02 23:30 | 440 | 438
2018-11-03 | 420 | 417
2018-11-03 00:30 | 445 | 441
2018-11-03 01:00 | 418 | 415
2018-11-03 01:30 | 422 | 419
2018-11-03 02:00 | 391 | 387
2018-11-03 02:30 | 384 | 379
2018-11-03 03:00 | 384 | 379
2018-11-03 03:30 | 362 | 356
2018-11-03 04:00 | 362 | 356
2018-11-03 04:30 | 362 | 356
2018-11-03 05:00 | 352 | 346
2018-11-03 05:30 | 357 | 350
2018-11-03 06:00 | 347 | 341
2018-11-03 06:30 | 304 | 296
2018-11-03 07:00 | 252 | 236
2018-11-03 07:30 | 230 | 208
2018-11-03 08:00 | 233 | 210
2018-11-03 08:30 | 185 | 155
2018-11-03 09:00 | 176 | 139
2018-11-03 09:30 | 195 | 162
2018-11-03 10:00 | 255 | 231
2018-11-03 10:30 | 229 | 206
2018-11-03 11:00 | 235 | 211
2018-11-03 11:30 | 245 | 222
2018-11-03 12:00 | 233 | 210
2018-11-03 12:30 | 213 | 186
2018-11-03 13:00 | 218 | 190
2018-11-03 13:30 | 242 | 218
2018-11-03 14:00 | 275 | 255
2018-11-03 14:30 | 284 | 267
2018-11-03 15:00 | 279 | 264
2018-11-03 15:30 | 278 | 261
2018-11-03 16:00 | 247 | 227
2018-11-03 16:30 | 280 | 262
2018-11-03 17:00 | 333 | 319
2018-11-03 17:30 | 397 | 387
2018-11-03 18:00 | 464 | 458
2018-11-03 18:30 | 490 | 487
2018-11-03 19:00 | 526 | 524
2018-11-03 19:30 | 521 | 520
2018-11-03 20:00 | 502 | 501
2018-11-03 20:30 | 488 | 486
2018-11-03 21:00 | 503 | 502
2018-11-03 21:30 | 492 | 491
2018-11-03 22:00 | 484 | 482
2018-11-03 22:30 | 463 | 461
2018-11-03 23:00 | 451 | 449
2018-11-03 23:30 | 456 | 454
2018-11-04 | 447 | 444
2018-11-04 00:30 | 453 | 449
2018-11-04 01:00 | 436 | 434
2018-11-04 01:30 | 439 | 436
2018-11-04 02:00 | 439 | 436
2018-11-04 02:30 | 425 | 422
2018-11-04 03:00 | 414 | 410
2018-11-04 03:30 | 420 | 416
2018-11-04 04:00 | 406 | 403
2018-11-04 04:30 | 411 | 407
2018-11-04 05:00 | 413 | 409
2018-11-04 05:30 | 416 | 412
2018-11-04 06:00 | 401 | 398
2018-11-04 06:30 | 364 | 359
2018-11-04 07:00 | 301 | 291
2018-11-04 07:30 | 240 | 223
2018-11-04 08:00 | 234 | 211
2018-11-04 08:30 | 252 | 230
2018-11-04 09:00 | 248 | 225
2018-11-04 09:30 | 244 | 220
2018-11-04 10:00 | 245 | 220
2018-11-04 10:30 | 245 | 220
2018-11-04 11:00 | 206 | 175
2018-11-04 11:30 | 209 | 175
2018-11-04 12:00 | 219 | 187
2018-11-04 12:30 | 203 | 169
2018-11-04 13:00 | 216 | 184
2018-11-04 13:30 | 237 | 209
2018-11-04 14:00 | 249 | 224
2018-11-04 14:30 | 270 | 249
2018-11-04 15:00 | 286 | 267
2018-11-04 15:30 | 297 | 280
2018-11-04 16:00 | 342 | 329
2018-11-04 16:30 | 325 | 314
2018-11-04 17:00 | 375 | 365
2018-11-04 17:30 | 414 | 406
2018-11-04 18:00 | 502 | 497
2018-11-04 18:30 | 552 | 550
2018-11-04 19:00 | 573 | 572
2018-11-04 19:30 | 551 | 550
2018-11-04 20:00 | 532 | 531
2018-11-04 20:30 | 549 | 548
2018-11-04 21:00 | 542 | 541
2018-11-04 21:30 | 557 | 556
2018-11-04 22:00 | 528 | 527
2018-11-04 22:30 | 503 | 502
2018-11-04 23:00 | 468 | 466
2018-11-04 23:30 | 446 | 444
2018-11-05 | 433 | 429
2018-11-05 00:30 | 456 | 453
2018-11-05 01:00 | 428 | 425
2018-11-05 01:30 | 429 | 426
2018-11-05 02:00 | 416 | 413
2018-11-05 02:30 | 418 | 415
2018-11-05 03:00 | 405 | 401
2018-11-05 03:30 | 402 | 397
2018-11-05 04:00 | 402 | 398
2018-11-05 04:30 | 412 | 408
2018-11-05 05:00 | 425 | 421
2018-11-05 05:30 | 440 | 436
2018-11-05 06:00 | 423 | 420
2018-11-05 06:30 | 396 | 391
2018-11-05 07:00 | 346 | 339
2018-11-05 07:30 | 334 | 324
2018-11-05 08:00 | 343 | 333
2018-11-05 08:30 | 304 | 293
2018-11-05 09:00 | 313 | 300
2018-11-05 09:30 | 294 | 280
2018-11-05 10:00 | 278 | 263
2018-11-05 10:30 | 268 | 250
2018-11-05 11:00 | 273 | 255
2018-11-05 11:30 | 278 | 260
2018-11-05 12:00 | 279 | 261
2018-11-05 12:30 | 285 | 267
2018-11-05 13:00 | 298 | 281
2018-11-05 13:30 | 300 | 285
2018-11-05 14:00 | 279 | 265
2018-11-05 14:30 | 310 | 296
2018-11-05 15:00 | 312 | 300
2018-11-05 15:30 | 268 | 254
2018-11-05 16:00 | 264 | 247
2018-11-05 16:30 | 243 | 225
2018-11-05 17:00 | 289 | 273
2018-11-05 17:30 | 348 | 336
2018-11-05 18:00 | 390 | 382
2018-11-05 18:30 | 426 | 420
2018-11-05 19:00 | 445 | 443
2018-11-05 19:30 | 441 | 440
2018-11-05 20:00 | 450 | 448
2018-11-05 20:30 | 421 | 419
2018-11-05 21:00 | 458 | 456
2018-11-05 21:30 | 452 | 451
2018-11-05 22:00 | 473 | 471
2018-11-05 22:30 | 511 | 510
2018-11-05 23:00 | 486 | 485
2018-11-05 23:30 | 456 | 454
2018-11-06 | 433 | 430
2018-11-06 00:30 | 426 | 423
2018-11-06 01:00 | 337 | 334
2018-11-06 01:30 | 326 | 319
2018-11-06 02:00 | 326 | 318
2018-11-06 02:30 | 312 | 304
2018-11-06 03:00 | 306 | 296
2018-11-06 03:30 | 303 | 293
2018-11-06 04:00 | 300 | 290
2018-11-06 04:30 | 295 | 284
2018-11-06 05:00 | 309 | 298
2018-11-06 05:30 | 330 | 321
2018-11-06 06:00 | 327 | 319
2018-11-06 06:30 | 308 | 299
2018-11-06 07:00 | 246 | 232
2018-11-06 07:30 | 269 | 251
2018-11-06 08:00 | 287 | 272
2018-11-06 08:30 | 266 | 252
2018-11-06 09:00 | 242 | 225
2018-11-06 09:30 | 239 | 222
2018-11-06 10:00 | 267 | 252
2018-11-06 10:30 | 276 | 262
2018-11-06 11:00 | 256 | 243
2018-11-06 11:30 | 233 | 215
2018-11-06 12:00 | 167 | 139
2018-11-06 12:30 | 162 | 129
2018-11-06 13:00 | 161 | 127
2018-11-06 13:30 | 156 | 122
2018-11-06 14:00 | 169 | 137
2018-11-06 14:30 | 163 | 130
2018-11-06 15:00 | 123 | 73
2018-11-06 15:30 | 162 | 124
2018-11-06 16:00 | 155 | 108
2018-11-06 16:30 | 139 | 84
2018-11-06 17:00 | 146 | 98
2018-11-06 17:30 | 199 | 170
2018-11-06 18:00 | 277 | 260
2018-11-06 18:30 | 309 | 298
2018-11-06 19:00 | 332 | 325
2018-11-06 19:30 | 339 | 334
2018-11-06 20:00 | 320 | 315
2018-11-06 20:30 | 324 | 318
2018-11-06 21:00 | 343 | 337
2018-11-06 21:30 | 348 | 343
2018-11-06 22:00 | 399 | 395
2018-11-06 22:30 | 364 | 360
2018-11-06 23:00 | 413 | 409
2018-11-06 23:30 | 402 | 399
2018-11-07 | 413 | 410
2018-11-07 00:30 | 496 | 493
2018-11-07 01:00 | 467 | 466
2018-11-07 01:30 | 436 | 434
2018-11-07 02:00 | 433 | 430
2018-11-07 02:30 | 423 | 421
2018-11-07 03:00 | 413 | 410
2018-11-07 03:30 | 410 | 405
2018-11-07 04:00 | 419 | 413
2018-11-07 04:30 | 436 | 430
2018-11-07 05:00 | 440 | 435
2018-11-07 05:30 | 465 | 461
2018-11-07 06:00 | 481 | 478
2018-11-07 06:30 | 437 | 432
2018-11-07 07:00 | 343 | 334
2018-11-07 07:30 | 359 | 345
2018-11-07 08:00 | 371 | 358
2018-11-07 08:30 | 353 | 339
2018-11-07 09:00 | 290 | 271
2018-11-07 09:30 | 245 | 217
2018-11-07 10:00 | 201 | 161
2018-11-07 10:30 | 194 | 147
2018-11-07 11:00 | 195 | 145
2018-11-07 11:30 | 159 | 95
2018-11-07 12:00 | 163 | 96
2018-11-07 12:30 | 169 | 101
2018-11-07 13:00 | 182 | 124
2018-11-07 13:30 | 195 | 135
2018-11-07 14:00 | 190 | 138
2018-11-07 14:30 | 158 | 92
2018-11-07 15:00 | 206 | 159
2018-11-07 15:30 | 202 | 158
2018-11-07 16:00 | 171 | 115
2018-11-07 16:30 | 191 | 140
2018-11-07 17:00 | 229 | 190
2018-11-07 17:30 | 324 | 300
2018-11-07 18:00 | 378 | 362
2018-11-07 18:30 | 413 | 401
2018-11-07 19:00 | 423 | 416
2018-11-07 19:30 | 428 | 423
2018-11-07 20:00 | 466 | 461
2018-11-07 20:30 | 534 | 531
2018-11-07 21:00 | 535 | 532
2018-11-07 21:30 | 527 | 525
2018-11-07 22:00 | 542 | 539
2018-11-07 22:30 | 593 | 590
2018-11-07 23:00 | 571 | 569
2018-11-07 23:30 | 542 | 541
2018-11-08 | 535 | 532
2018-11-08 00:30 | 545 | 543
2018-11-08 01:00 | 525 | 522
2018-11-08 01:30 | 513 | 510
2018-11-08 02:00 | 499 | 495
2018-11-08 02:30 | 493 | 488
2018-11-08 03:00 | 493 | 489
2018-11-08 03:30 | 486 | 481
2018-11-08 04:00 | 488 | 484
2018-11-08 04:30 | 486 | 481
2018-11-08 05:00 | 483 | 478
2018-11-08 05:30 | 489 | 485
2018-11-08 06:00 | 453 | 449
2018-11-08 06:30 | 440 | 434
2018-11-08 07:00 | 390 | 380
2018-11-08 07:30 | 378 | 365
2018-11-08 08:00 | 374 | 359
2018-11-08 08:30 | 363 | 347
2018-11-08 09:00 | 365 | 348
2018-11-08 09:30 | 369 | 353
2018-11-08 10:00 | 331 | 312
2018-11-08 10:30 | 295 | 272
2018-11-08 11:00 | 287 | 264
2018-11-08 11:30 | 305 | 283
2018-11-08 12:00 | 308 | 286
2018-11-08 12:30 | 259 | 175
2018-11-08 13:00 | 273 | 166
2018-11-08 13:30 | 246 | 178
2018-11-08 14:00 | 321 | 274
2018-11-08 14:30 | 372 | 348
2018-11-08 15:00 | 373 | 360
2018-11-08 15:30 | 408 | 396
2018-11-08 16:00 | 429 | 419
2018-11-08 16:30 | 491 | 475
2018-11-08 17:00 | 539 | 528
2018-11-08 17:30 | 576 | 572
2018-11-08 18:00 | 615 | 612
2018-11-08 18:30 | 628 | 627
2018-11-08 19:00 | 643 | 642
2018-11-08 19:30 | 631 | 630
2018-11-08 20:00 | 613 | 612
2018-11-08 20:30 | 630 | 630
2018-11-08 21:00 | 637 | 636
2018-11-08 21:30 | 610 | 610
2018-11-08 22:00 | 574 | 573
2018-11-08 22:30 | 538 | 536
2018-11-08 23:00 | 514 | 512
2018-11-08 23:30 | 543 | 540
2018-11-09 | 530 | 527
2018-11-09 00:30 | 521 | 518
2018-11-09 01:00 | 514 | 511
2018-11-09 01:30 | 506 | 503
2018-11-09 02:00 | 495 | 492
2018-11-09 02:30 | 479 | 476
2018-11-09 03:00 | 476 | 472
2018-11-09 03:30 | 467 | 463
2018-11-09 04:00 | 478 | 474
2018-11-09 04:30 | 482 | 478
2018-11-09 05:00 | 489 | 486
2018-11-09 05:30 | 496 | 492
2018-11-09 06:00 | 500 | 496
2018-11-09 06:30 | 499 | 495
2018-11-09 07:00 | 484 | 480
2018-11-09 07:30 | 522 | 518
2018-11-09 08:00 | 518 | 514
2018-11-09 08:30 | 495 | 491
2018-11-09 09:00 | 477 | 471
2018-11-09 09:30 | 487 | 481
2018-11-09 10:00 | 404 | 397
2018-11-09 10:30 | 407 | 398
2018-11-09 11:00 | 378 | 368
2018-11-09 11:30 | 394 | 384
2018-11-09 12:00 | 375 | 364
2018-11-09 12:30 | 361 | 348
2018-11-09 13:00 | 349 | 335
2018-11-09 13:30 | 365 | 352
2018-11-09 14:00 | 383 | 370
2018-11-09 14:30 | 350 | 337
2018-11-09 15:00 | 320 | 305
2018-11-09 15:30 | 348 | 333
2018-11-09 16:00 | 353 | 339
2018-11-09 16:30 | 364 | 352
2018-11-09 17:00 | 424 | 415
2018-11-09 17:30 | 490 | 484
2018-11-09 18:00 | 546 | 543
2018-11-09 18:30 | 541 | 539
2018-11-09 19:00 | 559 | 557
2018-11-09 19:30 | 554 | 552
2018-11-09 20:00 | 527 | 526
2018-11-09 20:30 | 545 | 543
2018-11-09 21:00 | 585 | 583
2018-11-09 21:30 | 577 | 575
2018-11-09 22:00 | 550 | 548
2018-11-09 22:30 | 524 | 521
2018-11-09 23:00 | 501 | 498
2018-11-09 23:30 | 453 | 449
2018-11-10 | 449 | 443
2018-11-10 00:30 | 442 | 436
2018-11-10 01:00 | 452 | 446
2018-11-10 01:30 | 447 | 441
2018-11-10 02:00 | 421 | 415
2018-11-10 02:30 | 426 | 420
2018-11-10 03:00 | 452 | 446
2018-11-10 03:30 | 453 | 448
2018-11-10 04:00 | 429 | 423
2018-11-10 04:30 | 435 | 429
2018-11-10 05:00 | 432 | 426
2018-11-10 05:30 | 435 | 428
2018-11-10 06:00 | 439 | 433
2018-11-10 06:30 | 408 | 401
2018-11-10 07:00 | 373 | 362
2018-11-10 07:30 | 368 | 356
2018-11-10 08:00 | 325 | 310
2018-11-10 08:30 | 313 | 295
2018-11-10 09:00 | 286 | 265
2018-11-10 09:30 | 295 | 271
2018-11-10 10:00 | 332 | 311
2018-11-10 10:30 | 304 | 283
2018-11-10 11:00 | 304 | 283
2018-11-10 11:30 | 277 | 258
2018-11-10 12:00 | 302 | 282
2018-11-10 12:30 | 289 | 271
2018-11-10 13:00 | 283 | 263
2018-11-10 13:30 | 296 | 276
2018-11-10 14:00 | 290 | 272
2018-11-10 14:30 | 311 | 295
2018-11-10 15:00 | 322 | 308
2018-11-10 15:30 | 314 | 299
2018-11-10 16:00 | 286 | 273
2018-11-10 16:30 | 359 | 346
2018-11-10 17:00 | 385 | 375
2018-11-10 17:30 | 472 | 466
2018-11-10 18:00 | 507 | 504
2018-11-10 18:30 | 513 | 511
2018-11-10 19:00 | 543 | 542
2018-11-10 19:30 | 550 | 550
2018-11-10 20:00 | 552 | 551
2018-11-10 20:30 | 559 | 558
2018-11-10 21:00 | 580 | 579
2018-11-10 21:30 | 560 | 559
2018-11-10 22:00 | 538 | 537
2018-11-10 22:30 | 507 | 506
2018-11-10 23:00 | 473 | 471
2018-11-10 23:30 | 476 | 474
2018-11-11 | 452 | 449
2018-11-11 00:30 | 452 | 448
2018-11-11 01:00 | 430 | 426
2018-11-11 01:30 | 431 | 427
2018-11-11 02:00 | 430 | 426
2018-11-11 02:30 | 428 | 424
2018-11-11 03:00 | 447 | 443
2018-11-11 03:30 | 449 | 445
2018-11-11 04:00 | 451 | 448
2018-11-11 04:30 | 462 | 459
2018-11-11 05:00 | 461 | 457
2018-11-11 05:30 | 455 | 452
2018-11-11 06:00 | 428 | 424
2018-11-11 06:30 | 393 | 389
2018-11-11 07:00 | 367 | 360
2018-11-11 07:30 | 292 | 281
2018-11-11 08:00 | 308 | 293
2018-11-11 08:30 | 298 | 284
2018-11-11 09:00 | 245 | 227
2018-11-11 09:30 | 235 | 214
2018-11-11 10:00 | 228 | 207
2018-11-11 10:30 | 214 | 190
2018-11-11 11:00 | 206 | 181
2018-11-11 11:30 | 236 | 214
2018-11-11 12:00 | 263 | 244
2018-11-11 12:30 | 242 | 225
2018-11-11 13:00 | 231 | 212
2018-11-11 13:30 | 224 | 204
2018-11-11 14:00 | 251 | 233
2018-11-11 14:30 | 190 | 166
2018-11-11 15:00 | 189 | 161
2018-11-11 15:30 | 215 | 191
2018-11-11 16:00 | 216 | 195
2018-11-11 16:30 | 236 | 218
2018-11-11 17:00 | 303 | 290
2018-11-11 17:30 | 383 | 377
2018-11-11 18:00 | 404 | 401
2018-11-11 18:30 | 432 | 429
2018-11-11 19:00 | 430 | 428
2018-11-11 19:30 | 482 | 481
2018-11-11 20:00 | 473 | 472
2018-11-11 20:30 | 478 | 476
2018-11-11 21:00 | 505 | 504
2018-11-11 21:30 | 516 | 515
2018-11-11 22:00 | 494 | 493
2018-11-11 22:30 | 463 | 462
2018-11-11 23:00 | 436 | 434
2018-11-11 23:30 | 422 | 419
2018-11-12 | 406 | 403
2018-11-12 00:30 | 417 | 413
2018-11-12 01:00 | 387 | 383
2018-11-12 01:30 | 375 | 370
2018-11-12 02:00 | 381 | 375
2018-11-12 02:30 | 362 | 356
2018-11-12 03:00 | 354 | 347
2018-11-12 03:30 | 346 | 339
2018-11-12 04:00 | 347 | 339
2018-11-12 04:30 | 359 | 352
2018-11-12 05:00 | 382 | 376
2018-11-12 05:30 | 408 | 403
2018-11-12 06:00 | 419 | 415
2018-11-12 06:30 | 408 | 404
2018-11-12 07:00 | 348 | 340
2018-11-12 07:30 | 346 | 335
2018-11-12 08:00 | 322 | 310
2018-11-12 08:30 | 306 | 293
2018-11-12 09:00 | 299 | 284
2018-11-12 09:30 | 325 | 310
2018-11-12 10:00 | 302 | 287
2018-11-12 10:30 | 297 | 281
2018-11-12 11:00 | 281 | 264
2018-11-12 11:30 | 282 | 265
2018-11-12 12:00 | 294 | 277
2018-11-12 12:30 | 286 | 270
2018-11-12 13:00 | 292 | 275
2018-11-12 13:30 | 286 | 270
2018-11-12 14:00 | 296 | 281
2018-11-12 14:30 | 324 | 310
2018-11-12 15:00 | 304 | 292
2018-11-12 15:30 | 324 | 312
2018-11-12 16:00 | 284 | 271
2018-11-12 16:30 | 257 | 241
2018-11-12 17:00 | 287 | 271
2018-11-12 17:30 | 316 | 304
2018-11-12 18:00 | 397 | 388
2018-11-12 18:30 | 452 | 448
2018-11-12 19:00 | 484 | 481
2018-11-12 19:30 | 488 | 486
2018-11-12 20:00 | 465 | 463
2018-11-12 20:30 | 487 | 486
2018-11-12 21:00 | 510 | 508
2018-11-12 21:30 | 549 | 548
2018-11-12 22:00 | 522 | 522
2018-11-12 22:30 | 490 | 488
2018-11-12 23:00 | 467 | 466
2018-11-12 23:30 | 439 | 437
2018-11-13 | 429 | 426
2018-11-13 00:30 | 434 | 430
2018-11-13 01:00 | 415 | 411
2018-11-13 01:30 | 400 | 396
2018-11-13 02:00 | 391 | 386
2018-11-13 02:30 | 388 | 382
2018-11-13 03:00 | 395 | 390
2018-11-13 03:30 | 394 | 389
2018-11-13 04:00 | 388 | 383
2018-11-13 04:30 | 394 | 388
2018-11-13 05:00 | 411 | 406
2018-11-13 05:30 | 411 | 406
2018-11-13 06:00 | 402 | 398
2018-11-13 06:30 | 376 | 370
2018-11-13 07:00 | 318 | 309
2018-11-13 07:30 | 286 | 272
2018-11-13 08:00 | 271 | 252
2018-11-13 08:30 | 246 | 224
2018-11-13 09:00 | 245 | 222
2018-11-13 09:30 | 235 | 211
2018-11-13 10:00 | 232 | 206
2018-11-13 10:30 | 193 | 161
2018-11-13 11:00 | 202 | 169
2018-11-13 11:30 | 217 | 187
2018-11-13 12:00 | 220 | 192
2018-11-13 12:30 | 225 | 197
2018-11-13 13:00 | 245 | 220
2018-11-13 13:30 | 249 | 226
2018-11-13 14:00 | 260 | 239
2018-11-13 14:30 | 286 | 268
2018-11-13 15:00 | 300 | 284
2018-11-13 15:30 | 320 | 306
2018-11-13 16:00 | 324 | 311
2018-11-13 16:30 | 362 | 351
2018-11-13 17:00 | 416 | 409
2018-11-13 17:30 | 463 | 459
2018-11-13 18:00 | 550 | 547
2018-11-13 18:30 | 580 | 578
2018-11-13 19:00 | 578 | 577
2018-11-13 19:30 | 567 | 566
2018-11-13 20:00 | 545 | 544
2018-11-13 20:30 | 543 | 542
2018-11-13 21:00 | 566 | 564
2018-11-13 21:30 | 590 | 589
2018-11-13 22:00 | 569 | 568
2018-11-13 22:30 | 535 | 534
2018-11-13 23:00 | 507 | 505
2018-11-13 23:30 | 480 | 479
2018-11-14 | 471 | 470
2018-11-14 00:30 | 475 | 474
2018-11-14 01:00 | 477 | 476
2018-11-14 01:30 | 473 | 472
2018-11-14 02:00 | 441 | 440
2018-11-14 02:30 | 450 | 449
2018-11-14 03:00 | 456 | 455
2018-11-14 03:30 | 447 | 445
2018-11-14 04:00 | 442 | 440
2018-11-14 04:30 | 449 | 447
2018-11-14 05:00 | 456 | 454
2018-11-14 05:30 | 463 | 461
2018-11-14 06:00 | 417 | 416
2018-11-14 06:30 | 375 | 371
2018-11-14 07:00 | 322 | 315
2018-11-14 07:30 | 330 | 321
2018-11-14 08:00 | 323 | 314
2018-11-14 08:30 | 299 | 288
2018-11-14 09:00 | 300 | 288
2018-11-14 09:30 | 282 | 268
2018-11-14 10:00 | 285 | 270
2018-11-14 10:30 | 267 | 252
2018-11-14 11:00 | 272 | 256
2018-11-14 11:30 | 295 | 279
2018-11-14 12:00 | 296 | 278
2018-11-14 12:30 | 298 | 282
2018-11-14 13:00 | 297 | 278
2018-11-14 13:30 | 314 | 296
2018-11-14 14:00 | 333 | 318
2018-11-14 14:30 | 367 | 354
2018-11-14 15:00 | 381 | 369
2018-11-14 15:30 | 345 | 333
2018-11-14 16:00 | 287 | 271
2018-11-14 16:30 | 238 | 221
2018-11-14 17:00 | 256 | 239
2018-11-14 17:30 | 301 | 286
2018-11-14 18:00 | 384 | 375
2018-11-14 18:30 | 385 | 381
2018-11-14 19:00 | 393 | 390
2018-11-14 19:30 | 432 | 430
2018-11-14 20:00 | 408 | 407
2018-11-14 20:30 | 416 | 414
2018-11-14 21:00 | 462 | 459
2018-11-14 21:30 | 452 | 450
2018-11-14 22:00 | 437 | 435
2018-11-14 22:30 | 461 | 458
2018-11-14 23:00 | 501 | 499
2018-11-14 23:30 | 489 | 487
2018-11-15 | 476 | 474
2018-11-15 00:30 | 474 | 471
2018-11-15 01:00 | 449 | 447
2018-11-15 01:30 | 435 | 432
2018-11-15 02:00 | 429 | 425
2018-11-15 02:30 | 421 | 416
2018-11-15 03:00 | 418 | 414
2018-11-15 03:30 | 425 | 421
2018-11-15 04:00 | 444 | 440
2018-11-15 04:30 | 439 | 436
2018-11-15 05:00 | 440 | 437
2018-11-15 05:30 | 455 | 451
2018-11-15 06:00 | 450 | 447
2018-11-15 06:30 | 432 | 428
2018-11-15 07:00 | 390 | 385
2018-11-15 07:30 | 384 | 375
2018-11-15 08:00 | 360 | 350
2018-11-15 08:30 | 343 | 326
2018-11-15 09:00 | 329 | 316
2018-11-15 09:30 | 332 | 319
2018-11-15 10:00 | 303 | 289
2018-11-15 10:30 | 274 | 257
2018-11-15 11:00 | 300 | 281
2018-11-15 11:30 | 295 | 278
2018-11-15 12:00 | 298 | 282
2018-11-15 12:30 | 276 | 259
2018-11-15 13:00 | 281 | 263
2018-11-15 13:30 | 277 | 259
2018-11-15 14:00 | 286 | 267
2018-11-15 14:30 | 299 | 282
2018-11-15 15:00 | 314 | 298
2018-11-15 15:30 | 333 | 320
2018-11-15 16:00 | 337 | 326
2018-11-15 16:30 | 349 | 339
2018-11-15 17:00 | 392 | 386
2018-11-15 17:30 | 464 | 460
2018-11-15 18:00 | 549 | 547
2018-11-15 18:30 | 599 | 598
2018-11-15 19:00 | 639 | 639
2018-11-15 19:30 | 670 | 670
2018-11-15 20:00 | 647 | 647
2018-11-15 20:30 | 631 | 631
2018-11-15 21:00 | 651 | 651
2018-11-15 21:30 | 640 | 640
2018-11-15 22:00 | 605 | 605
2018-11-15 22:30 | 574 | 574
2018-11-15 23:00 | 548 | 548
2018-11-15 23:30 | 520 | 519
2018-11-16 | 501 | 499
2018-11-16 00:30 | 508 | 506
2018-11-16 01:00 | 462 | 460
2018-11-16 01:30 | 441 | 439
2018-11-16 02:00 | 444 | 441
2018-11-16 02:30 | 433 | 430
2018-11-16 03:00 | 431 | 429
2018-11-16 03:30 | 426 | 423
2018-11-16 04:00 | 428 | 425
2018-11-16 04:30 | 430 | 427
2018-11-16 05:00 | 421 | 418
2018-11-16 05:30 | 430 | 426
2018-11-16 06:00 | 416 | 413
2018-11-16 06:30 | 392 | 388
2018-11-16 07:00 | 358 | 351
2018-11-16 07:30 | 329 | 319
2018-11-16 08:00 | 304 | 292
2018-11-16 08:30 | 313 | 301
2018-11-16 09:00 | 309 | 296
2018-11-16 09:30 | 262 | 248
2018-11-16 10:00 | 189 | 163
2018-11-16 10:30 | 198 | 170
2018-11-16 11:00 | 207 | 180
2018-11-16 11:30 | 204 | 178
2018-11-16 12:00 | 199 | 174
2018-11-16 12:30 | 210 | 186
2018-11-16 13:00 | 225 | 201
2018-11-16 13:30 | 224 | 201
2018-11-16 14:00 | 220 | 198
2018-11-16 14:30 | 233 | 212
2018-11-16 15:00 | 247 | 227
2018-11-16 15:30 | 265 | 248
2018-11-16 16:00 | 271 | 256
2018-11-16 16:30 | 288 | 275
2018-11-16 17:00 | 332 | 322
2018-11-16 17:30 | 407 | 400
2018-11-16 18:00 | 494 | 490
2018-11-16 18:30 | 567 | 566
2018-11-16 19:00 | 592 | 591
2018-11-16 19:30 | 624 | 624
2018-11-16 20:00 | 596 | 596
2018-11-16 20:30 | 567 | 567
2018-11-16 21:00 | 572 | 572
2018-11-16 21:30 | 572 | 571
2018-11-16 22:00 | 537 | 536
2018-11-16 22:30 | 507 | 506
2018-11-16 23:00 | 481 | 479
2018-11-16 23:30 | 465 | 463
2018-11-17 | 459 | 457
2018-11-17 00:30 | 466 | 463
2018-11-17 01:00 | 446 | 442
2018-11-17 01:30 | 421 | 417
2018-11-17 02:00 | 405 | 400
2018-11-17 02:30 | 399 | 393
2018-11-17 03:00 | 390 | 385
2018-11-17 03:30 | 380 | 375
2018-11-17 04:00 | 380 | 374
2018-11-17 04:30 | 403 | 398
2018-11-17 05:00 | 423 | 419
2018-11-17 05:30 | 450 | 447
2018-11-17 06:00 | 457 | 454
2018-11-17 06:30 | 401 | 396
2018-11-17 07:00 | 307 | 298
2018-11-17 07:30 | 258 | 241
2018-11-17 08:00 | 227 | 202
2018-11-17 08:30 | 272 | 250
2018-11-17 09:00 | 246 | 225
2018-11-17 09:30 | 222 | 196
2018-11-17 10:00 | 196 | 163
2018-11-17 10:30 | 178 | 139
2018-11-17 11:00 | 188 | 151
2018-11-17 11:30 | 191 | 155
2018-11-17 12:00 | 179 | 141
2018-11-17 12:30 | 173 | 133
2018-11-17 13:00 | 163 | 117
2018-11-17 13:30 | 156 | 108
2018-11-17 14:00 | 176 | 134
2018-11-17 14:30 | 202 | 171
2018-11-17 15:00 | 221 | 195
2018-11-17 15:30 | 258 | 237
2018-11-17 16:00 | 305 | 289
2018-11-17 16:30 | 315 | 302
2018-11-17 17:00 | 380 | 370
2018-11-17 17:30 | 475 | 470
2018-11-17 18:00 | 570 | 568
2018-11-17 18:30 | 615 | 614
2018-11-17 19:00 | 637 | 637
2018-11-17 19:30 | 651 | 651
2018-11-17 20:00 | 642 | 642
2018-11-17 20:30 | 622 | 622
2018-11-17 21:00 | 628 | 628
2018-11-17 21:30 | 634 | 634
2018-11-17 22:00 | 621 | 621
2018-11-17 22:30 | 590 | 590
2018-11-17 23:00 | 572 | 571
2018-11-17 23:30 | 548 | 548
2018-11-18 | 540 | 539
2018-11-18 00:30 | 539 | 539
2018-11-18 01:00 | 517 | 516
2018-11-18 01:30 | 525 | 524
2018-11-18 02:00 | 513 | 512
2018-11-18 02:30 | 489 | 487
2018-11-18 03:00 | 478 | 477
2018-11-18 03:30 | 475 | 474
2018-11-18 04:00 | 474 | 472
2018-11-18 04:30 | 474 | 473
2018-11-18 05:00 | 470 | 468
2018-11-18 05:30 | 467 | 465
2018-11-18 06:00 | 451 | 449
2018-11-18 06:30 | 396 | 392
2018-11-18 07:00 | 354 | 348
2018-11-18 07:30 | 308 | 298
2018-11-18 08:00 | 272 | 258
2018-11-18 08:30 | 265 | 249
2018-11-18 09:00 | 262 | 244
2018-11-18 09:30 | 253 | 235
2018-11-18 10:00 | 245 | 226
2018-11-18 10:30 | 194 | 169
2018-11-18 11:00 | 183 | 151
2018-11-18 11:30 | 194 | 164
2018-11-18 12:00 | 204 | 176
2018-11-18 12:30 | 191 | 161
2018-11-18 13:00 | 222 | 196
2018-11-18 13:30 | 242 | 221
2018-11-18 14:00 | 238 | 218
2018-11-18 14:30 | 247 | 228
2018-11-18 15:00 | 245 | 227
2018-11-18 15:30 | 270 | 252
2018-11-18 16:00 | 262 | 245
2018-11-18 16:30 | 301 | 287
2018-11-18 17:00 | 409 | 402
2018-11-18 17:30 | 493 | 490
2018-11-18 18:00 | 573 | 572
2018-11-18 18:30 | 602 | 602
2018-11-18 19:00 | 647 | 647
2018-11-18 19:30 | 655 | 655
2018-11-18 20:00 | 645 | 645
2018-11-18 20:30 | 635 | 635
2018-11-18 21:00 | 644 | 644
2018-11-18 21:30 | 629 | 629
2018-11-18 22:00 | 600 | 599
2018-11-18 22:30 | 565 | 564
2018-11-18 23:00 | 523 | 523
2018-11-18 23:30 | 496 | 495
2018-11-19 | 478 | 477
2018-11-19 00:30 | 481 | 480
2018-11-19 01:00 | 460 | 459
2018-11-19 01:30 | 440 | 438
2018-11-19 02:00 | 428 | 426
2018-11-19 02:30 | 418 | 415
2018-11-19 03:00 | 417 | 414
2018-11-19 03:30 | 414 | 412
2018-11-19 04:00 | 403 | 400
2018-11-19 04:30 | 398 | 394
2018-11-19 05:00 | 402 | 399
2018-11-19 05:30 | 408 | 404
2018-11-19 06:00 | 400 | 396
2018-11-19 06:30 | 400 | 396
2018-11-19 07:00 | 396 | 390
2018-11-19 07:30 | 377 | 370
2018-11-19 08:00 | 443 | 438
2018-11-19 08:30 | 383 | 379
2018-11-19 09:00 | 357 | 352
2018-11-19 09:30 | 378 | 370
2018-11-19 10:00 | 313 | 304
2018-11-19 10:30 | 326 | 315
2018-11-19 11:00 | 293 | 281
2018-11-19 11:30 | 349 | 337
2018-11-19 12:00 | 286 | 275
2018-11-19 12:30 | 285 | 273
2018-11-19 13:00 | 268 | 255
2018-11-19 13:30 | 279 | 264
2018-11-19 14:00 | 293 | 280
2018-11-19 14:30 | 327 | 316
2018-11-19 15:00 | 360 | 353
2018-11-19 15:30 | 353 | 347
2018-11-19 16:00 | 348 | 341
2018-11-19 16:30 | 337 | 329
2018-11-19 17:00 | 325 | 318
2018-11-19 17:30 | 369 | 363
2018-11-19 18:00 | 414 | 411
2018-11-19 18:30 | 447 | 445
2018-11-19 19:00 | 479 | 478
2018-11-19 19:30 | 522 | 522
2018-11-19 20:00 | 572 | 572
2018-11-19 20:30 | 561 | 561
2018-11-19 21:00 | 583 | 583
2018-11-19 21:30 | 661 | 661
2018-11-19 22:00 | 638 | 638
2018-11-19 22:30 | 596 | 596
2018-11-19 23:00 | 572 | 572
2018-11-19 23:30 | 542 | 541
2018-11-20 | 519 | 518
2018-11-20 00:30 | 522 | 521
2018-11-20 01:00 | 491 | 490
2018-11-20 01:30 | 469 | 468
2018-11-20 02:00 | 460 | 458
2018-11-20 02:30 | 467 | 465
2018-11-20 03:00 | 456 | 455
2018-11-20 03:30 | 442 | 441
2018-11-20 04:00 | 436 | 434
2018-11-20 04:30 | 458 | 456
2018-11-20 05:00 | 462 | 460
2018-11-20 05:30 | 482 | 481
2018-11-20 06:00 | 489 | 489
2018-11-20 06:30 | 485 | 485
2018-11-20 07:00 | 412 | 410
2018-11-20 07:30 | 445 | 442
2018-11-20 08:00 | 424 | 421
2018-11-20 08:30 | 364 | 360
2018-11-20 09:00 | 400 | 395
2018-11-20 09:30 | 440 | 436
2018-11-20 10:00 | 443 | 441
2018-11-20 10:30 | 391 | 387
2018-11-20 11:00 | 382 | 378
2018-11-20 11:30 | 393 | 388
2018-11-20 12:00 | 380 | 375
2018-11-20 12:30 | 371 | 366
2018-11-20 13:00 | 382 | 378
2018-11-20 13:30 | 383 | 379
2018-11-20 14:00 | 406 | 402
2018-11-20 14:30 | 375 | 371
2018-11-20 15:00 | 387 | 382
2018-11-20 15:30 | 396 | 392
2018-11-20 16:00 | 396 | 393
2018-11-20 16:30 | 392 | 389
2018-11-20 17:00 | 446 | 443
2018-11-20 17:30 | 517 | 515
2018-11-20 18:00 | 568 | 567
2018-11-20 18:30 | 609 | 608
2018-11-20 19:00 | 593 | 593
2018-11-20 19:30 | 656 | 656
2018-11-20 20:00 | 659 | 659
2018-11-20 20:30 | 636 | 636
2018-11-20 21:00 | 639 | 639
2018-11-20 21:30 | 649 | 649
2018-11-20 22:00 | 643 | 643
2018-11-20 22:30 | 613 | 613
2018-11-20 23:00 | 585 | 585
2018-11-20 23:30 | 558 | 558
2018-11-21 | 539 | 539
2018-11-21 00:30 | 564 | 564
2018-11-21 01:00 | 542 | 542
2018-11-21 01:30 | 541 | 541
2018-11-21 02:00 | 530 | 530
2018-11-21 02:30 | 527 | 527
2018-11-21 03:00 | 514 | 514
2018-11-21 03:30 | 505 | 504
2018-11-21 04:00 | 509 | 508
2018-11-21 04:30 | 513 | 512
2018-11-21 05:00 | 524 | 523
2018-11-21 05:30 | 539 | 539
2018-11-21 06:00 | 531 | 530
2018-11-21 06:30 | 519 | 518
2018-11-21 07:00 | 476 | 475
2018-11-21 07:30 | 432 | 429
2018-11-21 08:00 | 405 | 401
2018-11-21 08:30 | 407 | 402
2018-11-21 09:00 | 410 | 405
2018-11-21 09:30 | 379 | 374
2018-11-21 10:00 | 358 | 352
2018-11-21 10:30 | 334 | 327
2018-11-21 11:00 | 322 | 314
2018-11-21 11:30 | 322 | 313
2018-11-21 12:00 | 323 | 314
2018-11-21 12:30 | 325 | 317
2018-11-21 13:00 | 322 | 314
2018-11-21 13:30 | 321 | 312
2018-11-21 14:00 | 342 | 334
2018-11-21 14:30 | 335 | 328
2018-11-21 15:00 | 320 | 313
2018-11-21 15:30 | 256 | 246
2018-11-21 16:00 | 303 | 291
2018-11-21 16:30 | 319 | 310
2018-11-21 17:00 | 316 | 308
2018-11-21 17:30 | 373 | 366
2018-11-21 18:00 | 431 | 427
2018-11-21 18:30 | 463 | 461
2018-11-21 19:00 | 457 | 457
2018-11-21 19:30 | 521 | 520
2018-11-21 20:00 | 531 | 531
2018-11-21 20:30 | 543 | 543
2018-11-21 21:00 | 585 | 585
2018-11-21 21:30 | 605 | 605
2018-11-21 22:00 | 586 | 586
2018-11-21 22:30 | 582 | 582
2018-11-21 23:00 | 566 | 566
2018-11-21 23:30 | 606 | 606
2018-11-22 | 599 | 599
2018-11-22 00:30 | 603 | 603
2018-11-22 01:00 | 574 | 574
2018-11-22 01:30 | 555 | 555
2018-11-22 02:00 | 546 | 546
2018-11-22 02:30 | 540 | 540
2018-11-22 03:00 | 544 | 543
2018-11-22 03:30 | 544 | 544
2018-11-22 04:00 | 542 | 541
2018-11-22 04:30 | 544 | 544
2018-11-22 05:00 | 549 | 549
2018-11-22 05:30 | 562 | 562
2018-11-22 06:00 | 565 | 565
2018-11-22 06:30 | 584 | 584
2018-11-22 07:00 | 581 | 581
2018-11-22 07:30 | 540 | 539
2018-11-22 08:00 | 512 | 512
2018-11-22 08:30 | 467 | 466
2018-11-22 09:00 | 368 | 365
2018-11-22 09:30 | 412 | 408
2018-11-22 10:00 | 415 | 411
2018-11-22 10:30 | 398 | 396
2018-11-22 11:00 | 382 | 379
2018-11-22 11:30 | 385 | 380
2018-11-22 12:00 | 412 | 407
2018-11-22 12:30 | 442 | 438
2018-11-22 13:00 | 513 | 511
2018-11-22 13:30 | 447 | 446
2018-11-22 14:00 | 469 | 466
2018-11-22 14:30 | 476 | 473
2018-11-22 15:00 | 460 | 458
2018-11-22 15:30 | 494 | 492
2018-11-22 16:00 | 541 | 540
2018-11-22 16:30 | 576 | 575
2018-11-22 17:00 | 561 | 561
2018-11-22 17:30 | 492 | 492
2018-11-22 18:00 | 498 | 498
2018-11-22 18:30 | 486 | 486
2018-11-22 19:00 | 484 | 483
2018-11-22 19:30 | 499 | 498
2018-11-22 20:00 | 525 | 525
2018-11-22 20:30 | 510 | 510
2018-11-22 21:00 | 558 | 558
2018-11-22 21:30 | 578 | 578
2018-11-22 22:00 | 610 | 610
2018-11-22 22:30 | 613 | 613
2018-11-22 23:00 | 659 | 659
2018-11-22 23:30 | 648 | 648
2018-11-23 | 632 | 632
2018-11-23 00:30 | 626 | 626
2018-11-23 01:00 | 603 | 603
2018-11-23 01:30 | 588 | 588
2018-11-23 02:00 | 585 | 585
2018-11-23 02:30 | 583 | 583
2018-11-23 03:00 | 570 | 569
2018-11-23 03:30 | 565 | 565
2018-11-23 04:00 | 553 | 552
2018-11-23 04:30 | 555 | 555
2018-11-23 05:00 | 566 | 565
2018-11-23 05:30 | 578 | 577
2018-11-23 06:00 | 573 | 573
2018-11-23 06:30 | 585 | 584
2018-11-23 07:00 | 582 | 581
2018-11-23 07:30 | 572 | 571
2018-11-23 08:00 | 559 | 557
2018-11-23 08:30 | 563 | 561
2018-11-23 09:00 | 515 | 512
2018-11-23 09:30 | 507 | 503
2018-11-23 10:00 | 395 | 391
2018-11-23 10:30 | 393 | 386
2018-11-23 11:00 | 374 | 366
2018-11-23 11:30 | 298 | 288
2018-11-23 12:00 | 300 | 286
2018-11-23 12:30 | 297 | 283
2018-11-23 13:00 | 303 | 287
2018-11-23 13:30 | 388 | 376
2018-11-23 14:00 | 409 | 402
2018-11-23 14:30 | 437 | 431
2018-11-23 15:00 | 446 | 441
2018-11-23 15:30 | 482 | 478
2018-11-23 16:00 | 477 | 474
2018-11-23 16:30 | 483 | 481
2018-11-23 17:00 | 537 | 535
2018-11-23 17:30 | 557 | 556
2018-11-23 18:00 | 647 | 646
2018-11-23 18:30 | 680 | 680
2018-11-23 19:00 | 720 | 720
2018-11-23 19:30 | 713 | 712
2018-11-23 20:00 | 718 | 718
2018-11-23 20:30 | 728 | 728
2018-11-23 21:00 | 753 | 752
2018-11-23 21:30 | 751 | 751
2018-11-23 22:00 | 726 | 726
2018-11-23 22:30 | 701 | 701
2018-11-23 23:00 | 675 | 675
2018-11-23 23:30 | 648 | 648
2018-11-24 | 626 | 626
2018-11-24 00:30 | 623 | 623
2018-11-24 01:00 | 602 | 601
2018-11-24 01:30 | 584 | 584
2018-11-24 02:00 | 570 | 570
2018-11-24 02:30 | 564 | 564
2018-11-24 03:00 | 561 | 560
2018-11-24 03:30 | 555 | 554
2018-11-24 04:00 | 552 | 552
2018-11-24 04:30 | 550 | 549
2018-11-24 05:00 | 550 | 549
2018-11-24 05:30 | 546 | 545
2018-11-24 06:00 | 533 | 532
2018-11-24 06:30 | 501 | 500
2018-11-24 07:00 | 454 | 451
2018-11-24 07:30 | 393 | 388
2018-11-24 08:00 | 358 | 350
2018-11-24 08:30 | 360 | 349
2018-11-24 09:00 | 368 | 354
2018-11-24 09:30 | 370 | 356
2018-11-24 10:00 | 331 | 320
2018-11-24 10:30 | 321 | 308
2018-11-24 11:00 | 329 | 315
2018-11-24 11:30 | 319 | 306
2018-11-24 12:00 | 348 | 334
2018-11-24 12:30 | 367 | 355
2018-11-24 13:00 | 382 | 373
2018-11-24 13:30 | 377 | 368
2018-11-24 14:00 | 376 | 367
2018-11-24 14:30 | 390 | 382
2018-11-24 15:00 | 389 | 382
2018-11-24 15:30 | 395 | 386
2018-11-24 16:00 | 437 | 430
2018-11-24 16:30 | 515 | 511
2018-11-24 17:00 | 590 | 588
2018-11-24 17:30 | 642 | 641
2018-11-24 18:00 | 721 | 721
2018-11-24 18:30 | 770 | 770
2018-11-24 19:00 | 800 | 798
2018-11-24 19:30 | 822 | 821
2018-11-24 20:00 | 808 | 807
2018-11-24 20:30 | 774 | 773
2018-11-24 21:00 | 732 | 732
2018-11-24 21:30 | 711 | 711
2018-11-24 22:00 | 685 | 685
2018-11-24 22:30 | 678 | 678
2018-11-24 23:00 | 671 | 671
2018-11-24 23:30 | 652 | 652
2018-11-25 | 635 | 635
2018-11-25 00:30 | 617 | 617
2018-11-25 01:00 | 576 | 576
2018-11-25 01:30 | 558 | 558
2018-11-25 02:00 | 551 | 551
2018-11-25 02:30 | 541 | 541
2018-11-25 03:00 | 538 | 538
2018-11-25 03:30 | 529 | 528
2018-11-25 04:00 | 521 | 520
2018-11-25 04:30 | 551 | 551
2018-11-25 05:00 | 554 | 554
2018-11-25 05:30 | 539 | 539
2018-11-25 06:00 | 507 | 507
2018-11-25 06:30 | 466 | 465
2018-11-25 07:00 | 412 | 410
2018-11-25 07:30 | 370 | 366
2018-11-25 08:00 | 342 | 336
2018-11-25 08:30 | 320 | 313
2018-11-25 09:00 | 286 | 279
2018-11-25 09:30 | 297 | 289
2018-11-25 10:00 | 314 | 304
2018-11-25 10:30 | 318 | 308
2018-11-25 11:00 | 337 | 328
2018-11-25 11:30 | 344 | 337
2018-11-25 12:00 | 350 | 344
2018-11-25 12:30 | 360 | 354
2018-11-25 13:00 | 378 | 373
2018-11-25 13:30 | 389 | 384
2018-11-25 14:00 | 422 | 418
2018-11-25 14:30 | 432 | 429
2018-11-25 15:00 | 460 | 458
2018-11-25 15:30 | 510 | 508
2018-11-25 16:00 | 528 | 527
2018-11-25 16:30 | 544 | 544
2018-11-25 17:00 | 594 | 593
2018-11-25 17:30 | 688 | 688
2018-11-25 18:00 | 763 | 761
2018-11-25 18:30 | 783 | 780
2018-11-25 19:00 | 813 | 810
2018-11-25 19:30 | 850 | 847
2018-11-25 20:00 | 863 | 861
2018-11-25 20:30 | 890 | 888
2018-11-25 21:00 | 873 | 870
2018-11-25 21:30 | 842 | 839
2018-11-25 22:00 | 797 | 795
2018-11-25 22:30 | 745 | 743
2018-11-25 23:00 | 715 | 715
2018-11-25 23:30 | 684 | 683
2018-11-26 | 656 | 656
2018-11-26 00:30 | 641 | 641
2018-11-26 01:00 | 623 | 623
2018-11-26 01:30 | 604 | 604
2018-11-26 02:00 | 596 | 596
2018-11-26 02:30 | 562 | 562
2018-11-26 03:00 | 525 | 525
2018-11-26 03:30 | 508 | 508
2018-11-26 04:00 | 492 | 491
2018-11-26 04:30 | 511 | 510
2018-11-26 05:00 | 513 | 512
2018-11-26 05:30 | 518 | 518
2018-11-26 06:00 | 515 | 514
2018-11-26 06:30 | 509 | 508
2018-11-26 07:00 | 449 | 447
2018-11-26 07:30 | 418 | 415
2018-11-26 08:00 | 376 | 372
2018-11-26 08:30 | 392 | 387
2018-11-26 09:00 | 385 | 379
2018-11-26 09:30 | 376 | 369
2018-11-26 10:00 | 363 | 353
2018-11-26 10:30 | 372 | 362
2018-11-26 11:00 | 410 | 404
2018-11-26 11:30 | 443 | 439
2018-11-26 12:00 | 451 | 448
2018-11-26 12:30 | 470 | 468
2018-11-26 13:00 | 512 | 510
2018-11-26 13:30 | 511 | 510
2018-11-26 14:00 | 535 | 534
2018-11-26 14:30 | 581 | 581
2018-11-26 15:00 | 593 | 593
2018-11-26 15:30 | 602 | 602
2018-11-26 16:00 | 565 | 565
2018-11-26 16:30 | 478 | 478
2018-11-26 17:00 | 537 | 536
2018-11-26 17:30 | 576 | 576
2018-11-26 18:00 | 605 | 605
2018-11-26 18:30 | 667 | 667
2018-11-26 19:00 | 684 | 682
2018-11-26 19:30 | 706 | 705
2018-11-26 20:00 | 662 | 661
2018-11-26 20:30 | 702 | 702
2018-11-26 21:00 | 733 | 733
2018-11-26 21:30 | 811 | 810
2018-11-26 22:00 | 853 | 850
2018-11-26 22:30 | 800 | 796
2018-11-26 23:00 | 726 | 723
2018-11-26 23:30 | 686 | 685
2018-11-27 | 663 | 663
2018-11-27 00:30 | 637 | 637
2018-11-27 01:00 | 612 | 612
2018-11-27 01:30 | 597 | 597
2018-11-27 02:00 | 595 | 595
2018-11-27 02:30 | 583 | 583
2018-11-27 03:00 | 560 | 560
2018-11-27 03:30 | 541 | 541
2018-11-27 04:00 | 528 | 528
2018-11-27 04:30 | 532 | 532
2018-11-27 05:00 | 536 | 535
2018-11-27 05:30 | 560 | 560
2018-11-27 06:00 | 556 | 556
2018-11-27 06:30 | 555 | 555
2018-11-27 07:00 | 530 | 529
2018-11-27 07:30 | 510 | 509
2018-11-27 08:00 | 562 | 561
2018-11-27 08:30 | 538 | 537
2018-11-27 09:00 | 541 | 540
2018-11-27 09:30 | 528 | 527
2018-11-27 10:00 | 517 | 515
2018-11-27 10:30 | 490 | 489
2018-11-27 11:00 | 492 | 491
2018-11-27 11:30 | 501 | 499
2018-11-27 12:00 | 561 | 560
2018-11-27 12:30 | 626 | 626
2018-11-27 13:00 | 575 | 575
2018-11-27 13:30 | 588 | 588
2018-11-27 14:00 | 577 | 576
2018-11-27 14:30 | 576 | 575
2018-11-27 15:00 | 579 | 579
2018-11-27 15:30 | 708 | 708
2018-11-27 16:00 | 711 | 711
2018-11-27 16:30 | 712 | 712
2018-11-27 17:00 | 741 | 740
2018-11-27 17:30 | 798 | 796
2018-11-27 18:00 | 827 | 824
2018-11-27 18:30 | 844 | 837
2018-11-27 19:00 | 858 | 852
2018-11-27 19:30 | 853 | 850
2018-11-27 20:00 | 821 | 819
2018-11-27 20:30 | 768 | 766
2018-11-27 21:00 | 809 | 807
2018-11-27 21:30 | 835 | 832
2018-11-27 22:00 | 791 | 788
2018-11-27 22:30 | 772 | 769
2018-11-27 23:00 | 749 | 747
2018-11-27 23:30 | 683 | 682
2018-11-28 | 647 | 647
2018-11-28 00:30 | 629 | 629
2018-11-28 01:00 | 611 | 610
2018-11-28 01:30 | 613 | 613
2018-11-28 02:00 | 601 | 601
2018-11-28 02:30 | 597 | 597
2018-11-28 03:00 | 589 | 589
2018-11-28 03:30 | 583 | 583
2018-11-28 04:00 | 585 | 585
2018-11-28 04:30 | 580 | 580
2018-11-28 05:00 | 573 | 573
2018-11-28 05:30 | 578 | 578
2018-11-28 06:00 | 589 | 589
2018-11-28 06:30 | 579 | 578
2018-11-28 07:00 | 548 | 548
2018-11-28 07:30 | 526 | 526
2018-11-28 08:00 | 476 | 475
2018-11-28 08:30 | 450 | 447
2018-11-28 09:00 | 466 | 463
2018-11-28 09:30 | 482 | 479
2018-11-28 10:00 | 462 | 459
2018-11-28 10:30 | 484 | 482
2018-11-28 11:00 | 512 | 510
2018-11-28 11:30 | 516 | 514
2018-11-28 12:00 | 560 | 558
2018-11-28 12:30 | 569 | 569
2018-11-28 13:00 | 538 | 537
2018-11-28 13:30 | 562 | 561
2018-11-28 14:00 | 567 | 566
2018-11-28 14:30 | 576 | 576
2018-11-28 15:00 | 638 | 637
2018-11-28 15:30 | 633 | 633
2018-11-28 16:00 | 653 | 653
2018-11-28 16:30 | 661 | 661
2018-11-28 17:00 | 623 | 622
2018-11-28 17:30 | 625 | 624
2018-11-28 18:00 | 631 | 630
2018-11-28 18:30 | 648 | 647
2018-11-28 19:00 | 690 | 689
2018-11-28 19:30 | 707 | 706
2018-11-28 20:00 | 690 | 689
2018-11-28 20:30 | 705 | 705
2018-11-28 21:00 | 756 | 756
2018-11-28 21:30 | 810 | 809
2018-11-28 22:00 | 795 | 792
2018-11-28 22:30 | 750 | 748
2018-11-28 23:00 | 697 | 695
2018-11-28 23:30 | 643 | 642
2018-11-29 | 610 | 610
2018-11-29 00:30 | 584 | 584
2018-11-29 01:00 | 582 | 582
2018-11-29 01:30 | 568 | 568
2018-11-29 02:00 | 565 | 565
2018-11-29 02:30 | 557 | 557
2018-11-29 03:00 | 526 | 526
2018-11-29 03:30 | 530 | 530
2018-11-29 04:00 | 539 | 538
2018-11-29 04:30 | 545 | 545
2018-11-29 05:00 | 553 | 553
2018-11-29 05:30 | 558 | 557
2018-11-29 06:00 | 554 | 554
2018-11-29 06:30 | 550 | 550
2018-11-29 07:00 | 526 | 525
2018-11-29 07:30 | 503 | 502
2018-11-29 08:00 | 456 | 453
2018-11-29 08:30 | 422 | 419
2018-11-29 09:00 | 393 | 389
2018-11-29 09:30 | 333 | 327
2018-11-29 10:00 | 343 | 334
2018-11-29 10:30 | 359 | 351
2018-11-29 11:00 | 368 | 360
2018-11-29 11:30 | 386 | 380
2018-11-29 12:00 | 398 | 393
2018-11-29 12:30 | 416 | 411
2018-11-29 13:00 | 427 | 423
2018-11-29 13:30 | 487 | 483
2018-11-29 14:00 | 509 | 507
2018-11-29 14:30 | 518 | 516
2018-11-29 15:00 | 528 | 526
2018-11-29 15:30 | 581 | 580
2018-11-29 16:00 | 608 | 607
2018-11-29 16:30 | 610 | 610
2018-11-29 17:00 | 622 | 622
2018-11-29 17:30 | 705 | 704
2018-11-29 18:00 | 743 | 743
2018-11-29 18:30 | 766 | 765
2018-11-29 19:00 | 784 | 782
2018-11-29 19:30 | 763 | 760
2018-11-29 20:00 | 750 | 747
2018-11-29 20:30 | 738 | 736
2018-11-29 21:00 | 749 | 747
2018-11-29 21:30 | 765 | 763
2018-11-29 22:00 | 792 | 790
2018-11-29 22:30 | 754 | 751
2018-11-29 23:00 | 716 | 714
2018-11-29 23:30 | 680 | 679
2018-11-30 | 661 | 660
2018-11-30 00:30 | 644 | 644
2018-11-30 01:00 | 625 | 625
2018-11-30 01:30 | 612 | 612
2018-11-30 02:00 | 602 | 602
2018-11-30 02:30 | 591 | 591
2018-11-30 03:00 | 581 | 580
2018-11-30 03:30 | 573 | 573
2018-11-30 04:00 | 569 | 569
2018-11-30 04:30 | 568 | 567
2018-11-30 05:00 | 566 | 565
2018-11-30 05:30 | 574 | 574
2018-11-30 06:00 | 569 | 568
2018-11-30 06:30 | 542 | 541
2018-11-30 07:00 | 494 | 492
2018-11-30 07:30 | 435 | 431
2018-11-30 08:00 | 381 | 375
2018-11-30 08:30 | 373 | 364
2018-11-30 09:00 | 360 | 351
2018-11-30 09:30 | 394 | 385
2018-11-30 10:00 | 397 | 389
2018-11-30 10:30 | 389 | 382
2018-11-30 11:00 | 397 | 390
2018-11-30 11:30 | 406 | 399
2018-11-30 12:00 | 427 | 421
2018-11-30 12:30 | 446 | 440
2018-11-30 13:00 | 460 | 455
2018-11-30 13:30 | 474 | 469
2018-11-30 14:00 | 491 | 486
2018-11-30 14:30 | 511 | 507
2018-11-30 15:00 | 524 | 521
2018-11-30 15:30 | 543 | 541
2018-11-30 16:00 | 548 | 546
2018-11-30 16:30 | 595 | 593
2018-11-30 17:00 | 640 | 639
2018-11-30 17:30 | 696 | 695
2018-11-30 18:00 | 765 | 765
2018-11-30 18:30 | 810 | 810
2018-11-30 19:00 | 785 | 783
2018-11-30 19:30 | 825 | 824
2018-11-30 20:00 | 823 | 823
2018-11-30 20:30 | 818 | 817
2018-11-30 21:00 | 807 | 807
2018-11-30 21:30 | 776 | 776
2018-11-30 22:00 | 751 | 751
2018-11-30 22:30 | 723 | 723
2018-11-30 23:00 | 699 | 699
2018-11-30 23:30 | 669 | 669
2018-12-01 | 651 | 651
2018-12-01 00:30 | 655 | 655
2018-12-01 01:00 | 637 | 637
2018-12-01 01:30 | 626 | 626
2018-12-01 02:00 | 610 | 610
2018-12-01 02:30 | 599 | 599
2018-12-01 03:00 | 597 | 597
2018-12-01 03:30 | 594 | 593
2018-12-01 04:00 | 585 | 585
2018-12-01 04:30 | 582 | 581
2018-12-01 05:00 | 576 | 575
2018-12-01 05:30 | 567 | 566
2018-12-01 06:00 | 544 | 544
2018-12-01 06:30 | 514 | 513
2018-12-01 07:00 | 463 | 460
2018-12-01 07:30 | 420 | 415
2018-12-01 08:00 | 399 | 392
2018-12-01 08:30 | 405 | 397
2018-12-01 09:00 | 407 | 399
2018-12-01 09:30 | 377 | 368
2018-12-01 10:00 | 373 | 363
2018-12-01 10:30 | 364 | 354
2018-12-01 11:00 | 366 | 356
2018-12-01 11:30 | 373 | 363
2018-12-01 12:00 | 386 | 377
2018-12-01 12:30 | 397 | 389
2018-12-01 13:00 | 415 | 408
2018-12-01 13:30 | 427 | 422
2018-12-01 14:00 | 458 | 453
2018-12-01 14:30 | 472 | 468
2018-12-01 15:00 | 490 | 487
2018-12-01 15:30 | 506 | 503
2018-12-01 16:00 | 534 | 532
2018-12-01 16:30 | 592 | 591
2018-12-01 17:00 | 632 | 632
2018-12-01 17:30 | 686 | 686
2018-12-01 18:00 | 749 | 748
2018-12-01 18:30 | 815 | 814
2018-12-01 19:00 | 838 | 836
2018-12-01 19:30 | 848 | 846
2018-12-01 20:00 | 856 | 854
2018-12-01 20:30 | 853 | 851
2018-12-01 21:00 | 815 | 813
2018-12-01 21:30 | 771 | 770
2018-12-01 22:00 | 743 | 742
2018-12-01 22:30 | 678 | 677
2018-12-01 23:00 | 526 | 526
2018-12-01 23:30 | 511 | 510
2018-12-02 | 515 | 515
2018-12-02 00:30 | 514 | 514
2018-12-02 01:00 | 500 | 499
2018-12-02 01:30 | 482 | 481
2018-12-02 02:00 | 474 | 473
2018-12-02 02:30 | 456 | 455
2018-12-02 03:00 | 445 | 443
2018-12-02 03:30 | 446 | 445
2018-12-02 04:00 | 445 | 444
2018-12-02 04:30 | 451 | 449
2018-12-02 05:00 | 456 | 454
2018-12-02 05:30 | 456 | 454
2018-12-02 06:00 | 437 | 435
2018-12-02 06:30 | 414 | 410
2018-12-02 07:00 | 361 | 354
2018-12-02 07:30 | 339 | 329
2018-12-02 08:00 | 296 | 282
2018-12-02 08:30 | 313 | 299
2018-12-02 09:00 | 311 | 296
2018-12-02 09:30 | 305 | 289
2018-12-02 10:00 | 295 | 278
2018-12-02 10:30 | 297 | 281
2018-12-02 11:00 | 375 | 363
2018-12-02 11:30 | 388 | 379
2018-12-02 12:00 | 411 | 402
2018-12-02 12:30 | 423 | 416
2018-12-02 13:00 | 426 | 420
2018-12-02 13:30 | 429 | 424
2018-12-02 14:00 | 440 | 435
2018-12-02 14:30 | 469 | 465
2018-12-02 15:00 | 473 | 468
2018-12-02 15:30 | 491 | 488
2018-12-02 16:00 | 446 | 443
2018-12-02 16:30 | 421 | 417
2018-12-02 17:00 | 470 | 467
2018-12-02 17:30 | 558 | 556
2018-12-02 18:00 | 639 | 638
2018-12-02 18:30 | 685 | 685
2018-12-02 19:00 | 670 | 668
2018-12-02 19:30 | 649 | 648
2018-12-02 20:00 | 627 | 627
2018-12-02 20:30 | 612 | 612
2018-12-02 21:00 | 651 | 651
2018-12-02 21:30 | 725 | 725
2018-12-02 22:00 | 773 | 773
2018-12-02 22:30 | 742 | 741
2018-12-02 23:00 | 711 | 710
2018-12-02 23:30 | 676 | 675
2018-12-03 | 658 | 657
2018-12-03 00:30 | 642 | 642
2018-12-03 01:00 | 623 | 622
2018-12-03 01:30 | 594 | 594
2018-12-03 02:00 | 545 | 545
2018-12-03 02:30 | 535 | 535
2018-12-03 03:00 | 522 | 522
2018-12-03 03:30 | 519 | 519
2018-12-03 04:00 | 518 | 518
2018-12-03 04:30 | 508 | 508
2018-12-03 05:00 | 482 | 482
2018-12-03 05:30 | 448 | 448
2018-12-03 06:00 | 453 | 453
2018-12-03 06:30 | 472 | 472
2018-12-03 07:00 | 431 | 431
2018-12-03 07:30 | 406 | 404
2018-12-03 08:00 | 388 | 384
2018-12-03 08:30 | 397 | 392
2018-12-03 09:00 | 354 | 347
2018-12-03 09:30 | 321 | 311
2018-12-03 10:00 | 298 | 285
2018-12-03 10:30 | 279 | 264
2018-12-03 11:00 | 287 | 272
2018-12-03 11:30 | 304 | 289
2018-12-03 12:00 | 323 | 310
2018-12-03 12:30 | 343 | 332
2018-12-03 13:00 | 346 | 336
2018-12-03 13:30 | 347 | 337
2018-12-03 14:00 | 375 | 366
2018-12-03 14:30 | 379 | 372
2018-12-03 15:00 | 304 | 296
2018-12-03 15:30 | 398 | 390
2018-12-03 16:00 | 452 | 448
2018-12-03 16:30 | 525 | 523
2018-12-03 17:00 | 644 | 643
2018-12-03 17:30 | 714 | 713
2018-12-03 18:00 | 725 | 724
2018-12-03 18:30 | 760 | 759
2018-12-03 19:00 | 819 | 818
2018-12-03 19:30 | 785 | 781
2018-12-03 20:00 | 695 | 693
2018-12-03 20:30 | 647 | 647
2018-12-03 21:00 | 609 | 609
2018-12-03 21:30 | 586 | 586
2018-12-03 22:00 | 563 | 563
2018-12-03 22:30 | 519 | 519
2018-12-03 23:00 | 481 | 480
2018-12-03 23:30 | 460 | 459
2018-12-04 | 503 | 502
2018-12-04 00:30 | 523 | 522
2018-12-04 01:00 | 471 | 471
2018-12-04 01:30 | 454 | 453
2018-12-04 02:00 | 412 | 411
2018-12-04 02:30 | 452 | 450
2018-12-04 03:00 | 444 | 443
2018-12-04 03:30 | 436 | 435
2018-12-04 04:00 | 444 | 443
2018-12-04 04:30 | 465 | 464
2018-12-04 05:00 | 476 | 475
2018-12-04 05:30 | 497 | 497
2018-12-04 06:00 | 468 | 467
2018-12-04 06:30 | 411 | 410
2018-12-04 07:00 | 369 | 366
2018-12-04 07:30 | 338 | 333
2018-12-04 08:00 | 311 | 302
2018-12-04 08:30 | 294 | 284
2018-12-04 09:00 | 279 | 266
2018-12-04 09:30 | 270 | 255
2018-12-04 10:00 | 238 | 221
2018-12-04 10:30 | 280 | 263
2018-12-04 11:00 | 300 | 287
2018-12-04 11:30 | 304 | 292
2018-12-04 12:00 | 320 | 308
2018-12-04 12:30 | 331 | 320
2018-12-04 13:00 | 342 | 332
2018-12-04 13:30 | 353 | 344
2018-12-04 14:00 | 393 | 386
2018-12-04 14:30 | 353 | 347
2018-12-04 15:00 | 392 | 385
2018-12-04 15:30 | 422 | 417
2018-12-04 16:00 | 486 | 483
2018-12-04 16:30 | 544 | 543
2018-12-04 17:00 | 600 | 600
2018-12-04 17:30 | 696 | 696
2018-12-04 18:00 | 703 | 702
2018-12-04 18:30 | 710 | 710
2018-12-04 19:00 | 745 | 745
2018-12-04 19:30 | 754 | 754
2018-12-04 20:00 | 783 | 782
2018-12-04 20:30 | 797 | 795
2018-12-04 21:00 | 765 | 763
2018-12-04 21:30 | 713 | 712
2018-12-04 22:00 | 683 | 682
2018-12-04 22:30 | 708 | 707
2018-12-04 23:00 | 688 | 687
2018-12-04 23:30 | 645 | 645
2018-12-05 | 629 | 629
2018-12-05 00:30 | 640 | 640
2018-12-05 01:00 | 625 | 625
2018-12-05 01:30 | 616 | 616
2018-12-05 02:00 | 618 | 618
2018-12-05 02:30 | 616 | 616
2018-12-05 03:00 | 606 | 606
2018-12-05 03:30 | 598 | 598
2018-12-05 04:00 | 590 | 590
2018-12-05 04:30 | 589 | 589
2018-12-05 05:00 | 590 | 590
2018-12-05 05:30 | 607 | 607
2018-12-05 06:00 | 612 | 611
2018-12-05 06:30 | 612 | 612
2018-12-05 07:00 | 598 | 598
2018-12-05 07:30 | 579 | 578
2018-12-05 08:00 | 518 | 518
2018-12-05 08:30 | 486 | 484
2018-12-05 09:00 | 492 | 489
2018-12-05 09:30 | 477 | 474
2018-12-05 10:00 | 437 | 434
2018-12-05 10:30 | 418 | 414
2018-12-05 11:00 | 415 | 410
2018-12-05 11:30 | 435 | 430
2018-12-05 12:00 | 451 | 447
2018-12-05 12:30 | 457 | 454
2018-12-05 13:00 | 475 | 472
2018-12-05 13:30 | 446 | 444
2018-12-05 14:00 | 449 | 446
2018-12-05 14:30 | 399 | 396
2018-12-05 15:00 | 446 | 443
2018-12-05 15:30 | 494 | 492
2018-12-05 16:00 | 508 | 508
2018-12-05 16:30 | 531 | 530
2018-12-05 17:00 | 547 | 547
2018-12-05 17:30 | 631 | 631
2018-12-05 18:00 | 698 | 698
2018-12-05 18:30 | 696 | 696
2018-12-05 19:00 | 756 | 756
2018-12-05 19:30 | 781 | 780
2018-12-05 20:00 | 717 | 715
2018-12-05 20:30 | 675 | 674
2018-12-05 21:00 | 673 | 673
2018-12-05 21:30 | 656 | 656
2018-12-05 22:00 | 619 | 619
2018-12-05 22:30 | 595 | 595
2018-12-05 23:00 | 581 | 581
2018-12-05 23:30 | 543 | 542
2018-12-06 | 535 | 534
2018-12-06 00:30 | 528 | 527
2018-12-06 01:00 | 501 | 501
2018-12-06 01:30 | 504 | 502
2018-12-06 02:00 | 514 | 513
2018-12-06 02:30 | 519 | 517
2018-12-06 03:00 | 503 | 502
2018-12-06 03:30 | 512 | 511
2018-12-06 04:00 | 526 | 525
2018-12-06 04:30 | 526 | 525
2018-12-06 05:00 | 536 | 535
2018-12-06 05:30 | 547 | 546
2018-12-06 06:00 | 477 | 477
2018-12-06 06:30 | 525 | 523
2018-12-06 07:00 | 491 | 489
2018-12-06 07:30 | 534 | 532
2018-12-06 08:00 | 554 | 552
2018-12-06 08:30 | 555 | 554
2018-12-06 09:00 | 533 | 532
2018-12-06 09:30 | 483 | 481
2018-12-06 10:00 | 401 | 398
2018-12-06 10:30 | 354 | 348
2018-12-06 11:00 | 334 | 326
2018-12-06 11:30 | 336 | 325
2018-12-06 12:00 | 366 | 356
2018-12-06 12:30 | 420 | 412
2018-12-06 13:00 | 422 | 416
2018-12-06 13:30 | 402 | 396
2018-12-06 14:00 | 417 | 410
2018-12-06 14:30 | 438 | 432
2018-12-06 15:00 | 472 | 466
2018-12-06 15:30 | 546 | 542
2018-12-06 16:00 | 551 | 549
2018-12-06 16:30 | 578 | 576
2018-12-06 17:00 | 585 | 585
2018-12-06 17:30 | 607 | 607
2018-12-06 18:00 | 594 | 594
2018-12-06 18:30 | 568 | 568
2018-12-06 19:00 | 576 | 576
2018-12-06 19:30 | 613 | 613
2018-12-06 20:00 | 605 | 605
2018-12-06 20:30 | 583 | 583
2018-12-06 21:00 | 577 | 577
2018-12-06 21:30 | 605 | 605
2018-12-06 22:00 | 594 | 594
2018-12-06 22:30 | 592 | 592
2018-12-06 23:00 | 560 | 560
2018-12-06 23:30 | 534 | 534
2018-12-07 | 514 | 514
2018-12-07 00:30 | 511 | 510
2018-12-07 01:00 | 473 | 472
2018-12-07 01:30 | 461 | 459
2018-12-07 02:00 | 447 | 445
2018-12-07 02:30 | 437 | 435
2018-12-07 03:00 | 445 | 442
2018-12-07 03:30 | 460 | 457
2018-12-07 04:00 | 451 | 448
2018-12-07 04:30 | 459 | 456
2018-12-07 05:00 | 477 | 475
2018-12-07 05:30 | 502 | 500
2018-12-07 06:00 | 491 | 489
2018-12-07 06:30 | 482 | 480
2018-12-07 07:00 | 509 | 507
2018-12-07 07:30 | 528 | 526
2018-12-07 08:00 | 522 | 520
2018-12-07 08:30 | 508 | 505
2018-12-07 09:00 | 496 | 493
2018-12-07 09:30 | 433 | 430
2018-12-07 10:00 | 427 | 422
2018-12-07 10:30 | 405 | 399
2018-12-07 11:00 | 360 | 353
2018-12-07 11:30 | 402 | 394
2018-12-07 12:00 | 389 | 382
2018-12-07 12:30 | 362 | 355
2018-12-07 13:00 | 375 | 368
2018-12-07 13:30 | 446 | 440
2018-12-07 14:00 | 465 | 462
2018-12-07 14:30 | 448 | 445
2018-12-07 15:00 | 454 | 450
2018-12-07 15:30 | 454 | 451
2018-12-07 16:00 | 474 | 471
2018-12-07 16:30 | 468 | 465
2018-12-07 17:00 | 479 | 477
2018-12-07 17:30 | 492 | 491
2018-12-07 18:00 | 459 | 458
2018-12-07 18:30 | 466 | 465
2018-12-07 19:00 | 487 | 486
2018-12-07 19:30 | 495 | 494
2018-12-07 20:00 | 488 | 488
2018-12-07 20:30 | 469 | 468
2018-12-07 21:00 | 480 | 479
2018-12-07 21:30 | 498 | 497
2018-12-07 22:00 | 500 | 499
2018-12-07 22:30 | 495 | 494
2018-12-07 23:00 | 509 | 508
2018-12-07 23:30 | 520 | 519
2018-12-08 | 503 | 502
2018-12-08 00:30 | 528 | 528
2018-12-08 01:00 | 495 | 495
2018-12-08 01:30 | 462 | 461
2018-12-08 02:00 | 459 | 458
2018-12-08 02:30 | 458 | 457
2018-12-08 03:00 | 469 | 467
2018-12-08 03:30 | 463 | 462
2018-12-08 04:00 | 461 | 460
2018-12-08 04:30 | 440 | 438
2018-12-08 05:00 | 448 | 447
2018-12-08 05:30 | 452 | 450
2018-12-08 06:00 | 445 | 443
2018-12-08 06:30 | 411 | 409
2018-12-08 07:00 | 398 | 394
2018-12-08 07:30 | 384 | 380
2018-12-08 08:00 | 377 | 372
2018-12-08 08:30 | 393 | 387
2018-12-08 09:00 | 362 | 357
2018-12-08 09:30 | 330 | 322
2018-12-08 10:00 | 302 | 291
2018-12-08 10:30 | 288 | 275
2018-12-08 11:00 | 261 | 246
2018-12-08 11:30 | 271 | 254
2018-12-08 12:00 | 296 | 281
2018-12-08 12:30 | 288 | 274
2018-12-08 13:00 | 307 | 293
2018-12-08 13:30 | 335 | 324
2018-12-08 14:00 | 379 | 371
2018-12-08 14:30 | 413 | 408
2018-12-08 15:00 | 461 | 457
2018-12-08 15:30 | 489 | 487
2018-12-08 16:00 | 478 | 477
2018-12-08 16:30 | 495 | 493
2018-12-08 17:00 | 518 | 517
2018-12-08 17:30 | 558 | 557
2018-12-08 18:00 | 593 | 593
2018-12-08 18:30 | 632 | 632
2018-12-08 19:00 | 645 | 645
2018-12-08 19:30 | 647 | 647
2018-12-08 20:00 | 628 | 628
2018-12-08 20:30 | 615 | 615
2018-12-08 21:00 | 576 | 576
2018-12-08 21:30 | 574 | 574
2018-12-08 22:00 | 529 | 529
2018-12-08 22:30 | 511 | 511
2018-12-08 23:00 | 505 | 504
2018-12-08 23:30 | 495 | 495
2018-12-09 | 526 | 526
2018-12-09 00:30 | 540 | 540
2018-12-09 01:00 | 509 | 509
2018-12-09 01:30 | 490 | 489
2018-12-09 02:00 | 485 | 484
2018-12-09 02:30 | 483 | 482
2018-12-09 03:00 | 484 | 483
2018-12-09 03:30 | 474 | 473
2018-12-09 04:00 | 484 | 483
2018-12-09 04:30 | 488 | 487
2018-12-09 05:00 | 502 | 501
2018-12-09 05:30 | 506 | 506
2018-12-09 06:00 | 498 | 497
2018-12-09 06:30 | 492 | 491
2018-12-09 07:00 | 484 | 483
2018-12-09 07:30 | 479 | 478
2018-12-09 08:00 | 497 | 495
2018-12-09 08:30 | 464 | 462
2018-12-09 09:00 | 473 | 470
2018-12-09 09:30 | 461 | 459
2018-12-09 10:00 | 384 | 381
2018-12-09 10:30 | 358 | 353
2018-12-09 11:00 | 379 | 374
2018-12-09 11:30 | 429 | 425
2018-12-09 12:00 | 405 | 401
2018-12-09 12:30 | 402 | 398
2018-12-09 13:00 | 418 | 414
2018-12-09 13:30 | 361 | 357
2018-12-09 14:00 | 384 | 379
2018-12-09 14:30 | 408 | 403
2018-12-09 15:00 | 415 | 411
2018-12-09 15:30 | 440 | 437
2018-12-09 16:00 | 469 | 467
2018-12-09 16:30 | 492 | 490
2018-12-09 17:00 | 496 | 495
2018-12-09 17:30 | 513 | 512
2018-12-09 18:00 | 544 | 544
2018-12-09 18:30 | 529 | 529
2018-12-09 19:00 | 541 | 541
2018-12-09 19:30 | 531 | 530
2018-12-09 20:00 | 476 | 475
2018-12-09 20:30 | 505 | 504
2018-12-09 21:00 | 513 | 513
2018-12-09 21:30 | 493 | 493
2018-12-09 22:00 | 469 | 468
2018-12-09 22:30 | 432 | 431
2018-12-09 23:00 | 382 | 380
2018-12-09 23:30 | 339 | 336
2018-12-10 | 309 | 303
2018-12-10 00:30 | 318 | 312
2018-12-10 01:00 | 297 | 290
2018-12-10 01:30 | 292 | 284
2018-12-10 02:00 | 285 | 276
2018-12-10 02:30 | 283 | 274
2018-12-10 03:00 | 283 | 273
2018-12-10 03:30 | 287 | 277
2018-12-10 04:00 | 274 | 264
2018-12-10 04:30 | 265 | 253
2018-12-10 05:00 | 262 | 251
2018-12-10 05:30 | 276 | 265
2018-12-10 06:00 | 292 | 282
2018-12-10 06:30 | 312 | 303
2018-12-10 07:00 | 291 | 281
2018-12-10 07:30 | 358 | 350
2018-12-10 08:00 | 369 | 363
2018-12-10 08:30 | 337 | 330
2018-12-10 09:00 | 322 | 314
2018-12-10 09:30 | 298 | 288
2018-12-10 10:00 | 222 | 206
2018-12-10 10:30 | 248 | 230
2018-12-10 11:00 | 244 | 227
2018-12-10 11:30 | 281 | 265
2018-12-10 12:00 | 283 | 270
2018-12-10 12:30 | 287 | 274
2018-12-10 13:00 | 269 | 255
2018-12-10 13:30 | 294 | 279
2018-12-10 14:00 | 323 | 311
2018-12-10 14:30 | 315 | 304
2018-12-10 15:00 | 294 | 284
2018-12-10 15:30 | 328 | 318
2018-12-10 16:00 | 352 | 344
2018-12-10 16:30 | 373 | 366
2018-12-10 17:00 | 387 | 381
2018-12-10 17:30 | 398 | 393
2018-12-10 18:00 | 421 | 417
2018-12-10 18:30 | 455 | 451
2018-12-10 19:00 | 490 | 488
2018-12-10 19:30 | 468 | 467
2018-12-10 20:00 | 475 | 474
2018-12-10 20:30 | 451 | 450
2018-12-10 21:00 | 456 | 455
2018-12-10 21:30 | 435 | 434
2018-12-10 22:00 | 433 | 432
2018-12-10 22:30 | 419 | 417
2018-12-10 23:00 | 411 | 408
2018-12-10 23:30 | 390 | 387
2018-12-11 | 393 | 390
2018-12-11 00:30 | 394 | 391
2018-12-11 01:00 | 353 | 349
2018-12-11 01:30 | 324 | 319
2018-12-11 02:00 | 323 | 316
2018-12-11 02:30 | 312 | 304
2018-12-11 03:00 | 319 | 311
2018-12-11 03:30 | 322 | 315
2018-12-11 04:00 | 320 | 313
2018-12-11 04:30 | 327 | 320
2018-12-11 05:00 | 326 | 319
2018-12-11 05:30 | 354 | 347
2018-12-11 06:00 | 367 | 362
2018-12-11 06:30 | 389 | 383
2018-12-11 07:00 | 404 | 398
2018-12-11 07:30 | 383 | 377
2018-12-11 08:00 | 392 | 386
2018-12-11 08:30 | 340 | 333
2018-12-11 09:00 | 313 | 303
2018-12-11 09:30 | 357 | 348
2018-12-11 10:00 | 355 | 346
2018-12-11 10:30 | 349 | 341
2018-12-11 11:00 | 335 | 326
2018-12-11 11:30 | 324 | 314
2018-12-11 12:00 | 361 | 351
2018-12-11 12:30 | 308 | 298
2018-12-11 13:00 | 272 | 254
2018-12-11 13:30 | 275 | 253
2018-12-11 14:00 | 319 | 300
2018-12-11 14:30 | 322 | 307
2018-12-11 15:00 | 335 | 321
2018-12-11 15:30 | 399 | 387
2018-12-11 16:00 | 431 | 422
2018-12-11 16:30 | 373 | 365
2018-12-11 17:00 | 290 | 276
2018-12-11 17:30 | 322 | 307
2018-12-11 18:00 | 373 | 362
2018-12-11 18:30 | 415 | 407
2018-12-11 19:00 | 446 | 441
2018-12-11 19:30 | 463 | 461
2018-12-11 20:00 | 454 | 452
2018-12-11 20:30 | 437 | 434
2018-12-11 21:00 | 473 | 470
2018-12-11 21:30 | 520 | 518
2018-12-11 22:00 | 507 | 506
2018-12-11 22:30 | 482 | 480
2018-12-11 23:00 | 467 | 465
2018-12-11 23:30 | 451 | 447
2018-12-12 | 442 | 439
2018-12-12 00:30 | 441 | 437
2018-12-12 01:00 | 406 | 402
2018-12-12 01:30 | 399 | 394
2018-12-12 02:00 | 391 | 385
2018-12-12 02:30 | 373 | 367
2018-12-12 03:00 | 383 | 377
2018-12-12 03:30 | 391 | 384
2018-12-12 04:00 | 389 | 383
2018-12-12 04:30 | 386 | 380
2018-12-12 05:00 | 388 | 382
2018-12-12 05:30 | 388 | 382
2018-12-12 06:00 | 393 | 387
2018-12-12 06:30 | 409 | 404
2018-12-12 07:00 | 364 | 359
2018-12-12 07:30 | 376 | 368
2018-12-12 08:00 | 379 | 371
2018-12-12 08:30 | 377 | 369
2018-12-12 09:00 | 387 | 379
2018-12-12 09:30 | 335 | 327
2018-12-12 10:00 | 333 | 325
2018-12-12 10:30 | 298 | 287
2018-12-12 11:00 | 296 | 286
2018-12-12 11:30 | 294 | 281
2018-12-12 12:00 | 306 | 294
2018-12-12 12:30 | 318 | 307
2018-12-12 13:00 | 312 | 301
2018-12-12 13:30 | 306 | 294
2018-12-12 14:00 | 276 | 263
2018-12-12 14:30 | 303 | 290
2018-12-12 15:00 | 234 | 220
2018-12-12 15:30 | 267 | 251
2018-12-12 16:00 | 327 | 315
2018-12-12 16:30 | 363 | 354
2018-12-12 17:00 | 349 | 342
2018-12-12 17:30 | 429 | 423
2018-12-12 18:00 | 462 | 458
2018-12-12 18:30 | 461 | 459
2018-12-12 19:00 | 494 | 492
2018-12-12 19:30 | 507 | 506
2018-12-12 20:00 | 507 | 506
2018-12-12 20:30 | 554 | 553
2018-12-12 21:00 | 610 | 610
2018-12-12 21:30 | 599 | 599
2018-12-12 22:00 | 569 | 568
2018-12-12 22:30 | 561 | 561
2018-12-12 23:00 | 542 | 541
2018-12-12 23:30 | 519 | 518
2018-12-13 | 507 | 506
2018-12-13 00:30 | 505 | 504
2018-12-13 01:00 | 480 | 479
2018-12-13 01:30 | 465 | 464
2018-12-13 02:00 | 460 | 458
2018-12-13 02:30 | 454 | 452
2018-12-13 03:00 | 449 | 448
2018-12-13 03:30 | 449 | 447
2018-12-13 04:00 | 439 | 437
2018-12-13 04:30 | 434 | 432
2018-12-13 05:00 | 430 | 428
2018-12-13 05:30 | 416 | 413
2018-12-13 06:00 | 394 | 392
2018-12-13 06:30 | 386 | 383
2018-12-13 07:00 | 352 | 348
2018-12-13 07:30 | 379 | 373
2018-12-13 08:00 | 327 | 320
2018-12-13 08:30 | 340 | 331
2018-12-13 09:00 | 319 | 311
2018-12-13 09:30 | 263 | 252
2018-12-13 10:00 | 303 | 289
2018-12-13 10:30 | 303 | 291
2018-12-13 11:00 | 285 | 271
2018-12-13 11:30 | 246 | 232
2018-12-13 12:00 | 255 | 237
2018-12-13 12:30 | 265 | 249
2018-12-13 13:00 | 278 | 266
2018-12-13 13:30 | 282 | 271
2018-12-13 14:00 | 292 | 280
2018-12-13 14:30 | 251 | 237
2018-12-13 15:00 | 273 | 257
2018-12-13 15:30 | 346 | 334
2018-12-13 16:00 | 387 | 379
2018-12-13 16:30 | 419 | 413
2018-12-13 17:00 | 451 | 448
2018-12-13 17:30 | 522 | 520
2018-12-13 18:00 | 504 | 503
2018-12-13 18:30 | 513 | 512
2018-12-13 19:00 | 503 | 502
2018-12-13 19:30 | 496 | 495
2018-12-13 20:00 | 465 | 464
2018-12-13 20:30 | 499 | 498
2018-12-13 21:00 | 555 | 554
2018-12-13 21:30 | 541 | 541
2018-12-13 22:00 | 515 | 515
2018-12-13 22:30 | 488 | 487
2018-12-13 23:00 | 474 | 473
2018-12-13 23:30 | 468 | 467
2018-12-14 | 414 | 413
2018-12-14 00:30 | 410 | 408
2018-12-14 01:00 | 370 | 367
2018-12-14 01:30 | 352 | 349
2018-12-14 02:00 | 377 | 374
2018-12-14 02:30 | 389 | 387
2018-12-14 03:00 | 422 | 420
2018-12-14 03:30 | 441 | 439
2018-12-14 04:00 | 448 | 447
2018-12-14 04:30 | 450 | 449
2018-12-14 05:00 | 452 | 452
2018-12-14 05:30 | 465 | 464
2018-12-14 06:00 | 463 | 462
2018-12-14 06:30 | 451 | 450
2018-12-14 07:00 | 448 | 447
2018-12-14 07:30 | 420 | 419
2018-12-14 08:00 | 405 | 402
2018-12-14 08:30 | 374 | 370
2018-12-14 09:00 | 294 | 287
2018-12-14 09:30 | 295 | 285
2018-12-14 10:00 | 305 | 295
2018-12-14 10:30 | 283 | 272
2018-12-14 11:00 | 268 | 256
2018-12-14 11:30 | 299 | 287
2018-12-14 12:00 | 326 | 317
2018-12-14 12:30 | 272 | 262
2018-12-14 13:00 | 302 | 290
2018-12-14 13:30 | 305 | 295
2018-12-14 14:00 | 348 | 340
2018-12-14 14:30 | 444 | 437
2018-12-14 15:00 | 476 | 473
2018-12-14 15:30 | 518 | 516
2018-12-14 16:00 | 458 | 457
2018-12-14 16:30 | 453 | 451
2018-12-14 17:00 | 523 | 520
2018-12-14 17:30 | 532 | 531
2018-12-14 18:00 | 556 | 555
2018-12-14 18:30 | 561 | 560
2018-12-14 19:00 | 569 | 569
2018-12-14 19:30 | 571 | 571
2018-12-14 20:00 | 546 | 546
2018-12-14 20:30 | 573 | 573
2018-12-14 21:00 | 625 | 625
2018-12-14 21:30 | 614 | 614
2018-12-14 22:00 | 586 | 586
2018-12-14 22:30 | 555 | 555
2018-12-14 23:00 | 538 | 537
2018-12-14 23:30 | 523 | 523
2018-12-15 | 512 | 511
2018-12-15 00:30 | 511 | 510
2018-12-15 01:00 | 482 | 481
2018-12-15 01:30 | 491 | 490
2018-12-15 02:00 | 493 | 492
2018-12-15 02:30 | 486 | 486
2018-12-15 03:00 | 478 | 477
2018-12-15 03:30 | 472 | 471
2018-12-15 04:00 | 467 | 466
2018-12-15 04:30 | 454 | 453
2018-12-15 05:00 | 460 | 459
2018-12-15 05:30 | 467 | 466
2018-12-15 06:00 | 469 | 468
2018-12-15 06:30 | 475 | 474
2018-12-15 07:00 | 468 | 467
2018-12-15 07:30 | 450 | 449
2018-12-15 08:00 | 458 | 456
2018-12-15 08:30 | 436 | 434
2018-12-15 09:00 | 430 | 428
2018-12-15 09:30 | 436 | 433
2018-12-15 10:00 | 405 | 403
2018-12-15 10:30 | 441 | 439
2018-12-15 11:00 | 387 | 385
2018-12-15 11:30 | 450 | 447
2018-12-15 12:00 | 412 | 409
2018-12-15 12:30 | 432 | 429
2018-12-15 13:00 | 438 | 435
2018-12-15 13:30 | 478 | 475
2018-12-15 14:00 | 466 | 464
2018-12-15 14:30 | 500 | 499
2018-12-15 15:00 | 493 | 492
2018-12-15 15:30 | 485 | 484
2018-12-15 16:00 | 539 | 538
2018-12-15 16:30 | 562 | 561
2018-12-15 17:00 | 552 | 552
2018-12-15 17:30 | 569 | 569
2018-12-15 18:00 | 587 | 587
2018-12-15 18:30 | 618 | 618
2018-12-15 19:00 | 641 | 641
2018-12-15 19:30 | 624 | 624
2018-12-15 20:00 | 610 | 610
2018-12-15 20:30 | 563 | 563
2018-12-15 21:00 | 538 | 538
2018-12-15 21:30 | 518 | 518
2018-12-15 22:00 | 500 | 499
2018-12-15 22:30 | 481 | 480
2018-12-15 23:00 | 457 | 456
2018-12-15 23:30 | 424 | 422
2018-12-16 | 402 | 400
2018-12-16 00:30 | 416 | 414
2018-12-16 01:00 | 385 | 383
2018-12-16 01:30 | 368 | 364
2018-12-16 02:00 | 367 | 363
2018-12-16 02:30 | 366 | 362
2018-12-16 03:00 | 362 | 358
2018-12-16 03:30 | 361 | 357
2018-12-16 04:00 | 338 | 334
2018-12-16 04:30 | 351 | 345
2018-12-16 05:00 | 350 | 345
2018-12-16 05:30 | 328 | 322
2018-12-16 06:00 | 337 | 330
2018-12-16 06:30 | 365 | 359
2018-12-16 07:00 | 381 | 376
2018-12-16 07:30 | 404 | 400
2018-12-16 08:00 | 420 | 416
2018-12-16 08:30 | 432 | 429
2018-12-16 09:00 | 430 | 428
2018-12-16 09:30 | 414 | 411
2018-12-16 10:00 | 390 | 387
2018-12-16 10:30 | 361 | 357
2018-12-16 11:00 | 321 | 315
2018-12-16 11:30 | 287 | 280
2018-12-16 12:00 | 266 | 256
2018-12-16 12:30 | 276 | 265
2018-12-16 13:00 | 296 | 285
2018-12-16 13:30 | 277 | 265
2018-12-16 14:00 | 292 | 280
2018-12-16 14:30 | 293 | 281
2018-12-16 15:00 | 328 | 319
2018-12-16 15:30 | 323 | 314
2018-12-16 16:00 | 374 | 367
2018-12-16 16:30 | 426 | 421
2018-12-16 17:00 | 457 | 454
2018-12-16 17:30 | 506 | 504
2018-12-16 18:00 | 550 | 549
2018-12-16 18:30 | 580 | 580
2018-12-16 19:00 | 605 | 605
2018-12-16 19:30 | 609 | 609
2018-12-16 20:00 | 599 | 599
2018-12-16 20:30 | 578 | 578
2018-12-16 21:00 | 553 | 553
2018-12-16 21:30 | 531 | 531
2018-12-16 22:00 | 510 | 510
2018-12-16 22:30 | 489 | 488
2018-12-16 23:00 | 456 | 456
2018-12-16 23:30 | 428 | 427
2018-12-17 | 410 | 409
2018-12-17 00:30 | 414 | 412
2018-12-17 01:00 | 387 | 385
2018-12-17 01:30 | 391 | 389
2018-12-17 02:00 | 388 | 385
2018-12-17 02:30 | 384 | 381
2018-12-17 03:00 | 375 | 372
2018-12-17 03:30 | 378 | 374
2018-12-17 04:00 | 373 | 370
2018-12-17 04:30 | 372 | 369
2018-12-17 05:00 | 378 | 375
2018-12-17 05:30 | 379 | 376
2018-12-17 06:00 | 375 | 372
2018-12-17 06:30 | 388 | 385
2018-12-17 07:00 | 388 | 385
2018-12-17 07:30 | 385 | 382
2018-12-17 08:00 | 377 | 374
2018-12-17 08:30 | 371 | 367
2018-12-17 09:00 | 350 | 345
2018-12-17 09:30 | 324 | 319
2018-12-17 10:00 | 323 | 315
2018-12-17 10:30 | 331 | 324
2018-12-17 11:00 | 342 | 335
2018-12-17 11:30 | 349 | 342
2018-12-17 12:00 | 347 | 340
2018-12-17 12:30 | 342 | 334
2018-12-17 13:00 | 351 | 344
2018-12-17 13:30 | 365 | 358
2018-12-17 14:00 | 377 | 371
2018-12-17 14:30 | 397 | 391
2018-12-17 15:00 | 423 | 418
2018-12-17 15:30 | 446 | 442
2018-12-17 16:00 | 472 | 469
2018-12-17 16:30 | 520 | 518
2018-12-17 17:00 | 553 | 551
2018-12-17 17:30 | 593 | 593
2018-12-17 18:00 | 640 | 640
2018-12-17 18:30 | 672 | 672
2018-12-17 19:00 | 706 | 706
2018-12-17 19:30 | 718 | 718
2018-12-17 20:00 | 722 | 722
2018-12-17 20:30 | 709 | 708
2018-12-17 21:00 | 676 | 676
2018-12-17 21:30 | 645 | 645
2018-12-17 22:00 | 612 | 612
2018-12-17 22:30 | 572 | 572
2018-12-17 23:00 | 536 | 536
2018-12-17 23:30 | 506 | 505
2018-12-18 | 488 | 487
2018-12-18 00:30 | 481 | 480
2018-12-18 01:00 | 455 | 454
2018-12-18 01:30 | 460 | 458
2018-12-18 02:00 | 457 | 456
2018-12-18 02:30 | 451 | 449
2018-12-18 03:00 | 447 | 446
2018-12-18 03:30 | 444 | 443
2018-12-18 04:00 | 440 | 438
2018-12-18 04:30 | 431 | 429
2018-12-18 05:00 | 425 | 423
2018-12-18 05:30 | 433 | 431
2018-12-18 06:00 | 436 | 434
2018-12-18 06:30 | 438 | 436
2018-12-18 07:00 | 425 | 422
2018-12-18 07:30 | 416 | 411
2018-12-18 08:00 | 396 | 390
2018-12-18 08:30 | 370 | 364
2018-12-18 09:00 | 359 | 351
2018-12-18 09:30 | 357 | 349
2018-12-18 10:00 | 352 | 344
2018-12-18 10:30 | 355 | 346
2018-12-18 11:00 | 381 | 372
2018-12-18 11:30 | 403 | 395
2018-12-18 12:00 | 419 | 412
2018-12-18 12:30 | 446 | 440
2018-12-18 13:00 | 481 | 476
2018-12-18 13:30 | 494 | 490
2018-12-18 14:00 | 529 | 525
2018-12-18 14:30 | 549 | 546
2018-12-18 15:00 | 582 | 580
2018-12-18 15:30 | 571 | 569
2018-12-18 16:00 | 592 | 590
2018-12-18 16:30 | 626 | 625
2018-12-18 17:00 | 649 | 648
2018-12-18 17:30 | 700 | 699
2018-12-18 18:00 | 738 | 738
2018-12-18 18:30 | 746 | 745
2018-12-18 19:00 | 750 | 749
2018-12-18 19:30 | 771 | 770
2018-12-18 20:00 | 772 | 772
2018-12-18 20:30 | 780 | 779
2018-12-18 21:00 | 761 | 761
2018-12-18 21:30 | 725 | 725
2018-12-18 22:00 | 692 | 691
2018-12-18 22:30 | 650 | 650
2018-12-18 23:00 | 609 | 609
2018-12-18 23:30 | 612 | 612
2018-12-19 | 591 | 590
2018-12-19 00:30 | 578 | 578
2018-12-19 01:00 | 558 | 558
2018-12-19 01:30 | 537 | 537
2018-12-19 02:00 | 523 | 523
2018-12-19 02:30 | 516 | 515
2018-12-19 03:00 | 512 | 511
2018-12-19 03:30 | 508 | 507
2018-12-19 04:00 | 506 | 505
2018-12-19 04:30 | 503 | 503
2018-12-19 05:00 | 505 | 505
2018-12-19 05:30 | 512 | 511
2018-12-19 06:00 | 512 | 512
2018-12-19 06:30 | 496 | 494
2018-12-19 07:00 | 483 | 480
2018-12-19 07:30 | 476 | 472
2018-12-19 08:00 | 439 | 434
2018-12-19 08:30 | 415 | 409
2018-12-19 09:00 | 415 | 409
2018-12-19 09:30 | 397 | 390
2018-12-19 10:00 | 414 | 408
2018-12-19 10:30 | 422 | 416
2018-12-19 11:00 | 429 | 423
2018-12-19 11:30 | 402 | 396
2018-12-19 12:00 | 414 | 406
2018-12-19 12:30 | 444 | 438
2018-12-19 13:00 | 447 | 442
2018-12-19 13:30 | 458 | 452
2018-12-19 14:00 | 487 | 482
2018-12-19 14:30 | 497 | 492
2018-12-19 15:00 | 484 | 480
2018-12-19 15:30 | 504 | 501
2018-12-19 16:00 | 568 | 565
2018-12-19 16:30 | 632 | 631
2018-12-19 17:00 | 628 | 627
2018-12-19 17:30 | 657 | 656
2018-12-19 18:00 | 719 | 719
2018-12-19 18:30 | 744 | 744
2018-12-19 19:00 | 716 | 715
2018-12-19 19:30 | 704 | 703
2018-12-19 20:00 | 731 | 731
2018-12-19 20:30 | 730 | 730
2018-12-19 21:00 | 714 | 714
2018-12-19 21:30 | 704 | 704
2018-12-19 22:00 | 678 | 678
2018-12-19 22:30 | 649 | 649
2018-12-19 23:00 | 611 | 611
2018-12-19 23:30 | 589 | 588
2018-12-20 | 562 | 561
2018-12-20 00:30 | 538 | 537
2018-12-20 01:00 | 513 | 512
2018-12-20 01:30 | 518 | 516
2018-12-20 02:00 | 492 | 491
2018-12-20 02:30 | 490 | 488
2018-12-20 03:00 | 498 | 496
2018-12-20 03:30 | 493 | 491
2018-12-20 04:00 | 491 | 489
2018-12-20 04:30 | 496 | 494
2018-12-20 05:00 | 502 | 500
2018-12-20 05:30 | 509 | 507
2018-12-20 06:00 | 518 | 516
2018-12-20 06:30 | 521 | 519
2018-12-20 07:00 | 514 | 511
2018-12-20 07:30 | 506 | 502
2018-12-20 08:00 | 502 | 496
2018-12-20 08:30 | 468 | 462
2018-12-20 09:00 | 456 | 449
2018-12-20 09:30 | 452 | 444
2018-12-20 10:00 | 359 | 348
2018-12-20 10:30 | 341 | 326
2018-12-20 11:00 | 327 | 311
2018-12-20 11:30 | 347 | 331
2018-12-20 12:00 | 371 | 360
2018-12-20 12:30 | 387 | 379
2018-12-20 13:00 | 394 | 386
2018-12-20 13:30 | 390 | 384
2018-12-20 14:00 | 371 | 365
2018-12-20 14:30 | 367 | 361
2018-12-20 15:00 | 290 | 281
2018-12-20 15:30 | 246 | 232
2018-12-20 16:00 | 309 | 298
2018-12-20 16:30 | 357 | 349
2018-12-20 17:00 | 373 | 367
2018-12-20 17:30 | 442 | 438
2018-12-20 18:00 | 495 | 492
2018-12-20 18:30 | 561 | 560
2018-12-20 19:00 | 530 | 530
2018-12-20 19:30 | 511 | 510
2018-12-20 20:00 | 536 | 535
2018-12-20 20:30 | 611 | 611
2018-12-20 21:00 | 598 | 598
2018-12-20 21:30 | 533 | 533
2018-12-20 22:00 | 502 | 502
2018-12-20 22:30 | 452 | 452
2018-12-20 23:00 | 442 | 442
2018-12-20 23:30 | 426 | 425
2018-12-21 | 417 | 416
2018-12-21 00:30 | 411 | 408
2018-12-21 01:00 | 384 | 381
2018-12-21 01:30 | 383 | 379
2018-12-21 02:00 | 386 | 382
2018-12-21 02:30 | 380 | 376
2018-12-21 03:00 | 370 | 365
2018-12-21 03:30 | 365 | 361
2018-12-21 04:00 | 364 | 359
2018-12-21 04:30 | 364 | 359
2018-12-21 05:00 | 362 | 357
2018-12-21 05:30 | 369 | 364
2018-12-21 06:00 | 374 | 369
2018-12-21 06:30 | 379 | 373
2018-12-21 07:00 | 382 | 367
2018-12-21 07:30 | 344 | 337
2018-12-21 08:00 | 324 | 314
2018-12-21 08:30 | 314 | 301
2018-12-21 09:00 | 295 | 281
2018-12-21 09:30 | 287 | 264
2018-12-21 10:00 | 285 | 263
2018-12-21 10:30 | 292 | 272
2018-12-21 11:00 | 322 | 304
2018-12-21 11:30 | 346 | 332
2018-12-21 12:00 | 340 | 328
2018-12-21 12:30 | 350 | 337
2018-12-21 13:00 | 332 | 319
2018-12-21 13:30 | 320 | 306
2018-12-21 14:00 | 327 | 312
2018-12-21 14:30 | 343 | 330
2018-12-21 15:00 | 349 | 338
2018-12-21 15:30 | 360 | 350
2018-12-21 16:00 | 395 | 386
2018-12-21 16:30 | 396 | 388
2018-12-21 17:00 | 427 | 420
2018-12-21 17:30 | 469 | 463
2018-12-21 18:00 | 522 | 517
2018-12-21 18:30 | 531 | 528
2018-12-21 19:00 | 553 | 551
2018-12-21 19:30 | 559 | 559
2018-12-21 20:00 | 556 | 556
2018-12-21 20:30 | 584 | 584
2018-12-21 21:00 | 578 | 578
2018-12-21 21:30 | 578 | 578
2018-12-21 22:00 | 553 | 553
2018-12-21 22:30 | 524 | 523
2018-12-21 23:00 | 495 | 494
2018-12-21 23:30 | 517 | 515
2018-12-22 | 582 | 582
2018-12-22 00:30 | 583 | 583
2018-12-22 01:00 | 558 | 558
2018-12-22 01:30 | 541 | 541
2018-12-22 02:00 | 531 | 531
2018-12-22 02:30 | 522 | 521
2018-12-22 03:00 | 513 | 512
2018-12-22 03:30 | 511 | 510
2018-12-22 04:00 | 509 | 508
2018-12-22 04:30 | 508 | 507
2018-12-22 05:00 | 505 | 504
2018-12-22 05:30 | 505 | 503
2018-12-22 06:00 | 494 | 492
2018-12-22 06:30 | 477 | 475
2018-12-22 07:00 | 444 | 441
2018-12-22 07:30 | 448 | 443
2018-12-22 08:00 | 466 | 460
2018-12-22 08:30 | 427 | 421
2018-12-22 09:00 | 419 | 411
2018-12-22 09:30 | 369 | 361
2018-12-22 10:00 | 385 | 376
2018-12-22 10:30 | 433 | 426
2018-12-22 11:00 | 439 | 432
2018-12-22 11:30 | 406 | 399
2018-12-22 12:00 | 373 | 364
2018-12-22 12:30 | 471 | 462
2018-12-22 13:00 | 463 | 458
2018-12-22 13:30 | 460 | 454
2018-12-22 14:00 | 397 | 389
2018-12-22 14:30 | 405 | 396
2018-12-22 15:00 | 385 | 376
2018-12-22 15:30 | 377 | 367
2018-12-22 16:00 | 414 | 404
2018-12-22 16:30 | 383 | 374
2018-12-22 17:00 | 453 | 445
2018-12-22 17:30 | 536 | 532
2018-12-22 18:00 | 640 | 638
2018-12-22 18:30 | 695 | 694
2018-12-22 19:00 | 701 | 701
2018-12-22 19:30 | 690 | 690
2018-12-22 20:00 | 698 | 698
2018-12-22 20:30 | 718 | 718
2018-12-22 21:00 | 707 | 707
2018-12-22 21:30 | 689 | 689
2018-12-22 22:00 | 666 | 666
2018-12-22 22:30 | 640 | 639
2018-12-22 23:00 | 620 | 620
2018-12-22 23:30 | 595 | 595
2018-12-23 | 573 | 573
2018-12-23 00:30 | 578 | 577
2018-12-23 01:00 | 553 | 552
2018-12-23 01:30 | 536 | 535
2018-12-23 02:00 | 523 | 522
2018-12-23 02:30 | 518 | 516
2018-12-23 03:00 | 508 | 507
2018-12-23 03:30 | 500 | 499
2018-12-23 04:00 | 497 | 496
2018-12-23 04:30 | 498 | 496
2018-12-23 05:00 | 493 | 492
2018-12-23 05:30 | 496 | 495
2018-12-23 06:00 | 486 | 484
2018-12-23 06:30 | 471 | 469
2018-12-23 07:00 | 432 | 429
2018-12-23 07:30 | 418 | 412
2018-12-23 08:00 | 360 | 352
2018-12-23 08:30 | 341 | 330
2018-12-23 09:00 | 372 | 362
2018-12-23 09:30 | 356 | 347
2018-12-23 10:00 | 307 | 294
2018-12-23 10:30 | 329 | 315
2018-12-23 11:00 | 334 | 320
2018-12-23 11:30 | 322 | 308
2018-12-23 12:00 | 349 | 336
2018-12-23 12:30 | 363 | 350
2018-12-23 13:00 | 383 | 372
2018-12-23 13:30 | 367 | 356
2018-12-23 14:00 | 373 | 363
2018-12-23 14:30 | 362 | 351
2018-12-23 15:00 | 371 | 361
2018-12-23 15:30 | 382 | 375
2018-12-23 16:00 | 411 | 406
2018-12-23 16:30 | 502 | 499
2018-12-23 17:00 | 530 | 528
2018-12-23 17:30 | 598 | 597
2018-12-23 18:00 | 612 | 612
2018-12-23 18:30 | 638 | 638
2018-12-23 19:00 | 656 | 656
2018-12-23 19:30 | 665 | 665
2018-12-23 20:00 | 628 | 628
2018-12-23 20:30 | 604 | 604
2018-12-23 21:00 | 607 | 607
2018-12-23 21:30 | 593 | 593
2018-12-23 22:00 | 577 | 577
2018-12-23 22:30 | 577 | 577
2018-12-23 23:00 | 551 | 550
2018-12-23 23:30 | 520 | 519
2018-12-24 | 521 | 520
2018-12-24 00:30 | 524 | 523
2018-12-24 01:00 | 510 | 509
2018-12-24 01:30 | 501 | 500
2018-12-24 02:00 | 489 | 488
2018-12-24 02:30 | 433 | 432
2018-12-24 03:00 | 416 | 414
2018-12-24 03:30 | 423 | 420
2018-12-24 04:00 | 388 | 386
2018-12-24 04:30 | 355 | 352
2018-12-24 05:00 | 334 | 329
2018-12-24 05:30 | 343 | 337
2018-12-24 06:00 | 339 | 333
2018-12-24 06:30 | 342 | 336
2018-12-24 07:00 | 362 | 355
2018-12-24 07:30 | 354 | 347
2018-12-24 08:00 | 358 | 350
2018-12-24 08:30 | 340 | 330
2018-12-24 09:00 | 337 | 326
2018-12-24 09:30 | 349 | 337
2018-12-24 10:00 | 297 | 283
2018-12-24 10:30 | 259 | 239
2018-12-24 11:00 | 326 | 309
2018-12-24 11:30 | 305 | 289
2018-12-24 12:00 | 299 | 283
2018-12-24 12:30 | 281 | 264
2018-12-24 13:00 | 287 | 270
2018-12-24 13:30 | 311 | 295
2018-12-24 14:00 | 323 | 309
2018-12-24 14:30 | 298 | 285
2018-12-24 15:00 | 292 | 277
2018-12-24 15:30 | 239 | 220
2018-12-24 16:00 | 272 | 254
2018-12-24 16:30 | 307 | 292
2018-12-24 17:00 | 328 | 315
2018-12-24 17:30 | 364 | 353
2018-12-24 18:00 | 390 | 382
2018-12-24 18:30 | 406 | 400
2018-12-24 19:00 | 427 | 423
2018-12-24 19:30 | 429 | 426
2018-12-24 20:00 | 417 | 414
2018-12-24 20:30 | 403 | 400
2018-12-24 21:00 | 398 | 394
2018-12-24 21:30 | 391 | 387
2018-12-24 22:00 | 382 | 378
2018-12-24 22:30 | 373 | 368
2018-12-24 23:00 | 366 | 361
2018-12-24 23:30 | 344 | 338
2018-12-25 | 322 | 315
2018-12-25 00:30 | 345 | 337
2018-12-25 01:00 | 310 | 303
2018-12-25 01:30 | 285 | 277
2018-12-25 02:00 | 269 | 258
2018-12-25 02:30 | 267 | 255
2018-12-25 03:00 | 265 | 250
2018-12-25 03:30 | 264 | 250
2018-12-25 04:00 | 265 | 250
2018-12-25 04:30 | 275 | 262
2018-12-25 05:00 | 280 | 267
2018-12-25 05:30 | 274 | 261
2018-12-25 06:00 | 264 | 251
2018-12-25 06:30 | 248 | 231
2018-12-25 07:00 | 196 | 171
2018-12-25 07:30 | 190 | 158
2018-12-25 08:00 | 149 | 102
2018-12-25 08:30 | 161 | 115
2018-12-25 09:00 | 166 | 123
2018-12-25 09:30 | 156 | 109
2018-12-25 10:00 | 153 | 100
2018-12-25 10:30 | 143 | 82
2018-12-25 11:00 | 157 | 107
2018-12-25 11:30 | 151 | 99
2018-12-25 12:00 | 151 | 97
2018-12-25 12:30 | 150 | 94
2018-12-25 13:00 | 202 | 164
2018-12-25 13:30 | 166 | 108
2018-12-25 14:00 | 160 | 107
2018-12-25 14:30 | 149 | 92
2018-12-25 15:00 | 197 | 157
2018-12-25 15:30 | 220 | 190
2018-12-25 16:00 | 246 | 220
2018-12-25 16:30 | 273 | 252
2018-12-25 17:00 | 321 | 304
2018-12-25 17:30 | 368 | 356
2018-12-25 18:00 | 357 | 348
2018-12-25 18:30 | 410 | 402
2018-12-25 19:00 | 428 | 423
2018-12-25 19:30 | 435 | 432
2018-12-25 20:00 | 425 | 423
2018-12-25 20:30 | 416 | 414
2018-12-25 21:00 | 427 | 424
2018-12-25 21:30 | 395 | 392
2018-12-25 22:00 | 361 | 357
2018-12-25 22:30 | 354 | 349
2018-12-25 23:00 | 332 | 326
2018-12-25 23:30 | 322 | 316
2018-12-26 | 315 | 307
2018-12-26 00:30 | 335 | 327
2018-12-26 01:00 | 318 | 310
2018-12-26 01:30 | 296 | 287
2018-12-26 02:00 | 292 | 282
2018-12-26 02:30 | 276 | 265
2018-12-26 03:00 | 271 | 258
2018-12-26 03:30 | 261 | 247
2018-12-26 04:00 | 273 | 258
2018-12-26 04:30 | 274 | 260
2018-12-26 05:00 | 297 | 285
2018-12-26 05:30 | 276 | 263
2018-12-26 06:00 | 265 | 252
2018-12-26 06:30 | 269 | 256
2018-12-26 07:00 | 213 | 195
2018-12-26 07:30 | 183 | 155
2018-12-26 08:00 | 177 | 143
2018-12-26 08:30 | 154 | 110
2018-12-26 09:00 | 167 | 123
2018-12-26 09:30 | 158 | 105
2018-12-26 10:00 | 159 | 109
2018-12-26 10:30 | 161 | 114
2018-12-26 11:00 | 176 | 134
2018-12-26 11:30 | 180 | 142
2018-12-26 12:00 | 155 | 111
2018-12-26 12:30 | 191 | 154
2018-12-26 13:00 | 214 | 183
2018-12-26 13:30 | 178 | 141
2018-12-26 14:00 | 189 | 154
2018-12-26 14:30 | 227 | 199
2018-12-26 15:00 | 210 | 179
2018-12-26 15:30 | 216 | 187
2018-12-26 16:00 | 248 | 224
2018-12-26 16:30 | 272 | 252
2018-12-26 17:00 | 332 | 317
2018-12-26 17:30 | 387 | 377
2018-12-26 18:00 | 448 | 441
2018-12-26 18:30 | 509 | 505
2018-12-26 19:00 | 522 | 520
2018-12-26 19:30 | 549 | 548
2018-12-26 20:00 | 520 | 520
2018-12-26 20:30 | 483 | 482
2018-12-26 21:00 | 459 | 457
2018-12-26 21:30 | 424 | 421
2018-12-26 22:00 | 431 | 428
2018-12-26 22:30 | 426 | 423
2018-12-26 23:00 | 405 | 402
2018-12-26 23:30 | 391 | 387
2018-12-27 | 368 | 363
2018-12-27 00:30 | 379 | 374
2018-12-27 01:00 | 368 | 362
2018-12-27 01:30 | 351 | 345
2018-12-27 02:00 | 365 | 359
2018-12-27 02:30 | 388 | 383
2018-12-27 03:00 | 360 | 354
2018-12-27 03:30 | 350 | 343
2018-12-27 04:00 | 355 | 348
2018-12-27 04:30 | 345 | 338
2018-12-27 05:00 | 327 | 320
2018-12-27 05:30 | 332 | 324
2018-12-27 06:00 | 324 | 316
2018-12-27 06:30 | 333 | 325
2018-12-27 07:00 | 312 | 303
2018-12-27 07:30 | 270 | 257
2018-12-27 08:00 | 224 | 205
2018-12-27 08:30 | 236 | 214
2018-12-27 09:00 | 224 | 200
2018-12-27 09:30 | 230 | 206
2018-12-27 10:00 | 247 | 226
2018-12-27 10:30 | 228 | 205
2018-12-27 11:00 | 192 | 163
2018-12-27 11:30 | 185 | 153
2018-12-27 12:00 | 194 | 163
2018-12-27 12:30 | 215 | 188
2018-12-27 13:00 | 189 | 159
2018-12-27 13:30 | 164 | 128
2018-12-27 14:00 | 149 | 106
2018-12-27 14:30 | 182 | 146
2018-12-27 15:00 | 180 | 147
2018-12-27 15:30 | 236 | 213
2018-12-27 16:00 | 271 | 253
2018-12-27 16:30 | 284 | 267
2018-12-27 17:00 | 356 | 344
2018-12-27 17:30 | 437 | 430
2018-12-27 18:00 | 452 | 448
2018-12-27 18:30 | 468 | 465
2018-12-27 19:00 | 486 | 484
2018-12-27 19:30 | 501 | 500
2018-12-27 20:00 | 509 | 508
2018-12-27 20:30 | 495 | 495
2018-12-27 21:00 | 482 | 481
2018-12-27 21:30 | 458 | 457
2018-12-27 22:00 | 438 | 437
2018-12-27 22:30 | 423 | 421
2018-12-27 23:00 | 407 | 404
2018-12-27 23:30 | 388 | 385
2018-12-28 | 375 | 371
2018-12-28 00:30 | 373 | 369
2018-12-28 01:00 | 348 | 344
2018-12-28 01:30 | 336 | 330
2018-12-28 02:00 | 324 | 318
2018-12-28 02:30 | 320 | 313
2018-12-28 03:00 | 320 | 313
2018-12-28 03:30 | 318 | 310
2018-12-28 04:00 | 329 | 321
2018-12-28 04:30 | 327 | 320
2018-12-28 05:00 | 329 | 322
2018-12-28 05:30 | 329 | 323
2018-12-28 06:00 | 332 | 325
2018-12-28 06:30 | 308 | 301
2018-12-28 07:00 | 260 | 248
2018-12-28 07:30 | 222 | 203
2018-12-28 08:00 | 175 | 143
2018-12-28 08:30 | 151 | 107
2018-12-28 09:00 | 155 | 109
2018-12-28 09:30 | 164 | 121
2018-12-28 10:00 | 155 | 112
2018-12-28 10:30 | 153 | 111
2018-12-28 11:00 | 158 | 116
2018-12-28 11:30 | 178 | 143
2018-12-28 12:00 | 187 | 154
2018-12-28 12:30 | 195 | 164
2018-12-28 13:00 | 184 | 152
2018-12-28 13:30 | 183 | 150
2018-12-28 14:00 | 190 | 159
2018-12-28 14:30 | 165 | 129
2018-12-28 15:00 | 139 | 95
2018-12-28 15:30 | 166 | 129
2018-12-28 16:00 | 171 | 137
2018-12-28 16:30 | 175 | 142
2018-12-28 17:00 | 183 | 156
2018-12-28 17:30 | 244 | 225
2018-12-28 18:00 | 313 | 302
2018-12-28 18:30 | 353 | 346
2018-12-28 19:00 | 378 | 373
2018-12-28 19:30 | 383 | 380
2018-12-28 20:00 | 428 | 426
2018-12-28 20:30 | 440 | 438
2018-12-28 21:00 | 422 | 421
2018-12-28 21:30 | 448 | 447
2018-12-28 22:00 | 419 | 417
2018-12-28 22:30 | 376 | 374
2018-12-28 23:00 | 414 | 411
2018-12-28 23:30 | 399 | 397
2018-12-29 | 403 | 400
2018-12-29 00:30 | 400 | 396
2018-12-29 01:00 | 364 | 360
2018-12-29 01:30 | 353 | 348
2018-12-29 02:00 | 342 | 336
2018-12-29 02:30 | 333 | 327
2018-12-29 03:00 | 329 | 321
2018-12-29 03:30 | 335 | 328
2018-12-29 04:00 | 320 | 313
2018-12-29 04:30 | 327 | 320
2018-12-29 05:00 | 324 | 318
2018-12-29 05:30 | 329 | 322
2018-12-29 06:00 | 319 | 312
2018-12-29 06:30 | 286 | 278
2018-12-29 07:00 | 260 | 256
2018-12-29 07:30 | 262 | 254
2018-12-29 08:00 | 239 | 225
2018-12-29 08:30 | 278 | 264
2018-12-29 09:00 | 237 | 221
2018-12-29 09:30 | 186 | 161
2018-12-29 10:00 | 226 | 203
2018-12-29 10:30 | 189 | 163
2018-12-29 11:00 | 220 | 197
2018-12-29 11:30 | 219 | 198
2018-12-29 12:00 | 239 | 219
2018-12-29 12:30 | 169 | 142
2018-12-29 13:00 | 198 | 172
2018-12-29 13:30 | 185 | 157
2018-12-29 14:00 | 196 | 171
2018-12-29 14:30 | 218 | 197
2018-12-29 15:00 | 228 | 207
2018-12-29 15:30 | 231 | 212
2018-12-29 16:00 | 256 | 241
2018-12-29 16:30 | 302 | 290
2018-12-29 17:00 | 396 | 389
2018-12-29 17:30 | 434 | 431
2018-12-29 18:00 | 457 | 455
2018-12-29 18:30 | 487 | 485
2018-12-29 19:00 | 525 | 524
2018-12-29 19:30 | 520 | 520
2018-12-29 20:00 | 515 | 514
2018-12-29 20:30 | 507 | 507
2018-12-29 21:00 | 502 | 501
2018-12-29 21:30 | 464 | 464
2018-12-29 22:00 | 450 | 449
2018-12-29 22:30 | 441 | 440
2018-12-29 23:00 | 398 | 397
2018-12-29 23:30 | 390 | 387
2018-12-30 | 353 | 350
2018-12-30 00:30 | 352 | 348
2018-12-30 01:00 | 330 | 326
2018-12-30 01:30 | 327 | 322
2018-12-30 02:00 | 339 | 334
2018-12-30 02:30 | 351 | 346
2018-12-30 03:00 | 331 | 325
2018-12-30 03:30 | 331 | 324
2018-12-30 04:00 | 332 | 325
2018-12-30 04:30 | 335 | 327
2018-12-30 05:00 | 341 | 332
2018-12-30 05:30 | 332 | 323
2018-12-30 06:00 | 335 | 326
2018-12-30 06:30 | 308 | 298
2018-12-30 07:00 | 292 | 279
2018-12-30 07:30 | 268 | 252
2018-12-30 08:00 | 251 | 232
2018-12-30 08:30 | 237 | 214
2018-12-30 09:00 | 241 | 218
2018-12-30 09:30 | 232 | 207
2018-12-30 10:00 | 196 | 162
2018-12-30 10:30 | 196 | 161
2018-12-30 11:00 | 187 | 149
2018-12-30 11:30 | 169 | 125
2018-12-30 12:00 | 162 | 114
2018-12-30 12:30 | 161 | 112
2018-12-30 13:00 | 142 | 80
2018-12-30 13:30 | 128 | 56
2018-12-30 14:00 | 137 | 71
2018-12-30 14:30 | 139 | 76
2018-12-30 15:00 | 148 | 91
2018-12-30 15:30 | 188 | 145
2018-12-30 16:00 | 207 | 175
2018-12-30 16:30 | 230 | 203
2018-12-30 17:00 | 251 | 231
2018-12-30 17:30 | 251 | 234
2018-12-30 18:00 | 269 | 254
2018-12-30 18:30 | 322 | 311
2018-12-30 19:00 | 356 | 349
2018-12-30 19:30 | 402 | 397
2018-12-30 20:00 | 378 | 374
2018-12-30 20:30 | 492 | 488
2018-12-30 21:00 | 494 | 492
2018-12-30 21:30 | 472 | 470
2018-12-30 22:00 | 450 | 448
2018-12-30 22:30 | 433 | 430
2018-12-30 23:00 | 415 | 412
2018-12-30 23:30 | 396 | 393
2018-12-31 | 386 | 383
2018-12-31 00:30 | 388 | 384
2018-12-31 01:00 | 364 | 359
2018-12-31 01:30 | 355 | 350
2018-12-31 02:00 | 335 | 329
2018-12-31 02:30 | 337 | 330
2018-12-31 03:00 | 333 | 326
2018-12-31 03:30 | 315 | 307
2018-12-31 04:00 | 321 | 312
2018-12-31 04:30 | 326 | 316
2018-12-31 05:00 | 322 | 312
2018-12-31 05:30 | 327 | 317
2018-12-31 06:00 | 329 | 319
2018-12-31 06:30 | 317 | 308
2018-12-31 07:00 | 311 | 300
2018-12-31 07:30 | 286 | 271
2018-12-31 08:00 | 287 | 270
2018-12-31 08:30 | 297 | 281
2018-12-31 09:00 | 287 | 271
2018-12-31 09:30 | 240 | 223
2018-12-31 10:00 | 227 | 207
2018-12-31 10:30 | 244 | 224
2018-12-31 11:00 | 181 | 154
2018-12-31 11:30 | 143 | 102
2018-12-31 12:00 | 156 | 112
2018-12-31 12:30 | 161 | 122
2018-12-31 13:00 | 151 | 106
2018-12-31 13:30 | 139 | 90
2018-12-31 14:00 | 150 | 104
2018-12-31 14:30 | 155 | 113
2018-12-31 15:00 | 136 | 90
2018-12-31 15:30 | 205 | 176
2018-12-31 16:00 | 234 | 212
2018-12-31 16:30 | 244 | 226
2018-12-31 17:00 | 312 | 298
2018-12-31 17:30 | 378 | 370
2018-12-31 18:00 | 407 | 401
2018-12-31 18:30 | 448 | 445
2018-12-31 19:00 | 457 | 455
2018-12-31 19:30 | 459 | 457
2018-12-31 20:00 | 451 | 449
2018-12-31 20:30 | 437 | 435
2018-12-31 21:00 | 430 | 428
2018-12-31 21:30 | 407 | 404
2018-12-31 22:00 | 394 | 391
2018-12-31 22:30 | 381 | 378
2018-12-31 23:00 | 376 | 372
2018-12-31 23:30 | 365 | 360
2019-01-01 | 371 | 365
2019-01-01 00:30 | 374 | 369
2019-01-01 01:00 | 344 | 338
2019-01-01 01:30 | 329 | 322
2019-01-01 02:00 | 318 | 309
2019-01-01 02:30 | 304 | 294
2019-01-01 03:00 | 287 | 275
2019-01-01 03:30 | 284 | 271
2019-01-01 04:00 | 280 | 267
2019-01-01 04:30 | 277 | 262
2019-01-01 05:00 | 284 | 270
2019-01-01 05:30 | 284 | 271
2019-01-01 06:00 | 279 | 265
2019-01-01 06:30 | 239 | 223
2019-01-01 07:00 | 194 | 169
2019-01-01 07:30 | 166 | 128
2019-01-01 08:00 | 162 | 116
2019-01-01 08:30 | 161 | 107
2019-01-01 09:00 | 163 | 112
2019-01-01 09:30 | 192 | 149
2019-01-01 10:00 | 175 | 123
2019-01-01 10:30 | 173 | 124
2019-01-01 11:00 | 170 | 120
2019-01-01 11:30 | 153 | 96
2019-01-01 12:00 | 151 | 93
2019-01-01 12:30 | 166 | 116
2019-01-01 13:00 | 155 | 95
2019-01-01 13:30 | 154 | 93
2019-01-01 14:00 | 153 | 88
2019-01-01 14:30 | 157 | 100
2019-01-01 15:00 | 159 | 102
2019-01-01 15:30 | 153 | 93
2019-01-01 16:00 | 167 | 115
2019-01-01 16:30 | 203 | 166
2019-01-01 17:00 | 276 | 252
2019-01-01 17:30 | 382 | 368
2019-01-01 18:00 | 410 | 402
2019-01-01 18:30 | 458 | 453
2019-01-01 19:00 | 495 | 492
2019-01-01 19:30 | 520 | 519
2019-01-01 20:00 | 507 | 506
2019-01-01 20:30 | 487 | 485
2019-01-01 21:00 | 465 | 463
2019-01-01 21:30 | 433 | 431
2019-01-01 22:00 | 413 | 409
2019-01-01 22:30 | 387 | 382
2019-01-01 23:00 | 371 | 365
2019-01-01 23:30 | 357 | 351
2019-01-02 | 348 | 341
2019-01-02 00:30 | 364 | 357
2019-01-02 01:00 | 333 | 326
2019-01-02 01:30 | 322 | 314
2019-01-02 02:00 | 316 | 307
2019-01-02 02:30 | 305 | 296
2019-01-02 03:00 | 298 | 287
2019-01-02 03:30 | 310 | 299
2019-01-02 04:00 | 315 | 306
2019-01-02 04:30 | 322 | 313
2019-01-02 05:00 | 313 | 303
2019-01-02 05:30 | 314 | 304
2019-01-02 06:00 | 306 | 295
2019-01-02 06:30 | 317 | 306
2019-01-02 07:00 | 269 | 256
2019-01-02 07:30 | 234 | 211
2019-01-02 08:00 | 191 | 157
2019-01-02 08:30 | 180 | 138
2019-01-02 09:00 | 162 | 113
2019-01-02 09:30 | 169 | 121
2019-01-02 10:00 | 188 | 145
2019-01-02 10:30 | 181 | 135
2019-01-02 11:00 | 198 | 160
2019-01-02 11:30 | 159 | 106
2019-01-02 12:00 | 146 | 86
2019-01-02 12:30 | 164 | 122
2019-01-02 13:00 | 204 | 169
2019-01-02 13:30 | 227 | 193
2019-01-02 14:00 | 212 | 173
2019-01-02 14:30 | 165 | 114
2019-01-02 15:00 | 150 | 97
2019-01-02 15:30 | 144 | 91
2019-01-02 16:00 | 167 | 125
2019-01-02 16:30 | 228 | 203
2019-01-02 17:00 | 178 | 151
2019-01-02 17:30 | 265 | 246
2019-01-02 18:00 | 337 | 326
2019-01-02 18:30 | 380 | 373
2019-01-02 19:00 | 425 | 421
2019-01-02 19:30 | 497 | 495
2019-01-02 20:00 | 476 | 474
2019-01-02 20:30 | 453 | 450
2019-01-02 21:00 | 500 | 497
2019-01-02 21:30 | 477 | 475
2019-01-02 22:00 | 528 | 526
2019-01-02 22:30 | 505 | 503
2019-01-02 23:00 | 464 | 462
2019-01-02 23:30 | 431 | 427
2019-01-03 | 400 | 396
2019-01-03 00:30 | 413 | 408
2019-01-03 01:00 | 402 | 397
2019-01-03 01:30 | 367 | 361
2019-01-03 02:00 | 318 | 310
2019-01-03 02:30 | 314 | 304
2019-01-03 03:00 | 325 | 315
2019-01-03 03:30 | 325 | 316
2019-01-03 04:00 | 331 | 322
2019-01-03 04:30 | 334 | 325
2019-01-03 05:00 | 333 | 324
2019-01-03 05:30 | 359 | 350
2019-01-03 06:00 | 368 | 361
2019-01-03 06:30 | 371 | 365
2019-01-03 07:00 | 326 | 318
2019-01-03 07:30 | 289 | 277
2019-01-03 08:00 | 246 | 226
2019-01-03 08:30 | 219 | 192
2019-01-03 09:00 | 198 | 167
2019-01-03 09:30 | 186 | 152
2019-01-03 10:00 | 180 | 144
2019-01-03 10:30 | 176 | 138
2019-01-03 11:00 | 169 | 130
2019-01-03 11:30 | 179 | 142
2019-01-03 12:00 | 194 | 161
2019-01-03 12:30 | 227 | 200
2019-01-03 13:00 | 219 | 192
2019-01-03 13:30 | 219 | 192
2019-01-03 14:00 | 222 | 195
2019-01-03 14:30 | 195 | 166
2019-01-03 15:00 | 229 | 203
2019-01-03 15:30 | 271 | 252
2019-01-03 16:00 | 275 | 259
2019-01-03 16:30 | 321 | 308
2019-01-03 17:00 | 380 | 371
2019-01-03 17:30 | 451 | 446
2019-01-03 18:00 | 495 | 492
2019-01-03 18:30 | 567 | 566
2019-01-03 19:00 | 586 | 585
2019-01-03 19:30 | 601 | 601
2019-01-03 20:00 | 592 | 592
2019-01-03 20:30 | 570 | 569
2019-01-03 21:00 | 547 | 546
2019-01-03 21:30 | 513 | 511
2019-01-03 22:00 | 486 | 484
2019-01-03 22:30 | 453 | 450
2019-01-03 23:00 | 435 | 432
2019-01-03 23:30 | 428 | 426
2019-01-04 | 433 | 431
2019-01-04 00:30 | 436 | 434
2019-01-04 01:00 | 405 | 403
2019-01-04 01:30 | 411 | 409
2019-01-04 02:00 | 418 | 415
2019-01-04 02:30 | 408 | 405
2019-01-04 03:00 | 402 | 399
2019-01-04 03:30 | 397 | 394
2019-01-04 04:00 | 390 | 387
2019-01-04 04:30 | 417 | 414
2019-01-04 05:00 | 418 | 415
2019-01-04 05:30 | 395 | 392
2019-01-04 06:00 | 393 | 389
2019-01-04 06:30 | 395 | 391
2019-01-04 07:00 | 356 | 352
2019-01-04 07:30 | 315 | 307
2019-01-04 08:00 | 271 | 258
2019-01-04 08:30 | 257 | 240
2019-01-04 09:00 | 300 | 285
2019-01-04 09:30 | 273 | 261
2019-01-04 10:00 | 252 | 238
2019-01-04 10:30 | 265 | 250
2019-01-04 11:00 | 265 | 254
2019-01-04 11:30 | 273 | 261
2019-01-04 12:00 | 282 | 271
2019-01-04 12:30 | 231 | 219
2019-01-04 13:00 | 201 | 183
2019-01-04 13:30 | 158 | 128
2019-01-04 14:00 | 171 | 140
2019-01-04 14:30 | 180 | 151
2019-01-04 15:00 | 170 | 140
2019-01-04 15:30 | 147 | 112
2019-01-04 16:00 | 181 | 152
2019-01-04 16:30 | 247 | 228
2019-01-04 17:00 | 268 | 255
2019-01-04 17:30 | 292 | 282
2019-01-04 18:00 | 375 | 370
2019-01-04 18:30 | 442 | 439
2019-01-04 19:00 | 444 | 442
2019-01-04 19:30 | 437 | 436
2019-01-04 20:00 | 454 | 453
2019-01-04 20:30 | 486 | 485
2019-01-04 21:00 | 541 | 540
2019-01-04 21:30 | 521 | 521
2019-01-04 22:00 | 483 | 483
2019-01-04 22:30 | 460 | 459
2019-01-04 23:00 | 440 | 439
2019-01-04 23:30 | 419 | 418
2019-01-05 | 412 | 410
2019-01-05 00:30 | 429 | 427
2019-01-05 01:00 | 416 | 413
2019-01-05 01:30 | 420 | 417
2019-01-05 02:00 | 413 | 410
2019-01-05 02:30 | 408 | 405
2019-01-05 03:00 | 400 | 397
2019-01-05 03:30 | 397 | 394
2019-01-05 04:00 | 390 | 387
2019-01-05 04:30 | 396 | 393
2019-01-05 05:00 | 405 | 402
2019-01-05 05:30 | 419 | 416
2019-01-05 06:00 | 410 | 407
2019-01-05 06:30 | 388 | 385
2019-01-05 07:00 | 359 | 354
2019-01-05 07:30 | 313 | 305
2019-01-05 08:00 | 275 | 263
2019-01-05 08:30 | 248 | 232
2019-01-05 09:00 | 233 | 214
2019-01-05 09:30 | 227 | 207
2019-01-05 10:00 | 259 | 242
2019-01-05 10:30 | 224 | 205
2019-01-05 11:00 | 229 | 210
2019-01-05 11:30 | 277 | 262
2019-01-05 12:00 | 271 | 258
2019-01-05 12:30 | 256 | 243
2019-01-05 13:00 | 227 | 210
2019-01-05 13:30 | 204 | 183
2019-01-05 14:00 | 274 | 257
2019-01-05 14:30 | 258 | 245
2019-01-05 15:00 | 267 | 253
2019-01-05 15:30 | 239 | 226
2019-01-05 16:00 | 261 | 247
2019-01-05 16:30 | 310 | 300
2019-01-05 17:00 | 357 | 349
2019-01-05 17:30 | 429 | 424
2019-01-05 18:00 | 505 | 503
2019-01-05 18:30 | 545 | 545
2019-01-05 19:00 | 575 | 575
2019-01-05 19:30 | 576 | 576
2019-01-05 20:00 | 590 | 590
2019-01-05 20:30 | 583 | 583
2019-01-05 21:00 | 550 | 550
2019-01-05 21:30 | 517 | 517
2019-01-05 22:00 | 501 | 501
2019-01-05 22:30 | 507 | 506
2019-01-05 23:00 | 493 | 492
2019-01-05 23:30 | 467 | 466
2019-01-06 | 435 | 434
2019-01-06 00:30 | 418 | 416
2019-01-06 01:00 | 414 | 412
2019-01-06 01:30 | 425 | 423
2019-01-06 02:00 | 423 | 421
2019-01-06 02:30 | 447 | 445
2019-01-06 03:00 | 477 | 476
2019-01-06 03:30 | 481 | 480
2019-01-06 04:00 | 478 | 477
2019-01-06 04:30 | 475 | 475
2019-01-06 05:00 | 482 | 481
2019-01-06 05:30 | 485 | 485
2019-01-06 06:00 | 472 | 472
2019-01-06 06:30 | 438 | 437
2019-01-06 07:00 | 386 | 384
2019-01-06 07:30 | 310 | 305
2019-01-06 08:00 | 244 | 233
2019-01-06 08:30 | 221 | 205
2019-01-06 09:00 | 224 | 206
2019-01-06 09:30 | 187 | 165
2019-01-06 10:00 | 177 | 150
2019-01-06 10:30 | 170 | 141
2019-01-06 11:00 | 177 | 150
2019-01-06 11:30 | 175 | 147
2019-01-06 12:00 | 209 | 186
2019-01-06 12:30 | 186 | 161
2019-01-06 13:00 | 197 | 173
2019-01-06 13:30 | 238 | 219
2019-01-06 14:00 | 206 | 187
2019-01-06 14:30 | 201 | 181
2019-01-06 15:00 | 217 | 198
2019-01-06 15:30 | 266 | 252
2019-01-06 16:00 | 307 | 296
2019-01-06 16:30 | 338 | 330
2019-01-06 17:00 | 402 | 396
2019-01-06 17:30 | 490 | 487
2019-01-06 18:00 | 552 | 551
2019-01-06 18:30 | 620 | 620
2019-01-06 19:00 | 647 | 647
2019-01-06 19:30 | 664 | 664
2019-01-06 20:00 | 688 | 687
2019-01-06 20:30 | 684 | 684
2019-01-06 21:00 | 655 | 655
2019-01-06 21:30 | 630 | 630
2019-01-06 22:00 | 603 | 603
2019-01-06 22:30 | 566 | 566
2019-01-06 23:00 | 527 | 527
2019-01-06 23:30 | 517 | 517
2019-01-07 | 509 | 508
2019-01-07 00:30 | 505 | 505
2019-01-07 01:00 | 483 | 483
2019-01-07 01:30 | 473 | 473
2019-01-07 02:00 | 465 | 465
2019-01-07 02:30 | 462 | 462
2019-01-07 03:00 | 458 | 457
2019-01-07 03:30 | 461 | 460
2019-01-07 04:00 | 456 | 455
2019-01-07 04:30 | 458 | 457
2019-01-07 05:00 | 454 | 453
2019-01-07 05:30 | 465 | 464
2019-01-07 06:00 | 469 | 468
2019-01-07 06:30 | 455 | 454
2019-01-07 07:00 | 435 | 433
2019-01-07 07:30 | 386 | 384
2019-01-07 08:00 | 350 | 345
2019-01-07 08:30 | 305 | 298
2019-01-07 09:00 | 307 | 298
2019-01-07 09:30 | 281 | 272
2019-01-07 10:00 | 240 | 228
2019-01-07 10:30 | 264 | 251
2019-01-07 11:00 | 277 | 267
2019-01-07 11:30 | 273 | 261
2019-01-07 12:00 | 274 | 261
2019-01-07 12:30 | 314 | 304
2019-01-07 13:00 | 273 | 264
2019-01-07 13:30 | 270 | 260
2019-01-07 14:00 | 301 | 291
2019-01-07 14:30 | 323 | 315
2019-01-07 15:00 | 321 | 314
2019-01-07 15:30 | 330 | 323
2019-01-07 16:00 | 340 | 334
2019-01-07 16:30 | 437 | 433
2019-01-07 17:00 | 448 | 446
2019-01-07 17:30 | 415 | 414
2019-01-07 18:00 | 434 | 432
2019-01-07 18:30 | 472 | 471
2019-01-07 19:00 | 499 | 499
2019-01-07 19:30 | 516 | 516
2019-01-07 20:00 | 517 | 517
2019-01-07 20:30 | 495 | 495
2019-01-07 21:00 | 530 | 529
2019-01-07 21:30 | 600 | 600
2019-01-07 22:00 | 588 | 588
2019-01-07 22:30 | 568 | 568
2019-01-07 23:00 | 557 | 557
2019-01-07 23:30 | 560 | 560
2019-01-08 | 547 | 547
2019-01-08 00:30 | 549 | 549
2019-01-08 01:00 | 517 | 517
2019-01-08 01:30 | 497 | 497
2019-01-08 02:00 | 489 | 489
2019-01-08 02:30 | 484 | 483
2019-01-08 03:00 | 483 | 482
2019-01-08 03:30 | 478 | 477
2019-01-08 04:00 | 476 | 475
2019-01-08 04:30 | 472 | 472
2019-01-08 05:00 | 475 | 474
2019-01-08 05:30 | 490 | 489
2019-01-08 06:00 | 489 | 489
2019-01-08 06:30 | 495 | 495
2019-01-08 07:00 | 458 | 457
2019-01-08 07:30 | 410 | 409
2019-01-08 08:00 | 333 | 330
2019-01-08 08:30 | 307 | 302
2019-01-08 09:00 | 261 | 252
2019-01-08 09:30 | 243 | 230
2019-01-08 10:00 | 205 | 186
2019-01-08 10:30 | 226 | 207
2019-01-08 11:00 | 244 | 226
2019-01-08 11:30 | 267 | 250
2019-01-08 12:00 | 271 | 253
2019-01-08 12:30 | 291 | 276
2019-01-08 13:00 | 322 | 310
2019-01-08 13:30 | 304 | 293
2019-01-08 14:00 | 292 | 280
2019-01-08 14:30 | 304 | 291
2019-01-08 15:00 | 278 | 264
2019-01-08 15:30 | 238 | 220
2019-01-08 16:00 | 273 | 257
2019-01-08 16:30 | 275 | 262
2019-01-08 17:00 | 320 | 311
2019-01-08 17:30 | 356 | 351
2019-01-08 18:00 | 429 | 425
2019-01-08 18:30 | 487 | 485
2019-01-08 19:00 | 524 | 523
2019-01-08 19:30 | 533 | 533
2019-01-08 20:00 | 523 | 523
2019-01-08 20:30 | 500 | 500
2019-01-08 21:00 | 485 | 485
2019-01-08 21:30 | 544 | 543
2019-01-08 22:00 | 611 | 611
2019-01-08 22:30 | 614 | 614
2019-01-08 23:00 | 582 | 582
2019-01-08 23:30 | 558 | 558
2019-01-09 | 529 | 529
2019-01-09 00:30 | 529 | 529
2019-01-09 01:00 | 497 | 497
2019-01-09 01:30 | 493 | 492
2019-01-09 02:00 | 488 | 487
2019-01-09 02:30 | 479 | 478
2019-01-09 03:00 | 476 | 475
2019-01-09 03:30 | 478 | 477
2019-01-09 04:00 | 467 | 466
2019-01-09 04:30 | 457 | 456
2019-01-09 05:00 | 460 | 459
2019-01-09 05:30 | 470 | 469
2019-01-09 06:00 | 470 | 469
2019-01-09 06:30 | 468 | 467
2019-01-09 07:00 | 463 | 462
2019-01-09 07:30 | 453 | 451
2019-01-09 08:00 | 393 | 391
2019-01-09 08:30 | 347 | 342
2019-01-09 09:00 | 314 | 306
2019-01-09 09:30 | 289 | 277
2019-01-09 10:00 | 232 | 216
2019-01-09 10:30 | 241 | 221
2019-01-09 11:00 | 260 | 242
2019-01-09 11:30 | 257 | 241
2019-01-09 12:00 | 267 | 253
2019-01-09 12:30 | 325 | 314
2019-01-09 13:00 | 304 | 294
2019-01-09 13:30 | 388 | 380
2019-01-09 14:00 | 362 | 355
2019-01-09 14:30 | 354 | 348
2019-01-09 15:00 | 313 | 308
2019-01-09 15:30 | 320 | 314
2019-01-09 16:00 | 385 | 380
2019-01-09 16:30 | 395 | 392
2019-01-09 17:00 | 398 | 396
2019-01-09 17:30 | 416 | 414
2019-01-09 18:00 | 452 | 450
2019-01-09 18:30 | 480 | 479
2019-01-09 19:00 | 503 | 502
2019-01-09 19:30 | 546 | 545
2019-01-09 20:00 | 574 | 574
2019-01-09 20:30 | 556 | 556
2019-01-09 21:00 | 552 | 552
2019-01-09 21:30 | 609 | 609
2019-01-09 22:00 | 604 | 604
2019-01-09 22:30 | 576 | 576
2019-01-09 23:00 | 558 | 558
2019-01-09 23:30 | 533 | 532
2019-01-10 | 519 | 519
2019-01-10 00:30 | 513 | 513
2019-01-10 01:00 | 499 | 498
2019-01-10 01:30 | 488 | 487
2019-01-10 02:00 | 477 | 476
2019-01-10 02:30 | 463 | 462
2019-01-10 03:00 | 456 | 455
2019-01-10 03:30 | 438 | 438
2019-01-10 04:00 | 431 | 431
2019-01-10 04:30 | 428 | 428
2019-01-10 05:00 | 431 | 430
2019-01-10 05:30 | 445 | 444
2019-01-10 06:00 | 451 | 450
2019-01-10 06:30 | 452 | 451
2019-01-10 07:00 | 436 | 435
2019-01-10 07:30 | 475 | 474
2019-01-10 08:00 | 502 | 500
2019-01-10 08:30 | 502 | 501
2019-01-10 09:00 | 493 | 491
2019-01-10 09:30 | 481 | 480
2019-01-10 10:00 | 473 | 471
2019-01-10 10:30 | 468 | 467
2019-01-10 11:00 | 467 | 465
2019-01-10 11:30 | 448 | 446
2019-01-10 12:00 | 449 | 446
2019-01-10 12:30 | 453 | 451
2019-01-10 13:00 | 434 | 431
2019-01-10 13:30 | 464 | 461
2019-01-10 14:00 | 455 | 453
2019-01-10 14:30 | 471 | 469
2019-01-10 15:00 | 454 | 452
2019-01-10 15:30 | 449 | 447
2019-01-10 16:00 | 463 | 460
2019-01-10 16:30 | 433 | 431
2019-01-10 17:00 | 455 | 453
2019-01-10 17:30 | 462 | 459
2019-01-10 18:00 | 496 | 494
2019-01-10 18:30 | 523 | 522
2019-01-10 19:00 | 547 | 546
2019-01-10 19:30 | 543 | 543
2019-01-10 20:00 | 558 | 558
2019-01-10 20:30 | 570 | 570
2019-01-10 21:00 | 544 | 544
2019-01-10 21:30 | 528 | 528
2019-01-10 22:00 | 503 | 503
2019-01-10 22:30 | 450 | 449
2019-01-10 23:00 | 450 | 449
2019-01-10 23:30 | 437 | 436
2019-01-11 | 421 | 419
2019-01-11 00:30 | 443 | 441
2019-01-11 01:00 | 423 | 421
2019-01-11 01:30 | 409 | 407
2019-01-11 02:00 | 401 | 399
2019-01-11 02:30 | 398 | 396
2019-01-11 03:00 | 388 | 385
2019-01-11 03:30 | 384 | 381
2019-01-11 04:00 | 381 | 378
2019-01-11 04:30 | 375 | 373
2019-01-11 05:00 | 357 | 354
2019-01-11 05:30 | 362 | 359
2019-01-11 06:00 | 372 | 369
2019-01-11 06:30 | 387 | 384
2019-01-11 07:00 | 387 | 384
2019-01-11 07:30 | 379 | 376
2019-01-11 08:00 | 373 | 369
2019-01-11 08:30 | 372 | 368
2019-01-11 09:00 | 355 | 348
2019-01-11 09:30 | 360 | 354
2019-01-11 10:00 | 293 | 285
2019-01-11 10:30 | 271 | 261
2019-01-11 11:00 | 240 | 226
2019-01-11 11:30 | 247 | 233
2019-01-11 12:00 | 260 | 246
2019-01-11 12:30 | 267 | 255
2019-01-11 13:00 | 277 | 266
2019-01-11 13:30 | 205 | 191
2019-01-11 14:00 | 202 | 185
2019-01-11 14:30 | 173 | 148
2019-01-11 15:00 | 154 | 123
2019-01-11 15:30 | 172 | 143
2019-01-11 16:00 | 171 | 144
2019-01-11 16:30 | 219 | 202
2019-01-11 17:00 | 288 | 278
2019-01-11 17:30 | 298 | 292
2019-01-11 18:00 | 321 | 315
2019-01-11 18:30 | 360 | 355
2019-01-11 19:00 | 370 | 367
2019-01-11 19:30 | 410 | 408
2019-01-11 20:00 | 438 | 437
2019-01-11 20:30 | 424 | 423
2019-01-11 21:00 | 377 | 376
2019-01-11 21:30 | 352 | 350
2019-01-11 22:00 | 429 | 426
2019-01-11 22:30 | 453 | 452
2019-01-11 23:00 | 430 | 429
2019-01-11 23:30 | 401 | 400
2019-01-12 | 399 | 398
2019-01-12 00:30 | 408 | 406
2019-01-12 01:00 | 389 | 387
2019-01-12 01:30 | 368 | 366
2019-01-12 02:00 | 356 | 353
2019-01-12 02:30 | 358 | 354
2019-01-12 03:00 | 368 | 365
2019-01-12 03:30 | 365 | 362
2019-01-12 04:00 | 352 | 349
2019-01-12 04:30 | 330 | 327
2019-01-12 05:00 | 326 | 322
2019-01-12 05:30 | 329 | 325
2019-01-12 06:00 | 314 | 310
2019-01-12 06:30 | 298 | 294
2019-01-12 07:00 | 257 | 250
2019-01-12 07:30 | 214 | 200
2019-01-12 08:00 | 183 | 160
2019-01-12 08:30 | 152 | 121
2019-01-12 09:00 | 157 | 125
2019-01-12 09:30 | 148 | 113
2019-01-12 10:00 | 166 | 133
2019-01-12 10:30 | 146 | 109
2019-01-12 11:00 | 154 | 120
2019-01-12 11:30 | 150 | 112
2019-01-12 12:00 | 165 | 128
2019-01-12 12:30 | 172 | 138
2019-01-12 13:00 | 169 | 135
2019-01-12 13:30 | 157 | 121
2019-01-12 14:00 | 165 | 129
2019-01-12 14:30 | 189 | 160
2019-01-12 15:00 | 186 | 158
2019-01-12 15:30 | 178 | 149
2019-01-12 16:00 | 175 | 144
2019-01-12 16:30 | 207 | 183
2019-01-12 17:00 | 223 | 206
2019-01-12 17:30 | 296 | 284
2019-01-12 18:00 | 267 | 257
2019-01-12 18:30 | 283 | 273
2019-01-12 19:00 | 294 | 288
2019-01-12 19:30 | 317 | 311
2019-01-12 20:00 | 300 | 295
2019-01-12 20:30 | 300 | 295
2019-01-12 21:00 | 387 | 383
2019-01-12 21:30 | 450 | 448
2019-01-12 22:00 | 434 | 433
2019-01-12 22:30 | 407 | 406
2019-01-12 23:00 | 394 | 392
2019-01-12 23:30 | 377 | 374
2019-01-13 | 370 | 367
2019-01-13 00:30 | 363 | 360
2019-01-13 01:00 | 353 | 349
2019-01-13 01:30 | 337 | 333
2019-01-13 02:00 | 323 | 318
2019-01-13 02:30 | 333 | 328
2019-01-13 03:00 | 329 | 324
2019-01-13 03:30 | 316 | 311
2019-01-13 04:00 | 321 | 315
2019-01-13 04:30 | 372 | 367
2019-01-13 05:00 | 357 | 353
2019-01-13 05:30 | 317 | 313
2019-01-13 06:00 | 304 | 298
2019-01-13 06:30 | 288 | 281
2019-01-13 07:00 | 242 | 233
2019-01-13 07:30 | 202 | 185
2019-01-13 08:00 | 147 | 116
2019-01-13 08:30 | 162 | 126
2019-01-13 09:00 | 218 | 192
2019-01-13 09:30 | 213 | 184
2019-01-13 10:00 | 229 | 202
2019-01-13 10:30 | 200 | 167
2019-01-13 11:00 | 176 | 142
2019-01-13 11:30 | 146 | 103
2019-01-13 12:00 | 171 | 139
2019-01-13 12:30 | 168 | 137
2019-01-13 13:00 | 148 | 114
2019-01-13 13:30 | 191 | 166
2019-01-13 14:00 | 195 | 172
2019-01-13 14:30 | 276 | 260
2019-01-13 15:00 | 268 | 254
2019-01-13 15:30 | 283 | 271
2019-01-13 16:00 | 322 | 312
2019-01-13 16:30 | 288 | 280
2019-01-13 17:00 | 359 | 351
2019-01-13 17:30 | 414 | 409
2019-01-13 18:00 | 477 | 475
2019-01-13 18:30 | 480 | 480
2019-01-13 19:00 | 511 | 511
2019-01-13 19:30 | 538 | 537
2019-01-13 20:00 | 526 | 526
2019-01-13 20:30 | 511 | 511
2019-01-13 21:00 | 517 | 517
2019-01-13 21:30 | 492 | 492
2019-01-13 22:00 | 464 | 463
2019-01-13 22:30 | 449 | 448
2019-01-13 23:00 | 421 | 419
2019-01-13 23:30 | 407 | 405
2019-01-14 | 388 | 386
2019-01-14 00:30 | 390 | 387
2019-01-14 01:00 | 378 | 375
2019-01-14 01:30 | 367 | 364
2019-01-14 02:00 | 346 | 342
2019-01-14 02:30 | 333 | 329
2019-01-14 03:00 | 328 | 323
2019-01-14 03:30 | 349 | 344
2019-01-14 04:00 | 337 | 333
2019-01-14 04:30 | 321 | 316
2019-01-14 05:00 | 334 | 329
2019-01-14 05:30 | 339 | 334
2019-01-14 06:00 | 333 | 328
2019-01-14 06:30 | 343 | 338
2019-01-14 07:00 | 347 | 342
2019-01-14 07:30 | 357 | 351
2019-01-14 08:00 | 333 | 326
2019-01-14 08:30 | 273 | 263
2019-01-14 09:00 | 262 | 247
2019-01-14 09:30 | 287 | 271
2019-01-14 10:00 | 278 | 262
2019-01-14 10:30 | 298 | 283
2019-01-14 11:00 | 297 | 284
2019-01-14 11:30 | 279 | 266
2019-01-14 12:00 | 324 | 310
2019-01-14 12:30 | 293 | 281
2019-01-14 13:00 | 263 | 248
2019-01-14 13:30 | 329 | 316
2019-01-14 14:00 | 366 | 357
2019-01-14 14:30 | 270 | 260
2019-01-14 15:00 | 303 | 289
2019-01-14 15:30 | 250 | 235
2019-01-14 16:00 | 236 | 217
2019-01-14 16:30 | 217 | 195
2019-01-14 17:00 | 241 | 223
2019-01-14 17:30 | 299 | 285
2019-01-14 18:00 | 336 | 326
2019-01-14 18:30 | 344 | 337
2019-01-14 19:00 | 373 | 367
2019-01-14 19:30 | 381 | 377
2019-01-14 20:00 | 359 | 355
2019-01-14 20:30 | 381 | 377
2019-01-14 21:00 | 358 | 355
2019-01-14 21:30 | 400 | 397
2019-01-14 22:00 | 414 | 412
2019-01-14 22:30 | 403 | 401
2019-01-14 23:00 | 450 | 447
2019-01-14 23:30 | 434 | 432
2019-01-15 | 388 | 386
2019-01-15 00:30 | 357 | 353
2019-01-15 01:00 | 347 | 342
2019-01-15 01:30 | 373 | 368
2019-01-15 02:00 | 362 | 357
2019-01-15 02:30 | 356 | 350
2019-01-15 03:00 | 345 | 339
2019-01-15 03:30 | 356 | 350
2019-01-15 04:00 | 349 | 343
2019-01-15 04:30 | 357 | 351
2019-01-15 05:00 | 368 | 363
2019-01-15 05:30 | 378 | 373
2019-01-15 06:00 | 374 | 369
2019-01-15 06:30 | 390 | 386
2019-01-15 07:00 | 393 | 389
2019-01-15 07:30 | 402 | 397
2019-01-15 08:00 | 379 | 372
2019-01-15 08:30 | 408 | 402
2019-01-15 09:00 | 366 | 360
2019-01-15 09:30 | 343 | 336
2019-01-15 10:00 | 294 | 285
2019-01-15 10:30 | 251 | 235
2019-01-15 11:00 | 260 | 242
2019-01-15 11:30 | 286 | 269
2019-01-15 12:00 | 234 | 215
2019-01-15 12:30 | 293 | 275
2019-01-15 13:00 | 255 | 238
2019-01-15 13:30 | 239 | 219
2019-01-15 14:00 | 269 | 250
2019-01-15 14:30 | 259 | 240
2019-01-15 15:00 | 256 | 236
2019-01-15 15:30 | 199 | 174
2019-01-15 16:00 | 271 | 251
2019-01-15 16:30 | 260 | 243
2019-01-15 17:00 | 300 | 285
2019-01-15 17:30 | 354 | 343
2019-01-15 18:00 | 377 | 370
2019-01-15 18:30 | 439 | 434
2019-01-15 19:00 | 475 | 473
2019-01-15 19:30 | 478 | 477
2019-01-15 20:00 | 446 | 445
2019-01-15 20:30 | 429 | 427
2019-01-15 21:00 | 452 | 450
2019-01-15 21:30 | 446 | 444
2019-01-15 22:00 | 425 | 423
2019-01-15 22:30 | 396 | 393
2019-01-15 23:00 | 343 | 339
2019-01-15 23:30 | 327 | 321
2019-01-16 | 353 | 346
2019-01-16 00:30 | 385 | 379
2019-01-16 01:00 | 374 | 369
2019-01-16 01:30 | 321 | 315
2019-01-16 02:00 | 321 | 314
2019-01-16 02:30 | 310 | 303
2019-01-16 03:00 | 339 | 331
2019-01-16 03:30 | 308 | 301
2019-01-16 04:00 | 289 | 280
2019-01-16 04:30 | 277 | 267
2019-01-16 05:00 | 292 | 282
2019-01-16 05:30 | 321 | 312
2019-01-16 06:00 | 313 | 305
2019-01-16 06:30 | 300 | 292
2019-01-16 07:00 | 226 | 215
2019-01-16 07:30 | 209 | 188
2019-01-16 08:00 | 180 | 150
2019-01-16 08:30 | 157 | 121
2019-01-16 09:00 | 171 | 133
2019-01-16 09:30 | 174 | 136
2019-01-16 10:00 | 175 | 134
2019-01-16 10:30 | 156 | 112
2019-01-16 11:00 | 158 | 116
2019-01-16 11:30 | 163 | 122
2019-01-16 12:00 | 182 | 145
2019-01-16 12:30 | 178 | 143
2019-01-16 13:00 | 180 | 146
2019-01-16 13:30 | 202 | 173
2019-01-16 14:00 | 192 | 163
2019-01-16 14:30 | 161 | 125
2019-01-16 15:00 | 214 | 185
2019-01-16 15:30 | 214 | 181
2019-01-16 16:00 | 187 | 142
2019-01-16 16:30 | 148 | 91
2019-01-16 17:00 | 159 | 113
2019-01-16 17:30 | 182 | 148
2019-01-16 18:00 | 228 | 205
2019-01-16 18:30 | 290 | 275
2019-01-16 19:00 | 292 | 283
2019-01-16 19:30 | 289 | 280
2019-01-16 20:00 | 285 | 276
2019-01-16 20:30 | 248 | 236
2019-01-16 21:00 | 330 | 321
2019-01-16 21:30 | 363 | 357
2019-01-16 22:00 | 372 | 367
2019-01-16 22:30 | 360 | 355
2019-01-16 23:00 | 346 | 341
2019-01-16 23:30 | 293 | 286
2019-01-17 | 279 | 270
2019-01-17 00:30 | 276 | 265
2019-01-17 01:00 | 255 | 243
2019-01-17 01:30 | 259 | 245
2019-01-17 02:00 | 273 | 260
2019-01-17 02:30 | 319 | 310
2019-01-17 03:00 | 333 | 326
2019-01-17 03:30 | 334 | 327
2019-01-17 04:00 | 332 | 326
2019-01-17 04:30 | 311 | 303
2019-01-17 05:00 | 272 | 263
2019-01-17 05:30 | 252 | 240
2019-01-17 06:00 | 255 | 241
2019-01-17 06:30 | 279 | 266
2019-01-17 07:00 | 224 | 210
2019-01-17 07:30 | 204 | 182
2019-01-17 08:00 | 179 | 151
2019-01-17 08:30 | 161 | 126
2019-01-17 09:00 | 189 | 160
2019-01-17 09:30 | 144 | 98
2019-01-17 10:00 | 184 | 147
2019-01-17 10:30 | 175 | 141
2019-01-17 11:00 | 165 | 128
2019-01-17 11:30 | 167 | 130
2019-01-17 12:00 | 188 | 159
2019-01-17 12:30 | 164 | 133
2019-01-17 13:00 | 179 | 149
2019-01-17 13:30 | 196 | 166
2019-01-17 14:00 | 232 | 205
2019-01-17 14:30 | 192 | 156
2019-01-17 15:00 | 211 | 183
2019-01-17 15:30 | 201 | 169
2019-01-17 16:00 | 184 | 149
2019-01-17 16:30 | 151 | 103
2019-01-17 17:00 | 219 | 192
2019-01-17 17:30 | 240 | 219
2019-01-17 18:00 | 299 | 283
2019-01-17 18:30 | 340 | 331
2019-01-17 19:00 | 361 | 355
2019-01-17 19:30 | 355 | 351
2019-01-17 20:00 | 340 | 336
2019-01-17 20:30 | 309 | 304
2019-01-17 21:00 | 314 | 308
2019-01-17 21:30 | 400 | 395
2019-01-17 22:00 | 399 | 396
2019-01-17 22:30 | 372 | 370
2019-01-17 23:00 | 343 | 339
2019-01-17 23:30 | 336 | 331
2019-01-18 | 325 | 319
2019-01-18 00:30 | 338 | 332
2019-01-18 01:00 | 327 | 321
2019-01-18 01:30 | 327 | 320
2019-01-18 02:00 | 308 | 301
2019-01-18 02:30 | 303 | 294
2019-01-18 03:00 | 299 | 290
2019-01-18 03:30 | 298 | 289
2019-01-18 04:00 | 292 | 283
2019-01-18 04:30 | 308 | 299
2019-01-18 05:00 | 308 | 299
2019-01-18 05:30 | 316 | 308
2019-01-18 06:00 | 287 | 279
2019-01-18 06:30 | 305 | 297
2019-01-18 07:00 | 293 | 285
2019-01-18 07:30 | 305 | 296
2019-01-18 08:00 | 293 | 283
2019-01-18 08:30 | 223 | 210
2019-01-18 09:00 | 264 | 244
2019-01-18 09:30 | 291 | 275
2019-01-18 10:00 | 274 | 259
2019-01-18 10:30 | 262 | 246
2019-01-18 11:00 | 309 | 295
2019-01-18 11:30 | 294 | 281
2019-01-18 12:00 | 311 | 297
2019-01-18 12:30 | 322 | 310
2019-01-18 13:00 | 363 | 353
2019-01-18 13:30 | 305 | 296
2019-01-18 14:00 | 300 | 288
2019-01-18 14:30 | 223 | 206
2019-01-18 15:00 | 242 | 222
2019-01-18 15:30 | 241 | 221
2019-01-18 16:00 | 242 | 222
2019-01-18 16:30 | 277 | 262
2019-01-18 17:00 | 344 | 334
2019-01-18 17:30 | 367 | 360
2019-01-18 18:00 | 332 | 324
2019-01-18 18:30 | 351 | 344
2019-01-18 19:00 | 399 | 394
2019-01-18 19:30 | 420 | 418
2019-01-18 20:00 | 405 | 403
2019-01-18 20:30 | 411 | 409
2019-01-18 21:00 | 397 | 395
2019-01-18 21:30 | 487 | 485
2019-01-18 22:00 | 486 | 485
2019-01-18 22:30 | 448 | 447
2019-01-18 23:00 | 431 | 429
2019-01-18 23:30 | 410 | 408
2019-01-19 | 416 | 413
2019-01-19 00:30 | 434 | 431
2019-01-19 01:00 | 428 | 426
2019-01-19 01:30 | 408 | 405
2019-01-19 02:00 | 395 | 391
2019-01-19 02:30 | 399 | 395
2019-01-19 03:00 | 387 | 383
2019-01-19 03:30 | 384 | 380
2019-01-19 04:00 | 391 | 386
2019-01-19 04:30 | 407 | 402
2019-01-19 05:00 | 398 | 395
2019-01-19 05:30 | 395 | 392
2019-01-19 06:00 | 384 | 380
2019-01-19 06:30 | 383 | 378
2019-01-19 07:00 | 366 | 359
2019-01-19 07:30 | 334 | 325
2019-01-19 08:00 | 285 | 269
2019-01-19 08:30 | 240 | 217
2019-01-19 09:00 | 194 | 162
2019-01-19 09:30 | 164 | 126
2019-01-19 10:00 | 152 | 112
2019-01-19 10:30 | 166 | 129
2019-01-19 11:00 | 171 | 135
2019-01-19 11:30 | 167 | 130
2019-01-19 12:00 | 142 | 106
2019-01-19 12:30 | 152 | 116
2019-01-19 13:00 | 168 | 137
2019-01-19 13:30 | 198 | 174
2019-01-19 14:00 | 186 | 161
2019-01-19 14:30 | 186 | 161
2019-01-19 15:00 | 213 | 192
2019-01-19 15:30 | 222 | 204
2019-01-19 16:00 | 251 | 236
2019-01-19 16:30 | 313 | 301
2019-01-19 17:00 | 370 | 362
2019-01-19 17:30 | 400 | 394
2019-01-19 18:00 | 431 | 428
2019-01-19 18:30 | 488 | 486
2019-01-19 19:00 | 508 | 507
2019-01-19 19:30 | 518 | 518
2019-01-19 20:00 | 513 | 513
2019-01-19 20:30 | 474 | 474
2019-01-19 21:00 | 437 | 437
2019-01-19 21:30 | 396 | 395
2019-01-19 22:00 | 385 | 383
2019-01-19 22:30 | 366 | 364
2019-01-19 23:00 | 357 | 355
2019-01-19 23:30 | 357 | 354
2019-01-20 | 339 | 336
2019-01-20 00:30 | 347 | 344
2019-01-20 01:00 | 319 | 316
2019-01-20 01:30 | 313 | 309
2019-01-20 02:00 | 281 | 277
2019-01-20 02:30 | 263 | 256
2019-01-20 03:00 | 252 | 243
2019-01-20 03:30 | 251 | 242
2019-01-20 04:00 | 252 | 242
2019-01-20 04:30 | 272 | 263
2019-01-20 05:00 | 279 | 271
2019-01-20 05:30 | 279 | 272
2019-01-20 06:00 | 268 | 261
2019-01-20 06:30 | 261 | 252
2019-01-20 07:00 | 252 | 239
2019-01-20 07:30 | 267 | 251
2019-01-20 08:00 | 260 | 243
2019-01-20 08:30 | 263 | 246
2019-01-20 09:00 | 256 | 239
2019-01-20 09:30 | 247 | 229
2019-01-20 10:00 | 212 | 191
2019-01-20 10:30 | 163 | 134
2019-01-20 11:00 | 152 | 117
2019-01-20 11:30 | 157 | 122
2019-01-20 12:00 | 161 | 127
2019-01-20 12:30 | 171 | 141
2019-01-20 13:00 | 168 | 135
2019-01-20 13:30 | 178 | 148
2019-01-20 14:00 | 211 | 186
2019-01-20 14:30 | 194 | 163
2019-01-20 15:00 | 179 | 146
2019-01-20 15:30 | 164 | 129
2019-01-20 16:00 | 195 | 169
2019-01-20 16:30 | 238 | 220
2019-01-20 17:00 | 317 | 305
2019-01-20 17:30 | 365 | 358
2019-01-20 18:00 | 428 | 423
2019-01-20 18:30 | 479 | 477
2019-01-20 19:00 | 509 | 508
2019-01-20 19:30 | 523 | 523
2019-01-20 20:00 | 516 | 516
2019-01-20 20:30 | 538 | 538
2019-01-20 21:00 | 525 | 525
2019-01-20 21:30 | 495 | 495
2019-01-20 22:00 | 464 | 464
2019-01-20 22:30 | 404 | 404
2019-01-20 23:00 | 384 | 384
2019-01-20 23:30 | 353 | 353
2019-01-21 | 352 | 351
2019-01-21 00:30 | 371 | 371
2019-01-21 01:00 | 368 | 368
2019-01-21 01:30 | 359 | 358
2019-01-21 02:00 | 361 | 360
2019-01-21 02:30 | 344 | 343
2019-01-21 03:00 | 334 | 334
2019-01-21 03:30 | 323 | 322
2019-01-21 04:00 | 319 | 318
2019-01-21 04:30 | 322 | 321
2019-01-21 05:00 | 322 | 321
2019-01-21 05:30 | 343 | 342
2019-01-21 06:00 | 343 | 343
2019-01-21 06:30 | 338 | 337
2019-01-21 07:00 | 322 | 319
2019-01-21 07:30 | 280 | 275
2019-01-21 08:00 | 258 | 251
2019-01-21 08:30 | 213 | 202
2019-01-21 09:00 | 173 | 152
2019-01-21 09:30 | 191 | 169
2019-01-21 10:00 | 218 | 198
2019-01-21 10:30 | 239 | 223
2019-01-21 11:00 | 258 | 244
2019-01-21 11:30 | 269 | 257
2019-01-21 12:00 | 285 | 274
2019-01-21 12:30 | 246 | 233
2019-01-21 13:00 | 184 | 164
2019-01-21 13:30 | 175 | 150
2019-01-21 14:00 | 217 | 193
2019-01-21 14:30 | 196 | 164
2019-01-21 15:00 | 186 | 154
2019-01-21 15:30 | 173 | 140
2019-01-21 16:00 | 149 | 107
2019-01-21 16:30 | 188 | 162
2019-01-21 17:00 | 236 | 217
2019-01-21 17:30 | 227 | 211
2019-01-21 18:00 | 259 | 244
2019-01-21 18:30 | 337 | 328
2019-01-21 19:00 | 360 | 355
2019-01-21 19:30 | 383 | 381
2019-01-21 20:00 | 375 | 374
2019-01-21 20:30 | 355 | 354
2019-01-21 21:00 | 381 | 379
2019-01-21 21:30 | 423 | 422
2019-01-21 22:00 | 421 | 420
2019-01-21 22:30 | 395 | 394
2019-01-21 23:00 | 408 | 407
2019-01-21 23:30 | 425 | 424
2019-01-22 | 397 | 396
2019-01-22 00:30 | 402 | 401
2019-01-22 01:00 | 398 | 396
2019-01-22 01:30 | 390 | 388
2019-01-22 02:00 | 382 | 381
2019-01-22 02:30 | 351 | 350
2019-01-22 03:00 | 327 | 324
2019-01-22 03:30 | 298 | 295
2019-01-22 04:00 | 289 | 283
2019-01-22 04:30 | 296 | 290
2019-01-22 05:00 | 312 | 306
2019-01-22 05:30 | 299 | 293
2019-01-22 06:00 | 285 | 279
2019-01-22 06:30 | 293 | 286
2019-01-22 07:00 | 329 | 321
2019-01-22 07:30 | 343 | 335
2019-01-22 08:00 | 286 | 276
2019-01-22 08:30 | 229 | 212
2019-01-22 09:00 | 217 | 196
2019-01-22 09:30 | 194 | 169
2019-01-22 10:00 | 176 | 150
2019-01-22 10:30 | 179 | 153
2019-01-22 11:00 | 220 | 198
2019-01-22 11:30 | 260 | 242
2019-01-22 12:00 | 232 | 215
2019-01-22 12:30 | 261 | 245
2019-01-22 13:00 | 278 | 264
2019-01-22 13:30 | 249 | 236
2019-01-22 14:00 | 222 | 205
2019-01-22 14:30 | 189 | 168
2019-01-22 15:00 | 222 | 203
2019-01-22 15:30 | 243 | 226
2019-01-22 16:00 | 233 | 216
2019-01-22 16:30 | 175 | 152
2019-01-22 17:00 | 190 | 167
2019-01-22 17:30 | 271 | 254
2019-01-22 18:00 | 316 | 305
2019-01-22 18:30 | 348 | 341
2019-01-22 19:00 | 372 | 368
2019-01-22 19:30 | 413 | 411
2019-01-22 20:00 | 439 | 438
2019-01-22 20:30 | 397 | 397
2019-01-22 21:00 | 395 | 394
2019-01-22 21:30 | 405 | 404
2019-01-22 22:00 | 454 | 453
2019-01-22 22:30 | 449 | 449
2019-01-22 23:00 | 422 | 422
2019-01-22 23:30 | 382 | 382
2019-01-23 | 374 | 373
2019-01-23 00:30 | 372 | 370
2019-01-23 01:00 | 339 | 337
2019-01-23 01:30 | 322 | 319
2019-01-23 02:00 | 311 | 308
2019-01-23 02:30 | 317 | 314
2019-01-23 03:00 | 336 | 333
2019-01-23 03:30 | 375 | 373
2019-01-23 04:00 | 386 | 385
2019-01-23 04:30 | 380 | 378
2019-01-23 05:00 | 386 | 385
2019-01-23 05:30 | 400 | 399
2019-01-23 06:00 | 398 | 398
2019-01-23 06:30 | 425 | 424
2019-01-23 07:00 | 401 | 400
2019-01-23 07:30 | 387 | 384
2019-01-23 08:00 | 352 | 348
2019-01-23 08:30 | 304 | 298
2019-01-23 09:00 | 310 | 303
2019-01-23 09:30 | 287 | 279
2019-01-23 10:00 | 255 | 245
2019-01-23 10:30 | 207 | 199
2019-01-23 11:00 | 137 | 123
2019-01-23 11:30 | 123 | 104
2019-01-23 12:00 | 129 | 108
2019-01-23 12:30 | 221 | 207
2019-01-23 13:00 | 142 | 112
2019-01-23 13:30 | 211 | 192
2019-01-23 14:00 | 214 | 186
2019-01-23 14:30 | 193 | 162
2019-01-23 15:00 | 135 | 87
2019-01-23 15:30 | 140 | 103
2019-01-23 16:00 | 234 | 215
2019-01-23 16:30 | 232 | 217
2019-01-23 17:00 | 258 | 244
2019-01-23 17:30 | 242 | 228
2019-01-23 18:00 | 270 | 261
2019-01-23 18:30 | 281 | 274
2019-01-23 19:00 | 335 | 330
2019-01-23 19:30 | 341 | 338
2019-01-23 20:00 | 355 | 353
2019-01-23 20:30 | 337 | 335
2019-01-23 21:00 | 336 | 334
2019-01-23 21:30 | 308 | 305
2019-01-23 22:00 | 297 | 293
2019-01-23 22:30 | 347 | 343
2019-01-23 23:00 | 348 | 346
2019-01-23 23:30 | 337 | 334
2019-01-24 | 393 | 391
2019-01-24 00:30 | 406 | 405
2019-01-24 01:00 | 411 | 409
2019-01-24 01:30 | 398 | 397
2019-01-24 02:00 | 387 | 386
2019-01-24 02:30 | 380 | 378
2019-01-24 03:00 | 353 | 351
2019-01-24 03:30 | 344 | 341
2019-01-24 04:00 | 375 | 373
2019-01-24 04:30 | 367 | 365
2019-01-24 05:00 | 359 | 357
2019-01-24 05:30 | 369 | 367
2019-01-24 06:00 | 383 | 381
2019-01-24 06:30 | 405 | 403
2019-01-24 07:00 | 384 | 382
2019-01-24 07:30 | 425 | 422
2019-01-24 08:00 | 349 | 346
2019-01-24 08:30 | 290 | 283
2019-01-24 09:00 | 245 | 235
2019-01-24 09:30 | 280 | 268
2019-01-24 10:00 | 188 | 173
2019-01-24 10:30 | 149 | 124
2019-01-24 11:00 | 178 | 154
2019-01-24 11:30 | 158 | 125
2019-01-24 12:00 | 159 | 127
2019-01-24 12:30 | 148 | 118
2019-01-24 13:00 | 172 | 146
2019-01-24 13:30 | 172 | 144
2019-01-24 14:00 | 165 | 138
2019-01-24 14:30 | 161 | 131
2019-01-24 15:00 | 177 | 150
2019-01-24 15:30 | 272 | 258
2019-01-24 16:00 | 215 | 202
2019-01-24 16:30 | 222 | 207
2019-01-24 17:00 | 272 | 259
2019-01-24 17:30 | 263 | 252
2019-01-24 18:00 | 295 | 286
2019-01-24 18:30 | 342 | 336
2019-01-24 19:00 | 342 | 338
2019-01-24 19:30 | 354 | 352
2019-01-24 20:00 | 378 | 376
2019-01-24 20:30 | 348 | 347
2019-01-24 21:00 | 323 | 321
2019-01-24 21:30 | 301 | 298
2019-01-24 22:00 | 348 | 345
2019-01-24 22:30 | 356 | 354
2019-01-24 23:00 | 336 | 333
2019-01-24 23:30 | 373 | 370
2019-01-25 | 455 | 454
2019-01-25 00:30 | 462 | 462
2019-01-25 01:00 | 423 | 422
2019-01-25 01:30 | 400 | 399
2019-01-25 02:00 | 385 | 383
2019-01-25 02:30 | 364 | 362
2019-01-25 03:00 | 344 | 341
2019-01-25 03:30 | 344 | 341
2019-01-25 04:00 | 354 | 351
2019-01-25 04:30 | 362 | 359
2019-01-25 05:00 | 352 | 349
2019-01-25 05:30 | 349 | 347
2019-01-25 06:00 | 364 | 361
2019-01-25 06:30 | 399 | 397
2019-01-25 07:00 | 380 | 378
2019-01-25 07:30 | 380 | 377
2019-01-25 08:00 | 392 | 389
2019-01-25 08:30 | 328 | 323
2019-01-25 09:00 | 293 | 285
2019-01-25 09:30 | 292 | 283
2019-01-25 10:00 | 264 | 255
2019-01-25 10:30 | 231 | 219
2019-01-25 11:00 | 190 | 171
2019-01-25 11:30 | 177 | 156
2019-01-25 12:00 | 151 | 123
2019-01-25 12:30 | 141 | 110
2019-01-25 13:00 | 173 | 147
2019-01-25 13:30 | 176 | 153
2019-01-25 14:00 | 173 | 149
2019-01-25 14:30 | 140 | 110
2019-01-25 15:00 | 165 | 137
2019-01-25 15:30 | 154 | 124
2019-01-25 16:00 | 157 | 125
2019-01-25 16:30 | 146 | 115
2019-01-25 17:00 | 171 | 145
2019-01-25 17:30 | 195 | 175
2019-01-25 18:00 | 232 | 219
2019-01-25 18:30 | 218 | 210
2019-01-25 19:00 | 219 | 211
2019-01-25 19:30 | 206 | 197
2019-01-25 20:00 | 217 | 207
2019-01-25 20:30 | 222 | 213
2019-01-25 21:00 | 222 | 213
2019-01-25 21:30 | 205 | 195
2019-01-25 22:00 | 197 | 185
2019-01-25 22:30 | 246 | 236
2019-01-25 23:00 | 224 | 215
2019-01-25 23:30 | 214 | 204
2019-01-26 | 272 | 263
2019-01-26 00:30 | 368 | 363
2019-01-26 01:00 | 342 | 340
2019-01-26 01:30 | 312 | 309
2019-01-26 02:00 | 303 | 298
2019-01-26 02:30 | 307 | 302
2019-01-26 03:00 | 312 | 307
2019-01-26 03:30 | 329 | 324
2019-01-26 04:00 | 338 | 334
2019-01-26 04:30 | 322 | 318
2019-01-26 05:00 | 326 | 322
2019-01-26 05:30 | 339 | 334
2019-01-26 06:00 | 319 | 315
2019-01-26 06:30 | 315 | 310
2019-01-26 07:00 | 303 | 297
2019-01-26 07:30 | 300 | 292
2019-01-26 08:00 | 307 | 299
2019-01-26 08:30 | 281 | 270
2019-01-26 09:00 | 268 | 256
2019-01-26 09:30 | 312 | 301
2019-01-26 10:00 | 310 | 300
2019-01-26 10:30 | 211 | 195
2019-01-26 11:00 | 262 | 246
2019-01-26 11:30 | 244 | 231
2019-01-26 12:00 | 202 | 186
2019-01-26 12:30 | 162 | 140
2019-01-26 13:00 | 207 | 189
2019-01-26 13:30 | 269 | 256
2019-01-26 14:00 | 273 | 263
2019-01-26 14:30 | 248 | 238
2019-01-26 15:00 | 274 | 264
2019-01-26 15:30 | 297 | 290
2019-01-26 16:00 | 319 | 313
2019-01-26 16:30 | 311 | 306
2019-01-26 17:00 | 309 | 304
2019-01-26 17:30 | 327 | 323
2019-01-26 18:00 | 344 | 341
2019-01-26 18:30 | 351 | 348
2019-01-26 19:00 | 357 | 355
2019-01-26 19:30 | 360 | 358
2019-01-26 20:00 | 368 | 366
2019-01-26 20:30 | 348 | 347
2019-01-26 21:00 | 345 | 343
2019-01-26 21:30 | 355 | 353
2019-01-26 22:00 | 344 | 342
2019-01-26 22:30 | 339 | 337
2019-01-26 23:00 | 325 | 322
2019-01-26 23:30 | 360 | 357
2019-01-27 | 374 | 372
2019-01-27 00:30 | 407 | 406
2019-01-27 01:00 | 286 | 285
2019-01-27 01:30 | 271 | 266
2019-01-27 02:00 | 264 | 257
2019-01-27 02:30 | 268 | 261
2019-01-27 03:00 | 277 | 271
2019-01-27 03:30 | 261 | 254
2019-01-27 04:00 | 267 | 260
2019-01-27 04:30 | 262 | 256
2019-01-27 05:00 | 257 | 250
2019-01-27 05:30 | 266 | 259
2019-01-27 06:00 | 291 | 286
2019-01-27 06:30 | 295 | 291
2019-01-27 07:00 | 270 | 265
2019-01-27 07:30 | 252 | 246
2019-01-27 08:00 | 266 | 258
2019-01-27 08:30 | 273 | 265
2019-01-27 09:00 | 283 | 276
2019-01-27 09:30 | 272 | 265
2019-01-27 10:00 | 255 | 246
2019-01-27 10:30 | 255 | 245
2019-01-27 11:00 | 249 | 238
2019-01-27 11:30 | 248 | 236
2019-01-27 12:00 | 272 | 262
2019-01-27 12:30 | 198 | 185
2019-01-27 13:00 | 213 | 199
2019-01-27 13:30 | 240 | 227
2019-01-27 14:00 | 301 | 291
2019-01-27 14:30 | 318 | 311
2019-01-27 15:00 | 346 | 340
2019-01-27 15:30 | 343 | 338
2019-01-27 16:00 | 366 | 362
2019-01-27 16:30 | 352 | 348
2019-01-27 17:00 | 351 | 347
2019-01-27 17:30 | 386 | 383
2019-01-27 18:00 | 439 | 437
2019-01-27 18:30 | 458 | 458
2019-01-27 19:00 | 480 | 480
2019-01-27 19:30 | 492 | 492
2019-01-27 20:00 | 483 | 482
2019-01-27 20:30 | 455 | 454
2019-01-27 21:00 | 468 | 467
2019-01-27 21:30 | 467 | 467
2019-01-27 22:00 | 469 | 468
2019-01-27 22:30 | 441 | 440
2019-01-27 23:00 | 396 | 395
2019-01-27 23:30 | 405 | 403
2019-01-28 | 410 | 409
2019-01-28 00:30 | 429 | 428
2019-01-28 01:00 | 406 | 405
2019-01-28 01:30 | 384 | 383
2019-01-28 02:00 | 375 | 373
2019-01-28 02:30 | 377 | 375
2019-01-28 03:00 | 371 | 369
2019-01-28 03:30 | 367 | 365
2019-01-28 04:00 | 367 | 365
2019-01-28 04:30 | 379 | 377
2019-01-28 05:00 | 382 | 380
2019-01-28 05:30 | 386 | 385
2019-01-28 06:00 | 392 | 390
2019-01-28 06:30 | 404 | 402
2019-01-28 07:00 | 413 | 411
2019-01-28 07:30 | 428 | 427
2019-01-28 08:00 | 439 | 437
2019-01-28 08:30 | 448 | 446
2019-01-28 09:00 | 460 | 459
2019-01-28 09:30 | 464 | 462
2019-01-28 10:00 | 469 | 467
2019-01-28 10:30 | 466 | 464
2019-01-28 11:00 | 439 | 437
2019-01-28 11:30 | 451 | 449
2019-01-28 12:00 | 464 | 461
2019-01-28 12:30 | 481 | 479
2019-01-28 13:00 | 470 | 468
2019-01-28 13:30 | 441 | 439
2019-01-28 14:00 | 445 | 443
2019-01-28 14:30 | 430 | 428
2019-01-28 15:00 | 417 | 415
2019-01-28 15:30 | 419 | 416
2019-01-28 16:00 | 403 | 401
2019-01-28 16:30 | 413 | 411
2019-01-28 17:00 | 425 | 424
2019-01-28 17:30 | 437 | 436
2019-01-28 18:00 | 452 | 452
2019-01-28 18:30 | 474 | 473
2019-01-28 19:00 | 505 | 505
2019-01-28 19:30 | 525 | 525
2019-01-28 20:00 | 530 | 530
2019-01-28 20:30 | 514 | 514
2019-01-28 21:00 | 487 | 487
2019-01-28 21:30 | 469 | 468
2019-01-28 22:00 | 446 | 445
2019-01-28 22:30 | 426 | 425
2019-01-28 23:00 | 440 | 439
2019-01-28 23:30 | 418 | 417
2019-01-29 | 405 | 404
2019-01-29 00:30 | 402 | 401
2019-01-29 01:00 | 392 | 391
2019-01-29 01:30 | 390 | 389
2019-01-29 02:00 | 383 | 381
2019-01-29 02:30 | 370 | 368
2019-01-29 03:00 | 363 | 361
2019-01-29 03:30 | 358 | 356
2019-01-29 04:00 | 361 | 359
2019-01-29 04:30 | 371 | 369
2019-01-29 05:00 | 356 | 354
2019-01-29 05:30 | 353 | 350
2019-01-29 06:00 | 387 | 385
2019-01-29 06:30 | 411 | 410
2019-01-29 07:00 | 400 | 398
2019-01-29 07:30 | 462 | 460
2019-01-29 08:00 | 466 | 464
2019-01-29 08:30 | 489 | 488
2019-01-29 09:00 | 506 | 504
2019-01-29 09:30 | 507 | 506
2019-01-29 10:00 | 503 | 503
2019-01-29 10:30 | 487 | 487
2019-01-29 11:00 | 477 | 475
2019-01-29 11:30 | 427 | 424
2019-01-29 12:00 | 397 | 391
2019-01-29 12:30 | 419 | 411
2019-01-29 13:00 | 463 | 459
2019-01-29 13:30 | 498 | 495
2019-01-29 14:00 | 495 | 493
2019-01-29 14:30 | 490 | 489
2019-01-29 15:00 | 489 | 488
2019-01-29 15:30 | 460 | 459
2019-01-29 16:00 | 442 | 441
2019-01-29 16:30 | 420 | 418
2019-01-29 17:00 | 281 | 277
2019-01-29 17:30 | 297 | 289
2019-01-29 18:00 | 322 | 315
2019-01-29 18:30 | 336 | 331
2019-01-29 19:00 | 341 | 336
2019-01-29 19:30 | 366 | 361
2019-01-29 20:00 | 368 | 364
2019-01-29 20:30 | 353 | 349
2019-01-29 21:00 | 333 | 328
2019-01-29 21:30 | 433 | 428
2019-01-29 22:00 | 467 | 465
2019-01-29 22:30 | 449 | 448
2019-01-29 23:00 | 416 | 414
2019-01-29 23:30 | 416 | 414
2019-01-30 | 410 | 408
2019-01-30 00:30 | 412 | 409
2019-01-30 01:00 | 385 | 383
2019-01-30 01:30 | 368 | 364
2019-01-30 02:00 | 353 | 349
2019-01-30 02:30 | 359 | 354
2019-01-30 03:00 | 365 | 361
2019-01-30 03:30 | 365 | 360
2019-01-30 04:00 | 371 | 367
2019-01-30 04:30 | 380 | 376
2019-01-30 05:00 | 383 | 379
2019-01-30 05:30 | 395 | 391
2019-01-30 06:00 | 408 | 405
2019-01-30 06:30 | 417 | 414
2019-01-30 07:00 | 441 | 438
2019-01-30 07:30 | 495 | 493
2019-01-30 08:00 | 509 | 508
2019-01-30 08:30 | 517 | 516
2019-01-30 09:00 | 527 | 526
2019-01-30 09:30 | 535 | 534
2019-01-30 10:00 | 526 | 525
2019-01-30 10:30 | 523 | 522
2019-01-30 11:00 | 511 | 509
2019-01-30 11:30 | 504 | 502
2019-01-30 12:00 | 490 | 488
2019-01-30 12:30 | 484 | 482
2019-01-30 13:00 | 479 | 477
2019-01-30 13:30 | 460 | 458
2019-01-30 14:00 | 449 | 447
2019-01-30 14:30 | 440 | 437
2019-01-30 15:00 | 376 | 373
2019-01-30 15:30 | 306 | 302
2019-01-30 16:00 | 315 | 308
2019-01-30 16:30 | 328 | 322
2019-01-30 17:00 | 353 | 348
2019-01-30 17:30 | 358 | 353
2019-01-30 18:00 | 422 | 418
2019-01-30 18:30 | 459 | 456
2019-01-30 19:00 | 458 | 457
2019-01-30 19:30 | 421 | 420
2019-01-30 20:00 | 468 | 466
2019-01-30 20:30 | 508 | 507
2019-01-30 21:00 | 532 | 532
2019-01-30 21:30 | 513 | 513
2019-01-30 22:00 | 483 | 482
2019-01-30 22:30 | 454 | 452
2019-01-30 23:00 | 433 | 431
2019-01-30 23:30 | 398 | 396
2019-01-31 | 393 | 389
2019-01-31 00:30 | 399 | 396
2019-01-31 01:00 | 386 | 382
2019-01-31 01:30 | 381 | 377
2019-01-31 02:00 | 389 | 385
2019-01-31 02:30 | 382 | 378
2019-01-31 03:00 | 373 | 369
2019-01-31 03:30 | 375 | 371
2019-01-31 04:00 | 377 | 372
2019-01-31 04:30 | 381 | 377
2019-01-31 05:00 | 388 | 384
2019-01-31 05:30 | 402 | 398
2019-01-31 06:00 | 413 | 410
2019-01-31 06:30 | 421 | 418
2019-01-31 07:00 | 413 | 410
2019-01-31 07:30 | 468 | 465
2019-01-31 08:00 | 501 | 499
2019-01-31 08:30 | 513 | 511
2019-01-31 09:00 | 533 | 532
2019-01-31 09:30 | 523 | 522
2019-01-31 10:00 | 514 | 513
2019-01-31 10:30 | 498 | 497
2019-01-31 11:00 | 496 | 495
2019-01-31 11:30 | 487 | 486
2019-01-31 12:00 | 492 | 491
2019-01-31 12:30 | 479 | 479
2019-01-31 13:00 | 471 | 470
2019-01-31 13:30 | 390 | 389
2019-01-31 14:00 | 323 | 320
2019-01-31 14:30 | 328 | 323
2019-01-31 15:00 | 301 | 295
2019-01-31 15:30 | 287 | 270
2019-01-31 16:00 | 300 | 291
2019-01-31 16:30 | 279 | 272
2019-01-31 17:00 | 289 | 282
2019-01-31 17:30 | 301 | 295
2019-01-31 18:00 | 339 | 334
2019-01-31 18:30 | 385 | 381
2019-01-31 19:00 | 451 | 449
2019-01-31 19:30 | 478 | 477
2019-01-31 20:00 | 462 | 461
2019-01-31 20:30 | 561 | 560
2019-01-31 21:00 | 576 | 576
2019-01-31 21:30 | 552 | 552
2019-01-31 22:00 | 530 | 530
2019-01-31 22:30 | 505 | 505
2019-01-31 23:00 | 483 | 482
2019-01-31 23:30 | 464 | 463
2019-02-01 | 451 | 449
2019-02-01 00:30 | 455 | 453
2019-02-01 01:00 | 429 | 427
2019-02-01 01:30 | 415 | 413
2019-02-01 02:00 | 401 | 398
2019-02-01 02:30 | 398 | 394
2019-02-01 03:00 | 399 | 395
2019-02-01 03:30 | 385 | 381
2019-02-01 04:00 | 365 | 361
2019-02-01 04:30 | 369 | 364
2019-02-01 05:00 | 368 | 364
2019-02-01 05:30 | 382 | 377
2019-02-01 06:00 | 398 | 394
2019-02-01 06:30 | 420 | 416
2019-02-01 07:00 | 432 | 429
2019-02-01 07:30 | 461 | 458
2019-02-01 08:00 | 490 | 489
2019-02-01 08:30 | 501 | 499
2019-02-01 09:00 | 483 | 481
2019-02-01 09:30 | 488 | 484
2019-02-01 10:00 | 502 | 498
2019-02-01 10:30 | 494 | 492
2019-02-01 11:00 | 473 | 471
2019-02-01 11:30 | 440 | 438
2019-02-01 12:00 | 443 | 440
2019-02-01 12:30 | 437 | 432
2019-02-01 13:00 | 445 | 441
2019-02-01 13:30 | 469 | 466
2019-02-01 14:00 | 481 | 477
2019-02-01 14:30 | 507 | 504
2019-02-01 15:00 | 501 | 499
2019-02-01 15:30 | 480 | 479
2019-02-01 16:00 | 493 | 491
2019-02-01 16:30 | 475 | 474
2019-02-01 17:00 | 483 | 482
2019-02-01 17:30 | 516 | 515
2019-02-01 18:00 | 535 | 535
2019-02-01 18:30 | 543 | 542
2019-02-01 19:00 | 559 | 559
2019-02-01 19:30 | 564 | 564
2019-02-01 20:00 | 544 | 544
2019-02-01 20:30 | 528 | 528
2019-02-01 21:00 | 512 | 511
2019-02-01 21:30 | 500 | 499
2019-02-01 22:00 | 482 | 481
2019-02-01 22:30 | 459 | 458
2019-02-01 23:00 | 445 | 444
2019-02-01 23:30 | 425 | 424
2019-02-02 | 415 | 413
2019-02-02 00:30 | 421 | 419
2019-02-02 01:00 | 389 | 387
2019-02-02 01:30 | 285 | 282
2019-02-02 02:00 | 282 | 275
2019-02-02 02:30 | 267 | 259
2019-02-02 03:00 | 270 | 262
2019-02-02 03:30 | 272 | 264
2019-02-02 04:00 | 265 | 257
2019-02-02 04:30 | 261 | 252
2019-02-02 05:00 | 288 | 281
2019-02-02 05:30 | 321 | 316
2019-02-02 06:00 | 330 | 326
2019-02-02 06:30 | 348 | 344
2019-02-02 07:00 | 353 | 349
2019-02-02 07:30 | 367 | 363
2019-02-02 08:00 | 385 | 381
2019-02-02 08:30 | 403 | 399
2019-02-02 09:00 | 416 | 413
2019-02-02 09:30 | 421 | 417
2019-02-02 10:00 | 420 | 416
2019-02-02 10:30 | 412 | 407
2019-02-02 11:00 | 398 | 394
2019-02-02 11:30 | 415 | 411
2019-02-02 12:00 | 452 | 449
2019-02-02 12:30 | 439 | 436
2019-02-02 13:00 | 441 | 438
2019-02-02 13:30 | 442 | 438
2019-02-02 14:00 | 426 | 422
2019-02-02 14:30 | 403 | 400
2019-02-02 15:00 | 417 | 413
2019-02-02 15:30 | 441 | 438
2019-02-02 16:00 | 462 | 459
2019-02-02 16:30 | 445 | 443
2019-02-02 17:00 | 431 | 429
2019-02-02 17:30 | 443 | 441
2019-02-02 18:00 | 462 | 461
2019-02-02 18:30 | 481 | 481
2019-02-02 19:00 | 485 | 484
2019-02-02 19:30 | 491 | 490
2019-02-02 20:00 | 491 | 491
2019-02-02 20:30 | 468 | 468
2019-02-02 21:00 | 453 | 452
2019-02-02 21:30 | 426 | 425
2019-02-02 22:00 | 411 | 410
2019-02-02 22:30 | 399 | 397
2019-02-02 23:00 | 381 | 378
2019-02-02 23:30 | 357 | 355
2019-02-03 | 348 | 346
2019-02-03 00:30 | 353 | 351
2019-02-03 01:00 | 326 | 324
2019-02-03 01:30 | 315 | 312
2019-02-03 02:00 | 317 | 314
2019-02-03 02:30 | 312 | 309
2019-02-03 03:00 | 310 | 307
2019-02-03 03:30 | 304 | 301
2019-02-03 04:00 | 301 | 297
2019-02-03 04:30 | 302 | 298
2019-02-03 05:00 | 307 | 304
2019-02-03 05:30 | 307 | 303
2019-02-03 06:00 | 308 | 304
2019-02-03 06:30 | 317 | 313
2019-02-03 07:00 | 319 | 316
2019-02-03 07:30 | 330 | 327
2019-02-03 08:00 | 346 | 341
2019-02-03 08:30 | 365 | 361
2019-02-03 09:00 | 368 | 364
2019-02-03 09:30 | 374 | 370
2019-02-03 10:00 | 380 | 377
2019-02-03 10:30 | 393 | 390
2019-02-03 11:00 | 414 | 411
2019-02-03 11:30 | 399 | 396
2019-02-03 12:00 | 396 | 392
2019-02-03 12:30 | 361 | 356
2019-02-03 13:00 | 367 | 361
2019-02-03 13:30 | 377 | 372
2019-02-03 14:00 | 377 | 372
2019-02-03 14:30 | 355 | 351
2019-02-03 15:00 | 354 | 350
2019-02-03 15:30 | 410 | 406
2019-02-03 16:00 | 415 | 411
2019-02-03 16:30 | 451 | 448
2019-02-03 17:00 | 478 | 475
2019-02-03 17:30 | 486 | 484
2019-02-03 18:00 | 509 | 508
2019-02-03 18:30 | 510 | 509
2019-02-03 19:00 | 493 | 492
2019-02-03 19:30 | 488 | 488
2019-02-03 20:00 | 446 | 446
2019-02-03 20:30 | 426 | 425
2019-02-03 21:00 | 403 | 402
2019-02-03 21:30 | 375 | 374
2019-02-03 22:00 | 349 | 347
2019-02-03 22:30 | 333 | 330
2019-02-03 23:00 | 322 | 319
2019-02-03 23:30 | 303 | 299
2019-02-04 | 299 | 294
2019-02-04 00:30 | 308 | 303
2019-02-04 01:00 | 266 | 262
2019-02-04 01:30 | 262 | 257
2019-02-04 02:00 | 263 | 257
2019-02-04 02:30 | 259 | 253
2019-02-04 03:00 | 257 | 250
2019-02-04 03:30 | 237 | 229
2019-02-04 04:00 | 236 | 227
2019-02-04 04:30 | 238 | 229
2019-02-04 05:00 | 243 | 234
2019-02-04 05:30 | 246 | 237
2019-02-04 06:00 | 267 | 260
2019-02-04 06:30 | 291 | 285
2019-02-04 07:00 | 317 | 313
2019-02-04 07:30 | 340 | 337
2019-02-04 08:00 | 356 | 354
2019-02-04 08:30 | 359 | 356
2019-02-04 09:00 | 338 | 335
2019-02-04 09:30 | 343 | 340
2019-02-04 10:00 | 325 | 321
2019-02-04 10:30 | 323 | 319
2019-02-04 11:00 | 324 | 318
2019-02-04 11:30 | 324 | 318
2019-02-04 12:00 | 311 | 306
2019-02-04 12:30 | 256 | 249
2019-02-04 13:00 | 246 | 236
2019-02-04 13:30 | 201 | 186
2019-02-04 14:00 | 230 | 215
2019-02-04 14:30 | 199 | 184
2019-02-04 15:00 | 244 | 232
2019-02-04 15:30 | 248 | 239
2019-02-04 16:00 | 249 | 240
2019-02-04 16:30 | 257 | 249
2019-02-04 17:00 | 261 | 254
2019-02-04 17:30 | 284 | 278
2019-02-04 18:00 | 297 | 293
2019-02-04 18:30 | 300 | 297
2019-02-04 19:00 | 317 | 314
2019-02-04 19:30 | 323 | 320
2019-02-04 20:00 | 303 | 300
2019-02-04 20:30 | 277 | 274
2019-02-04 21:00 | 297 | 292
2019-02-04 21:30 | 311 | 307
2019-02-04 22:00 | 291 | 288
2019-02-04 22:30 | 325 | 322
2019-02-04 23:00 | 315 | 312
2019-02-04 23:30 | 298 | 295
2019-02-05 | 291 | 287
2019-02-05 00:30 | 306 | 303
2019-02-05 01:00 | 275 | 271
2019-02-05 01:30 | 261 | 256
2019-02-05 02:00 | 243 | 237
2019-02-05 02:30 | 250 | 243
2019-02-05 03:00 | 247 | 240
2019-02-05 03:30 | 226 | 219
2019-02-05 04:00 | 227 | 219
2019-02-05 04:30 | 235 | 228
2019-02-05 05:00 | 247 | 240
2019-02-05 05:30 | 254 | 248
2019-02-05 06:00 | 277 | 272
2019-02-05 06:30 | 306 | 302
2019-02-05 07:00 | 319 | 316
2019-02-05 07:30 | 354 | 351
2019-02-05 08:00 | 361 | 358
2019-02-05 08:30 | 346 | 343
2019-02-05 09:00 | 327 | 323
2019-02-05 09:30 | 307 | 303
2019-02-05 10:00 | 282 | 275
2019-02-05 10:30 | 274 | 265
2019-02-05 11:00 | 280 | 271
2019-02-05 11:30 | 273 | 263
2019-02-05 12:00 | 268 | 259
2019-02-05 12:30 | 274 | 266
2019-02-05 13:00 | 243 | 235
2019-02-05 13:30 | 260 | 251
2019-02-05 14:00 | 284 | 276
2019-02-05 14:30 | 299 | 290
2019-02-05 15:00 | 363 | 351
2019-02-05 15:30 | 421 | 408
2019-02-05 16:00 | 459 | 456
2019-02-05 16:30 | 456 | 455
2019-02-05 17:00 | 518 | 512
2019-02-05 17:30 | 523 | 522
2019-02-05 18:00 | 538 | 538
2019-02-05 18:30 | 507 | 507
2019-02-05 19:00 | 533 | 533
2019-02-05 19:30 | 538 | 538
2019-02-05 20:00 | 520 | 520
2019-02-05 20:30 | 503 | 503
2019-02-05 21:00 | 485 | 485
2019-02-05 21:30 | 450 | 450
2019-02-05 22:00 | 437 | 437
2019-02-05 22:30 | 423 | 422
2019-02-05 23:00 | 401 | 400
2019-02-05 23:30 | 371 | 369
2019-02-06 | 361 | 359
2019-02-06 00:30 | 376 | 373
2019-02-06 01:00 | 358 | 356
2019-02-06 01:30 | 341 | 338
2019-02-06 02:00 | 333 | 330
2019-02-06 02:30 | 319 | 315
2019-02-06 03:00 | 311 | 307
2019-02-06 03:30 | 312 | 308
2019-02-06 04:00 | 317 | 313
2019-02-06 04:30 | 314 | 310
2019-02-06 05:00 | 310 | 306
2019-02-06 05:30 | 313 | 309
2019-02-06 06:00 | 320 | 316
2019-02-06 06:30 | 355 | 352
2019-02-06 07:00 | 391 | 388
2019-02-06 07:30 | 431 | 429
2019-02-06 08:00 | 450 | 449
2019-02-06 08:30 | 456 | 454
2019-02-06 09:00 | 444 | 443
2019-02-06 09:30 | 436 | 434
2019-02-06 10:00 | 420 | 418
2019-02-06 10:30 | 392 | 389
2019-02-06 11:00 | 368 | 364
2019-02-06 11:30 | 340 | 336
2019-02-06 12:00 | 299 | 292
2019-02-06 12:30 | 289 | 280
2019-02-06 13:00 | 286 | 276
2019-02-06 13:30 | 284 | 274
2019-02-06 14:00 | 293 | 282
2019-02-06 14:30 | 278 | 265
2019-02-06 15:00 | 273 | 252
2019-02-06 15:30 | 231 | 216
2019-02-06 16:00 | 198 | 172
2019-02-06 16:30 | 215 | 190
2019-02-06 17:00 | 287 | 273
2019-02-06 17:30 | 319 | 310
2019-02-06 18:00 | 342 | 334
2019-02-06 18:30 | 335 | 329
2019-02-06 19:00 | 357 | 351
2019-02-06 19:30 | 349 | 346
2019-02-06 20:00 | 355 | 352
2019-02-06 20:30 | 359 | 357
2019-02-06 21:00 | 414 | 412
2019-02-06 21:30 | 396 | 394
2019-02-06 22:00 | 380 | 379
2019-02-06 22:30 | 389 | 387
2019-02-06 23:00 | 369 | 367
2019-02-06 23:30 | 374 | 371
2019-02-07 | 354 | 352
2019-02-07 00:30 | 360 | 357
2019-02-07 01:00 | 341 | 339
2019-02-07 01:30 | 331 | 328
2019-02-07 02:00 | 313 | 309
2019-02-07 02:30 | 309 | 304
2019-02-07 03:00 | 306 | 300
2019-02-07 03:30 | 290 | 284
2019-02-07 04:00 | 281 | 275
2019-02-07 04:30 | 281 | 275
2019-02-07 05:00 | 291 | 285
2019-02-07 05:30 | 304 | 299
2019-02-07 06:00 | 316 | 311
2019-02-07 06:30 | 359 | 354
2019-02-07 07:00 | 386 | 383
2019-02-07 07:30 | 424 | 421
2019-02-07 08:00 | 435 | 432
2019-02-07 08:30 | 433 | 430
2019-02-07 09:00 | 404 | 401
2019-02-07 09:30 | 393 | 389
2019-02-07 10:00 | 398 | 393
2019-02-07 10:30 | 362 | 357
2019-02-07 11:00 | 360 | 355
2019-02-07 11:30 | 399 | 394
2019-02-07 12:00 | 393 | 389
2019-02-07 12:30 | 449 | 432
2019-02-07 13:00 | 450 | 433
2019-02-07 13:30 | 405 | 387
2019-02-07 14:00 | 390 | 375
2019-02-07 14:30 | 377 | 369
2019-02-07 15:00 | 318 | 310
2019-02-07 15:30 | 316 | 308
2019-02-07 16:00 | 354 | 346
2019-02-07 16:30 | 367 | 360
2019-02-07 17:00 | 367 | 361
2019-02-07 17:30 | 376 | 369
2019-02-07 18:00 | 393 | 388
2019-02-07 18:30 | 414 | 410
2019-02-07 19:00 | 427 | 424
2019-02-07 19:30 | 436 | 433
2019-02-07 20:00 | 428 | 426
2019-02-07 20:30 | 413 | 411
2019-02-07 21:00 | 436 | 434
2019-02-07 21:30 | 400 | 398
2019-02-07 22:00 | 391 | 388
2019-02-07 22:30 | 428 | 425
2019-02-07 23:00 | 409 | 407
2019-02-07 23:30 | 392 | 390
2019-02-08 | 380 | 377
2019-02-08 00:30 | 397 | 393
2019-02-08 01:00 | 383 | 379
2019-02-08 01:30 | 372 | 368
2019-02-08 02:00 | 367 | 364
2019-02-08 02:30 | 366 | 363
2019-02-08 03:00 | 360 | 356
2019-02-08 03:30 | 358 | 353
2019-02-08 04:00 | 357 | 352
2019-02-08 04:30 | 359 | 355
2019-02-08 05:00 | 365 | 361
2019-02-08 05:30 | 377 | 374
2019-02-08 06:00 | 395 | 391
2019-02-08 06:30 | 411 | 408
2019-02-08 07:00 | 434 | 431
2019-02-08 07:30 | 456 | 454
2019-02-08 08:00 | 454 | 451
2019-02-08 08:30 | 450 | 447
2019-02-08 09:00 | 443 | 440
2019-02-08 09:30 | 418 | 414
2019-02-08 10:00 | 382 | 371
2019-02-08 10:30 | 347 | 323
2019-02-08 11:00 | 331 | 308
2019-02-08 11:30 | 375 | 342
2019-02-08 12:00 | 359 | 329
2019-02-08 12:30 | 378 | 349
2019-02-08 13:00 | 395 | 378
2019-02-08 13:30 | 407 | 388
2019-02-08 14:00 | 448 | 441
2019-02-08 14:30 | 473 | 468
2019-02-08 15:00 | 448 | 444
2019-02-08 15:30 | 487 | 483
2019-02-08 16:00 | 475 | 472
2019-02-08 16:30 | 489 | 487
2019-02-08 17:00 | 513 | 511
2019-02-08 17:30 | 519 | 518
2019-02-08 18:00 | 544 | 542
2019-02-08 18:30 | 564 | 562
2019-02-08 19:00 | 571 | 569
2019-02-08 19:30 | 582 | 581
2019-02-08 20:00 | 574 | 574
2019-02-08 20:30 | 556 | 556
2019-02-08 21:00 | 535 | 535
2019-02-08 21:30 | 508 | 507
2019-02-08 22:00 | 490 | 488
2019-02-08 22:30 | 465 | 463
2019-02-08 23:00 | 438 | 435
2019-02-08 23:30 | 418 | 414
2019-02-09 | 398 | 393
2019-02-09 00:30 | 395 | 390
2019-02-09 01:00 | 366 | 360
2019-02-09 01:30 | 352 | 345
2019-02-09 02:00 | 352 | 344
2019-02-09 02:30 | 352 | 344
2019-02-09 03:00 | 368 | 361
2019-02-09 03:30 | 374 | 368
2019-02-09 04:00 | 375 | 370
2019-02-09 04:30 | 375 | 369
2019-02-09 05:00 | 367 | 361
2019-02-09 05:30 | 370 | 363
2019-02-09 06:00 | 370 | 364
2019-02-09 06:30 | 367 | 361
2019-02-09 07:00 | 356 | 350
2019-02-09 07:30 | 374 | 368
2019-02-09 08:00 | 374 | 367
2019-02-09 08:30 | 335 | 324
2019-02-09 09:00 | 342 | 331
2019-02-09 09:30 | 324 | 313
2019-02-09 10:00 | 337 | 325
2019-02-09 10:30 | 313 | 296
2019-02-09 11:00 | 298 | 280
2019-02-09 11:30 | 320 | 302
2019-02-09 12:00 | 317 | 300
2019-02-09 12:30 | 312 | 294
2019-02-09 13:00 | 300 | 281
2019-02-09 13:30 | 297 | 278
2019-02-09 14:00 | 315 | 298
2019-02-09 14:30 | 314 | 295
2019-02-09 15:00 | 318 | 300
2019-02-09 15:30 | 337 | 322
2019-02-09 16:00 | 354 | 341
2019-02-09 16:30 | 394 | 383
2019-02-09 17:00 | 422 | 414
2019-02-09 17:30 | 482 | 476
2019-02-09 18:00 | 531 | 527
2019-02-09 18:30 | 559 | 556
2019-02-09 19:00 | 596 | 595
2019-02-09 19:30 | 596 | 596
2019-02-09 20:00 | 588 | 587
2019-02-09 20:30 | 569 | 569
2019-02-09 21:00 | 556 | 556
2019-02-09 21:30 | 541 | 541
2019-02-09 22:00 | 536 | 535
2019-02-09 22:30 | 508 | 507
2019-02-09 23:00 | 486 | 485
2019-02-09 23:30 | 451 | 450
2019-02-10 | 422 | 419
2019-02-10 00:30 | 423 | 420
2019-02-10 01:00 | 401 | 397
2019-02-10 01:30 | 387 | 382
2019-02-10 02:00 | 378 | 372
2019-02-10 02:30 | 367 | 361
2019-02-10 03:00 | 352 | 345
2019-02-10 03:30 | 345 | 337
2019-02-10 04:00 | 333 | 324
2019-02-10 04:30 | 337 | 327
2019-02-10 05:00 | 346 | 337
2019-02-10 05:30 | 346 | 337
2019-02-10 06:00 | 338 | 329
2019-02-10 06:30 | 311 | 301
2019-02-10 07:00 | 281 | 268
2019-02-10 07:30 | 261 | 242
2019-02-10 08:00 | 236 | 213
2019-02-10 08:30 | 228 | 201
2019-02-10 09:00 | 227 | 184
2019-02-10 09:30 | 218 | 192
2019-02-10 10:00 | 232 | 208
2019-02-10 10:30 | 239 | 216
2019-02-10 11:00 | 237 | 215
2019-02-10 11:30 | 239 | 218
2019-02-10 12:00 | 248 | 228
2019-02-10 12:30 | 256 | 237
2019-02-10 13:00 | 270 | 252
2019-02-10 13:30 | 287 | 270
2019-02-10 14:00 | 301 | 285
2019-02-10 14:30 | 326 | 312
2019-02-10 15:00 | 346 | 333
2019-02-10 15:30 | 396 | 387
2019-02-10 16:00 | 436 | 429
2019-02-10 16:30 | 418 | 412
2019-02-10 17:00 | 528 | 523
2019-02-10 17:30 | 589 | 587
2019-02-10 18:00 | 606 | 606
2019-02-10 18:30 | 608 | 608
2019-02-10 19:00 | 649 | 649
2019-02-10 19:30 | 639 | 639
2019-02-10 20:00 | 631 | 631
2019-02-10 20:30 | 623 | 623
2019-02-10 21:00 | 598 | 598
2019-02-10 21:30 | 575 | 575
2019-02-10 22:00 | 550 | 550
2019-02-10 22:30 | 514 | 513
2019-02-10 23:00 | 486 | 485
2019-02-10 23:30 | 452 | 449
2019-02-11 | 430 | 427
2019-02-11 00:30 | 412 | 409
2019-02-11 01:00 | 377 | 373
2019-02-11 01:30 | 358 | 354
2019-02-11 02:00 | 342 | 337
2019-02-11 02:30 | 338 | 331
2019-02-11 03:00 | 333 | 326
2019-02-11 03:30 | 338 | 331
2019-02-11 04:00 | 341 | 335
2019-02-11 04:30 | 344 | 337
2019-02-11 05:00 | 348 | 342
2019-02-11 05:30 | 365 | 359
2019-02-11 06:00 | 384 | 379
2019-02-11 06:30 | 408 | 404
2019-02-11 07:00 | 399 | 395
2019-02-11 07:30 | 385 | 379
2019-02-11 08:00 | 374 | 366
2019-02-11 08:30 | 355 | 346
2019-02-11 09:00 | 351 | 340
2019-02-11 09:30 | 341 | 329
2019-02-11 10:00 | 337 | 325
2019-02-11 10:30 | 301 | 289
2019-02-11 11:00 | 236 | 217
2019-02-11 11:30 | 221 | 198
2019-02-11 12:00 | 234 | 211
2019-02-11 12:30 | 244 | 223
2019-02-11 13:00 | 252 | 231
2019-02-11 13:30 | 264 | 245
2019-02-11 14:00 | 259 | 241
2019-02-11 14:30 | 246 | 227
2019-02-11 15:00 | 272 | 253
2019-02-11 15:30 | 297 | 281
2019-02-11 16:00 | 330 | 316
2019-02-11 16:30 | 379 | 369
2019-02-11 17:00 | 410 | 403
2019-02-11 17:30 | 466 | 460
2019-02-11 18:00 | 496 | 494
2019-02-11 18:30 | 507 | 505
2019-02-11 19:00 | 539 | 539
2019-02-11 19:30 | 554 | 554
2019-02-11 20:00 | 559 | 559
2019-02-11 20:30 | 571 | 571
2019-02-11 21:00 | 554 | 553
2019-02-11 21:30 | 524 | 523
2019-02-11 22:00 | 514 | 513
2019-02-11 22:30 | 433 | 432
2019-02-11 23:00 | 396 | 393
2019-02-11 23:30 | 476 | 473
2019-02-12 | 483 | 482
2019-02-12 00:30 | 480 | 479
2019-02-12 01:00 | 458 | 457
2019-02-12 01:30 | 443 | 442
2019-02-12 02:00 | 430 | 428
2019-02-12 02:30 | 416 | 414
2019-02-12 03:00 | 397 | 395
2019-02-12 03:30 | 375 | 373
2019-02-12 04:00 | 355 | 351
2019-02-12 04:30 | 355 | 351
2019-02-12 05:00 | 352 | 348
2019-02-12 05:30 | 371 | 366
2019-02-12 06:00 | 381 | 377
2019-02-12 06:30 | 389 | 385
2019-02-12 07:00 | 385 | 381
2019-02-12 07:30 | 422 | 418
2019-02-12 08:00 | 413 | 409
2019-02-12 08:30 | 350 | 343
2019-02-12 09:00 | 349 | 339
2019-02-12 09:30 | 350 | 339
2019-02-12 10:00 | 334 | 322
2019-02-12 10:30 | 323 | 311
2019-02-12 11:00 | 312 | 298
2019-02-12 11:30 | 316 | 301
2019-02-12 12:00 | 319 | 306
2019-02-12 12:30 | 346 | 333
2019-02-12 13:00 | 347 | 335
2019-02-12 13:30 | 297 | 284
2019-02-12 14:00 | 324 | 310
2019-02-12 14:30 | 333 | 320
2019-02-12 15:00 | 332 | 320
2019-02-12 15:30 | 315 | 303
2019-02-12 16:00 | 288 | 274
2019-02-12 16:30 | 280 | 265
2019-02-12 17:00 | 287 | 273
2019-02-12 17:30 | 343 | 331
2019-02-12 18:00 | 385 | 375
2019-02-12 18:30 | 443 | 438
2019-02-12 19:00 | 432 | 429
2019-02-12 19:30 | 457 | 456
2019-02-12 20:00 | 502 | 501
2019-02-12 20:30 | 506 | 505
2019-02-12 21:00 | 508 | 507
2019-02-12 21:30 | 495 | 494
2019-02-12 22:00 | 467 | 466
2019-02-12 22:30 | 429 | 428
2019-02-12 23:00 | 393 | 391
2019-02-12 23:30 | 365 | 361
2019-02-13 | 343 | 338
2019-02-13 00:30 | 339 | 333
2019-02-13 01:00 | 314 | 307
2019-02-13 01:30 | 304 | 296
2019-02-13 02:00 | 293 | 284
2019-02-13 02:30 | 281 | 270
2019-02-13 03:00 | 272 | 260
2019-02-13 03:30 | 258 | 245
2019-02-13 04:00 | 256 | 242
2019-02-13 04:30 | 255 | 241
2019-02-13 05:00 | 250 | 237
2019-02-13 05:30 | 259 | 247
2019-02-13 06:00 | 263 | 250
2019-02-13 06:30 | 252 | 240
2019-02-13 07:00 | 269 | 257
2019-02-13 07:30 | 270 | 257
2019-02-13 08:00 | 232 | 213
2019-02-13 08:30 | 200 | 176
2019-02-13 09:00 | 187 | 158
2019-02-13 09:30 | 186 | 155
2019-02-13 10:00 | 189 | 158
2019-02-13 10:30 | 187 | 153
2019-02-13 11:00 | 192 | 159
2019-02-13 11:30 | 199 | 168
2019-02-13 12:00 | 200 | 170
2019-02-13 12:30 | 219 | 191
2019-02-13 13:00 | 218 | 190
2019-02-13 13:30 | 232 | 208
2019-02-13 14:00 | 248 | 226
2019-02-13 14:30 | 254 | 234
2019-02-13 15:00 | 265 | 246
2019-02-13 15:30 | 255 | 236
2019-02-13 16:00 | 242 | 222
2019-02-13 16:30 | 239 | 219
2019-02-13 17:00 | 233 | 213
2019-02-13 17:30 | 197 | 160
2019-02-13 18:00 | 217 | 190
2019-02-13 18:30 | 249 | 228
2019-02-13 19:00 | 269 | 256
2019-02-13 19:30 | 280 | 273
2019-02-13 20:00 | 287 | 281
2019-02-13 20:30 | 236 | 229
2019-02-13 21:00 | 221 | 210
2019-02-13 21:30 | 293 | 284
2019-02-13 22:00 | 207 | 198
2019-02-13 22:30 | 346 | 338
2019-02-13 23:00 | 380 | 376
2019-02-13 23:30 | 347 | 344
2019-02-14 | 327 | 323
2019-02-14 00:30 | 343 | 339
2019-02-14 01:00 | 315 | 311
2019-02-14 01:30 | 304 | 298
2019-02-14 02:00 | 295 | 289
2019-02-14 02:30 | 282 | 275
2019-02-14 03:00 | 278 | 270
2019-02-14 03:30 | 276 | 267
2019-02-14 04:00 | 265 | 255
2019-02-14 04:30 | 265 | 254
2019-02-14 05:00 | 268 | 257
2019-02-14 05:30 | 272 | 262
2019-02-14 06:00 | 214 | 201
2019-02-14 06:30 | 224 | 208
2019-02-14 07:00 | 230 | 214
2019-02-14 07:30 | 231 | 215
2019-02-14 08:00 | 280 | 265
2019-02-14 08:30 | 255 | 238
2019-02-14 09:00 | 249 | 230
2019-02-14 09:30 | 237 | 218
2019-02-14 10:00 | 228 | 207
2019-02-14 10:30 | 209 | 186
2019-02-14 11:00 | 189 | 162
2019-02-14 11:30 | 193 | 165
2019-02-14 12:00 | 192 | 161
2019-02-14 12:30 | 211 | 183
2019-02-14 13:00 | 230 | 206
2019-02-14 13:30 | 239 | 219
2019-02-14 14:00 | 261 | 242
2019-02-14 14:30 | 297 | 282
2019-02-14 15:00 | 317 | 304
2019-02-14 15:30 | 336 | 324
2019-02-14 16:00 | 360 | 350
2019-02-14 16:30 | 416 | 408
2019-02-14 17:00 | 475 | 470
2019-02-14 17:30 | 507 | 504
2019-02-14 18:00 | 542 | 540
2019-02-14 18:30 | 559 | 558
2019-02-14 19:00 | 569 | 568
2019-02-14 19:30 | 562 | 562
2019-02-14 20:00 | 561 | 561
2019-02-14 20:30 | 556 | 556
2019-02-14 21:00 | 549 | 549
2019-02-14 21:30 | 510 | 509
2019-02-14 22:00 | 494 | 492
2019-02-14 22:30 | 429 | 427
2019-02-14 23:00 | 434 | 432
2019-02-14 23:30 | 467 | 465
2019-02-15 | 519 | 517
2019-02-15 00:30 | 500 | 500
2019-02-15 01:00 | 486 | 485
2019-02-15 01:30 | 472 | 471
2019-02-15 02:00 | 465 | 463
2019-02-15 02:30 | 453 | 451
2019-02-15 03:00 | 447 | 445
2019-02-15 03:30 | 444 | 442
2019-02-15 04:00 | 415 | 413
2019-02-15 04:30 | 368 | 365
2019-02-15 05:00 | 349 | 344
2019-02-15 05:30 | 398 | 393
2019-02-15 06:00 | 447 | 444
2019-02-15 06:30 | 470 | 468
2019-02-15 07:00 | 474 | 472
2019-02-15 07:30 | 476 | 474
2019-02-15 08:00 | 449 | 445
2019-02-15 08:30 | 407 | 401
2019-02-15 09:00 | 397 | 389
2019-02-15 09:30 | 365 | 357
2019-02-15 10:00 | 314 | 303
2019-02-15 10:30 | 308 | 296
2019-02-15 11:00 | 302 | 289
2019-02-15 11:30 | 305 | 292
2019-02-15 12:00 | 308 | 295
2019-02-15 12:30 | 315 | 303
2019-02-15 13:00 | 329 | 317
2019-02-15 13:30 | 344 | 333
2019-02-15 14:00 | 366 | 356
2019-02-15 14:30 | 409 | 402
2019-02-15 15:00 | 419 | 414
2019-02-15 15:30 | 439 | 435
2019-02-15 16:00 | 503 | 500
2019-02-15 16:30 | 478 | 476
2019-02-15 17:00 | 522 | 520
2019-02-15 17:30 | 548 | 547
2019-02-15 18:00 | 596 | 596
2019-02-15 18:30 | 619 | 619
2019-02-15 19:00 | 632 | 632
2019-02-15 19:30 | 656 | 656
2019-02-15 20:00 | 646 | 646
2019-02-15 20:30 | 621 | 621
2019-02-15 21:00 | 589 | 589
2019-02-15 21:30 | 583 | 582
2019-02-15 22:00 | 562 | 562
2019-02-15 22:30 | 536 | 536
2019-02-15 23:00 | 516 | 515
2019-02-15 23:30 | 488 | 487
2019-02-16 | 466 | 464
2019-02-16 00:30 | 465 | 463
2019-02-16 01:00 | 433 | 431
2019-02-16 01:30 | 421 | 417
2019-02-16 02:00 | 424 | 420
2019-02-16 02:30 | 414 | 409
2019-02-16 03:00 | 386 | 382
2019-02-16 03:30 | 367 | 362
2019-02-16 04:00 | 348 | 342
2019-02-16 04:30 | 331 | 325
2019-02-16 05:00 | 328 | 321
2019-02-16 05:30 | 342 | 335
2019-02-16 06:00 | 336 | 330
2019-02-16 06:30 | 315 | 308
2019-02-16 07:00 | 308 | 299
2019-02-16 07:30 | 309 | 298
2019-02-16 08:00 | 286 | 271
2019-02-16 08:30 | 265 | 245
2019-02-16 09:00 | 256 | 236
2019-02-16 09:30 | 267 | 247
2019-02-16 10:00 | 277 | 259
2019-02-16 10:30 | 275 | 257
2019-02-16 11:00 | 259 | 240
2019-02-16 11:30 | 270 | 251
2019-02-16 12:00 | 289 | 272
2019-02-16 12:30 | 289 | 272
2019-02-16 13:00 | 283 | 267
2019-02-16 13:30 | 293 | 277
2019-02-16 14:00 | 296 | 281
2019-02-16 14:30 | 305 | 291
2019-02-16 15:00 | 336 | 323
2019-02-16 15:30 | 356 | 346
2019-02-16 16:00 | 380 | 371
2019-02-16 16:30 | 379 | 371
2019-02-16 17:00 | 431 | 425
2019-02-16 17:30 | 462 | 457
2019-02-16 18:00 | 527 | 524
2019-02-16 18:30 | 570 | 569
2019-02-16 19:00 | 594 | 594
2019-02-16 19:30 | 604 | 604
2019-02-16 20:00 | 592 | 592
2019-02-16 20:30 | 557 | 557
2019-02-16 21:00 | 553 | 552
2019-02-16 21:30 | 567 | 566
2019-02-16 22:00 | 565 | 564
2019-02-16 22:30 | 527 | 526
2019-02-16 23:00 | 499 | 498
2019-02-16 23:30 | 487 | 486
2019-02-17 | 474 | 473
2019-02-17 00:30 | 471 | 469
2019-02-17 01:00 | 440 | 438
2019-02-17 01:30 | 424 | 421
2019-02-17 02:00 | 409 | 406
2019-02-17 02:30 | 398 | 394
2019-02-17 03:00 | 400 | 396
2019-02-17 03:30 | 398 | 395
2019-02-17 04:00 | 410 | 406
2019-02-17 04:30 | 411 | 407
2019-02-17 05:00 | 408 | 404
2019-02-17 05:30 | 406 | 402
2019-02-17 06:00 | 409 | 405
2019-02-17 06:30 | 397 | 393
2019-02-17 07:00 | 390 | 385
2019-02-17 07:30 | 394 | 388
2019-02-17 08:00 | 381 | 374
2019-02-17 08:30 | 319 | 307
2019-02-17 09:00 | 305 | 291
2019-02-17 09:30 | 308 | 293
2019-02-17 10:00 | 292 | 274
2019-02-17 10:30 | 308 | 291
2019-02-17 11:00 | 324 | 308
2019-02-17 11:30 | 310 | 294
2019-02-17 12:00 | 306 | 290
2019-02-17 12:30 | 374 | 360
2019-02-17 13:00 | 354 | 342
2019-02-17 13:30 | 413 | 403
2019-02-17 14:00 | 377 | 367
2019-02-17 14:30 | 400 | 391
2019-02-17 15:00 | 378 | 369
2019-02-17 15:30 | 385 | 377
2019-02-17 16:00 | 471 | 465
2019-02-17 16:30 | 432 | 428
2019-02-17 17:00 | 425 | 419
2019-02-17 17:30 | 534 | 529
2019-02-17 18:00 | 568 | 566
2019-02-17 18:30 | 588 | 587
2019-02-17 19:00 | 606 | 605
2019-02-17 19:30 | 617 | 617
2019-02-17 20:00 | 603 | 603
2019-02-17 20:30 | 594 | 593
2019-02-17 21:00 | 597 | 596
2019-02-17 21:30 | 572 | 571
2019-02-17 22:00 | 537 | 536
2019-02-17 22:30 | 512 | 510
2019-02-17 23:00 | 485 | 483
2019-02-17 23:30 | 463 | 461
2019-02-18 | 463 | 460
2019-02-18 00:30 | 471 | 469
2019-02-18 01:00 | 443 | 441
2019-02-18 01:30 | 426 | 424
2019-02-18 02:00 | 418 | 416
2019-02-18 02:30 | 413 | 410
2019-02-18 03:00 | 407 | 405
2019-02-18 03:30 | 408 | 406
2019-02-18 04:00 | 405 | 402
2019-02-18 04:30 | 407 | 404
2019-02-18 05:00 | 409 | 406
2019-02-18 05:30 | 421 | 418
2019-02-18 06:00 | 433 | 430
2019-02-18 06:30 | 448 | 446
2019-02-18 07:00 | 464 | 461
2019-02-18 07:30 | 468 | 465
2019-02-18 08:00 | 442 | 438
2019-02-18 08:30 | 403 | 397
2019-02-18 09:00 | 363 | 355
2019-02-18 09:30 | 357 | 347
2019-02-18 10:00 | 328 | 317
2019-02-18 10:30 | 342 | 330
2019-02-18 11:00 | 349 | 338
2019-02-18 11:30 | 325 | 313
2019-02-18 12:00 | 317 | 304
2019-02-18 12:30 | 332 | 319
2019-02-18 13:00 | 351 | 340
2019-02-18 13:30 | 368 | 358
2019-02-18 14:00 | 413 | 404
2019-02-18 14:30 | 405 | 397
2019-02-18 15:00 | 420 | 412
2019-02-18 15:30 | 416 | 409
2019-02-18 16:00 | 432 | 426
2019-02-18 16:30 | 483 | 478
2019-02-18 17:00 | 548 | 544
2019-02-18 17:30 | 581 | 579
2019-02-18 18:00 | 614 | 613
2019-02-18 18:30 | 653 | 653
2019-02-18 19:00 | 681 | 681
2019-02-18 19:30 | 695 | 695
2019-02-18 20:00 | 681 | 681
2019-02-18 20:30 | 651 | 651
2019-02-18 21:00 | 628 | 628
2019-02-18 21:30 | 628 | 628
2019-02-18 22:00 | 592 | 592
2019-02-18 22:30 | 557 | 557
2019-02-18 23:00 | 525 | 524
2019-02-18 23:30 | 498 | 497
2019-02-19 | 482 | 480
2019-02-19 00:30 | 486 | 484
2019-02-19 01:00 | 462 | 460
2019-02-19 01:30 | 446 | 444
2019-02-19 02:00 | 444 | 441
2019-02-19 02:30 | 437 | 434
2019-02-19 03:00 | 427 | 424
2019-02-19 03:30 | 420 | 416
2019-02-19 04:00 | 408 | 405
2019-02-19 04:30 | 401 | 396
2019-02-19 05:00 | 397 | 393
2019-02-19 05:30 | 369 | 364
2019-02-19 06:00 | 353 | 347
2019-02-19 06:30 | 362 | 357
2019-02-19 07:00 | 378 | 373
2019-02-19 07:30 | 358 | 351
2019-02-19 08:00 | 348 | 338
2019-02-19 08:30 | 325 | 311
2019-02-19 09:00 | 315 | 300
2019-02-19 09:30 | 291 | 275
2019-02-19 10:00 | 284 | 266
2019-02-19 10:30 | 282 | 263
2019-02-19 11:00 | 274 | 255
2019-02-19 11:30 | 272 | 252
2019-02-19 12:00 | 274 | 254
2019-02-19 12:30 | 290 | 272
2019-02-19 13:00 | 317 | 301
2019-02-19 13:30 | 325 | 309
2019-02-19 14:00 | 351 | 338
2019-02-19 14:30 | 355 | 343
2019-02-19 15:00 | 359 | 346
2019-02-19 15:30 | 349 | 336
2019-02-19 16:00 | 377 | 365
2019-02-19 16:30 | 445 | 435
2019-02-19 17:00 | 482 | 475
2019-02-19 17:30 | 513 | 510
2019-02-19 18:00 | 576 | 575
2019-02-19 18:30 | 619 | 619
2019-02-19 19:00 | 625 | 625
2019-02-19 19:30 | 651 | 651
2019-02-19 20:00 | 659 | 658
2019-02-19 20:30 | 680 | 680
2019-02-19 21:00 | 659 | 659
2019-02-19 21:30 | 640 | 640
2019-02-19 22:00 | 599 | 599
2019-02-19 22:30 | 564 | 564
2019-02-19 23:00 | 536 | 536
2019-02-19 23:30 | 516 | 515
2019-02-20 | 489 | 488
2019-02-20 00:30 | 481 | 480
2019-02-20 01:00 | 455 | 454
2019-02-20 01:30 | 438 | 436
2019-02-20 02:00 | 436 | 434
2019-02-20 02:30 | 417 | 415
2019-02-20 03:00 | 407 | 404
2019-02-20 03:30 | 406 | 403
2019-02-20 04:00 | 406 | 403
2019-02-20 04:30 | 404 | 400
2019-02-20 05:00 | 409 | 406
2019-02-20 05:30 | 420 | 417
2019-02-20 06:00 | 433 | 430
2019-02-20 06:30 | 389 | 386
2019-02-20 07:00 | 381 | 377
2019-02-20 07:30 | 326 | 319
2019-02-20 08:00 | 298 | 285
2019-02-20 08:30 | 261 | 244
2019-02-20 09:00 | 222 | 201
2019-02-20 09:30 | 203 | 177
2019-02-20 10:00 | 207 | 178
2019-02-20 10:30 | 219 | 189
2019-02-20 11:00 | 219 | 187
2019-02-20 11:30 | 215 | 183
2019-02-20 12:00 | 211 | 175
2019-02-20 12:30 | 230 | 194
2019-02-20 13:00 | 240 | 214
2019-02-20 13:30 | 252 | 231
2019-02-20 14:00 | 270 | 250
2019-02-20 14:30 | 298 | 278
2019-02-20 15:00 | 306 | 290
2019-02-20 15:30 | 311 | 294
2019-02-20 16:00 | 346 | 333
2019-02-20 16:30 | 378 | 367
2019-02-20 17:00 | 435 | 426
2019-02-20 17:30 | 485 | 483
2019-02-20 18:00 | 543 | 543
2019-02-20 18:30 | 579 | 579
2019-02-20 19:00 | 605 | 605
2019-02-20 19:30 | 601 | 601
2019-02-20 20:00 | 587 | 587
2019-02-20 20:30 | 570 | 570
2019-02-20 21:00 | 614 | 614
2019-02-20 21:30 | 658 | 658
2019-02-20 22:00 | 716 | 716
2019-02-20 22:30 | 665 | 664
2019-02-20 23:00 | 601 | 600
2019-02-20 23:30 | 560 | 560
2019-02-21 | 524 | 524
2019-02-21 00:30 | 502 | 502
2019-02-21 01:00 | 491 | 490
2019-02-21 01:30 | 477 | 476
2019-02-21 02:00 | 468 | 467
2019-02-21 02:30 | 460 | 459
2019-02-21 03:00 | 455 | 454
2019-02-21 03:30 | 445 | 444
2019-02-21 04:00 | 437 | 436
2019-02-21 04:30 | 434 | 432
2019-02-21 05:00 | 442 | 440
2019-02-21 05:30 | 445 | 443
2019-02-21 06:00 | 456 | 455
2019-02-21 06:30 | 464 | 463
2019-02-21 07:00 | 468 | 467
2019-02-21 07:30 | 444 | 442
2019-02-21 08:00 | 393 | 389
2019-02-21 08:30 | 358 | 351
2019-02-21 09:00 | 323 | 314
2019-02-21 09:30 | 285 | 272
2019-02-21 10:00 | 228 | 214
2019-02-21 10:30 | 239 | 224
2019-02-21 11:00 | 249 | 235
2019-02-21 11:30 | 269 | 257
2019-02-21 12:00 | 293 | 283
2019-02-21 12:30 | 304 | 295
2019-02-21 13:00 | 276 | 266
2019-02-21 13:30 | 271 | 261
2019-02-21 14:00 | 211 | 198
2019-02-21 14:30 | 219 | 201
2019-02-21 15:00 | 238 | 222
2019-02-21 15:30 | 258 | 243
2019-02-21 16:00 | 299 | 286
2019-02-21 16:30 | 297 | 283
2019-02-21 17:00 | 357 | 345
2019-02-21 17:30 | 419 | 411
2019-02-21 18:00 | 478 | 473
2019-02-21 18:30 | 518 | 516
2019-02-21 19:00 | 559 | 558
2019-02-21 19:30 | 574 | 574
2019-02-21 20:00 | 563 | 563
2019-02-21 20:30 | 544 | 543
2019-02-21 21:00 | 514 | 513
2019-02-21 21:30 | 584 | 583
2019-02-21 22:00 | 614 | 614
2019-02-21 22:30 | 678 | 678
2019-02-21 23:00 | 625 | 625
2019-02-21 23:30 | 579 | 578
2019-02-22 | 545 | 545
2019-02-22 00:30 | 506 | 505
2019-02-22 01:00 | 481 | 480
2019-02-22 01:30 | 465 | 464
2019-02-22 02:00 | 465 | 464
2019-02-22 02:30 | 459 | 458
2019-02-22 03:00 | 455 | 454
2019-02-22 03:30 | 442 | 441
2019-02-22 04:00 | 431 | 430
2019-02-22 04:30 | 427 | 425
2019-02-22 05:00 | 432 | 430
2019-02-22 05:30 | 449 | 448
2019-02-22 06:00 | 472 | 471
2019-02-22 06:30 | 491 | 490
2019-02-22 07:00 | 495 | 494
2019-02-22 07:30 | 475 | 474
2019-02-22 08:00 | 432 | 428
2019-02-22 08:30 | 408 | 401
2019-02-22 09:00 | 408 | 400
2019-02-22 09:30 | 426 | 419
2019-02-22 10:00 | 419 | 412
2019-02-22 10:30 | 382 | 376
2019-02-22 11:00 | 380 | 372
2019-02-22 11:30 | 415 | 407
2019-02-22 12:00 | 428 | 422
2019-02-22 12:30 | 432 | 426
2019-02-22 13:00 | 437 | 432
2019-02-22 13:30 | 436 | 431
2019-02-22 14:00 | 447 | 443
2019-02-22 14:30 | 454 | 450
2019-02-22 15:00 | 517 | 513
2019-02-22 15:30 | 455 | 452
2019-02-22 16:00 | 475 | 472
2019-02-22 16:30 | 512 | 509
2019-02-22 17:00 | 539 | 536
2019-02-22 17:30 | 574 | 572
2019-02-22 18:00 | 620 | 619
2019-02-22 18:30 | 613 | 613
2019-02-22 19:00 | 584 | 583
2019-02-22 19:30 | 610 | 610
2019-02-22 20:00 | 637 | 637
2019-02-22 20:30 | 625 | 625
2019-02-22 21:00 | 610 | 610
2019-02-22 21:30 | 572 | 572
2019-02-22 22:00 | 530 | 530
2019-02-22 22:30 | 553 | 553
2019-02-22 23:00 | 543 | 543
2019-02-22 23:30 | 513 | 512
2019-02-23 | 498 | 497
2019-02-23 00:30 | 493 | 492
2019-02-23 01:00 | 466 | 465
2019-02-23 01:30 | 456 | 455
2019-02-23 02:00 | 446 | 445
2019-02-23 02:30 | 436 | 435
2019-02-23 03:00 | 426 | 425
2019-02-23 03:30 | 418 | 417
2019-02-23 04:00 | 430 | 429
2019-02-23 04:30 | 440 | 438
2019-02-23 05:00 | 442 | 442
2019-02-23 05:30 | 440 | 439
2019-02-23 06:00 | 433 | 432
2019-02-23 06:30 | 440 | 439
2019-02-23 07:00 | 439 | 437
2019-02-23 07:30 | 412 | 409
2019-02-23 08:00 | 393 | 388
2019-02-23 08:30 | 398 | 391
2019-02-23 09:00 | 415 | 409
2019-02-23 09:30 | 409 | 403
2019-02-23 10:00 | 385 | 378
2019-02-23 10:30 | 384 | 377
2019-02-23 11:00 | 349 | 342
2019-02-23 11:30 | 381 | 373
2019-02-23 12:00 | 381 | 373
2019-02-23 12:30 | 352 | 345
2019-02-23 13:00 | 332 | 323
2019-02-23 13:30 | 361 | 354
2019-02-23 14:00 | 398 | 394
2019-02-23 14:30 | 441 | 437
2019-02-23 15:00 | 446 | 443
2019-02-23 15:30 | 489 | 487
2019-02-23 16:00 | 522 | 521
2019-02-23 16:30 | 511 | 509
2019-02-23 17:00 | 545 | 544
2019-02-23 17:30 | 563 | 562
2019-02-23 18:00 | 603 | 603
2019-02-23 18:30 | 594 | 594
2019-02-23 19:00 | 584 | 584
2019-02-23 19:30 | 555 | 555
2019-02-23 20:00 | 526 | 526
2019-02-23 20:30 | 523 | 523
2019-02-23 21:00 | 522 | 522
2019-02-23 21:30 | 496 | 495
2019-02-23 22:00 | 470 | 470
2019-02-23 22:30 | 435 | 434
2019-02-23 23:00 | 412 | 410
2019-02-23 23:30 | 396 | 395
2019-02-24 | 387 | 385
2019-02-24 00:30 | 390 | 387
2019-02-24 01:00 | 363 | 360
2019-02-24 01:30 | 369 | 366
2019-02-24 02:00 | 388 | 386
2019-02-24 02:30 | 388 | 386
2019-02-24 03:00 | 365 | 363
2019-02-24 03:30 | 366 | 363
2019-02-24 04:00 | 353 | 350
2019-02-24 04:30 | 354 | 351
2019-02-24 05:00 | 345 | 341
2019-02-24 05:30 | 350 | 347
2019-02-24 06:00 | 342 | 339
2019-02-24 06:30 | 345 | 342
2019-02-24 07:00 | 372 | 368
2019-02-24 07:30 | 380 | 375
2019-02-24 08:00 | 364 | 358
2019-02-24 08:30 | 379 | 371
2019-02-24 09:00 | 388 | 380
2019-02-24 09:30 | 355 | 347
2019-02-24 10:00 | 328 | 320
2019-02-24 10:30 | 294 | 282
2019-02-24 11:00 | 296 | 283
2019-02-24 11:30 | 285 | 272
2019-02-24 12:00 | 269 | 253
2019-02-24 12:30 | 279 | 267
2019-02-24 13:00 | 292 | 280
2019-02-24 13:30 | 285 | 271
2019-02-24 14:00 | 262 | 247
2019-02-24 14:30 | 299 | 287
2019-02-24 15:00 | 346 | 336
2019-02-24 15:30 | 377 | 368
2019-02-24 16:00 | 382 | 374
2019-02-24 16:30 | 397 | 390
2019-02-24 17:00 | 416 | 411
2019-02-24 17:30 | 428 | 422
2019-02-24 18:00 | 449 | 447
2019-02-24 18:30 | 475 | 473
2019-02-24 19:00 | 473 | 472
2019-02-24 19:30 | 470 | 470
2019-02-24 20:00 | 471 | 471
2019-02-24 20:30 | 439 | 438
2019-02-24 21:00 | 438 | 437
2019-02-24 21:30 | 427 | 427
2019-02-24 22:00 | 411 | 410
2019-02-24 22:30 | 398 | 396
2019-02-24 23:00 | 389 | 387
2019-02-24 23:30 | 375 | 373
2019-02-25 | 327 | 324
2019-02-25 00:30 | 339 | 335
2019-02-25 01:00 | 299 | 294
2019-02-25 01:30 | 281 | 275
2019-02-25 02:00 | 281 | 274
2019-02-25 02:30 | 254 | 246
2019-02-25 03:00 | 244 | 234
2019-02-25 03:30 | 262 | 252
2019-02-25 04:00 | 261 | 252
2019-02-25 04:30 | 295 | 287
2019-02-25 05:00 | 312 | 306
2019-02-25 05:30 | 331 | 326
2019-02-25 06:00 | 350 | 345
2019-02-25 06:30 | 347 | 344
2019-02-25 07:00 | 372 | 368
2019-02-25 07:30 | 386 | 381
2019-02-25 08:00 | 344 | 336
2019-02-25 08:30 | 346 | 335
2019-02-25 09:00 | 258 | 243
2019-02-25 09:30 | 243 | 224
2019-02-25 10:00 | 210 | 186
2019-02-25 10:30 | 218 | 195
2019-02-25 11:00 | 235 | 210
2019-02-25 11:30 | 226 | 199
2019-02-25 12:00 | 220 | 193
2019-02-25 12:30 | 216 | 188
2019-02-25 13:00 | 264 | 244
2019-02-25 13:30 | 298 | 282
2019-02-25 14:00 | 314 | 300
2019-02-25 14:30 | 308 | 293
2019-02-25 15:00 | 276 | 260
2019-02-25 15:30 | 357 | 344
2019-02-25 16:00 | 365 | 355
2019-02-25 16:30 | 298 | 287
2019-02-25 17:00 | 361 | 349
2019-02-25 17:30 | 390 | 381
2019-02-25 18:00 | 431 | 425
2019-02-25 18:30 | 457 | 454
2019-02-25 19:00 | 492 | 491
2019-02-25 19:30 | 493 | 493
2019-02-25 20:00 | 435 | 435
2019-02-25 20:30 | 406 | 406
2019-02-25 21:00 | 393 | 392
2019-02-25 21:30 | 410 | 408
2019-02-25 22:00 | 380 | 378
2019-02-25 22:30 | 355 | 353
2019-02-25 23:00 | 328 | 325
2019-02-25 23:30 | 310 | 306
2019-02-26 | 304 | 299
2019-02-26 00:30 | 312 | 306
2019-02-26 01:00 | 297 | 291
2019-02-26 01:30 | 274 | 266
2019-02-26 02:00 | 267 | 259
2019-02-26 02:30 | 257 | 248
2019-02-26 03:00 | 259 | 249
2019-02-26 03:30 | 261 | 251
2019-02-26 04:00 | 261 | 251
2019-02-26 04:30 | 260 | 250
2019-02-26 05:00 | 265 | 255
2019-02-26 05:30 | 278 | 269
2019-02-26 06:00 | 287 | 279
2019-02-26 06:30 | 300 | 292
2019-02-26 07:00 | 307 | 299
2019-02-26 07:30 | 290 | 280
2019-02-26 08:00 | 253 | 234
2019-02-26 08:30 | 210 | 183
2019-02-26 09:00 | 230 | 203
2019-02-26 09:30 | 243 | 216
2019-02-26 10:00 | 234 | 205
2019-02-26 10:30 | 257 | 232
2019-02-26 11:00 | 193 | 156
2019-02-26 11:30 | 166 | 125
2019-02-26 12:00 | 208 | 181
2019-02-26 12:30 | 189 | 156
2019-02-26 13:00 | 225 | 199
2019-02-26 13:30 | 231 | 207
2019-02-26 14:00 | 260 | 239
2019-02-26 14:30 | 264 | 244
2019-02-26 15:00 | 274 | 254
2019-02-26 15:30 | 279 | 259
2019-02-26 16:00 | 285 | 267
2019-02-26 16:30 | 327 | 312
2019-02-26 17:00 | 369 | 357
2019-02-26 17:30 | 371 | 361
2019-02-26 18:00 | 433 | 424
2019-02-26 18:30 | 438 | 433
2019-02-26 19:00 | 461 | 459
2019-02-26 19:30 | 470 | 470
2019-02-26 20:00 | 461 | 460
2019-02-26 20:30 | 449 | 448
2019-02-26 21:00 | 430 | 429
2019-02-26 21:30 | 420 | 419
2019-02-26 22:00 | 396 | 394
2019-02-26 22:30 | 364 | 362
2019-02-26 23:00 | 330 | 327
2019-02-26 23:30 | 309 | 304
2019-02-27 | 301 | 295
2019-02-27 00:30 | 312 | 306
2019-02-27 01:00 | 289 | 283
2019-02-27 01:30 | 276 | 268
2019-02-27 02:00 | 265 | 256
2019-02-27 02:30 | 260 | 250
2019-02-27 03:00 | 269 | 259
2019-02-27 03:30 | 272 | 263
2019-02-27 04:00 | 265 | 257
2019-02-27 04:30 | 277 | 268
2019-02-27 05:00 | 297 | 289
2019-02-27 05:30 | 302 | 295
2019-02-27 06:00 | 303 | 296
2019-02-27 06:30 | 319 | 312
2019-02-27 07:00 | 344 | 337
2019-02-27 07:30 | 308 | 299
2019-02-27 08:00 | 257 | 241
2019-02-27 08:30 | 215 | 195
2019-02-27 09:00 | 198 | 175
2019-02-27 09:30 | 186 | 157
2019-02-27 10:00 | 196 | 165
2019-02-27 10:30 | 203 | 173
2019-02-27 11:00 | 203 | 174
2019-02-27 11:30 | 239 | 215
2019-02-27 12:00 | 249 | 227
2019-02-27 12:30 | 275 | 256
2019-02-27 13:00 | 274 | 256
2019-02-27 13:30 | 342 | 328
2019-02-27 14:00 | 285 | 273
2019-02-27 14:30 | 258 | 242
2019-02-27 15:00 | 264 | 247
2019-02-27 15:30 | 281 | 265
2019-02-27 16:00 | 300 | 285
2019-02-27 16:30 | 374 | 364
2019-02-27 17:00 | 303 | 296
2019-02-27 17:30 | 372 | 365
2019-02-27 18:00 | 421 | 417
2019-02-27 18:30 | 476 | 474
2019-02-27 19:00 | 496 | 495
2019-02-27 19:30 | 505 | 505
2019-02-27 20:00 | 471 | 470
2019-02-27 20:30 | 471 | 470
2019-02-27 21:00 | 458 | 457
2019-02-27 21:30 | 447 | 446
2019-02-27 22:00 | 419 | 418
2019-02-27 22:30 | 373 | 372
2019-02-27 23:00 | 361 | 358
2019-02-27 23:30 | 320 | 317
2019-02-28 | 294 | 289
2019-02-28 00:30 | 318 | 312
2019-02-28 01:00 | 296 | 290
2019-02-28 01:30 | 269 | 263
2019-02-28 02:00 | 260 | 251
2019-02-28 02:30 | 250 | 241
2019-02-28 03:00 | 256 | 246
2019-02-28 03:30 | 261 | 251
2019-02-28 04:00 | 276 | 267
2019-02-28 04:30 | 278 | 270
2019-02-28 05:00 | 287 | 279
2019-02-28 05:30 | 301 | 293
2019-02-28 06:00 | 323 | 316
2019-02-28 06:30 | 364 | 358
2019-02-28 07:00 | 355 | 350
2019-02-28 07:30 | 350 | 342
2019-02-28 08:00 | 297 | 281
2019-02-28 08:30 | 276 | 254
2019-02-28 09:00 | 216 | 184
2019-02-28 09:30 | 222 | 187
2019-02-28 10:00 | 227 | 192
2019-02-28 10:30 | 261 | 230
2019-02-28 11:00 | 242 | 210
2019-02-28 11:30 | 201 | 165
2019-02-28 12:00 | 225 | 197
2019-02-28 12:30 | 187 | 149
2019-02-28 13:00 | 226 | 200
2019-02-28 13:30 | 245 | 216
2019-02-28 14:00 | 200 | 163
2019-02-28 14:30 | 219 | 191
2019-02-28 15:00 | 245 | 219
2019-02-28 15:30 | 187 | 148
2019-02-28 16:00 | 170 | 125
2019-02-28 16:30 | 171 | 127
2019-02-28 17:00 | 170 | 132
2019-02-28 17:30 | 236 | 212
2019-02-28 18:00 | 295 | 280
2019-02-28 18:30 | 375 | 366
2019-02-28 19:00 | 413 | 410
2019-02-28 19:30 | 402 | 401
2019-02-28 20:00 | 405 | 404
2019-02-28 20:30 | 400 | 399
2019-02-28 21:00 | 365 | 363
2019-02-28 21:30 | 346 | 343
2019-02-28 22:00 | 300 | 297
2019-02-28 22:30 | 385 | 381
2019-02-28 23:00 | 398 | 396
2019-02-28 23:30 | 371 | 370
2019-03-01 | 360 | 358

## 24. Historic ratings
|  | 2016 Winter | 2016/17 Summer | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer
PQ Rating (MVA) |  | 3569 | 3117 | 3569 | 3102 | 3578 | 3102
Feeders | 878 | 1242 | 1088 | 1242 | 1096 | 1252 | 1096
| 822 | 1085 | 941 | 1085 | 910 | 1074 | 910
| 8845 | 1242 | 1088 | 1242 | 1096 | 1252 | 1096

## 26. Unplanned outages
Unplanned Outage Date/Time | Element Affected | Element Type | Outage Cause | Outage Duration (mins) | Customer Outage Duration (mins) | MW Lost (Instantaneous) | MW Minutes
42372.1792 | H035 275KV 1 SVC | STATIC VAR COMPENSATOR | SVC Equipment malfunction or failure | 317.0333 | - | - | -
42404.0983 | 7208 - H035 Strathmore to T193 Clare South | FEEDER | Storm | 0.11667 | - | - | -
42406.0142 | 7360 - H035 Strathmore to T181 Bowen | FEEDER | Storm | 2.4167 | - | - | -
42594.0313 | 0879 - H035 Strathmore to H013 Ross | FEEDER | Fire | 116.8833 | - | - | -
42594.0313 | 8845 - H035 Strathmore to H011 Nebo | FEEDER | Fire | 116.8833 | - | - | -
42623.2563 | 0879 - H035 Strathmore to H013 Ross | FEEDER | Transient Feeder Fault of Unknown Origin | 287.0167 | - | - | -
42623.2563 | 8845 - H035 Strathmore to H011 Nebo | FEEDER | Transient Feeder Fault of Unknown Origin | 287.0167 | - | - | -
42635.3279 | H035 275KV 1 SVC | STATIC VAR COMPENSATOR | HV Maint | 1646.05 | - | - | -
42796.5654 | H035 275KV 1 SVC | STATIC VAR COMPENSATOR | HV Maint | 233.25 | - | - | -
42825.6221 | H035 275KV 1 SVC | STATIC VAR COMPENSATOR | HV Maint | 176.3333 | - | - | -
42825.9175 | 0879 - H035 Strathmore to H013 Ross | FEEDER | Transient Feeder Fault of Unknown Origin | 0.083333 | - | - | -
42905.6665 | H035 275KV 1 SVC | STATIC VAR COMPENSATOR | Human Error | 39.9667 | - | - | -
42910.5213 | H035 275KV 1 SVC | STATIC VAR COMPENSATOR | Sec Maint | 13.6 | - | - | -
42947.4623 | 7127 - T220 Collinsville North to H035 Strathmore | FEEDER | Secondary system malfunction or failure | 413.15 | 12 | 9 | 104.65
42947.4623 | 7208 - H035 Strathmore to T193 Clare South | FEEDER | Secondary system malfunction or failure | 32.3833 | - | - | -
42947.4623 | 7264 - H035 Strathmore to H035 Strathmore | FEEDER | Secondary system malfunction or failure | 32.3833 | - | - | -
42947.4623 | 7360 - H035 Strathmore to T181 Bowen | FEEDER | Secondary system malfunction or failure | 37.8333 | - | - | -
42947.4623 | H035 275KV 1 TRANSFORMER | TRANSFORMER | Secondary system malfunction or failure | 32.3833 | - | - | -
43041.5704 | 0879 - H035 Strathmore to H013 Ross | FEEDER | Storm | 0.083333 | - | - | -
43102.76 | 8857 - H013 Ross to H035 Strathmore | FEEDER | Storm | 0.083333 | - | - | -
43103.7234 | 0879 - H035 Strathmore to H091 Haughton River | FEEDER | Natural Hazard | 0.083333 | - | - | -
43151.9824 | 7360 - H035 Strathmore to T181 Bowen | FEEDER | Storm | 26.1667 | 8.38 | 7 | 58.68
43157.7107 | 0879 - H035 Strathmore to H091 Haughton River | FEEDER | Storm | 0.083333 | - | - | -
43164.8504 | 7127 - T220 Collinsville North to H035 Strathmore | FEEDER | Secondary system malfunction or failure | 17.6 | - | - | -
43204.9122 | 0879 - H035 Strathmore to H091 Haughton River | FEEDER | HV Equipment malfunction or failure | 0.083333 | - | - | -
43246.3993 | 7127 - T220 Collinsville North to H035 Strathmore | FEEDER | Process and Systems | 55.9333 | - | - | -
43246.3993 | 7208 - H035 Strathmore to T193 Clare South | FEEDER | Process and Systems | 55.6167 | - | - | -
43246.3993 | 7264 - H035 Strathmore to H035 Strathmore | FEEDER | Process and Systems | 55.6167 | - | - | -
43246.3993 | 7360 - H035 Strathmore to T181 Bowen | FEEDER | Process and Systems | 61.9833 | - | - | -
43246.3993 | H035 275KV 1 TRANSFORMER | TRANSFORMER | Process and Systems | 55.6167 | - | - | -
43267.3748 | 7360 - H035 Strathmore to T181 Bowen | FEEDER | Sec Maint | 200.4833 | - | - | -
43312.5682 | 0878 - H035 Strathmore to H011 Nebo | FEEDER | Accidental Contact with live equipment | 113.95 | - | - | -
43312.5682 | 8845 - H035 Strathmore to H011 Nebo | FEEDER | Accidental Contact with live equipment | 111.7 | - | - | -
43313.6514 | 7208 - H035 Strathmore to T193 Clare South | FEEDER | HV Maint | 205.95 | - | - | -
43326.5469 | 7360 - H035 Strathmore to T181 Bowen | FEEDER | HV Equipment malfunction or failure | 5.7333 | - | - | -
43334.3389 | 8845 - H035 Strathmore to H011 Nebo | FEEDER | HV Maint | 241.6667 | - | - | -